## Review Summary
Summary of Relaying Reviews -- 12-31-04 Reporting
This form shall be used without modification to provide a summary of relaying reviews performed by each Transmisission System Protection Owner (TPSO) as of December 31, 2004. Fill out this form in its entirety.
Transmission System Protection Owner Name
Regional Reliability Council Name
Reliability Coordinator Name
Certification Statements
Submittal Date
Contact Name
Title
Phone
Fax
E-mail
Review Summary
Number of line terminals reviewed
Number of line terminals not conforming to Rec. 8A
|  | Number of line terminals to be mitigated by 12-31-05 |  | *
|  | Number of line terminals requiring Temporary Exceptions |  | (not expected to be completed by 12-31-05)
Number of line terminals requesting Technical Exceptions
Mitigation Plans (Number of line terminals) |  |  | Planned for mitigation or already mitigated by 12-31-04 | Planned for mitigation in 2005
Setting Changes
Disable Function
Equipment Replacement / Addition
Other
|  | Total mitigations | 0 | 0 | 0 | *
* Should Agree

## Mitigation (opt)
Mitigation Reporting Form | [6 empty] | 12-31-04 Reporting
This optional Form can be used by the TPSOs and the Regions to track all circuits not meeting the NERC 8a parameters which will be mitigated by December 31, 2005.
Transmission System Owner Name
Regional Reliability Council Name
Reliability Coordinator Name
Submittal Date
|  | Unique Circuit Identifier (one or more as necessary) |  |  |  | Mitigation Dates |  | Mitigation Plan
Station Name | Nominal Voltage | Local Breaker ID(s) | Remote Terminal Name(s) | Circuit Name | Circuit Number | Planned | Actual | Setting Change | Disable Function | Equipment Replacement / Addition | Other | Region Recommendation

## Temporary Exceptions
Temporary Exception Reporting Form | [6 empty] | 12-31-04 Reporting
This Form shall be used to report all Temporary Exception Requests for NERC Recommendation 8a. All information requested in the table shall be provided for each Temporary Exception being requested.
Transmission System Owner Name
Regional Reliability Council Name
Reliability Coordinator Name
Submittal Date
|  | Unique Circuit Identifier (one or more as necessary) |  |  |  | Mitigation Dates |  | Mitigation Plan
Station Name | Nominal Voltage | Local Breaker ID(s) | Remote Terminal Name(s) | Circuit Name | Circuit Number | Planned | Actual | Setting Change | Disable Function | Equipment Replacement / Addition | Other | Justification for Temporary Exception | Region Recommendation

## Technical Exceptions
Technical Exception Reporting Form | [5 empty] | 12-31-04 Reporting
This Form shall be used to report all Technical Exception Requests for NERC Recommendation 8a. All information requested in the table shall be provided for each Technical Exception being requested.
Note: Complete Supplemental Information Sheet for Exceptions 7-8. For Exceptions 9 through 12, submit system maps (physical, switching, and relaying, as appropriate), and sufficient system studies and working papers to facilitate adequate and timely review of the request by the SPCTF. If necessary, the SPCTF will request additional supporting information. All submissions should be in electronic format.
Transmission System Owner Name
Regional Reliability Council Name
Reliability Coordinator Name
Submittal Date
Unique Circuit Identifier (one or more as necessary)
Station Name | Nominal Voltage | Local Breaker ID(s) | Remote Terminal Name(s) | Circuit Name | Circuit Number | Line Length in Miles | Line Impedance in Ohms (Z) | Exception Number | Region Recommendation

## Supp Info for Excep 7 & 8
Technical Exception 7 and 8 Supplemental Data Reporting Form | [6 empty] | 12-31-04 Reporting
Complete all information in this tabel for each Exception 7 or Exception 8 being requested.
Transmission System Owner Name
Regional Reliability Council Name
Reliability Coordinator Name
Submittal Date
|  | Unique Circuit Identifier (one or more as necessary) |  |  |  | Respond Yes or No
Station Name | Nominal Voltage | Local Breaker ID(s) | Remote Terminal Name(s) | Circuit Name | Circuit Number | Relay Reach < 125%? | MTA Closest to 90-deg | Iemergency Used in all Studies | No Contingencies > Iemergency | Reliability Coordinator Commitment to Action for Current > Iemergency

## Exception 2 Job Aid
Exception Calculation - Exception 2 - Alternate Rating Based Transmission Line Parameters Only
Instructions: Provide the Relevant Information for the Yellow-Shaded Boxes
Transmission Owner:
Line Name:
Line kV | 345 | kV Phase-to-phase
Input Quantities (primary Ohms/Mhos):
Line Parameters |  | Resistance | 3.594 | Ohms | Reactance |  | 56.68 | Ohms
|  |  |  | Line Susceptance (B/2): |  |  | 0.00029 | Mhos
Calculated Quantities:
Impedance Magnitude (ZL+Zs+Zr): |  |  | 56.7938 | Ohms
Impedance Angle: |  |  | 86.3718 | Degrees | 1.5075 | radians
Power Transfer Angle: |  |  | 90 | Degrees | 1.5708 | radians
Equivalent Voltage: |  |  | 1 | per-unit | 345 | kV
Complex Power Flow Quantities
Sending End Real Power Flow: |  |  | 2224.1592 | MW
Sending End Reactive Power Flow: |  |  | 1924.399 | MVAR
Sending End Complex Power Flow: |  |  | 2941.1215 | MVA
Sending End Current Flow: |  |  | 4921.9052 | Amperes
Note: The use of the complex power equations is optional, and may result in a lower maximum power transfer level. The equations, as listed in the "Relay Loadability Exceptions" document can be used directly if it provides the TPSO the necessary relief

## Exception 3 Job Aid
Exception Calculation - Exception 3 - Alternate Rating Based on Breaker Ratings
Instructions: Provide the Relevant Information for the Yellow-Shaded Boxes
Transmission Owner:
Line Name:
Line kV | 345 | kV Phase-to-phase
Input Quantities (primary Ohms/Mhos):
Line Parameters |  | Resistance |  | 3.594 | Ohms | Reactance |  | 56.68 | Ohms
[5 empty] | Line Susceptance (B/2): |  |  | 0.00029 | Mhos
Source Impedances from Breaker Ratings:
Sending End Breaker Rating |  |  | 40000 | Amps |  | 4.9796 | Ohms Reactance
Receiving End Breaker Rating |  |  | 63000 | Amps |  | 3.1617 | Ohms Reactance
Calculated Quantities:
Impedance Magnitude (ZL+Zs+Zr): |  |  |  | 64.9209 | Ohms
Impedance Angle: |  |  |  | 86.8265 | Degrees | 1.5154 | radians
Power Transfer Angle: |  |  |  | 90 | Degrees | 1.5708 | radians
Equivalent Voltage: |  |  |  | 1.05 | per-unit | 362.25 | kV
Complex Power Flow Quantities
Sending End Real Power Flow: |  |  |  | 2130.1066 | MW
Sending End Reactive Power Flow: |  |  |  | 1868.2535 | MVAR
Sending End Complex Power Flow: |  |  |  | 2833.3241 | MVA
Sending End Current Flow: |  |  |  | 4741.5084 | Amperes
Note: The use of the complex power equations is optional, and may result in a lower maximum power transfer level. The equations, as listed in the "Relay Loadability Exceptions" document can be used directly.

## Exception 4 Job Aid
Exception Calculation - Exception 4 - Alternate Rating Based on Actual Source Impedances
Instructions: Provide the Relevant Information for the Yellow-Shaded Boxes
Transmission Owner:
Line Name:
Line kV | 345 | kV Phase-to-phase
Input Quantities (primary Ohms/Mhos):
Line Parameters |  | Resistance | 3.594 | Ohms | Reactance |  | 56.68 | Ohms
|  |  |  | Line Susceptance (B/2): |  |  | 0.00029 | Mhos
Source Impedances:
Sending End |  | Resistance | 2.142 | Ohms | Reactance |  | 5.082 | Ohms
Receiving End |  | Resistance | 0.821 | Ohms | Reactance |  | 11.355 | Ohms
Calculated Quantities:
Impedance Magnitude (ZL+Zs+Zr): |  |  | 73.4104 | Ohms
Impedance Angle: |  |  | 85.904 | Degrees | 1.4993 | radians
Power Transfer Angle: |  |  | 90 | Degrees | 1.5708 | radians
Equivalent Voltage: |  |  | 1.05 | per-unit | 362.25 | kV
Complex Power Flow Quantities
Sending End Real Power Flow: |  |  | 1910.6697 | MW
Sending End Reactive Power Flow: |  |  | 1617.2505 | MVAR
Sending End Complex Power Flow: |  |  | 2503.2295 | MVA
Sending End Current Flow: |  |  | 4189.102 | Amperes
Note: The use of the complex power equations is optional, and may result in a lower maximum power transfer level. The equations, as listed in the "Relay Loadability Exceptions" document can be used directly.

## Exception 6 Job Aid
Exception Calculation - Exception 6 - Alternate Rating Based on Line-End Fault Magnitude
Instructions: Provide the Relevant Information for the Yellow-Shaded Boxes
Transmission Owner:
Line Name:
Line kV | 345 | kV Phase-to-phase
Input Quantities (primary Amperes):
Line-End Three Phase Fault Magnitude |  |  | 2500 | Amperes
Calculated Quantities:
Imax Per Exception 6 |  |  | 3712.3106 | Amperes

## Exception 7 Job Aid
Exception Calculation - Exception 7 - Alternate Rating Based on Long Line Protection
Instructions: Provide the Relevant Information for the Yellow-Shaded Boxes
Transmission Owner:
Line Name:
Line kV | 345 | kV Phase-to-phase
Input Quantities (primary Ohms/Mhos):
Line Parameters |  | Resistance |  | 3.594 | Ohms | Reactance |  | 56.68 | Ohms
Line Impedance: |  |  |  | 56.7938 | Ohms | Line Angle: |  | 86.3718 | Degrees
Sending End Relay Information and Settings (Mho Relay Only)
Relay Manufacturer: |  |  |  |  | Relay Model:
Primary Setting |  | 70 | Ohms | Max Torque Angle |  | 75 | degrees | 1.309 | radians
Maximum Sanctioned Relay Max Torque Angle: | [5 empty] | 75 | degrees
Calculated Quantities:
Maximum Relay Reach (125% of ZL) | [7 empty] | 72.4139 | Ohms
Iemergency Per Exception 7 Calculation - 125% of Line | [7 empty] | 2875.2303 | Amperes

## Exception 8 Job Aid
Exception Calculation - Exception 8 - Alternate Rating Based on Multiterminal Line Protection
Instructions: Provide the Relevant Information for the Yellow-Shaded Boxes
Transmission Owner:
Line Name:
Line kV | 345 | kV Phase-to-phase
Input Quantities (primary Ohms/Mhos):
Line Parameters (Calculated Apparent Line Impedance)
|  | Resistance |  | 3.594 | Ohms | Reactance |  | 56.68 | Ohms
Apparent Line Impedance: |  |  |  | 56.7938 | Ohms | Line Angle: |  | 86.3718 | Degrees
Sending End Relay Information and Settings (Mho Relay Only)
Relay Manufacturer: |  |  |  |  | Relay Model:
Primary Setting |  | 70 | Ohms | Max Torque Angle |  | 75 | degrees | 1.309 | radians
Maximum Sanctioned Relay Max Torque Angle: | [5 empty] | 75 | degrees
Calculated Quantities:
Maximum Relay Reach (125% of ZApparent) | [7 empty] | 72.4139 | Ohms
Iemergency Per Exception 7 Calculation - 125% of Apparent Impedance | [7 empty] | 2875.2303 | Amperes