## 2020-3
Generator Catagory/Classification | Start | End | # Units | Unit-Years | NMC | NDC | Attempts | Actual | SH | RSH | # RSH | Pump Hr | SCH | AH | FOH | # FOH | POH | # POH | SEPO | # SEPO | MOH | # MOH | SEMO | # SEMO | UAH | PH | EFDH | ESDH | EFDHRS | EDOH | POF | MOF | ART | SR | NCF | NOF | SF | AF | EAF | FOR | EFOR | EFORd | SOF | FOF | UOF | EUOF | EUOR | WSF | WAF | WEAF | WFOR | WEFOR | WSOF | WFOF
FOSSIL All Fuel Types All Sizes | 2016 | 2020 | 1189 | 4966.58 | 326 | 325 | 29.19 | 28.87 | 4204.57 | 2442.31 | 13.84 | 0 | 0 | 6646.88 | 427.08 | 5.35 | 682.89 | 1.33 | 37.27 | 0.13 | 310.05 | 2.5 | 6.2 | 0.05 | 1463.48 | 8110.36 | 144.01 | 50.94 | 36.92 | 194.95 | 8.88 | 3.9 | 145.64 | 98.9 | 40.64 | 69.91 | 51.84 | 81.96 | 79.14 | 9.22 | 12.23 | 9.36 | 12.78 | 5.27 | 9.17 | 11.19 | 18.18 | 58.14 | 81.01 | 78.33 | 8.34 | 11.18 | 13.7 | 5.29
FOSSIL All Fuel Types 001-099 | 2016 | 2020 | 252 | 1040 | 52 | 51 | 32.53 | 32.35 | 3475.31 | 3094.25 | 16.89 | 0 | 0 | 6569.56 | 417.01 | 4.37 | 478.51 | 1.15 | 34.32 | 0.08 | 290.81 | 1.66 | 1.98 | 0.01 | 1222.63 | 7792.19 | 129.19 | 57.79 | 38.54 | 186.98 | 6.58 | 3.76 | 107.43 | 99.45 | 29.75 | 64.64 | 44.6 | 84.31 | 81.08 | 10.71 | 13.9 | 9.49 | 10.34 | 5.35 | 9.11 | 11.07 | 20.4 | 46.02 | 84.4 | 81.3 | 10.15 | 13.36 | 10.41 | 5.2
FOSSIL All Fuel Types 100-199 | 2016 | 2020 | 272 | 1066.83 | 137 | 136 | 61.85 | 61.58 | 3036.9 | 3233.17 | 16.49 | 0 | 0 | 6270.07 | 374.82 | 4.03 | 636.75 | 1.25 | 29.74 | 0.1 | 285.89 | 2.08 | 4.68 | 0.03 | 1331.89 | 7601.95 | 120.44 | 59.03 | 52.24 | 179.47 | 8.77 | 3.82 | 49.32 | 99.56 | 24.97 | 60.12 | 39.95 | 82.48 | 79.61 | 10.99 | 14.3 | 8.64 | 12.59 | 4.93 | 8.75 | 10.55 | 21.29 | 41.54 | 82.3 | 79.35 | 10.79 | 14.06 | 12.68 | 5.02
FOSSIL All Fuel Types 200-299 | 2016 | 2020 | 136 | 543 | 230 | 229 | 16.69 | 16.27 | 4433.96 | 2164.74 | 14.04 | 0 | 0 | 6598.7 | 394.28 | 5.48 | 650.82 | 1.29 | 19.79 | 0.12 | 316.65 | 3.19 | 8.85 | 0.08 | 1390.4 | 7989.11 | 130.74 | 39.34 | 36.64 | 170.07 | 8.39 | 4.07 | 272.52 | 97.48 | 36.62 | 66.33 | 55.5 | 82.6 | 80.14 | 8.17 | 10.79 | 8.9 | 12.47 | 4.94 | 9.01 | 10.88 | 16.72 | 55.21 | 82.89 | 80.47 | 8.04 | 10.62 | 12.28 | 4.83
FOSSIL All Fuel Types 300-399 | 2016 | 2020 | 111 | 475.25 | 336 | 335 | 20.55 | 20.16 | 4126.1 | 2755.15 | 17.96 | 0 | 0 | 6881.25 | 402.54 | 5.98 | 854.27 | 1.62 | 56.17 | 0.17 | 302.88 | 3.05 | 13.12 | 0.07 | 1628.98 | 8510.23 | 159.13 | 44.83 | 33.74 | 203.96 | 10.7 | 3.71 | 204.67 | 98.1 | 29.96 | 62.52 | 48.48 | 80.86 | 78.3 | 8.89 | 12.31 | 9.55 | 14.41 | 4.73 | 8.44 | 10.5 | 18.28 | 47.91 | 80.81 | 78.32 | 8.91 | 12.31 | 14.5 | 4.69
FOSSIL All Fuel Types 400-599 | 2016 | 2020 | 198 | 883 | 482 | 480 | 15.38 | 15 | 5041.99 | 1751.04 | 10.41 | 0 | 0 | 6793.03 | 550.47 | 7.06 | 767.41 | 1.45 | 49.15 | 0.17 | 328.1 | 2.89 | 5.76 | 0.08 | 1700.89 | 8493.92 | 176.74 | 46.2 | 30.97 | 222.94 | 9.61 | 3.93 | 336.13 | 97.53 | 40.97 | 68.77 | 59.36 | 79.98 | 77.1 | 9.84 | 12.93 | 11.13 | 13.54 | 6.48 | 10.41 | 12.71 | 18.1 | 59.57 | 80.1 | 77.25 | 9.74 | 12.79 | 13.47 | 6.43
FOSSIL All Fuel Types 600-799 | 2016 | 2020 | 145 | 622.5 | 662 | 659 | 11.31 | 10.93 | 5472.59 | 1428.26 | 6.33 | 0 | 0 | 6900.85 | 414.36 | 6.28 | 792.21 | 1.35 | 36.91 | 0.14 | 315.36 | 2.82 | 9.13 | 0.06 | 1567.98 | 8468.83 | 165.52 | 43.4 | 27.9 | 208.92 | 9.79 | 3.83 | 500.69 | 96.64 | 48.62 | 75.09 | 64.62 | 81.49 | 78.75 | 7.04 | 9.8 | 8.76 | 13.62 | 4.89 | 8.72 | 10.91 | 14.8 | 64.75 | 81.4 | 78.68 | 7.06 | 9.81 | 13.68 | 4.92
FOSSIL All Fuel Types 800-999 | 2016 | 2020 | 59 | 276 | 827 | 827 | 18.54 | 18.17 | 5418.66 | 1665.35 | 14.33 | 0 | 0 | 7084 | 388.5 | 5.38 | 788.29 | 1.33 | 48.34 | 0.23 | 329.59 | 2.83 | 6.87 | 0.07 | 1561.59 | 8645.6 | 138.43 | 44.94 | 22.16 | 183.37 | 9.68 | 3.89 | 298.22 | 98 | 44.85 | 71.09 | 62.68 | 81.94 | 79.79 | 6.69 | 9.04 | 7.78 | 13.57 | 4.49 | 8.39 | 10.38 | 14.53 | 63.09 | 82.05 | 79.91 | 6.58 | 8.91 | 13.5 | 4.44
FOSSIL All Fuel Types 1000 Plus | 2016 | 2020 | 16 | 55 | 1234 | 1231 | 9.53 | 9.16 | 5489.23 | 919.86 | 4.69 | 0 | 0 | 6409.09 | 529.62 | 5.15 | 1122.74 | 1.35 | 9.43 | 0.05 | 698.28 | 3.76 | 0 | 0 | 2360.07 | 8769.16 | 148.1 | 125.73 | 12.04 | 273.83 | 12.91 | 7.96 | 599.26 | 96.12 | 47.38 | 74.31 | 62.6 | 73.09 | 69.72 | 8.8 | 11.24 | 10.3 | 20.87 | 6.04 | 14 | 16.15 | 21.01 | 63.76 | 73.24 | 70 | 8.82 | 11.19 | 20.59 | 6.17
FOSSIL Coal Primary All Sizes | 2016 | 2020 | 727 | 2878.08 | 394 | 392 | 20.96 | 20.65 | 5110.35 | 1507.34 | 6.33 | 0 | 0 | 6617.69 | 423.07 | 5.93 | 654.52 | 1.15 | 35.77 | 0.13 | 304.02 | 2.66 | 7.07 | 0.07 | 1424.45 | 8042.14 | 139.84 | 59.04 | 20.62 | 198.88 | 8.58 | 3.87 | 247.47 | 98.52 | 49.73 | 73.04 | 63.54 | 82.29 | 79.47 | 7.65 | 10.14 | 8.71 | 12.45 | 5.26 | 9.13 | 11.14 | 15.26 | 68.09 | 81.39 | 78.69 | 7.31 | 9.71 | 13.24 | 5.37
FOSSIL Coal Primary 001-099 | 2016 | 2020 | 101 | 333.08 | 56 | 56 | 14.03 | 13.82 | 3517.4 | 3078.9 | 11.55 | 0 | 0 | 6596.3 | 301.85 | 4.67 | 488.58 | 1.11 | 26.99 | 0.08 | 181.73 | 1.43 | 1.07 | 0.02 | 1000.21 | 7596.51 | 93.73 | 72.74 | 37.42 | 166.48 | 6.79 | 2.41 | 254.52 | 98.5 | 35.75 | 72.94 | 46.3 | 86.83 | 84.14 | 7.9 | 10.26 | 8.02 | 9.19 | 3.97 | 6.38 | 8 | 14.98 | 49.02 | 87.45 | 84.77 | 7.08 | 9.4 | 8.81 | 3.73
FOSSIL Coal Primary 100-199 | 2016 | 2020 | 160 | 541 | 143 | 142 | 60.85 | 60.63 | 3788.43 | 1952.58 | 6.18 | 0 | 0 | 5741.01 | 360.23 | 4.19 | 497.71 | 0.93 | 23.57 | 0.09 | 278.84 | 2 | 5.97 | 0.04 | 1166.31 | 6907.32 | 119.41 | 82.44 | 35.49 | 201.85 | 7.55 | 4.12 | 62.48 | 99.64 | 36.34 | 66.06 | 54.85 | 83.11 | 79.65 | 8.68 | 11.46 | 8.42 | 11.67 | 5.22 | 9.34 | 11.29 | 17.43 | 55.01 | 82.94 | 79.5 | 8.92 | 11.81 | 11.67 | 5.39
FOSSIL Coal Primary 200-299 | 2016 | 2020 | 90 | 357.5 | 229 | 227 | 11.13 | 10.75 | 4938.32 | 1536.62 | 6.9 | 0 | 0 | 6474.95 | 429.87 | 5.89 | 590.03 | 1.16 | 18.03 | 0.13 | 347.66 | 3.49 | 13.43 | 0.12 | 1399.01 | 7873.96 | 108.99 | 46.19 | 12.47 | 155.18 | 7.72 | 4.59 | 459.38 | 96.59 | 43.95 | 70.9 | 62.72 | 82.23 | 79.8 | 8.01 | 10.01 | 8.87 | 12.31 | 5.46 | 10.05 | 11.64 | 15.96 | 62 | 82.7 | 80.25 | 7.98 | 9.99 | 11.93 | 5.37
FOSSIL Coal Primary 300-399 | 2016 | 2020 | 65 | 271 | 328 | 327 | 13.49 | 13.1 | 5230.31 | 1682.98 | 7.89 | 0 | 0 | 6913.29 | 457.65 | 7.02 | 744.14 | 1.11 | 60.52 | 0.18 | 355.07 | 3.24 | 10.79 | 0.09 | 1628.17 | 8541.46 | 201.15 | 62.42 | 23.68 | 263.56 | 9.42 | 4.28 | 399.26 | 97.11 | 42.24 | 69.07 | 61.23 | 80.94 | 77.7 | 8.05 | 11.53 | 10.02 | 13.7 | 5.36 | 9.64 | 12.25 | 17.18 | 61.16 | 81.01 | 77.81 | 8.02 | 11.5 | 13.66 | 5.33
FOSSIL Coal Primary 400-599 | 2016 | 2020 | 137 | 605.42 | 485 | 484 | 11.92 | 11.58 | 6042.32 | 864.79 | 5.01 | 0 | 0 | 6907.11 | 521.51 | 7.39 | 724.89 | 1.25 | 52.14 | 0.17 | 292.32 | 2.8 | 7.53 | 0.09 | 1598.39 | 8505.51 | 173.04 | 43.79 | 14.53 | 216.83 | 9.14 | 3.53 | 521.79 | 97.15 | 51.14 | 71.84 | 71.04 | 81.21 | 78.36 | 7.95 | 10.56 | 9.79 | 12.66 | 6.13 | 9.66 | 11.93 | 14.75 | 71.19 | 81.27 | 78.45 | 7.87 | 10.46 | 12.65 | 6.08
FOSSIL Coal Primary 600-799 | 2016 | 2020 | 118 | 516.17 | 662 | 660 | 10.6 | 10.26 | 6100.38 | 932.35 | 4.53 | 0 | 0 | 7032.73 | 402.37 | 6.4 | 730.7 | 1.21 | 31.3 | 0.13 | 312.39 | 2.89 | 5.95 | 0.06 | 1482.72 | 8515.45 | 144.42 | 48.11 | 6.81 | 192.53 | 8.95 | 3.74 | 594.58 | 96.79 | 54.66 | 76.25 | 71.64 | 82.59 | 80.03 | 6.19 | 8.4 | 7.78 | 12.69 | 4.73 | 8.46 | 10.41 | 12.99 | 71.68 | 82.55 | 79.98 | 6.2 | 8.41 | 12.71 | 4.73
FOSSIL Coal Primary 800-999 | 2016 | 2020 | 42 | 197.92 | 835 | 834 | 9.44 | 9.03 | 6061.13 | 918.97 | 3.77 | 0 | 0 | 6980.09 | 455.9 | 5.84 | 811.47 | 1.37 | 51.19 | 0.23 | 351 | 2.91 | 7.08 | 0.06 | 1676.63 | 8656.73 | 136.32 | 51.11 | 21.8 | 187.43 | 9.97 | 4.14 | 671.22 | 95.66 | 50.92 | 72.58 | 70.02 | 80.63 | 78.44 | 7 | 9.06 | 8.42 | 14.1 | 5.27 | 9.4 | 11.42 | 14.33 | 70.16 | 80.86 | 78.69 | 6.85 | 8.89 | 13.98 | 5.16
FOSSIL Coal Primary 1000 Plus | 2016 | 2020 | 14 | 51 | 1255 | 1251 | 9.76 | 9.39 | 5767.2 | 625.6 | 4.41 | 0 | 0 | 6392.8 | 569.62 | 5.43 | 1124.73 | 1.39 | 10.17 | 0.06 | 671.61 | 3.88 | 0 | 0 | 2376.14 | 8768.94 | 128.29 | 119.58 | 0.85 | 247.87 | 12.94 | 7.66 | 614.19 | 96.21 | 49.76 | 75.05 | 65.77 | 72.9 | 69.82 | 8.99 | 11.01 | 10.33 | 20.6 | 6.5 | 14.15 | 16.01 | 20.03 | 66.3 | 73.11 | 70.09 | 8.96 | 11.01 | 20.36 | 6.53
FOSSIL Oil Primary All Sizes | 2016 | 2020 | 73 | 238.17 | 292 | 292 | 21.33 | 21.14 | 1903.55 | 4589.88 | 19.14 | 0 | 0 | 6493.43 | 368.02 | 2.55 | 614.57 | 1.02 | 18.1 | 0.08 | 427.89 | 1.79 | 7.85 | 0.04 | 1436.43 | 7929.86 | 158.32 | 19.77 | 62.28 | 178.1 | 7.98 | 5.49 | 90.04 | 99.11 | 5.74 | 42.74 | 24 | 81.89 | 79.57 | 16.2 | 22.55 | 11.2 | 13.47 | 4.64 | 10.14 | 12.29 | 35.14 | 13.44 | 82.14 | 80.48 | 15.07 | 22.06 | 15.48 | 2.39
FOSSIL Oil Primary 001-099 | 2016 | 2020 | 16 | 76.75 | 65 | 65 | 48.35 | 48.21 | 3626.52 | 2045.57 | 34.48 | 0 | 0 | 5672.09 | 516.09 | 3.02 | 279.68 | 0.23 | 0 | 0 | 645.19 | 1.77 | 0 | 0 | 1440.96 | 7113.06 | 327.87 | 28.69 | 106.54 | 356.56 | 3.93 | 9.07 | 75.22 | 99.71 | 28.98 | 48.42 | 50.98 | 79.74 | 74.73 | 12.46 | 19.86 | 14.2 | 13 | 7.26 | 16.33 | 21.34 | 31.01 | 59.85 | 80.38 | 74.99 | 8.27 | 15.45 | 14.23 | 5.4
FOSSIL Oil Primary 100-199 | 2016 | 2020 | 17 | 47.75 | 123 | 123 | 6.39 | 6.16 | 1541.2 | 5179.09 | 8.21 | 0 | 0 | 6720.3 | 548.74 | 1.82 | 536.76 | 0.8 | 2.16 | 0.02 | 352.96 | 1.59 | 0 | 0 | 1440.62 | 8160.92 | 115.37 | 9.01 | 43.79 | 124.38 | 6.6 | 4.33 | 250.19 | 96.4 | 13 | 59.73 | 18.89 | 82.35 | 80.82 | 26.26 | 31.12 | 17.38 | 10.93 | 6.72 | 11.05 | 12.53 | 41.04 | 21.76 | 82.25 | 80.61 | 22.08 | 27.03 | 11.59 | 6.17
FOSSIL Oil Primary 200-299 | 2016 | 2020 | **** | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [10 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: POF to FOR
FOSSIL Oil Primary 300-399 | 2016 | 2020 | 11 | 43 | 367 | 367 | 8.56 | 8.44 | 1792.65 | 4547.39 | 12.47 | 0 | 0 | 6340.04 | 283.09 | 2.56 | 886.55 | 1.81 | 27.17 | 0.09 | 213.34 | 1.58 | 0.13 | 0.02 | 1410.29 | 7750.33 | 22.31 | 15.38 | 5.91 | 37.69 | 11.79 | 2.75 | 212.4 | 98.6 | 8.35 | 35.28 | 23.13 | 81.8 | 81.32 | 13.64 | 14.67 | 10.25 | 14.54 | 3.65 | 6.41 | 6.71 | 22.66 | 23.67 | 82.04 | 81.54 | 12.62 | 13.65 | 14.54 | 3.42
FOSSIL Oil Primary 400-599 | 2016 | 2020 | 10 | 29.17 | 453 | 452 | 8.26 | 8.16 | 163.3 | 7394.65 | 12.62 | 0 | 0 | 7557.95 | 242.75 | 2.74 | 743.65 | 1.61 | 44.07 | 0.1 | 182.44 | 1.99 | 0 | 0 | 1212.92 | 8770.87 | 49.05 | 12.54 | 31.47 | 61.59 | 8.98 | 2.08 | 20.01 | 98.79 | 0.51 | 28.29 | 1.86 | 86.17 | 85.22 | 59.78 | 66.69 | 23.32 | 11.06 | 2.77 | 4.85 | 5.42 | 76.41 | 1.8 | 86.17 | 85.24 | 60.63 | 67.28 | 11.07 | 2.77
FOSSIL Oil Primary 600-799 | 2016 | 2020 | 9 | 24.33 | 627 | 625 | 15.41 | 15.21 | 425.92 | 6943.15 | 20.05 | 0 | 0 | 7369.07 | 91.67 | 2.92 | 730.98 | 1.56 | 23.39 | 0.21 | 487.26 | 2.14 | 65.89 | 0.21 | 1399.19 | 8768.26 | 84.99 | 9.6 | 74.82 | 94.59 | 8.6 | 6.31 | 28 | 98.7 | 1.88 | 40.01 | 4.86 | 84.04 | 82.74 | 17.71 | 29.82 | 10.55 | 14.91 | 1.05 | 7.35 | 8.35 | 63.65 | 4.7 | 83 | 81.6 | 17.77 | 31.35 | 15.98 | 1.02
FOSSIL Oil Primary 800-999 | 2016 | 2020 | 7 | 12.92 | 814 | 812 | 3.79 | 3.25 | 108.91 | 6809.84 | 6.89 | 0 | 0 | 6918.75 | 17.33 | 1.39 | 1338.28 | 1.55 | 91.8 | 0.54 | 385.61 | 1.94 | 20.23 | 0.23 | 1853.25 | 8772 | 75.35 | 0 | 73.86 | 75.35 | 16.3 | 4.63 | 33.51 | 85.75 | 0.51 | 41.41 | 1.24 | 78.87 | 77.81 | 13.73 | 46.32 | 11.39 | 20.93 | 0.2 | 4.82 | 5.68 | 82.27 | 1.22 | 79.01 | 77.94 | 13.73 | 46.78 | 20.8 | 0.19
FOSSIL Gas Primary All Sizes | 2016 | 2020 | 370 | 1440.08 | 233 | 232 | 38.37 | 38.01 | 2187.74 | 4337.06 | 27.54 | 0 | 0 | 6524.8 | 451.87 | 4.29 | 788.64 | 1.66 | 44.1 | 0.12 | 345.71 | 2.48 | 5.07 | 0.04 | 1635.39 | 8160.19 | 131.72 | 26.6 | 73.11 | 158.32 | 10.2 | 4.3 | 57.56 | 99.06 | 12.84 | 44.19 | 26.81 | 79.96 | 77.65 | 17.12 | 21.51 | 11.41 | 14.5 | 5.54 | 9.84 | 11.6 | 30.77 | 29.07 | 78.06 | 75.53 | 16.71 | 21.51 | 16.11 | 5.83
FOSSIL Gas Primary 001-099 | 2016 | 2020 | 99 | 374.08 | 52 | 52 | 32.22 | 32.04 | 1589.29 | 4555.17 | 17.37 | 0 | 0 | 6144.46 | 528.19 | 2.68 | 458.51 | 1.04 | 45.33 | 0.07 | 390.62 | 1.55 | 1.29 | 0.01 | 1423.93 | 7568.39 | 71.69 | 2.49 | 44.61 | 74.18 | 6.66 | 5.18 | 49.6 | 99.44 | 12.64 | 49.11 | 21 | 81.19 | 79.45 | 24.94 | 27.75 | 12.14 | 11.84 | 6.98 | 12.16 | 13.13 | 38.9 | 25.74 | 80.99 | 79.12 | 22.13 | 24.73 | 11.69 | 7.32
FOSSIL Gas Primary 100-199 | 2016 | 2020 | 113 | 454.75 | 130 | 130 | 53.33 | 52.99 | 2152.36 | 4650.68 | 30.03 | 0 | 0 | 6803.04 | 344.8 | 4.08 | 821.77 | 1.68 | 41.02 | 0.12 | 295.02 | 2.22 | 3.87 | 0.03 | 1506.49 | 8309.53 | 124.78 | 34.01 | 75.72 | 158.79 | 10.38 | 3.6 | 40.62 | 99.36 | 12.19 | 45.31 | 25.9 | 81.87 | 79.52 | 13.81 | 18.25 | 8.92 | 13.98 | 4.15 | 7.75 | 9.46 | 27.18 | 26.89 | 81.59 | 79.07 | 13.49 | 17.76 | 14.22 | 4.2
FOSSIL Gas Primary 200-299 | 2016 | 2020 | 42 | 159.25 | 232 | 232 | 27.79 | 27.45 | 2952.39 | 3763.65 | 29.27 | 0 | 0 | 6716.04 | 294.67 | 4.05 | 805.25 | 1.58 | 21.85 | 0.09 | 280.95 | 2.76 | 0 | 0 | 1402.72 | 8118.76 | 173.28 | 24.19 | 94.91 | 197.47 | 10.19 | 3.46 | 107.56 | 98.78 | 17.63 | 47.41 | 36.37 | 82.72 | 80.27 | 9.07 | 14 | 8.89 | 13.65 | 3.63 | 7.09 | 9.51 | 21.22 | 37.2 | 82.7 | 80.37 | 8.54 | 13.18 | 13.83 | 3.47
FOSSIL Gas Primary 300-399 | 2016 | 2020 | 38 | 147.75 | 345 | 344 | 33.92 | 33.43 | 2475.32 | 4399.47 | 35.47 | 0 | 0 | 6874.79 | 367.61 | 5.18 | 1073.67 | 2.44 | 59.53 | 0.18 | 253.88 | 3.29 | 22.37 | 0.06 | 1777.07 | 8651.86 | 133.97 | 25.05 | 63.25 | 159.02 | 13.1 | 3.19 | 74.04 | 98.56 | 11.93 | 41.64 | 28.61 | 79.46 | 77.4 | 12.93 | 17.26 | 10.18 | 16.29 | 4.25 | 7.44 | 9.1 | 24.69 | 28.64 | 79.23 | 77.25 | 12.94 | 17.13 | 16.52 | 4.25
FOSSIL Gas Primary 400-599 | 2016 | 2020 | 51 | 217.33 | 481 | 481 | 26.47 | 25.99 | 2567.05 | 3700.21 | 26.42 | 0 | 0 | 6267.26 | 698.11 | 6.52 | 909.52 | 2.02 | 38.38 | 0.14 | 469.44 | 3.41 | 2.34 | 0.06 | 2117.79 | 8385.05 | 185.88 | 56.29 | 81.15 | 242.17 | 11.3 | 5.63 | 98.77 | 98.19 | 13.26 | 43.27 | 30.61 | 74.74 | 71.74 | 21.38 | 26.42 | 16.96 | 16.93 | 8.33 | 13.95 | 16.31 | 35.68 | 30.64 | 75.17 | 72.15 | 21.11 | 26.11 | 16.63 | 8.2
FOSSIL Gas Primary 600-799 | 2016 | 2020 | 17 | 53.75 | 695 | 695 | 16.07 | 15.11 | 2148.06 | 3661.77 | 16.19 | 0 | 0 | 5809.83 | 651.99 | 7.14 | 1523 | 2.75 | 116.33 | 0.32 | 382.54 | 3.27 | 18.77 | 0.11 | 2692.63 | 8502.46 | 314.6 | 22.91 | 210.94 | 337.51 | 19.28 | 4.72 | 142.16 | 94.03 | 13.32 | 49.92 | 25.26 | 68.33 | 64.36 | 23.28 | 32.1 | 21.71 | 24 | 7.67 | 12.39 | 16.23 | 40.23 | 26.69 | 69.02 | 65.3 | 22.29 | 30.52 | 23.33 | 7.65
FOSSIL Gas Primary 800-999 | 2016 | 2020 | 10 | 33.17 | 787 | 787 | 87.26 | 86.92 | 2048.88 | 5319.79 | 90.42 | 0 | 0 | 7368.67 | 251.39 | 3.38 | 726.21 | 1.36 | 30.87 | 0.06 | 383.87 | 4.28 | 7.05 | 0.15 | 1399.39 | 8768.05 | 42.98 | 26.95 | 22.02 | 69.93 | 8.63 | 4.46 | 23.57 | 99.61 | 7.57 | 32.46 | 23.37 | 84.04 | 83.24 | 10.93 | 12.68 | 5.37 | 13.09 | 2.87 | 7.33 | 8.09 | 25.79 | 23.34 | 83.79 | 82.97 | 11.13 | 12.88 | 13.29 | 2.92
FOSSIL Lignite Primary All Sizes | 2016 | 2020 | 34 | 110.75 | 499 | 499 | 83.04 | 82.41 | 6911.43 | 366.12 | 1.58 | 0 | 0 | 7277.56 | 352.77 | 6.55 | 485.18 | 1.03 | 41.19 | 0.23 | 115.18 | 1.35 | 10.85 | 0.05 | 1005.18 | 8282.74 | 272.67 | 39.19 | 0.89 | 311.87 | 6.36 | 1.52 | 83.87 | 99.24 | 65.84 | 78.11 | 83.44 | 87.86 | 83.32 | 4.86 | 8.61 | 8.21 | 7.88 | 4.26 | 5.78 | 9.33 | 10.45 | 84.29 | 88.52 | 84.3 | 4.68 | 8.71 | 7.35 | 4.13
FOSSIL Oil/Gas Primary 001-099 | 2016 | 2020 | 114 | 450.83 | 55 | 54 | 34.96 | 34.8 | 1936.11 | 4127.93 | 20.28 | 0 | 0 | 6064.04 | 526.13 | 2.74 | 428.06 | 0.9 | 37.61 | 0.06 | 433.96 | 1.59 | 1.07 | 0.01 | 1426.83 | 7490.87 | 115.3 | 6.95 | 55.15 | 122.25 | 6.22 | 5.81 | 55.64 | 99.54 | 15.85 | 48.86 | 25.85 | 80.95 | 78.68 | 21.37 | 25.48 | 12.22 | 12.02 | 7.02 | 12.83 | 14.46 | 36.67 | 32.44 | 80.87 | 78.31 | 17.62 | 21.71 | 12.19 | 6.94
FOSSIL Oil/Gas Primary 100-199 | 2016 | 2020 | 122 | 502.5 | 130 | 129 | 48.87 | 48.54 | 2094.29 | 4700.89 | 27.96 | 0 | 0 | 6795.18 | 364.18 | 3.86 | 794.69 | 1.59 | 37.33 | 0.11 | 300.52 | 2.16 | 3.51 | 0.03 | 1500.23 | 8295.41 | 123.89 | 31.63 | 72.68 | 155.52 | 10.03 | 3.67 | 43.15 | 99.32 | 12.26 | 46.35 | 25.25 | 81.91 | 79.64 | 14.81 | 19.28 | 9.32 | 13.69 | 4.39 | 8.06 | 9.74 | 28.33 | 26.45 | 81.65 | 79.2 | 14.17 | 18.48 | 13.99 | 4.37
FOSSIL Oil/Gas Primary 200-299 | 2016 | 2020 | 42 | 159.5 | 232 | 232 | 27.77 | 27.43 | 2947.99 | 3770.57 | 29.27 | 0 | 0 | 6718.56 | 294.53 | 4.07 | 803.99 | 1.58 | 21.81 | 0.09 | 280.83 | 2.78 | 0 | 0 | 1401.16 | 8119.72 | 173.01 | 24.15 | 94.76 | 197.16 | 10.17 | 3.46 | 107.47 | 98.78 | 17.6 | 47.41 | 36.31 | 82.74 | 80.29 | 9.08 | 14.01 | 8.9 | 13.63 | 3.63 | 7.09 | 9.5 | 21.23 | 37.13 | 82.72 | 80.4 | 8.55 | 13.18 | 13.81 | 3.47
FOSSIL Oil/Gas Primary 300-399 | 2016 | 2020 | 49 | 190.75 | 350 | 349 | 28.2 | 27.8 | 2321.43 | 4432.82 | 30.28 | 0 | 0 | 6754.24 | 348.56 | 4.59 | 1031.49 | 2.3 | 52.24 | 0.16 | 244.74 | 2.9 | 17.36 | 0.05 | 1694.39 | 8448.63 | 108.8 | 22.87 | 50.32 | 131.67 | 12.83 | 3.1 | 83.5 | 98.58 | 11.15 | 40.46 | 27.48 | 79.94 | 78.21 | 13.05 | 16.81 | 9.98 | 15.93 | 4.13 | 7.23 | 8.61 | 24.34 | 27.56 | 79.83 | 78.18 | 12.88 | 16.5 | 16.09 | 4.07
FOSSIL Oil/Gas Primary 400-599 | 2016 | 2020 | 60 | 246.5 | 478 | 477 | 24.31 | 23.88 | 2282.64 | 4137.34 | 24.79 | 0 | 0 | 6419.98 | 644.23 | 6.07 | 889.89 | 1.97 | 39.06 | 0.14 | 435.49 | 3.25 | 2.06 | 0.05 | 2010.72 | 8430.7 | 169.69 | 51.11 | 75.27 | 220.8 | 11.02 | 5.19 | 95.59 | 98.23 | 11.77 | 43.16 | 27.08 | 76.15 | 73.4 | 22.01 | 27.11 | 16.62 | 16.21 | 7.64 | 12.83 | 14.97 | 36.55 | 27.27 | 76.45 | 73.68 | 21.71 | 26.77 | 15.98 | 7.56
FOSSIL Oil/Gas Primary 600-799 | 2016 | 2020 | 22 | 78.08 | 674 | 673 | 15.87 | 15.14 | 1611.38 | 4684.36 | 17.39 | 0 | 0 | 6295.74 | 477.37 | 5.83 | 1276.19 | 2.38 | 87.36 | 0.28 | 415.17 | 2.92 | 33.45 | 0.14 | 2289.55 | 8585.29 | 243.05 | 18.76 | 168.52 | 261.81 | 15.88 | 5.23 | 106.43 | 95.4 | 9.93 | 49.24 | 18.77 | 73.33 | 70.21 | 22.85 | 31.92 | 18.86 | 21.11 | 5.56 | 10.79 | 13.72 | 43.32 | 20.18 | 73.16 | 70.13 | 21.99 | 30.58 | 21.15 | 5.69
FOSSIL Oil/Gas Primary 800-999 | 2016 | 2020 | 12 | 46.08 | 794 | 794 | 63.86 | 63.47 | 1505.13 | 5737.43 | 67.01 | 0 | 0 | 7242.56 | 185.78 | 2.82 | 897.77 | 1.41 | 47.95 | 0.2 | 384.36 | 3.62 | 10.74 | 0.17 | 1526.6 | 8769.16 | 52.05 | 19.4 | 36.55 | 71.45 | 10.78 | 4.51 | 23.71 | 99.39 | 5.54 | 32.64 | 17.16 | 82.59 | 81.72 | 10.99 | 13.77 | 5.21 | 15.29 | 2.12 | 6.62 | 7.41 | 30.25 | 16.98 | 82.41 | 81.53 | 11.19 | 14.01 | 15.45 | 2.14
FOSSIL Oil/Gas Primary All Sizes | 2016 | 2020 | 423 | 1678.25 | 241 | 240 | 35.95 | 35.62 | 2147.41 | 4372.94 | 26.35 | 0 | 0 | 6520.35 | 439.97 | 4.04 | 763.94 | 1.57 | 40.41 | 0.11 | 357.37 | 2.39 | 5.46 | 0.04 | 1607.15 | 8127.5 | 135.49 | 25.63 | 71.57 | 161.13 | 9.9 | 4.46 | 60.29 | 99.08 | 11.63 | 44.06 | 26.42 | 80.23 | 77.91 | 17 | 21.64 | 11.38 | 14.36 | 5.41 | 9.88 | 11.7 | 31.34 | 26.39 | 78.76 | 76.38 | 16.57 | 21.56 | 16 | 5.24
NUCLEAR All Types All Sizes | 2016 | 2020 | 102 | 466.75 | 1013 | 1009 | 1.6 | 1.57 | 8087.26 | 0.09 | 0 | 0 | 0 | 8087.35 | 143.89 | 0.87 | 459.95 | 0.93 | 19.13 | 0.09 | 19.5 | 0.16 | 0.29 | 0.01 | 642.78 | 8730.12 | 44.53 | 81.04 | 0 | 125.57 | 5.49 | 0.23 | 5151.12 | 98.13 | 91.64 | 99.12 | 92.64 | 92.64 | 90.79 | 1.75 | 2.29 | 2.29 | 5.71 | 1.65 | 1.87 | 2.74 | 2.9 | 92.45 | 92.46 | 90.62 | 1.84 | 2.37 | 5.82 | 1.73
NUCLEAR All Types 400-799 | 2016 | 2020 | 13 | 55 | 622 | 616 | 1.38 | 1.33 | 8015.69 | 0 | 0 | 0 | 0 | 8015.69 | 134.98 | 1.04 | 383.25 | 0.82 | 22.98 | 0.09 | 32.77 | 0.2 | 0.22 | 0.02 | 574.2 | 8589.89 | 58.43 | 76.65 | 0 | 135.08 | 4.73 | 0.38 | 6026.83 | 96.38 | 90.89 | 97.53 | 93.32 | 93.32 | 90.82 | 1.66 | 2.37 | 2.37 | 5.11 | 1.57 | 1.96 | 2.91 | 3.05 | 93.19 | 93.19 | 90.73 | 1.7 | 2.43 | 5.2 | 1.61
NUCLEAR All Types 800-999 | 2016 | 2020 | 35 | 160.75 | 888 | 885 | 1.6 | 1.56 | 8180.35 | 0 | 0 | 0 | 0 | 8180.35 | 114.17 | 0.83 | 415.93 | 0.89 | 24.02 | 0.09 | 19.37 | 0.16 | 0.01 | 0.01 | 573.5 | 8753.85 | 45.14 | 71.3 | 0 | 116.44 | 5.03 | 0.22 | 5243.81 | 97.5 | 93.02 | 99.61 | 93.45 | 93.45 | 91.88 | 1.38 | 1.92 | 1.92 | 5.25 | 1.3 | 1.53 | 2.45 | 2.58 | 93.39 | 93.39 | 91.82 | 1.41 | 1.96 | 5.28 | 1.33
NUCLEAR All Types 1000 Plus | 2016 | 2020 | 54 | 251 | 1180 | 1174 | 1.65 | 1.63 | 8043.32 | 0.16 | 0.01 | 0 | 0 | 8043.48 | 164.88 | 0.87 | 504.96 | 0.98 | 15.16 | 0.1 | 16.69 | 0.16 | 0.49 | 0 | 702.17 | 8745.65 | 41.09 | 88.24 | 0 | 129.34 | 5.95 | 0.2 | 4934.55 | 98.79 | 91.05 | 99.05 | 91.97 | 91.97 | 90.08 | 2.01 | 2.51 | 2.51 | 6.14 | 1.89 | 2.08 | 2.9 | 3.08 | 91.92 | 91.92 | 90.02 | 2.06 | 2.56 | 6.14 | 1.93
NUCLEAR PWR All Sizes | 2016 | 2020 | 62 | 287 | 1034 | 1029 | 1.52 | 1.48 | 8072.68 | 0 | 0 | 0 | 0 | 8072.68 | 127.13 | 0.84 | 501.29 | 0.89 | 24.66 | 0.11 | 11.49 | 0.1 | 0.04 | 0 | 664.61 | 8737.29 | 31.45 | 56.15 | 0 | 87.6 | 6.02 | 0.13 | 5454.51 | 97.37 | 92 | 99.64 | 92.39 | 92.39 | 91 | 1.55 | 1.93 | 1.93 | 6.15 | 1.46 | 1.59 | 2.13 | 2.27 | 92.33 | 92.33 | 90.93 | 1.56 | 1.95 | 6.21 | 1.46
NUCLEAR PWR 400-799 | 2016 | 2020 | 5 | 19 | 601 | 594 | 1.37 | 1.37 | 8083.84 | 0 | 0 | 0 | 0 | 8083.84 | 121.08 | 1.37 | 459.23 | 1 | 42.61 | 0.16 | 23.56 | 0.16 | 0.63 | 0.05 | 647.11 | 8730.95 | 13.09 | 84.34 | 0 | 97.43 | 5.75 | 0.28 | 5900.61 | 100 | 91.64 | 99.2 | 92.59 | 92.59 | 90.29 | 1.48 | 1.64 | 1.64 | 6.02 | 1.39 | 1.66 | 2.02 | 2.15 | 92.38 | 92.38 | 90.21 | 1.48 | 1.64 | 6.23 | 1.39
NUCLEAR PWR 800-999 | 2016 | 2020 | 22 | 102 | 888 | 886 | 1.51 | 1.44 | 8139.47 | 0 | 0 | 0 | 0 | 8139.47 | 106.73 | 0.77 | 458.33 | 0.87 | 27.24 | 0.08 | 12.59 | 0.11 | 0 | 0 | 604.88 | 8744.35 | 29.66 | 43.26 | 0 | 72.92 | 5.55 | 0.14 | 5652.41 | 95.36 | 93.15 | 100.17 | 93.08 | 93.08 | 92.09 | 1.29 | 1.65 | 1.65 | 5.7 | 1.22 | 1.36 | 1.88 | 1.99 | 92.99 | 92.99 | 91.98 | 1.33 | 1.7 | 5.76 | 1.25
NUCLEAR PWR 1000 Plus | 2016 | 2020 | 35 | 166 | 1173 | 1167 | 1.54 | 1.51 | 8030.36 | 0 | 0.01 | 0 | 0 | 8030.36 | 140.36 | 0.81 | 532.5 | 0.88 | 21.03 | 0.13 | 9.43 | 0.09 | 0 | 0 | 703.32 | 8733.68 | 34.64 | 60.85 | 0 | 95.49 | 6.34 | 0.11 | 5318.12 | 98.05 | 91.48 | 99.42 | 91.95 | 91.95 | 90.41 | 1.72 | 2.14 | 2.14 | 6.45 | 1.61 | 1.72 | 2.3 | 2.46 | 92.02 | 92.02 | 90.48 | 1.67 | 2.09 | 6.42 | 1.56
NUCLEAR BWR All Sizes | 2016 | 2020 | 32 | 144 | 1034 | 1030 | 1.7 | 1.67 | 8160.25 | 0.29 | 0.01 | 0 | 0 | 8160.53 | 146.74 | 0.88 | 365.72 | 0.98 | 8.6 | 0.06 | 33.73 | 0.31 | 0.87 | 0.01 | 555.67 | 8716.2 | 65.22 | 126.17 | 0 | 191.39 | 4.29 | 0.4 | 4886.38 | 98.24 | 91.88 | 98.59 | 93.62 | 93.62 | 91.01 | 1.77 | 2.55 | 2.55 | 4.69 | 1.68 | 2.08 | 3.5 | 3.66 | 93.19 | 93.2 | 90.61 | 1.98 | 2.73 | 4.92 | 1.88
NUCLEAR BWR 400-799 | 2016 | 2020 | 4 | 16 | 644 | 639 | 1.63 | 1.44 | 7927.52 | 0 | 0 | 0 | 0 | 7927.52 | 152.46 | 1.19 | 140.32 | 0.38 | 28.4 | 0.13 | 40.61 | 0.38 | 0 | 0 | 361.79 | 8289.31 | 109.09 | 95.49 | 0 | 204.58 | 2.04 | 0.49 | 5505.22 | 88.34 | 91.9 | 96.2 | 95.64 | 95.64 | 92.4 | 1.89 | 3.24 | 3.24 | 2.53 | 1.84 | 2.33 | 4.27 | 4.36 | 95.53 | 95.53 | 92.27 | 1.99 | 3.36 | 2.54 | 1.93
NUCLEAR BWR 800-999 | 2016 | 2020 | 10 | 46 | 889 | 885 | 1.54 | 1.54 | 8326.99 | 0 | 0 | 0 | 0 | 8326.99 | 97.64 | 0.74 | 299.58 | 0.89 | 11.2 | 0.09 | 34.45 | 0.28 | 0.05 | 0.02 | 442.92 | 8769.91 | 74.75 | 102.89 | 0 | 177.64 | 3.54 | 0.39 | 5407.14 | 100 | 94.42 | 99.43 | 94.95 | 94.95 | 92.47 | 1.16 | 2.05 | 2.05 | 3.94 | 1.11 | 1.51 | 3.02 | 3.13 | 94.97 | 94.97 | 92.54 | 1.16 | 2.04 | 3.92 | 1.12
NUCLEAR BWR 1000 Plus | 2016 | 2020 | 18 | 82 | 1192 | 1188 | 1.8 | 1.79 | 8112.11 | 0.5 | 0.01 | 0 | 0 | 8112.62 | 173.17 | 0.9 | 446.8 | 1.15 | 3.28 | 0.04 | 31.99 | 0.3 | 1.5 | 0.01 | 656.75 | 8769.37 | 51.32 | 145.21 | 0 | 196.53 | 5.13 | 0.38 | 4531.91 | 99.44 | 90.82 | 98.48 | 92.51 | 92.51 | 89.94 | 2.09 | 2.71 | 2.71 | 5.51 | 1.97 | 2.36 | 3.63 | 3.82 | 92.22 | 92.22 | 89.64 | 2.33 | 2.96 | 5.58 | 2.2
NUCLEAR CANDU All Sizes | 2016 | 2020 | **** | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | [10 empty] | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: POF to FOR
JET ENGINE All Sizes | 2016 | 2020 | 267 | 1085.5 | 39 | 38 | 81.53 | 80.67 | 393.9 | 7230.23 | 85.33 | 0 | 120.33 | 7744.46 | 257.73 | 5.99 | 323.51 | 1.86 | 14.61 | 0.08 | 249.22 | 4.41 | 12.54 | 0.05 | 857.62 | 8602.08 | 29.47 | 25.66 | 27.73 | 55.13 | 3.93 | 3.04 | 4.88 | 98.95 | 4.95 | 79.37 | 4.58 | 90.03 | 87.64 | 33.39 | 35.91 | 8.97 | 6.97 | 3 | 6.04 | 6.57 | 51.84 | 6.23 | 89.67 | 86.25 | 29.4 | 32.61 | 7.09 | 3.24
JET ENGINE 001-019 | 2016 | 2020 | 27 | 121 | 15 | 15 | 14.66 | 14.3 | 104.22 | 7939.47 | 19.33 | 0 | 0 | 8043.69 | 192.84 | 3.3 | 307.28 | 1.18 | 6.02 | 0.07 | 168.85 | 3.67 | 20.68 | 0.11 | 695.67 | 8739.36 | 0.13 | 2.68 | 0 | 2.81 | 3.58 | 2.17 | 7.29 | 97.54 | 0.2 | 18.89 | 1.19 | 92.04 | 92 | 64.92 | 64.96 | 18.31 | 5.75 | 2.21 | 4.38 | 4.41 | 78.4 | 1.07 | 91.73 | 91.69 | 66.44 | 66.49 | 6.15 | 2.12
JET ENGINE 20 Plus | 2016 | 2020 | 240 | 964.5 | 42 | 41 | 89.91 | 89 | 430.24 | 7141.25 | 93.61 | 0 | 135.43 | 7706.92 | 265.87 | 6.33 | 325.55 | 1.95 | 15.69 | 0.08 | 259.3 | 4.5 | 11.52 | 0.04 | 877.93 | 8584.86 | 33.15 | 28.54 | 31.2 | 61.69 | 3.97 | 3.15 | 4.83 | 98.99 | 5.16 | 79.82 | 5.01 | 89.77 | 87.08 | 31.97 | 34.66 | 8.86 | 7.13 | 3.1 | 6.25 | 6.84 | 50.43 | 6.46 | 89.58 | 86 | 28.93 | 32.2 | 7.13 | 3.3
GAS TURBINE All Sizes | 2016 | 2020 | 709 | 3108.25 | 66 | 64 | 52.73 | 51.96 | 433.88 | 7177.06 | 55 | 0 | 0 | 7610.94 | 359.93 | 4.02 | 347.04 | 1.7 | 19.48 | 0.07 | 196.04 | 3.07 | 19.61 | 0.08 | 942.09 | 8553.03 | 19.8 | 7.04 | 17.6 | 26.84 | 4.29 | 2.52 | 8.35 | 98.54 | 5 | 70.5 | 5.07 | 88.99 | 86.57 | 45.34 | 46.8 | 10.22 | 6.81 | 4.21 | 6.73 | 6.99 | 57.99 | 7.1 | 89.66 | 87 | 31.01 | 32.53 | 7.15 | 3.19
GAS TURBINE 001-019 | 2016 | 2020 | 107 | 446 | 15 | 15 | 27.27 | 26.17 | 87.62 | 7036.09 | 33.18 | 0 | 0 | 7123.71 | 476.77 | 3.76 | 205.79 | 0.85 | 25.7 | 0.05 | 191.6 | 2.55 | 62.71 | 0.17 | 962.57 | 8086.27 | 10.09 | 4.74 | 9.78 | 14.82 | 2.86 | 3.14 | 3.35 | 95.97 | 0.71 | 66.13 | 1.08 | 88.1 | 87.21 | 84.48 | 84.79 | 17.21 | 6.01 | 5.9 | 9.04 | 9.17 | 89.45 | 1.07 | 88.09 | 87.2 | 84.75 | 85.04 | 5.98 | 5.93
GAS TURBINE 020-049 | 2016 | 2020 | 143 | 603.25 | 29 | 28 | 65.66 | 65.1 | 347.58 | 7138.4 | 59.73 | 0 | 0 | 7485.98 | 477.95 | 3.7 | 269.81 | 1.47 | 16.33 | 0.04 | 178.46 | 3.05 | 6.18 | 0.03 | 948.73 | 8434.72 | 12.28 | 0.45 | 10.59 | 12.74 | 3.39 | 2.19 | 5.34 | 99.15 | 4.71 | 79.08 | 4.12 | 88.75 | 86.09 | 57.9 | 58.63 | 10.4 | 5.58 | 5.67 | 7.86 | 8.01 | 66.13 | 5.96 | 89.03 | 86.31 | 44.3 | 45.24 | 6.24 | 4.74
GAS TURBINE 50 Plus | 2016 | 2020 | 459 | 2059 | 88 | 86 | 54.46 | 53.7 | 534.17 | 7218.91 | 58.34 | 0 | 0 | 7753.09 | 300.04 | 4.17 | 400.26 | 1.96 | 19.05 | 0.09 | 202.15 | 3.19 | 14.21 | 0.08 | 935.71 | 8688.79 | 24.11 | 9.46 | 21.34 | 33.57 | 4.83 | 2.49 | 9.95 | 98.6 | 5.18 | 69.88 | 6.15 | 89.23 | 86.58 | 35.97 | 37.89 | 9.27 | 7.32 | 3.45 | 5.94 | 6.26 | 50.48 | 7.42 | 89.78 | 87.05 | 28.45 | 30.08 | 7.27 | 2.95
COMBINED CYCLE All Sizes | 2016 | 2020 | 345 | 1420.08 | 298 | 291 | 61.73 | 61.02 | 4833.52 | 2822.55 | 54.43 | 0 | 0 | 7656.08 | 204.94 | 5.51 | 653.34 | 2.49 | 31.81 | 0.19 | 148.84 | 2.18 | 1.51 | 0.03 | 1040.45 | 8696.53 | 48.23 | 49.01 | 12.89 | 97.24 | 7.88 | 1.73 | 79.21 | 98.85 | 54.25 | 80.81 | 55.58 | 88.04 | 84.92 | 4.07 | 5.01 | 3.87 | 9.61 | 2.36 | 4.09 | 4.84 | 8.08 | 67.12 | 88.4 | 84.95 | 2.55 | 3.54 | 9.85 | 1.76
HYDRO All Sizes | 2016 | 2020 | 1059 | 4403 | 67 | 67 | 159.8 | 159.7 | 5523.09 | 1304.97 | 38 | 5.98 | 131.84 | 6965.87 | 583.34 | 3.53 | 989.82 | 2.84 | 14.32 | 0.03 | 152.38 | 2.63 | 7.91 | 0.01 | 1747.77 | 8713.64 | 12.61 | 7.38 | 2.06 | 19.99 | 11.52 | 1.84 | 34.58 | 99.94 | 36.3 | 57.32 | 63.38 | 79.94 | 79.42 | 9.34 | 9.54 | 8.1 | 13.36 | 6.69 | 8.53 | 8.7 | 11.83 | 63.33 | 81.48 | 81.06 | 4.7 | 4.81 | 15.32 | 3.2
HYDRO 001-029 | 2016 | 2020 | 401 | 1659 | 11 | 11 | 45.08 | 45.02 | 5325.31 | 1008.61 | 14.93 | 13.25 | 118.07 | 6465.23 | 1032.34 | 5.03 | 940.42 | 1.85 | 14.75 | 0.03 | 166.63 | 2.41 | 2.93 | 0.01 | 2157.07 | 8622.29 | 24.09 | 7.52 | 3.75 | 31.61 | 11.08 | 1.97 | 118.29 | 99.87 | 34.71 | 52.62 | 61.76 | 74.98 | 74.5 | 15.91 | 16.27 | 14.53 | 13.04 | 11.97 | 13.94 | 14.23 | 18.42 | 65.97 | 80.55 | 80.14 | 8.88 | 9.28 | 12.81 | 6.64
HYDRO 30 Plus | 2016 | 2020 | 658 | 2744 | 101 | 100 | 229.16 | 229.03 | 5642.66 | 1484.14 | 51.94 | 1.58 | 140.17 | 7268.55 | 311.88 | 2.62 | 1019.69 | 3.44 | 14.06 | 0.03 | 143.77 | 2.77 | 10.93 | 0.01 | 1500.31 | 8768.87 | 5.66 | 7.3 | 1.03 | 12.97 | 11.79 | 1.76 | 24.64 | 99.94 | 36.41 | 57.66 | 64.35 | 82.89 | 82.34 | 5.12 | 5.21 | 4.31 | 13.55 | 3.56 | 5.32 | 5.4 | 7.58 | 63.15 | 81.55 | 81.13 | 4.38 | 4.47 | 15.49 | 2.96
PUMPED STORAGE All Sizes | 2016 | 2020 | 111 | 536 | 132 | 131 | 256.03 | 255.83 | 2516.27 | 3371.97 | 212.97 | 1014.61 | 244.34 | 7147.19 | 273.59 | 2.86 | 1120.17 | 3.18 | 36.25 | 0.11 | 191.5 | 4.67 | 0.7 | 0.01 | 1622.2 | 8769.4 | 2.38 | 1.98 | 0.71 | 4.37 | 13.19 | 2.19 | 9.84 | 99.92 | 7.92 | 45.16 | 28.69 | 81.5 | 81.3 | 6.76 | 6.81 | 4.79 | 15.38 | 3.12 | 5.31 | 5.35 | 11.05 | 17.55 | 79.38 | 78.85 | 7.8 | 8.01 | 17.76 | 2.86
MULTIBOILER/MULTI-TURBINE All Sizes | 2016 | 2020 | 24 | 102 | 315 | 313 | 14.76 | 14.49 | 4988.94 | 2271.32 | 12.18 | 0 | 0 | 7260.26 | 260.17 | 4.58 | 791.71 | 1.49 | 29.58 | 0.1 | 271.82 | 2.15 | 0.34 | 0.01 | 1353.61 | 8613.87 | 417.08 | 172.82 | 20.89 | 589.9 | 9.53 | 3.16 | 344.3 | 98.17 | 26.23 | 58.16 | 57.92 | 84.29 | 76.45 | 4.96 | 12.85 | 9.94 | 12.69 | 3.02 | 6.18 | 11.73 | 18.13 | 45.11 | 81.25 | 77.3 | 4.2 | 8.85 | 16.77 | 1.98
DIESEL All Sizes | 2016 | 2020 | 151 | 657.17 | 8 | 8 | 78.54 | 78.01 | 724.41 | 7340.59 | 80.12 | 0 | 0 | 8065 | 225.89 | 6.48 | 213.13 | 0.81 | 0.62 | 0 | 145.34 | 3.07 | 3.62 | 0.05 | 588.59 | 8653.59 | 18.23 | 13.44 | 14.71 | 31.67 | 2.47 | 1.72 | 9.29 | 99.33 | 11 | 65.86 | 8.37 | 93.2 | 92.6 | 23.77 | 25.3 | 7.92 | 4.19 | 2.61 | 4.33 | 4.6 | 35.56 | 16.7 | 93.77 | 92.22 | 12.82 | 15.81 | 3.78 | 2.46
* Column title definitions and calculations can be found in the GADS Data Reporting Instructsions - Appendix F Equations
**Caution: EFOR and WEFOR values may be low since deratings during reserve shutdown periods may not have been reported for a large number of these units.
*** The two methods for calculating combined cycle units is not available at this time.
**** Less than three generating companies are reporting this type of unit. To retain confidentiality of the data, no data is reported here.