## Part
Part Number | Part ID | Part Language | Additional Information | Part Applicability | BA | DP | DPUF | FRSG | GO | GOP | IA | LSE | NERC | PA | PSE | RC | RE | RP | RRO | RRSG | RSG | TO | TOP | TP | TSP | Measure | Effective Date of Part | Pending Inactive? | Inactive Date of Part | Additional Effective Date Details | Additional Applicability Details | Prior Version(s) | RankId (Part) | Region - Jurisdiction | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1 | 79780000018 | A Balancing Authority may elect to fulfill its Contingency Reserve obligations by participating as a member of a Reserve Sharing Group. In such cases, the Reserve Sharing Group shall have the same responsibilities and obligations as each Balancing Authority with respect to monitoring and meeting the requirements of Standard BAL-002. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000020 | The minimum reserve requirement for the group. |  | RRO, RSG | [14 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780000027 | As a minimum, the Balancing Authority or Reserve Sharing Group shall carry at least enough Contingency Reserve to cover the most severe single contingency. All Balancing Authorities and Reserve Sharing Groups shall review, no less frequently than annually, their probable contingencies to determine their prospective most severe single contingencies. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780000029 | A Balancing Authority shall return its ACE to zero if its ACE just prior to the Reportable Disturbance was positive or equal to zero. For negative initial ACE values just prior to the Disturbance, the Balancing Authority shall return ACE to its pre-Disturbance value. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780000032 | The Reserve Sharing Group reviews group ACE (or equivalent) and demonstrates compliance to the DCS. To be in compliance, the group ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. Or |  | RSG | [16 empty] | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780000035 | The Contingency Reserve Restoration Period begins at the end of the Disturbance Recovery Period. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780000054 | The Balancing Authority may change its Frequency Bias Setting, and the method used to determine the setting, whenever any of the factors used to determine the current bias value change. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000057 | The Balancing Authority may use a fixed Frequency Bias value which is based on a fixed, straight-line function of Tie Line deviation versus Frequency Deviation. The Balancing Authority shall determine the fixed value by observing and averaging the Frequency Response for several Disturbances during on-peak hours. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780000061 | Fixed schedules for Jointly Owned Units mandate that Balancing Authority (A) that contains the Jointly Owned Unit must incorporate the respective share of the unit governor droop response for any Balancing Authorities that have fixed schedules (B and C). See the diagram below. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780000064 | Balancing Authorities that do not serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of its estimated maximum generation level in the coming year per 0.1 Hz change. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780000067 | The Balancing Authority may change its Frequency Bias Setting, and the method used to determine the setting, whenever any of the factors used to determine the current bias value change. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2015-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000070 | The Balancing Authority may use a fixed Frequency Bias value which is based on a fixed, straight-line function of Tie Line deviation versus Frequency Deviation. The Balancing Authority shall determine the fixed value by observing and averaging the Frequency Response for several Disturbances during on-peak hours. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2015-03-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780000074 | Fixed schedules for Jointly Owned Units mandate that Balancing Authority (A) that contains the Jointly Owned Unit must incorporate the respective share of the unit governor droop response for any Balancing Authorities that have fixed schedules (B and C). See the diagram below. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2015-03-31 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780000077 | Balancing Authorities that do not serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of its estimated maximum generation level in the coming year per 0.1 Hz change. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2015-03-31 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780000080 | The Balancing Authority may change its Frequency Bias Setting, and the method used to determine the setting, whenever any of the factors used to determine the current bias value change. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000083 | The Balancing Authority may use a fixed Frequency Bias value which is based on a fixed, straight-line function of Tie Line deviation versus Frequency Deviation. The Balancing Authority shall determine the fixed value by observing and averaging the Frequency Response for several Disturbances during on-peak hours. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780000087 | Fixed schedules for Jointly Owned Units mandate that Balancing Authority (A) that contains the Jointly Owned Unit must incorporate the respective share of the unit governor droop response for any Balancing Authorities that have fixed schedules (B and C). See the diagram below. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780000090 | Balancing Authorities that do not serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of its estimated maximum generation level in the coming year per 0.1 Hz change. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780000093 | The Balancing Authority may change its Frequency Bias Setting, and the method used to determine the setting, whenever any of the factors used to determine the current bias value change. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2009-06-28 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000096 | The Balancing Authority may use a fixed Frequency Bias value which is based on a fixed, straight-line function of Tie Line deviation versus Frequency Deviation. The Balancing Authority shall determine the fixed value by observing and averaging the Frequency Response for several Disturbances during on-peak hours. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2009-06-28 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780000100 | Fixed schedules for Jointly Owned Units mandate that Balancing Authority (A) that contains the Jointly Owned Unit must incorporate the respective share of the unit governor droop response for any Balancing Authorities that have fixed schedules (B and C). See the diagram below. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2009-06-28 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780000103 | Balancing Authorities that do not serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of its estimated maximum generation level in the coming year per 0.1 Hz change. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2009-06-28 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780000116 | The Balancing Authority shall offset its frequency schedule by 0.02 Hertz, leaving the Frequency Bias Setting normal; or |  | BA | BA | [21 empty] | 2007-06-18 |  | 2017-04-01 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780000119 | Balancing Authorities that have reliability concerns with the execution of a Time Error Correction shall notify their Reliability Coordinator and request the termination of a Time Error Correction in progress. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2017-04-01 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780000122 | The Balancing Authority shall offset its frequency schedule by 0.02 Hertz, leaving the Frequency Bias Setting normal; or |  | BA | BA | [23 empty] | 2012-08-16 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780000125 | Balancing Authorities that have reliability concerns with the execution of a Time Error Correction shall notify their Reliability Coordinator and request the termination of a Time Error Correction in progress. |  | BA | BA | [23 empty] | 2012-08-16 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780000137 | Each Generator Operator with generation facilities operating in an Interconnection shall ensure that those generation facilities are included within the metered boundaries of a Balancing Authority Area. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000143 | Balancing Authorities that share a tie shall ensure Tie Line MW metering is telemetered to both control centers, and emanates from a common, agreed-upon source using common primary metering equipment. Balancing Authorities shall ensure that megawatt-hour data is telemetered or reported at the end of each hour. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 121000000 | NPCC-ON |  | NPCC-US
1 | 79780000158 | Each Balancing Authority shall provide redundant and independent frequency metering equipment that shall automatically activate upon detection of failure of the primary source. This overall installation shall provide a minimum availability of 99.95%. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780000160 | Balancing Authorities with a high voltage direct current (HVDC) link to another Balancing Authority connected asynchronously to their Interconnection may choose to omit the Interchange Schedule related to the HVDC link from the ACE equation if it is modeled as internal generation or load. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780000162 | Each Generator Operator with generation facilities operating in an Interconnection shall ensure that those generation facilities are included within the metered boundaries of a Balancing Authority Area. |  | GOP | [5 empty] | GOP | [16 empty] | 2009-05-13 |  | 2012-09-12 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000168 | Balancing Authorities that share a tie shall ensure Tie Line MW metering is telemetered to both control centers, and emanates from a common, agreed-upon source using common primary metering equipment. Balancing Authorities shall ensure that megawatt-hour data is telemetered or reported at the end of each hour. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2012-09-12 |  |  |  | 121000000 | NPCC-ON |  | NPCC-US
1 | 79780000183 | Each Balancing Authority shall provide redundant and independent frequency metering equipment that shall automatically activate upon detection of failure of the primary source. This overall installation shall provide a minimum availability of 99.95%. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2012-09-12 |  |  |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780000185 | Balancing Authorities with a high voltage direct current (HVDC) link to another Balancing Authority connected asynchronously to their Interconnection may choose to omit the Interchange Schedule related to the HVDC link from the ACE equation if it is modeled as internal generation or load. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2012-09-12 |  |  |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780000187 | Each Generator Operator with generation facilities operating in an Interconnection shall ensure that those generation facilities are included within the metered boundaries of a Balancing Authority Area. |  | GOP | [5 empty] | GOP | [16 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000193 | Balancing Authorities that share a tie shall ensure Tie Line MW metering is telemetered to both control centers, and emanates from a common, agreed-upon source using common primary metering equipment. Balancing Authorities shall ensure that megawatt-hour data is telemetered or reported at the end of each hour. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 121000000 | NPCC-ON |  | NPCC-US
1 | 79780000208 | Each Balancing Authority shall provide redundant and independent frequency metering equipment that shall automatically activate upon detection of failure of the primary source. This overall installation shall provide a minimum availability of 99.95%. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780000210 | Balancing Authorities with a high voltage direct current (HVDC) link to another Balancing Authority connected asynchronously to their Interconnection may choose to omit the Interchange Schedule related to the HVDC link from the ACE equation if it is modeled as internal generation or load. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780000215 | Each Balancing Authority, by the end of the next business day, shall agree with its Adjacent Balancing Authorities to: |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780000216 | The hourly values of Net Interchange Schedule. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | 41100000 | NPCC-ON |  | NPCC-US
1 | 79780000225 | Each Balancing Authority, by the end of the next business day, shall agree with its Adjacent Balancing Authorities to: |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-03-31 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780000226 | The hourly values of Net Interchange Schedule. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-03-31 |  |  |  | 41100000 | NPCC-ON |  | NPCC-US
1 | 79780000245 | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000247 | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 12100000 | NPCC-ON |  | NPCC-US
1 | 79780000256 | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780000261 | The cyber security policy addresses the requirements in Standards CIP-002 through CIP-009, including provision for emergency situations. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000265 | The senior manager shall be identified by name, title, business phone, business address, and date of designation. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780000269 | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780000273 | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP-002, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780000277 | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780000278 | Personnel shall be identified by name, title, business phone and the information for which they are responsible for authorizing access. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 51100000 | NPCC-ON |  | NPCC-US
1 | 79780000285 | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained within ninety calendar days of such authorization. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-04-07 |  | 2010-03-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780000287 | The proper use of Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 22100000 | NPCC-ON |  | NPCC-US
1 | 79780000293 | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780000297 | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780000300 | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000307 | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780000312 | The processes for access request and authorization. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 25100000 | NPCC-ON |  | NPCC-US
1 | 79780000318 | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780000321 | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780000327 | The Responsible Entity shall ensure that all documentation required by Standard CIP-005 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005 at least annually. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780000331 | Processes to ensure and document that all Cyber Assets within an Electronic Security Perimeter also reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000341 | Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780000346 | Alarm Systems: Systems that alarm to indicate a door, gate or window has been pened without authorization. These alarms must provide for immediate notificationto personnel responsible for response. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780000349 | Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780000354 | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780000358 | Processes to ensure and document that all Cyber Assets within an Electronic Security Perimeter also reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000368 | Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780000373 | Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780000376 | Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780000381 | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780000385 | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-04-07 |  | 2010-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000389 | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780000393 | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780000396 | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure or an acceptance of risk. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780000399 | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780000400 | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003 Requirement R5. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 51100000 | NPCC-ON |  | NPCC-US
1 | 79780000404 | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 52100000 | NPCC-ON |  | NPCC-US
1 | 79780000408 | Each password shall be a minimum of six characters. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 53100000 | NPCC-ON |  | NPCC-US
1 | 79780000412 | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780000418 | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780000422 | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780000428 | Procedures to characterize and classify events as reportable Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000436 | Specify the required actions in response to events or conditions of varying duration and severity that would activate the recovery plan(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000443 | Internally. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000453 | Internally. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2009-05-13 |  | 2015-09-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000463 | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator, and all other potentially affected Balancing Authorities and Transmission Operators through predetermined communication paths of any condition that could threaten the reliability of its area or when firm load shedding is anticipated. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000468 | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780000473 | Communications protocols to be used during emergencies. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780000480 | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780000486 | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780000491 | Communications protocols to be used during emergencies. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780000498 | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780000508 | Loading all available generating capacity. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780000515 | Manually shed firm load without delay to return its ACE to zero; and |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780000519 | The deficient Load-Serving Entity shall request its Reliability Coordinator to initiate an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0. |  | LSE | [7 empty] | LSE | [14 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780000529 | Loading all available generating capacity. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-09-30 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780000536 | Manually shed firm load without delay to return its ACE to zero; and |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-09-30 |  |  |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780000540 | The deficient Load-Serving Entity shall request its Reliability Coordinator to initiate an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0. |  | LSE | [7 empty] | LSE | [14 empty] | 2009-05-13 |  | 2011-09-30 |  |  |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780000555 | The affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator or Load-Serving Entity shall submit within 24 hours of the disturbance or unusual occurrence either a copy of the report submitted to DOE, or, if no DOE report is required, a copy of the NERC Interconnection Reliability Operating Limit and Preliminary Disturbance Report form. Events that are not identified until some time after they occur shall be reported within 24 hours of being recognized. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-12-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780000563 | The Transmission Operator shall perform this simulation or testing at least once every five years. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  |  | 101000000 | NPCC-ON |  | NPCC-US
1 | 79780000565 | The affected Transmission Operators and Balancing Authorities shall work in conjunction with their Reliability Coordinator(s) to determine the extent and condition of the isolated area(s). |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  |  | 111000000 | NPCC-ON |  | NPCC-US
1 | 79780000570 | Voltage, frequency, and phase angle permit. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  |  | 115100000 | NPCC-ON |  | NPCC-US
1 | 79780000589 | A requirement to have a database that contains all blackstart generators1 designated for use in an SRP within the respective areas. This database shall be updated on an annual basis. The database shall include the name, location, megawatt capacity, type of unit, latest date of test, and starting method. |  | RRO | [14 empty] | RRO | [7 empty] | 2011-05-23 |  | 2011-05-23 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000592 | Testing frequency (minimum of one third of the units each year). |  | RRO | [14 empty] | RRO | [9 empty] | 2011-05-23 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780000598 | The contingency plan shall not rely on data or voice communication from the primary control facility to be viable. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000609 | Generation facilities, |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000613 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780000614 | Procedures for coordinated joint studies of new facilities and their impacts on the interconnected transmission systems. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780000632 | Evaluation of the reliability impact of the new facilities and their connections on the interconnected transmission systems. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [14 empty] | 2007-06-18 |  | 2011-09-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000639 | The TVMP shall define a schedule for and the type (aerial, ground) of ROW vegetation inspections. This schedule should be flexible enough to adjust for changing conditions. The inspection schedule shall be based on the anticipated growth of vegetation and any other environmental or operational factors that could impact the relationship of vegetation to the Transmission Owner’s transmission lines. |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000641 | Clearance 1 — The Transmission Owner shall determine and document appropriate clearance distances to be achieved at the time of transmission vegetation management work based upon local conditions and the expected time frame in which the Transmission Owner plans to return for future vegetation management work. Local conditions may include, but are not limited to: operating voltage, appropriate vegetation management techniques, fire risk, reasonably anticipated tree and conductor movement, species types and growth rates, species failure characteristics, local climate and rainfall patterns, line terrain and elevation, location of the vegetation within the span, and worker approach distance requirements. Clearance 1 distances shall be greater than those defined by Clearance 2 below. |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  |  | 12100000 | NPCC-ON |  | NPCC-US
1 | 79780000643 | Where transmission system transient overvoltage factors are not known, clearances shall be derived from Table 5, IEEE 516-2003, phase-to-ground distances, with appropriate altitude correction factors applied. |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  |  | 12210000 | NPCC-ON |  | NPCC-US
1 | 79780000650 | Multiple sustained outages on an individual line, if caused by the same vegetation, shall be reported as one outage regardless of the actual number of outages within a 24-hour period. |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780000654 | Category 1 — Grow-ins: Outages caused by vegetation growing into lines from vegetation inside and/or outside of the ROW; |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  |  | 34100000 | NPCC-ON |  | NPCC-US
1 | 79780000686 | A statement that a Facility Rating shall equal the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2012-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000688 | The scope of equipment addressed shall include, but not be limited to, generators, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2012-12-31 |  |  |  | 12100000 | NPCC-ON |  | NPCC-US
1 | 79780000691 | Ratings provided by equipment manufacturers. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2012-12-31 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780000701 | Be applicable for developing SOLs used in the planning horizon. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000705 | In the pre-contingency state and with all Facilities in service, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect expected system conditions and shall reflect changes to system topology such as Facility outages. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-05-29 |  | 2009-04-28 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780000707 | Single line to ground or three-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-07-01 |  | 2009-04-28 |  |  |  | 22100000 | NPCC-ON |  | NPCC-US
1 | 79780000711 | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-07-01 |  | 2009-04-28 |  |  |  | 23100000 | NPCC-ON |  | NPCC-US
1 | 79780000716 | Planned or controlled interruption of electric supply to customers (load shedding), the planned removal from service of certain generators, and/or the curtailment of contracted Firm (non-recallable reserved) electric power Transfers. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-07-01 |  | 2009-04-28 |  |  |  | 25100000 | NPCC-ON |  | NPCC-US
1 | 79780000718 | Study model (must include at least the entire Planning Authority Area as well as the critical modeling details from other Planning Authority Areas that would impact the Facility or Facilities under study). |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780000725 | Each adjacent Planning Authority and each Planning Authority that indicated it has a reliability-related need for the methodology. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780000730 | Be applicable for developing SOLs used in the planning horizon. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000734 | In the pre-contingency state and with all Facilities in service, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect expected system conditions and shall reflect changes to system topology such as Facility outages. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780000736 | Single line to ground or three-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 22100000 | NPCC-ON |  | NPCC-US
1 | 79780000740 | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 23100000 | NPCC-ON |  | NPCC-US
1 | 79780000745 | Planned or controlled interruption of electric supply to customers (load shedding), the planned removal from service of certain generators, and/or the curtailment of contracted Firm (non-recallable reserved) electric power Transfers. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 26100000 | NPCC-ON |  | NPCC-US
1 | 79780000747 | Study model (must include at least the entire Planning Authority Area as well as the critical modeling details from other Planning Authority Areas that would impact the Facility or Facilities under study). |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780000754 | Each adjacent Planning Authority and each Planning Authority that indicated it has a reliability-related need for the methodology. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780000759 | Be applicable for developing SOLs used in the operations horizon. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000763 | In the pre-contingency state, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect current or expected system conditions and shall reflect changes to system topology such as Facility outages. |  | RC | [11 empty] | RC | [10 empty] | 2008-05-29 |  | 2009-04-28 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780000765 | Single line to ground or 3-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. |  | RC | [11 empty] | RC | [10 empty] | 2008-10-01 |  | 2009-04-28 |  |  |  | 22100000 | NPCC-ON |  | NPCC-US
1 | 79780000769 | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. |  | RC | [11 empty] | RC | [10 empty] | 2008-10-01 |  | 2009-04-28 |  |  |  | 23100000 | NPCC-ON |  | NPCC-US
1 | 79780000774 | Study model (must include at least the entire Reliability Coordinator Area as well as the critical modeling details from other Reliability Coordinator Areas that would impact the Facility or Facilities under study.) |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780000777 | This process shall address the need to modify these limits, to modify the list of limits, and to modify the list of associated multiple contingencies. |  | RC | [11 empty] | RC | [10 empty] | 2008-10-01 |  | 2009-04-28 |  |  |  | 33100000 | NPCC-ON |  | NPCC-US
1 | 79780000783 | Each adjacent Reliability Coordinator and each Reliability Coordinator that indicated it has a reliability-related need for the methodology. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780000788 | Be applicable for developing SOLs used in the operations horizon. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000792 | In the pre-contingency state, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect current or expected system conditions and shall reflect changes to system topology such as Facility outages. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780000794 | Single line to ground or 3-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 22100000 | NPCC-ON |  | NPCC-US
1 | 79780000798 | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 23100000 | NPCC-ON |  | NPCC-US
1 | 79780000803 | Study model (must include at least the entire Reliability Coordinator Area as well as the critical modeling details from other Reliability Coordinator Areas that would impact the Facility or Facilities under study.) |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780000806 | This process shall address the need to modify these limits, to modify the list of limits, and to modify the list of associated multiple contingencies |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 33100000 | NPCC-ON |  | NPCC-US
1 | 79780000812 | Each adjacent Reliability Coordinator and each Reliability Coordinator that indicated it has a reliability-related need for the methodology. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780000817 | A statement that Transfer Capabilities shall respect all applicable System Operating Limits (SOLs). |  | PCPA, RC | [9 empty] | PA |  | RC | [12 empty] | 2013-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000820 | Transmission system topology |  | PCPA, RC | [9 empty] | PA |  | RC | [12 empty] | 2013-03-31 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780000825 | Each Adjacent Reliability Coordinator and each Reliability Coordinator that indicated a reliability-related need for the methodology. |  | RC | [11 empty] | RC | [12 empty] | 2013-03-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780000829 | Each Transmission Planner that works in the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PA | [14 empty] | 2013-03-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780000835 | The Reliability Coordinator shall provide its Transfer Capabilities to its associated Regional Reliability Organization(s), to its adjacent Reliability Coordinators, and to the Transmission Operators, Transmission Service Providers and Planning Authorities that work in its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2013-03-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780000842 | The Reliability Coordinator shall provide its SOLs (including the subset of SOLs that are IROLs) to adjacent Reliability Coordinators and Reliability Coordinators who indicate a reliability-related need for those limits, and to the Transmission Operators, Transmission Planners, Transmission Service Providers and Planning Authorities within its Reliability Coordinator Area. For each IROL, the Reliability Coordinator shall provide the following supporting information: |  | RC | [11 empty] | RC | [10 empty] | 2008-05-29 |  | 2009-04-28 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780000843 | Identification and status of the associated Facility (or group of Facilities) that is (are) critical to the derivation of the IROL. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-01 |  | 2009-04-28 |  |  |  | 51100000 | NPCC-ON |  | NPCC-US
1 | 79780000851 | The Planning Authority shall provide this list of multiple contingencies and the associated stability limits to the Reliability Coordinators that monitor the facilities associated with these contingencies and limits. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780000858 | The Reliability Coordinator shall provide its SOLs (including the subset of SOLs that are IROLs) to adjacent Reliability Coordinators and Reliability Coordinators who indicate a reliability-related need for those limits, and to the Transmission Operators, Transmission Planners, Transmission Service Providers and Planning Authorities within its Reliability Coordinator Area. For each IROL, the Reliability Coordinator shall provide the following supporting information: |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 | [5 empty] | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780000859 | Identification and status of the associated Facility (or group of Facilities) that is (are) critical to the derivation of the IROL. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 | [5 empty] | 51100000 | NPCC-ON |  | NPCC-US
1 | 79780000867 | The Planning Authority shall provide this list of multiple contingencies and the associated stability limits to the Reliability Coordinators that monitor the facilities associated with these contingencies and limits. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 | [5 empty] | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780000874 | All Dynamic Schedules at the expected average MW profile for each hour. |  | PSE | [10 empty] | PSE | [11 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000876 | If a Purchasing-Selling Entity is not involved in the Interchange, such as delivery from a jointly owned generator. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780000879 | All Dynamic Schedules at the expected average MW profile for each hour. |  | PSE | [10 empty] | PSE | [11 empty] | 2008-08-27 |  | 2014-09-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000881 | If a Purchasing-Selling Entity is not involved in the Interchange, such as delivery from a jointly owned generator. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2014-09-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780000884 | The Sending Balancing Authority and Receiving Balancing Authority shall agree on Interchange as received from the Interchange Authority, including: |  | BA | BA | [21 empty] | 2007-06-18 |  | 2011-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000885 | Interchange Schedule start and end time. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2011-03-31 |  |  |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780000893 | The average energy profile in an hour is greater than 250 MW and in that hour the actual hourly integrated energy deviates from the hourly average energy profile indicated on the tag by more than +10%. |  | PSE | [10 empty] | PSE | [11 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780000898 | The average energy profile in an hour is greater than 250 MW and in that hour the actual hourly integrated energy deviates from the hourly average energy profile indicated on the tag by more than +10%. |  | PSE | [10 empty] | PSE | [11 empty] | 2008-08-27 |  | 2014-09-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780000902 | When a Balancing Authority or Reliability Coordinator initiates a Curtailment to Confirmed or Implemented Interchange for reliability, the Interchange Authority shall distribute the Arranged Interchange information for reliability assessment only to the Source Balancing Authority and the Sink Balancing Authority. |  | IA | [6 empty] | IA | [15 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000904 | When a Balancing Authority or Reliability Coordinator initiates a Curtailment to Confirmed or Implemented Interchange for reliability, the Interchange Authority shall distribute the Arranged Interchange information for reliability assessment only to the Source Balancing Authority and the Sink Balancing Authority. |  | IA | [6 empty] | IA | [15 empty] | 2008-08-27 |  | 2010-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000906 | When a Balancing Authority or Reliability Coordinator initiates a Curtailment to Confirmed or Implemented Interchange for reliability, the Interchange Authority shall distribute the Arranged Interchange information for reliability assessment only to the Source Balancing Authority and the Sink Balancing Authority. |  | IA | [6 empty] | IA | [15 empty] | 2010-01-25 |  | 2014-09-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000908 | Each involved Balancing Authority shall evaluate the Arranged Interchange with respect to: |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000909 | Energy profile (ability to support the magnitude of the Interchange). |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780000914 | Each involved Balancing Authority shall evaluate the Arranged Interchange with respect to: |  | BA | BA | [21 empty] | 2008-08-27 |  | 2010-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000915 | Energy profile (ability to support the magnitude of the Interchange). |  | BA | BA | [21 empty] | 2008-08-27 |  | 2010-06-30 |  |  |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780000920 | Each involved Balancing Authority shall evaluate the Arranged Interchange with respect to: |  | BA | BA | [21 empty] | 2010-01-25 |  | 2014-09-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000921 | Energy profile (ability to support the magnitude of the Interchange). |  | BA | BA | [21 empty] | 2010-07-01 |  | 2014-09-30 |  |  |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780000926 | Source Balancing Authority megawatts equal sink Balancing Authority megawatts (adjusted for losses, if appropriate). |  | IA | [6 empty] | IA | [15 empty] | 2007-06-18 |  | 2014-09-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000929 | Generation source and load sink. |  | IA | [6 empty] | IA | [15 empty] | 2007-06-18 |  | 2014-09-30 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780000935 | For Confirmed Interchange, the Interchange Authority shall also communicate: |  | IA | [6 empty] | IA | [15 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000936 | Start and stop times, ramps, and megawatt profile to Balancing Authorities. |  | IA | [6 empty] | IA | [15 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780000939 | For Confirmed Interchange, the Interchange Authority shall also communicate: |  | IA | [6 empty] | IA | [15 empty] | 2008-08-27 |  | 2010-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000940 | Start and stop times, ramps, and megawatt profile to Balancing Authorities. |  | IA | [6 empty] | IA | [15 empty] | 2008-08-27 |  | 2010-06-30 |  |  |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780000943 | For Confirmed Interchange, the Interchange Authority shall also communicate: |  | IA | [6 empty] | IA | [15 empty] | 2010-01-25 |  | 2014-09-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780000944 | Start and stop times, ramps, and megawatt profile to Balancing Authorities. |  | IA | [6 empty] | IA | [15 empty] | 2010-07-01 |  | 2014-09-30 |  |  |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780000996 | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001023 | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001050 | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001073 | The Interconnection-wide Transmission Loading Relief (TLR) procedure for use in the Eastern Interconnection is provided in Attachment 1-IRO-006-0. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-04-22 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780001081 | The Interconnection-wide Transmission Loading Relief (TLR) procedure for use in the Eastern Interconnection provided in Attachment 1-IRO-006-4. The TLR procedure alone is an inappropriate and ineffective tool to mitigate an IROL violation due to the time required to implement the procedure. Other acceptable and more effective procedures to mitigate actual IROL violations include: reconfiguration, redispatch, or load shedding. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-23 |  | 2009-12-09 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001099 | List of required data and information needed by the Reliability Coordinator to support Real-Time Monitoring, Operational Planning Analyses, and Real-Time Assessments. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2009-08-05 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001106 | These Operating Procedures, Processes, or Plans shall collectively address, as a minimum, the following: |  | RC | [11 empty] | RC | [9 empty] | M1.1 These Operating Procedures, Processes, or Plans shall address: | 2007-06-18 |  | 2017-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001107 | Communications and notifications, including the conditions under which one Reliability Coordinator notifies other Reliability Coordinators; the process to follow in making those notifications; and the data and information to be exchanged with other Reliability Coordinators. |  | RC | [11 empty] | RC | [9 empty] | M1.1.1 Communications and notifications, including the conditions under which&lt;br/&gt;one Reliability Coordinator notifies other Reliability Coordinators; the&lt;br/&gt;process to follow in making those notifications; and the data and&lt;br/&gt;information to be exchanged with other Reliability Coordinators. | 2007-06-18 |  | 2017-03-31 |  |  |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780001114 | Agreed to by all the Reliability Coordinators required to take the indicated action(s). |  | RC | [11 empty] | RC | [9 empty] | M2.1 Agreed to by all the Reliability Coordinators required to take the indicated action(s). | 2007-06-18 |  | 2017-03-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780001117 | A reference to the associated Reliability Coordinator-to-Reliability Coordinator Operating Procedure, Process, or Plan. |  | RC | [11 empty] | RC | [9 empty] | M3.1 Be available to the Reliability Coordinator’s System Operators for Real-time use, | 2007-06-18 |  | 2017-03-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780001120 | Include version control number or date. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780001124 | The Reliability Coordinator shall make notifications to other Reliability Coordinators of conditions in its Reliability Coordinator Area that may impact other Reliability Coordinator Areas. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001126 | The frequency of these conference calls shall be agreed upon by all involved Reliability Coordinators and shall be at least weekly. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780001129 | If the involved Reliability Coordinators agree on the problem and the actions to take to prevent or mitigate the system condition, each involved Reliability Coordinator shall implement the agreed-upon solution, and notify the involved Reliability Coordinators of the action(s) taken. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001131 | If time permits, this re-evaluation shall be done before taking corrective actions. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 12100000 | NPCC-ON |  | NPCC-US
1 | 79780001137 | A narrative explaining how TTC and ATC values are determined. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001142 | Daily values for current week at least once per day. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 15100000 | NPCC-ON |  | NPCC-US
1 | 79780001152 | Hourly values for at least the next 48 hours. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780001156 | Information describing how the selected methodology (or methodologies) has been implemented, in such detail that, given the same information used by the Transmission Service Provider, the results of the ATC or AFC calculations can be validated. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780001158 | How confirmed Transmission reservations, expected Interchange and internal counterflow are addressed in firm and non-firm ATC or AFC calculations. |  | TSP | [20 empty] | TSP |  |  |  | 2010-09-16 |  |  |  | 32100000 | NPCC-ON |  | NPCC-US
1 | 79780001164 | The criteria used to determine when an outage that is in effect part of a day impacts a daily calculation. |  | TSP | [20 empty] | TSP |  |  |  | 2010-09-16 |  |  |  | 36100000 | NPCC-ON |  | NPCC-US
1 | 79780001168 | Each Planning Coordinator associated with the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780001178 | Hourly values, once per hour. Transmission Service Providers are allowed up to 175 hours per calendar year during which calculations are not required to be performed, despite a change in a calculated value identified in the ATC equation. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780001182 | The Transmission Service Provider shall make its own current data available, in the format maintained by the Transmission Service Provider, for up to 13 months into the future (subject to confidentiality and security requirements). |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780001183 | If the Transmission Service Provider uses the data requested in its transfer or Flowgate capability calculations, it shall make the data used available |  | TSP | [20 empty] | TSP |  |  |  | 2010-09-16 |  |  |  | 91100000 | NPCC-ON |  | NPCC-US
1 | 79780001191 | The name, telephone number and email address of a contact person to whom concerns are to be addressed. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001197 | Specify that the method used by each Regional Reliability Organization member to determine its generation reliability requirements as the basis for CBM shall be consistent with its generation planning criteria. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001209 | The process through which a Load-Serving Entity within a Balancing Authority Area associated with the Transmission Service Provider, or the Resource Planner associated with that Balancing Authority Area, may ensure that its need for Transmission capacity to be set aside as CBM will be reviewed and accommodated by the Transmission Service Provider to the extent Transmission capacity is available. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001215 | The CBM is available |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 121000000 | NPCC-ON |  | NPCC-US
1 | 79780001220 | Using one or more of the following to determine the GCIR: Loss of Load Expectation (LOLE) studies; Loss of Load Probability (LOLP) studies; Deterministic risk-analysis studies; Reserve margin or resource adequacy requirements established by other entities, such as municipalities, state commissions, regional transmission organizations, independent system operators, Regional Reliability Organizations, or regional entities |  | LSE | [7 empty] | LSE | [14 empty] | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780001223 | Using one or more of the following to determine the GCIR: Loss of Load Expectation (LOLE) studies; Loss of Load Probability (LOLP) studies; Deterministic risk-analysis studies; Reserve margin or resource adequacy requirements established by other entities, such as municipalities, state commissions, regional transmission organizations, independent system operators, Regional Reliability Organizations, or regional entities |  | RP | [13 empty] | RP | [8 empty] | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780001226 | Reflect consideration of each of the following if available: Any studies (as described in R3.1) performed by Load-Serving Entities for loads within the Transmission Service Provider’s area; Any studies (as described in R4.1) performed by Resource Planners for loads within the Transmission Service Provider’s area; Any reserve margin or resource adequacy requirements for loads within the Transmission Service Provider’s area established by other entities, such as municipalities, state commissions, regional transmission organizations, independent system operators, Regional Reliability Organizations, or regional entities |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780001229 | Reflect consideration of each of the following if available: Any studies (as described in R3.1) performed by Load-Serving Entities for loads within the Transmission Planner’s area; Any studies (as described in R4.1) performed by Resource Planners for loads within the Transmission Planner’s area; Any reserve margin or resource adequacy requirements for loads within the Transmission Planner’s area established by other entities, such as municipalities, state commissions, regional transmission organizations, independent system operators, Regional Reliability Organizations, or regional entities |  | TP | [19 empty] | TP |  |  | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780001234 | Each of its associated Transmission Operators within 30 calendar days of their making a request for the data. |  | TP, TSP | [19 empty] | TP | TSP |  | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780001237 | Indicate the frequency under which the verification review shall be implemented. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001244 | Require that CBM be used only after the following steps have been taken (as time permits): all non-firm sales have been terminated, Direct-Control Load Management has been implemented, and customer interruptible demands have been interrupted. CBM may be used to reestablish Operating Reserves. |  | TSP | [20 empty] | TSP |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001249 | Require that CBM be used only after the following steps have been taken (as time permits): all non-firm sales have been terminated, Direct-Control Load Management has been implemented, and customer interruptible demands have been interrupted. CBM may be used to reestablish Operating Reserves. |  | TSP | [20 empty] | TSP |  | 2009-05-13 |  | 2011-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001255 | Circumstances. |  | TSP | [20 empty] | TSP |  | 2007-06-18 |  | 2011-03-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780001259 | Specify the update frequency of TRM calculations. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001262 | Aggregate Load forecast error (not included in determining generation reliability requirements). |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780001274 | Identification of (on each of its respective ATC Paths or Flowgates) each of the following components of uncertainty if used in establishing TRM, and a description of how that component is used to establish a TRM value: Aggregate Load forecast.; Load distribution uncertainty.; Forecast uncertainty in Transmission system topology (including, but not limited to, forced or unplanned outages and maintenance outages).; Allowances for parallel path (loop flow) impacts.; Allowances for simultaneous path interactions.; Variations in generation dispatch (including, but not limited to, forced or unplanned outages, maintenance outages and location of future generation).; Short-term System Operator response (Operating Reserve actions ).; Reserve sharing requirements.; Inertial response and frequency bias. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001277 | Same day and real-time. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 | [5 empty] | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780001285 | Indicate the frequency under which the verification review shall be implemented. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001294 | Bus (substation): name, nominal voltage, electrical demand supplied (consistent with the aggregated and dispersed substation demand data supplied per Reliability Standards MOD-016-0, MOD-017-0, and MOD-020-0 ), and location. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001305 | Design data shall be provided for new or refurbished excitation systems (for synchronous generators and synchronous condensers) at least three months prior to the installation date. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001306 | If design data is unavailable from the manufacturer 3 months prior to the installation date, estimated or typical manufacturer’s data, based on excitation systems of similar design and characteristics, shall be provided. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780001308 | Estimated or typical manufacturer’s dynamics data, based on units of similar design and characteristics, may be submitted when unit-specific dynamics data cannot be obtained. In no case shall other than unit-specific data be reported for generator units installed after 1990. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 12100000 | NPCC-ON |  | NPCC-US
1 | 79780001317 | The Regional Reliability Organization(s) shall develop Interconnectionspecific dynamics system models for at least two timeframes (present or nearterm model and a future or longer-term model), and additional seasonal and demand level models, as necessary, to analyze the dynamic response of that Interconnection. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001320 | The Regional Reliability Organization(s) shall develop Interconnection specific dynamics system models for at least two timeframes (present or near-term model and a future or longer-term model), and additional seasonal and demand level models, as necessary, to analyze the dynamic response of that Interconnection. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001323 | The aggregated and dispersed data submittal requirements shall ensure that consistent data is supplied for Reliability Standards TPL-005, TPL-006, MOD-010, MOD-011, MOD-012, MOD-013, MOD-014, MOD-015, MOD-016, MOD-017, MOD-018, MOD-019, MOD-020, and MOD-021. The data submittal requirements shall stipulate that each Load-Serving Entity count its customer Demand once and only once, on an aggregated and dispersed basis, in developing its actual and forecast customer Demand values. |  | PCPA, RRO | [9 empty] | PA |  |  |  |  | RRO | [7 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001325 | The Regional Reliability Organization shall make this distribution within 30 calendar days of approval. |  | RRO | [14 empty] | RRO | [7 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780001327 | The Planning Authority shall make this distribution within 30 calendar days of approval. |  | PCPA | [9 empty] | PA | [12 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780001329 | The aggregated and dispersed data submittal requirements shall ensure that consistent data is supplied for Reliability Standards TPL-005, TPL-006, MOD-010, MOD-011, MOD-012, MOD-013, MOD-014, MOD-015, MOD-016, MOD-017, MOD-018, MOD-019, MOD-020, and MOD-021. The data submittal requirements shall stipulate that each Load-Serving Entity count its customer Demand once and only once, on an aggregated and dispersed basis, in developing its actual and forecast customer Demand values. |  | PCPA, RRO | [9 empty] | PA |  |  |  |  | RRO | [7 empty] | 2009-05-13 |  | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001331 | The Regional Reliability Organization shall make this distribution within 30 calendar days of approval. |  | RRO | [14 empty] | RRO | [7 empty] | 2009-05-13 |  | 2016-06-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780001333 | The Planning Authority shall make this distribution within 30 calendar days of approval. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-05-13 |  | 2016-06-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780001335 | Integrated hourly demands in megawatts (MW) for the prior year. |  | LSE, PCPA, RP | [7 empty] | LSE |  | PA |  |  |  | RP | [8 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001340 | Integrated hourly demands in megawatts (MW) for the prior year. |  | LSE, PCPA, RP | [7 empty] | LSE |  | PA |  |  |  | RP | [8 empty] | 2009-05-13 |  | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001345 | Indicate whether the demand data of nonmember entities within an area or Regional Reliability Organization are included, and |  | LSE, PCPA, RP, TP | [7 empty] | LSE |  | PA |  |  |  | RP | [5 empty] | TP |  |  | 2007-06-18 |  | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001356 | Generating unit exemption criteria including documentation of those units that are exempt from a portion or all of these procedures. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001361 | Seasonal gross and net Real Power generating capabilities. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 15100000 | NPCC-ON |  | NPCC-US
1 | 79780001367 | Generating unit exemption criteria including documentation of those units that are exempt from a portion or all of these procedures. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001372 | Verified maximum gross and net Reactive Power capability (both lagging and leading) at Seasonal Real Power generating capabilities as reported in accordance with Reliability Standard MOD-024 Requirement 1.5.1. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 15100000 | NPCC-ON |  | NPCC-US
1 | 79780001379 | Information describing how the selected methodology has been implemented, in such detail that, given the same information used by the Transmission Operator, the results of the TTC calculations can be validated. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2013-09-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001384 | Define if the source used for Available Transfer Capability (ATC) calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2013-09-30 |  |  |  | 15100000 | NPCC-ON |  | NPCC-US
1 | 79780001391 | Modeling data and topology of its Reliability Coordinator’s area of responsibility. Equivalent representation of radial lines and facilities 161 kV or below is allowed. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780001395 | For on-peak and off-peak intra-day and next-day TTCs, use the following (as well as any other values and additional parameters as specified in the ATCID): |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780001396 | Expected generation and Transmission outages, additions, and retirements, included as specified in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2013-09-30 |  |  |  | 31100000 | NPCC-ON |  | NPCC-US
1 | 79780001400 | Expected generation and Transmission outages, additions, and Retirements, included as specified in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2013-09-30 |  |  |  | 32100000 | NPCC-ON |  | NPCC-US
1 | 79780001404 | Use all Contingencies meeting the criteria described in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780001408 | At least once within the seven calendar days prior to the specified period for TTCs used in hourly and daily ATC calculations. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780001412 | Determine the incremental Transfer Capability for each ATC Path by increasing generation and/or decreasing load within the source Balancing Authority area and decreasing generation and/or increasing load within the sink Balancing Authority area until either: - A System Operating Limit is reached on the Transmission Service Provider’s system, or - A SOL is reached on any other adjacent system in the Transmission model that is not on the study path and the distribution factor is 5% or greater . |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780001417 | One calendar day after its determination for TTCs used in hourly and daily ATC calculations. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780001422 | The model utilizes data and assumptions consistent with the time period being studied and that meets the following criteria: |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001423 | Includes at least: |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780001438 | Except where otherwise specified within MOD-029-1, adjust base case generation and Load levels within the updated power flow model to determine the TTC (maximum flow or reliability limit) that can be simulated on the ATC Path while at the same time satisfying all planning criteria contingencies as follows: |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780001439 | When modeling normal conditions, all Transmission Elements will be modeled at or below 100% of their continuous rating. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780001456 | The criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates that are to be considered in Available Flowgate Capability (AFC) calculations. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001458 | Define if the source used for AFC calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 12100000 | NPCC-ON |  | NPCC-US
1 | 79780001463 | For hourly AFC, once per hour. Transmission Service Providers are allowed up to 175 hours per calendar year during which calculations are not required to be performed, despite a change in a calculated value identified in the AFC equation. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 101000000 | NPCC-ON |  | NPCC-US
1 | 79780001468 | Include Flowgates used in the AFC process based, at a minimum, on the following criteria: |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780001469 | Results of a first Contingency transfer analysis for ATC Paths internal to a Transmission Operator’s system up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an OTDF of at least 5% and within the Transmission Operator’s system are included as Flowgates. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780001470 | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Special Protection Systems. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 21110000 | NPCC-ON |  | NPCC-US
1 | 79780001473 | Use first Contingency criteria consistent with those first Contignency criteria used in planning of operations for the applicable time periods, including use of Special Protection Systems. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 21210000 | NPCC-ON |  | NPCC-US
1 | 79780001477 | The coordination of the limiting Element/Contingency combination is not already addressed through a different methodology, and -Any generator within the Transmission Service Provider’s area has at least a 5% Power Transfer Distribution Factor (PTDF) or Outage Transfer Distribution Factor (OTDF) impact on the Flowgate when delivered to the aggregate load of its own area, or -A transfer from any Balancing Area within the Transmission Service Provider’s area to a Balancing Area adjacent has at least a 5% PTDF or OTDF impact on the Flowgate. -The Transmission Operator may utilize distribution factors less than 5% if desired. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 21410000 | NPCC-ON |  | NPCC-US
1 | 79780001483 | If notified of a change in the Rating by the Transmission Owner that would affect the TFC of a flowgate used in the AFC process, the TFC should be updated within seven calendar days of the notification. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 25100000 | NPCC-ON |  | NPCC-US
1 | 79780001486 | Contains generation Facility Ratings, such as generation maximum and minimum output levels, specified by the Generator Owners of the Facilities within the model. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780001493 | Use the models provided by the Transmission Operator. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780001497 | The impact of firm Network Integration Transmission Service, including the impacts of generation to load, in the model referenced in R5.2 for the Transmission Service Provider’s area, based on: |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780001498 | Load forecast for the time period being calculated, including Native Load and Network Service load |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 61100000 | NPCC-ON |  | NPCC-US
1 | 79780001501 | Load forecast for the time period being calculated, including Native Load and Network Service load |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 62100000 | NPCC-ON |  | NPCC-US
1 | 79780001509 | The impact of all confirmed non-firm Point-to-Point Transmission Service expected to be scheduled for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780001519 | The criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates that are to be considered in Available Flowgate Capability (AFC) calculations. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001521 | Define if the source used for AFC calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 12100000 | NPCC-ON |  | NPCC-US
1 | 79780001526 | For hourly AFC, once per hour. Transmission Service Providers are allowed up to 175 hours per calendar year during which calculations are not required to be performed, despite a change in a calculated value identified in the AFC equation. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 101000000 | NPCC-ON |  | NPCC-US
1 | 79780001531 | Include Flowgates used in the AFC process based, at a minimum, on the following criteria: |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780001532 | Results of a first Contingency transfer analysis for ATC Paths internal to a Transmission Operator’s system up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an OTDF of at least 5% and within the Transmission Operator’s system are included as Flowgates. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780001533 | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Special Protection Systems. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21110000 | NPCC-ON |  | NPCC-US
1 | 79780001537 | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Special Protection Systems. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21210000 | NPCC-ON |  | NPCC-US
1 | 79780001542 | The coordination of the limiting Element/Contingency combination is not already addressed through a different methodology, and - Any generator within the Transmission Service Provider’s area has at least a 5% Power Transfer Distribution Factor (PTDF) or Outage Transfer Distribution Factor (OTDF) impact on the Flowgate when delivered to the aggregate load of its own area, or - A transfer from any Balancing Area within the Transmission Service Provider’s area to a Balancing Area adjacent has at least a 5% PTDF or OTDF impact on the Flowgate. - The Transmission Operator may utilize distribution factors less than 5% if desired. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21410000 | NPCC-ON |  | NPCC-US
1 | 79780001548 | If notified of a change in the Rating by the Transmission Owner that would affect the TFC of a flowgate used in the AFC process, the TFC should be updated within seven calendar days of the notification. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 25100000 | NPCC-ON |  | NPCC-US
1 | 79780001551 | Contains generation Facility Ratings, such as generation maximum and minimum output levels, specified by the Generator Owners of the Facilities within the model. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780001558 | Use the models provided by the Transmission Operator. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780001562 | The impact of firm Network Integration Transmission Service, including the impacts of generation to load, in the model referenced in R5.2 for the Transmission Service Provider’s area, based on: |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780001563 | Load forecast for the time period being calculated, including Native Load and Network Service load |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 61100000 | NPCC-ON |  | NPCC-US
1 | 79780001566 | Load forecast for the time period being calculated, including Native Load and Network Service load |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 62100000 | NPCC-ON |  | NPCC-US
1 | 79780001574 | The impact of all confirmed non-firm Point-to-Point Transmission Service expected to be scheduled for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780001587 | Incorporate the NPIRs into their operating analyses of the electric system. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2008-11-26 |  | 2010-03-31 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780001595 | Administrative elements: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2008-11-26 |  | 2010-03-31 |  |  |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780001596 | Definitions of key terms used in the agreement. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 91100000 | NPCC-ON |  | NPCC-US
1 | 79780001601 | Identification of parameters, limits, configurations, and operatingscenarios included in the NPIRs and, as applicable, procedures forproviding any specific data not provided within the agreement. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 92100000 | NPCC-ON |  | NPCC-US
1 | 79780001605 | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 93100000 | NPCC-ON |  | NPCC-US
1 | 79780001613 | Provisions for communications between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of terms. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 94100000 | NPCC-ON |  | NPCC-US
1 | 79780001621 | Positions that have the primary responsibility, either directly or through communications with others, for the real-time operation of the interconnected Bulk Electric System. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-03-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780001624 | A set of training program objectives must be defined, based on NERC and Regional Reliability Organization standards, entity operating procedures, and applicable regulatory requirements. These objectives shall reference the knowledge and competencies needed to apply those standards, procedures, and requirements to normal, emergency, and restoration conditions for the Transmission Operator and Balancing Authority operating positions. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-03-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780001630 | Positions that have the primary responsibility, either directly or through communications with others, for the real-time operation of the interconnected Bulk Electric System. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2012-09-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001640 | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall create a list of BES company-specific reliability-related tasks performed by its System Operators. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | M1.1 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection its company-specific reliability-related task list, with the date of the last review and/or revision, as specified in R1.1. | 2013-04-01 |  | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001641 | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall update its list of BES company-specific reliability-related tasks performed by its System Operators each calendar year to identify new or modified tasks for inclusion in training. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2013-04-01 |  | 2016-06-30 |  |  |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780001646 | Within six months of a modification of the BES company-specific reliability-related tasks, each Reliability Coordinator, Balancing Authority and Transmission Operator shall verify each of its System Operator’s capabilities to perform the new or modified tasks. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2013-04-01 |  | 2016-06-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780001648 | Each Reliability Coordinator, Balancing Authority and Transmission Operator that has operational authority or control over Facilities with established IROLs or has established operating guides or protection systems to mitigate IROL violations shall provide each System Operator with emergency operations training using simulation technology such as a simulator, virtual technology, or other technology that replicates the operational behavior of the BES during normal and emergency conditions. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2014-04-01 |  | 2016-06-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780001651 | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2013-03-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780001654 | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2013-03-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780001658 | Each Generator Operator shall notify its Transmission Operator in advance of changes in generation or operating conditions that could require changes in the Transmission Operator’s protection systems. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2013-03-31 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780001662 | Location, monitoring and recording requirements, including the following: |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001663 | Criteria for equipment location (e.g., by voltage, geographic area, station size, etc.). |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780001666 | Location, monitoring and recording requirements, including the following: |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780001667 | Criteria for equipment location (e.g., by voltage, geographic area, station size, etc.). |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780001670 | Three phase to neutral voltages. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 21310000 | NPCC-ON |  | NPCC-US
1 | 79780001676 | Recording duration requirements. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 22100000 | NPCC-ON |  | NPCC-US
1 | 79780001680 | Location, monitoring and recording requirements including the following: |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780001681 | Criteria for equipment location giving consideration to the following: &lt;br/&gt; - Site(s) in or near major load centers &lt;br/&gt; - Site(s) in or near major generation clusters &lt;br/&gt;- Site(s) in or near major voltage sensitive areas &lt;br/&gt; - Site(s) on both sides of major transmission interfaces&lt;br/&gt;- A major transmission junction&lt;br/&gt;- Elements associated with Interconnection Reliability Operating Limits &lt;br/&gt;- Major EHV interconnections between control areas&lt;br/&gt;- Coordination with neighboring regions within the interconnection |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 31100000 | NPCC-ON |  | NPCC-US
1 | 79780001684 | Voltage, current and frequency. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 31310000 | NPCC-ON |  | NPCC-US
1 | 79780001687 | Capability for continuous recording for devices installed after January 1, 2009. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 32100000 | NPCC-ON |  | NPCC-US
1 | 79780001690 | Criteria for events that require the collection of data from DMEs. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780001699 | The Protection Systems to be reviewed and analyzed for Misoperations (due to theirpotential impact on BES reliability). |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001728 | Maintenance and testing intervals and their basis. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2007-06-18 |  | 2011-09-25 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001731 | Evidence Protection System devices were maintained and tested within the defined intervals. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2007-06-18 |  | 2011-09-25 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780001734 | Requirements for coordination of UFLS programs within the subregions, Regional Reliability Organization and, where appropriate, among Regional Reliability Organizations. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001736 | Frequency set points. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  |  | 12100000 | NPCC-ON |  | NPCC-US
1 | 79780001746 | A review of the frequency set points and timing, and |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  |  | 14100000 | NPCC-ON |  | NPCC-US
1 | 79780001756 | A description of the event including initiating conditions. |  | DP, LSE, TO, TOP |  | DP | [5 empty] | LSE | [9 empty] | TO | TOP |  |  |  | 2007-06-18 |  | 2013-09-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001762 | This assessment shall include, but is not limited to: |  | DP, LSE, TO, TOP |  | DP | [5 empty] | LSE | [9 empty] | TO | TOP |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001763 | Coordination of the UVLS programs with other protection and control systems in the Region and with other Regional Reliability Organizations, as appropriate. |  | DP, LSE, TO, TOP |  | DP | [5 empty] | LSE | [9 empty] | TO | TOP |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780001768 | The UVLS system identification which shall include but is not limited to: |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2021-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001769 | Relays. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2021-03-31 |  |  |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780001780 | Description of the process for submitting a proposed SPS for Regional Reliability Organization review. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001791 | Design Objectives — Contingencies and system conditions for which the SPS was designed, |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001798 | Identification of group conducting the assessment and the date the assessment was performed. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780001813 | SPS identification shall include but is not limited to: |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001814 | Relays. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780001825 | Internal Clocks in DME devices shall be synchronized to within 2 milliseconds or less of Universal Coordinated Time scale (UTC) |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2022-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001829 | Type of DME (sequence of event recorder, fault recorder, or dynamic disturbance recorder). |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2022-06-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780001840 | Maintenance and testing intervals and their basis. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2022-06-30 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780001843 | Owner and operator of the UVLS program. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001851 | Size and location of customer load, or percent of connected load, to be interrupted. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001858 | A description of the event including initiating conditions. |  | DP, LSE, TOP |  | DP | [5 empty] | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001865 | Set transmission line relays so they do not operate at or below 150% of the highest seasonal Facility Rating of a circuit, for the available defined loading duration nearest 4 hours (expressed in amperes). |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001869 | Set the maximum torque angle (MTA) to 90 degrees or the highest supported by the manufacturer. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  |  | 20300000 | NPCC-ON |  | NPCC-US
1 | 79780001875 | An infinite source (zero source impedance) with a 1.00 per unit bus voltage at each end of the line. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780001885 | The Planning Coordinator shall have a process to determine the facilities that are critical to the reliability of the Bulk Electric System. |  | PCPA | [9 empty] | PA | [12 empty] | 2011-11-17 |  | 2012-06-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780001886 | This process shall consider input from adjoining Planning Coordinators and affected Reliability Coordinators. |  | PCPA | [9 empty] | PA | [12 empty] | 2011-11-17 |  | 2012-06-30 |  |  |  | 31100000 | NPCC-ON |  | NPCC-US
1 | 79780001899 | For a generator outage, the Generator Operator shall notify and coordinate with the Transmission Operator. The Transmission Operator shall notify the Reliability Coordinator and other affected Transmission Operators, and coordinate the impact of removing the Bulk Electric System facility. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-11-20 |  |  |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780001909 | Changes in real output capabilities. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2009-12-01 |  |  |  | 141000000 | NPCC-ON |  | NPCC-US
1 | 79780001913 | Changes in transmission facility status. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-12-01 |  |  |  | 161000000 | NPCC-ON |  | NPCC-US
1 | 79780001932 | Changes in real output capabilities. |  | GOP | [5 empty] | GOP | [16 empty] | 2009-12-02 |  | 2011-10-19 |  |  |  | 141000000 | NPCC-ON |  | NPCC-US
1 | 79780001936 | Changes in transmission facility status. |  | TOP | [18 empty] | TOP |  |  |  | 2009-12-02 |  | 2011-10-19 |  |  |  | 161000000 | NPCC-ON |  | NPCC-US
1 | 79780001950 | Each Generator Operator shall provide outage information daily to its Transmission Operator for scheduled generator outages planned for the next day (any foreseen outage of a generator greater than 50 MW). The Transmission Operator shall establish the outage reporting requirements. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-09-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001957 | Each Generator Operator shall provide outage information daily to its Transmission Operator for scheduled generator outages planned for the next day (any foreseen outage of a generator greater than 50 MW). The Transmission Operator shall establish the outage reporting requirements. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-05-23 |  | 2017-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001969 | Equipment ratings. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-01-21 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780001981 | Monitoring and controlling voltage levels and real and reactive power flows. |  | TOP | [18 empty] | TOP |  |  |  | 2009-01-22 |  | 2017-03-31 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780001986 | Each Reliability Coordinator shall identify the data requirements from the list in Attachment 1-TOP-005-0 “Electric System Reliability Data” and any additional operating information requirements relating to operation of the bulk power system within the Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780001991 | Each Reliability Coordinator shall identify the data requirements from the list in Attachment 1-TOP-005-0 “Electric System Reliability Data” and any additional operating information requirements relating to operation of the bulk power system within the Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2009-05-13 |  | 2011-05-25 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002004 | Each Generator Operator shall inform its Host Balancing Authority and the Transmission Operator of all generation resources available for use. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2011-09-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002013 | Each Generator Operator shall inform its Host Balancing Authority and the Transmission Operator of all generation resources available for use. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-05-23 |  | 2017-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002034 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002037 | Cover critical system conditions and study years as deemed appropriate by the entity performing the study. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780002048 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780002049 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780002055 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002058 | Cover critical system conditions and study years as deemed appropriate by the entity performing the study. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780002069 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780002070 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780002076 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002079 | Be performed and evaluated only for those Category B contingencies that would produce the more severe System results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780002094 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780002095 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780002101 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002104 | Be performed and evaluated only for those Category B contingencies that would produce the more severe System results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780002119 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780002120 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780002126 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002129 | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780002144 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780002145 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780002151 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002154 | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780002169 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780002170 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780002176 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002179 | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780002191 | Current year: |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002192 | Winter. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780002200 | Security assessments. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780002207 | Electric Demand and Net Energy for Load (actual and projected demands and Net Energy for Load, forecast methodologies, forecast assumptions and uncertainties, and treatment of Demand-Side Management.) |  | RRO | [14 empty] | RRO | [9 empty] | 2009-04-15 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002220 | Each Transmission Operator shall maintain a list of generators in its area that are exempt from following a voltage or Reactive Power schedule. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-09-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780002225 | When notified of the loss of an automatic voltage regulator control, the Transmission Operator shall direct the Generator Operator to maintain or change either its voltage schedule or its Reactive Power schedule. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-09-30 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780002229 | Each Transmission Operator shall disperse and locate the reactive resources so that the resources can be applied effectively and quickly when Contingencies occur. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-09-30 |  |  |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780002236 | Each Transmission Operator shall maintain a list of generators in its area that are exempt from following a voltage or Reactive Power schedule. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-05-21 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780002241 | When notified of the loss of an automatic voltage regulator control, the Transmission Operator shall direct the Generator Operator to maintain or change either its voltage schedule or its Reactive Power schedule. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-05-21 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780002245 | Each Transmission Operator shall disperse and locate the reactive resources so that the resources can be applied effectively and quickly when Contingencies occur. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-05-21 |  |  |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780002248 | When a generator’s automatic voltage regulator is out of service, the Generator Operator shall use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780002251 | A status or capability change on any generator Reactive Power resource, including the status of each automatic voltage regulator and power system stabilizer and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780002254 | For generator step-up transformers and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: |  | GO | [22 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780002255 | Tap settings. |  | GO | [22 empty] | 2007-08-02 |  | 2008-08-26 |  |  |  | 41100000 | NPCC-ON |  | NPCC-US
1 | 79780002260 | If the Generator Operator can’t comply with the Transmission Operator’s specifications, the Generator Operator shall notify the Transmission Operator and shall provide the technical justification. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780002263 | When a generator’s automatic voltage regulator is out of service, the Generator Operator shall use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2009-05-13 |  | 2010-09-15 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780002266 | A status or capability change on any generator Reactive Power resource, including the status of each automatic voltage regulator and power system stabilizer and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2009-05-13 |  | 2010-09-15 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780002269 | For generator step-up transformers and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: |  | GO | [22 empty] | 2009-05-13 |  | 2010-09-15 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780002270 | Tap settings. |  | GO | [22 empty] | 2009-05-13 |  | 2010-09-15 |  |  |  | 41100000 | NPCC-ON |  | NPCC-US
1 | 79780002275 | If the Generator Operator can’t comply with the Transmission Operator’s specifications, the Generator Operator shall notify the Transmission Operator and shall provide the technical justification. |  | GOP | [5 empty] | GOP | [16 empty] | 2009-05-13 |  | 2010-09-15 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780002278 | When a generator’s automatic voltage regulator is out of service, the Generator Operator shall use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2010-09-16 |  | 2013-06-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780002281 | A status or capability change on any generator Reactive Power resource, including the status of each automatic voltage regulator and power system stabilizer and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2010-09-16 |  | 2013-06-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780002284 | For generator step-up transformers and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: |  | GO | [22 empty] | 2010-09-16 |  | 2013-06-30 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780002285 | Tap settings. |  | GO | [22 empty] | 2010-09-16 |  | 2013-06-30 |  |  |  | 41100000 | NPCC-ON |  | NPCC-US
1 | 79780002290 | If the Generator Operator can’t comply with the Transmission Operator’s specifications, the Generator Operator shall notify the Transmission Operator and shall provide the technical justification. |  | GOP | [5 empty] | GOP | [16 empty] | 2010-09-16 |  | 2013-06-30 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780002293 | When a generator’s automatic voltage regulator is out of service, the Generator Operator shall use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780002296 | A status or capability change on any generator Reactive Power resource, including the status of each automatic voltage regulator and power system stabilizer and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780002299 | For generator step-up transformers and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: |  | GO | [22 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780002300 | Tap settings. |  | GO | [22 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 41100000 | NPCC-ON |  | NPCC-US
1 | 79780002305 | If the Generator Operator can’t comply with the Transmission Operator’s specifications, the Generator Operator shall notify the Transmission Operator and shall provide the technical justification. |  | GOP | [5 empty] | GOP | [16 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780002335 | The Interconnection-wide Transmission Loading Relief (TLR) procedure for use in the Eastern Interconnection provided in Attachment 1-IRO-006-4. The TLR procedure alone is an inappropriate and ineffective tool to mitigate an IROL violation due to the time required to implement the procedure. Other acceptable and more effective procedures to mitigate actual IROL violations include: reconfiguration, redispatch, or load shedding. |  | RC | [11 empty] | RC | [10 empty] | 2009-12-10 |  | 2011-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002347 | Electric Demand and Net Energy for Load (actual and projected demands and Net Energy for Load, forecast methodologies, forecast assumptions and uncertainties, and treatment of Demand-Side Management.) |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002355 | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002357 | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 12100000 | NPCC-ON |  | NPCC-US
1 | 79780002366 | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780002371 | The cyber security policy addresses the requirements in Standards CIP-002-2 through CIP-009-2, including provision for emergency situations. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002375 | The senior manager shall be identified by name, title, and date of designation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780002380 | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780002384 | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP-002-2, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780002388 | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780002389 | Personnel shall be identified by name, title, and the information for which they are responsible for authorizing access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 51100000 | NPCC-ON |  | NPCC-US
1 | 79780002396 | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780002398 | The proper use of Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 22100000 | NPCC-ON |  | NPCC-US
1 | 79780002404 | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780002408 | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780002411 | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002418 | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780002423 | The processes for access request and authorization. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 25100000 | NPCC-ON |  | NPCC-US
1 | 79780002429 | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780002432 | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780002438 | The Responsible Entity shall ensure that all documentation required by Standard CIP-005-2 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005-2 at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780002442 | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002451 | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780002459 | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780002463 | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002467 | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780002471 | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780002474 | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780002477 | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780002478 | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-2 Requirement R5. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 51100000 | NPCC-ON |  | NPCC-US
1 | 79780002482 | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 52100000 | NPCC-ON |  | NPCC-US
1 | 79780002486 | Each password shall be a minimum of six characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 53100000 | NPCC-ON |  | NPCC-US
1 | 79780002490 | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780002496 | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780002500 | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780002506 | Procedures to characterize and classify events as reportable Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002514 | Specify the required actions in response to events or conditions of varying duration and severity that would activate the recovery plan(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002524 | Incorporate the NPIRs into their operating analyses of the electric system. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780002532 | Administrative elements: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2014-01-21 |  |  |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780002533 | Definitions of key terms used in the agreement. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2014-01-21 |  |  |  | 91100000 | NPCC-ON |  | NPCC-US
1 | 79780002538 | Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the agreement. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 92100000 | NPCC-ON |  | NPCC-US
1 | 79780002542 | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 93100000 | NPCC-ON |  | NPCC-US
1 | 79780002550 | Provisions for communications between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of terms. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 94100000 | NPCC-ON |  | NPCC-US
1 | 79780002557 | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780002561 | Communications protocols to be used during emergencies. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780002568 | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780002573 | Strategies for system restoration that are coordinated with the Reliability Coordinator’s high level strategy for restoring the Interconnection. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002583 | System restoration plan including coordination with the Reliability Coordinator and Generator Operators included in the restoration plan. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  |  | 101000000 | NPCC-ON |  | NPCC-US
1 | 79780002593 | Testing records shall include at a minimum: name of the Blackstart Resource, unit tested, date of the test, duration of the test, time required to start the unit, an indication of any testing requirements not met under Requirement R9. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-05-23 |  | 2019-03-31 |  |  |  | 161000000 | NPCC-ON |  | NPCC-US
1 | 79780002596 | System restoration plan including coordination with the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-05-23 |  | 2019-03-31 |  |  |  | 171000000 | NPCC-ON |  | NPCC-US
1 | 79780002601 | If there are no changes to the previously submitted restoration plan, the Transmission Operator shall confirm annually on a predetermined schedule to its Reliability Coordinator that it has reviewed its restoration plan and no changes were necessary. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780002603 | Each Transmission Operator shall submit its revised restoration plan to its Reliability Coordinator for approval within the same 90 calendar day period. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780002606 | The capability of Blackstart Resources to meet the Real and Reactive Power requirements of the Cranking Paths and the dynamic capability to supply initial Loads. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780002612 | The frequency of testing such that each Blackstart Resource is tested at least once every three calendar years. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780002614 | The ability to start the unit when isolated with no support from the BES or when designed to remain energized without connection to the remainder of the System. |  | TOP | [18 empty] | TOP |  |  |  | 2013-07-01 |  | 2019-03-31 |  |  |  | 92100000 | NPCC-ON |  | NPCC-US
1 | 79780002618 | A description of the high level strategy to be employed during restoration events for restoring the Interconnection including minimum criteria for meeting the objectives of the Reliability Coordinator’s restoration plan. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002628 | Each Reliability Coordinator shall request each Transmission Operator identified in its restoration plan and each Generator Operator identified in the Transmission Operators’ restoration plans to participate in a drill, exercise, or simulation at least every two calendar years. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  |  | 101000000 | NPCC-ON |  | NPCC-US
1 | 79780002632 | If the Reliability Coordinator finds conflicts between its restoration plans and any of its neighbors, the conflicts shall be resolved in 30 calendar days. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780002634 | The Reliability Coordinator shall determine whether the Transmission Operator’s restoration plan is coordinated and compatible with the Reliability Coordinator’s restoration plan and other Transmission Operators’ restoration plans within its Reliability Coordinator Area. The Reliability Coordinator shall approve or disapprove, with stated reasons, the Transmission Operator’s submitted restoration plan within 30 calendar days following the receipt of the restoration plan from the Transmission Operator. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780002639 | The coordination role of the Reliability Coordinator. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780002651 | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002654 | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780002656 | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780002659 | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780002661 | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780002664 | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-2 Requirement R5. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 51100000 | NPCC-ON |  | NPCC-US
1 | 79780002667 | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 52100000 | NPCC-ON |  | NPCC-US
1 | 79780002670 | Each password shall be a minimum of six characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 53100000 | NPCC-ON |  | NPCC-US
1 | 79780002676 | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780002678 | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780002683 | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780002690 | Be applicable for developing SOLs used in the planning horizon. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002694 | In the pre-contingency state and with all Facilities in service, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect expected system conditions and shall reflect changes to system topology such as Facility outages. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780002700 | Single line to ground or three-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 22100000 | NPCC-ON |  | NPCC-US
1 | 79780002702 | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 23100000 | NPCC-ON |  | NPCC-US
1 | 79780002703 | Planned or controlled interruption of electric supply to customers (load shedding), the planned removal from service of certain generators, and/or the curtailment of contracted Firm (non-recallable reserved) electric power Transfers. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 26100000 | NPCC-ON |  | NPCC-US
1 | 79780002708 | Study model (must include at least the entire Planning Authority Area as well as the critical modeling details from other Planning Authority Areas that would impact the Facility or Facilities under study). |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780002712 | Each adjacent Planning Authority and each Planning Authority that indicated it has a reliability-related need for the methodology. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780002714 | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002716 | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | 12100000 | NPCC-ON |  | NPCC-US
1 | 79780002725 | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780002730 | The cyber security policy addresses the requirements in Standards CIP-002-3 through CIP-009-3, including provision for emergency situations. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002734 | The senior manager shall be identified by name, title, and date of designation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780002739 | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780002743 | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP-002-3, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780002747 | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780002748 | Personnel shall be identified by name, title, and the information for which they are responsible for authorizing access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  |  |  | 51100000 | NPCC-ON |  | NPCC-US
1 | 79780002755 | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2012-12-11 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780002757 | The proper use of Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2012-12-11 |  |  |  | 22100000 | NPCC-ON |  | NPCC-US
1 | 79780002763 | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2012-12-11 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780002767 | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2012-12-11 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780002770 | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002777 | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780002782 | The processes for access request and authorization. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2011-02-01 |  |  |  | 25100000 | NPCC-ON |  | NPCC-US
1 | 79780002788 | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780002791 | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780002797 | The Responsible Entity shall ensure that all documentation required by Standard CIP-005-3 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005-3 at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780002801 | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002807 | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-09-30 |  |  |  | 16100000 | NPCC-ON |  | NPCC-US
1 | 79780002812 | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780002820 | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780002824 | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002828 | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780002832 | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780002835 | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780002838 | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780002839 | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-3 Requirement R5. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 51100000 | NPCC-ON |  | NPCC-US
1 | 79780002843 | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 52100000 | NPCC-ON |  | NPCC-US
1 | 79780002847 | Each password shall be a minimum of six characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 53100000 | NPCC-ON |  | NPCC-US
1 | 79780002851 | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780002857 | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780002861 | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780002867 | Procedures to characterize and classify events as reportable Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002875 | Specify the required actions in response to events or conditions of varying duration and severity that would activate the recovery plan(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002893 | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002898 | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780002899 | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780002914 | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002919 | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780002920 | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780002936 | Processes to ensure and document that all Cyber Assets within an Electronic Security Perimeter also reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002941 | Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780002942 | Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780002945 | Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780002947 | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780002958 | Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780002959 | Processes to ensure and document that all Cyber Assets within an Electronic Security Perimeter also reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002971 | Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780002973 | Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780002976 | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780002989 | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780002993 | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  |  | 16100000 | NPCC-ON |  | NPCC-US
1 | 79780002995 | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780002997 | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780003010 | Hourly values for at least the next 48 hours. |  | TSP | [20 empty] | TSP | M2.1 - There has been at least 48 hours of hourly values calculated at all times. | 2010-09-16 | [5 empty] | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780003014 | Information describing how the selected methodology (or methodologies) has been implemented, in such detail that, given the same information used by the Transmission Service Provider, the results of the ATC or AFC calculations can be validated. |  | TSP | [20 empty] | TSP |  | 2010-09-16 | [5 empty] | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780003019 | How confirmed Transmission reservations, expected Interchange and internal counterflow are addressed in firm and non-firm ATC or AFC calculations. |  | TSP | [20 empty] | TSP |  | 2011-04-01 | [5 empty] | 32100000 | NPCC-ON |  | NPCC-US
1 | 79780003022 | The criteria used to determine when an outage that is in effect part of a day impacts a daily calculation. |  | TSP | [20 empty] | TSP |  | 2011-04-01 | [5 empty] | 36100000 | NPCC-ON |  | NPCC-US
1 | 79780003028 | Each Planning Coordinator associated with the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-09-16 | [5 empty] | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780003030 | Hourly values, once per hour. Transmission Service Providers are allowed up to 175 hours per calendar year during which calculations are not required to be performed, despite a change in a calculated value identified in the ATC equation. |  | TSP | [20 empty] | TSP |  | 2010-09-16 | [5 empty] | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780003032 | The Transmission Service Provider shall make its own current data available, in the format maintained by the Transmission Service Provider, for up to 13 months into the future (subject to confidentiality and security requirements). |  | TSP | [20 empty] | TSP |  | 2010-09-16 | [5 empty] | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780003036 | If the Transmission Service Provider uses the data requested in its transfer or Flowgate capability calculations, it shall make the data used available |  | TSP | [20 empty] | TSP |  | 2011-04-01 | [5 empty] | 91100000 | NPCC-ON |  | NPCC-US
1 | 79780003045 | The model utilizes data and assumptions consistent with the time period being studied and that meets the following criteria: |  | TOP | [18 empty] | TOP |  |  | M1.1. Production shall be in the same form and format used by the Transmission Operator to calculate the TTC, as required in R1. | 2010-09-16 |  | 2017-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780003054 | Includes at least: |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780003057 | The Transmission Operator area. Equivalent representation of radial lines and facilities 161kV or below is allowed. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 11110000 | NPCC-ON |  | NPCC-US
1 | 79780003061 | Except where otherwise specified within MOD-029-1, adjust base case generation and Load levels within the updated power flow model to determine the TTC (maximum flow or reliability limit) that can be simulated on the ATC Path while at the same time satisfying all planning criteria contingencies as follows: |  | TOP | [18 empty] | TOP |  |  |  | 2010-09-16 |  | 2017-03-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780003068 | When modeling normal conditions, all Transmission Elements will be modeled at or below 100% of their continuous rating. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780003075 | List of required data and information needed by the Reliability Coordinator to support Real-Time Monitoring, Operational Planning Analyses, and Real-Time Assessments. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2017-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780003160 | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780003163 | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780003171 | The processes for access request and authorization. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | 25100000 | NPCC-ON |  | NPCC-US
1 | 79780003174 | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780003177 | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780003180 | The Responsible Entity shall ensure that all documentation required by Standard CIP-005-3 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005-3 at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780003184 | A Balancing Authority may elect to fulfill its Contingency Reserve obligations by participating as a member of a Reserve Sharing Group. In such cases, the Reserve Sharing Group shall have the same responsibilities and obligations as each Balancing Authority with respect to monitoring and meeting the requirements of Standard BAL-002. |  | RSG | [16 empty] | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780003186 | The minimum reserve requirement for the group. |  | RRO, RSG | [14 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780003193 | As a minimum, the Balancing Authority or Reserve Sharing Group shall carry at least enough Contingency Reserve to cover the most severe single contingency. All Balancing Authorities and Reserve Sharing Groups shall review, no less frequently than annually, their probable contingencies to determine their prospective most severe single contingencies. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780003195 | A Balancing Authority shall return its ACE to zero if its ACE just prior to the Reportable Disturbance was positive or equal to zero. For negative initial ACE values just prior to the Disturbance, the Balancing Authority shall return ACE to its pre-Disturbance value. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780003198 | The Reserve Sharing Group reviews group ACE (or equivalent) and demonstrates compliance to the DCS. To be in compliance, the group ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. |  | RSG | [16 empty] | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780003201 | The Contingency Reserve Restoration Period begins at the end of the Disturbance Recovery Period. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780003207 | Each Balancing Authority, by the end of the next business day, shall agree with its Adjacent Balancing Authorities to: |  | BA | BA | [21 empty] | 2011-04-01 |  | 2018-12-31 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780003208 | The hourly values of Net Interchange Schedule. |  | BA | BA | [21 empty] | 2011-04-01 |  | 2018-12-31 |  |  |  | 41100000 | NPCC-ON |  | NPCC-US
1 | 79780003219 | The cyber security policy addresses the requirements in Standards CIP-002-4 through CIP-009-4, including provision for emergency situations. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780003223 | The senior manager shall be identified by name, title, and date of designation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780003228 | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780003232 | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP-002-4, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780003236 | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780003237 | Personnel shall be identified by name, title, and the information for which they are responsible for authorizing access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 51100000 | NPCC-ON |  | NPCC-US
1 | 79780003244 | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2012-12-11 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780003246 | The proper use of Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2012-12-11 |  |  |  | 22100000 | NPCC-ON |  | NPCC-US
1 | 79780003252 | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2012-12-11 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780003256 | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2012-12-11 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780003259 | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780003266 | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780003271 | The processes for access request and authorization. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 25100000 | NPCC-ON |  | NPCC-US
1 | 79780003277 | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780003280 | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780003286 | The Responsible Entity shall ensure that all documentation required by Standard CIP-005-4 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005-4 at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780003290 | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780003296 | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 16100000 | NPCC-ON |  | NPCC-US
1 | 79780003301 | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780003309 | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780003313 | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780003317 | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780003321 | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780003324 | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780003327 | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780003328 | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-4 Requirement R5. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 51100000 | NPCC-ON |  | NPCC-US
1 | 79780003332 | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 52100000 | NPCC-ON |  | NPCC-US
1 | 79780003336 | Each password shall be a minimum of six characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 53100000 | NPCC-ON |  | NPCC-US
1 | 79780003340 | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780003346 | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780003350 | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780003356 | Procedures to characterize and classify events as reportable Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780003364 | Specify the required actions in response to events or conditions of varying duration and severity that would activate the recovery plan(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780003376 | Loading all available generating capacity. |  | BA | BA | [21 empty] | 2011-01-10 |  | 2012-09-12 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780003383 | Manually shed firm load without delay to return its ACE to zero; and |  | BA | BA | [21 empty] | 2011-01-10 |  | 2012-09-12 |  |  |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780003387 | The deficient Load-Serving Entity shall request its Reliability Coordinator to initiate an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0. |  | LSE | [7 empty] | LSE | [14 empty] | 2011-01-10 |  | 2012-09-12 |  |  |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780003408 | Evaluation of the reliability impact of the new facilities and their connections on the interconnected transmission systems. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [14 empty] | 2011-01-10 |  | 2015-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780003421 | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780003453 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780003456 | Cover critical system conditions and study years as deemed appropriate by the entity performing the study. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780003467 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780003468 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780003474 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780003477 | Be performed and evaluated only for those Category B contingencies that would produce the more severe System results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780003492 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780003493 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780003499 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780003502 | Be performed and evaluated only for those Category B contingencies that would produce the more severe System results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780003517 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780003518 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780003524 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780003527 | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780003542 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780003543 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780003549 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780003552 | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780003567 | The Sending Balancing Authority and Receiving Balancing Authority shall agree on Interchange as received from the Interchange Authority, including: |  | BA | BA | [21 empty] | 2011-04-01 |  | 2014-09-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780003568 | Interchange Schedule start and end time. |  | BA | BA | [21 empty] | 2011-04-01 |  | 2014-09-30 |  |  |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780003592 | Each Reliability Coordinator shall identify the data requirements from the list in Attachment 1-TOP-005-0 “Electric System Reliability Data” and any additional operating information requirements relating to operation of the bulk power system within the Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780003602 | Each Transmission Operator shall maintain a list of generators in its area that are exempt from following a voltage or Reactive Power schedule. |  | TOP | [18 empty] | TOP |  |  |  | 2011-01-10 |  | 2013-12-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780003607 | When notified of the loss of an automatic voltage regulator control, the Transmission Operator shall direct the Generator Operator to maintain or change either its voltage schedule or its Reactive Power schedule. |  | TOP | [18 empty] | TOP |  |  |  | 2011-01-10 |  | 2013-12-31 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780003611 | Each Transmission Operator shall disperse and locate the reactive resources so that the resources can be applied effectively and quickly when Contingencies occur. |  | TOP | [18 empty] | TOP |  |  |  | 2011-01-10 |  | 2013-12-31 |  |  |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780003624 | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780003627 | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780003635 | The processes for access request and authorization. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 25100000 | NPCC-ON |  | NPCC-US
1 | 79780003638 | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780003641 | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780003644 | The Responsible Entity shall ensure that all documentation required by Standard CIP-005 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005 at least annually. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780003655 | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780003658 | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780003666 | The processes for access request and authorization. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 25100000 | NPCC-ON |  | NPCC-US
1 | 79780003669 | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780003672 | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780003675 | The Responsible Entity shall ensure that all documentation required by Standard CIP-005-2 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005-2 at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780003697 | Each Generator Operator with generation facilities operating in an Interconnection shall ensure that those generation facilities are included within the metered boundaries of a Balancing Authority Area. |  | GOP | [5 empty] | GOP | [18 empty] | 2008-04-15 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780003698 | Balancing Authorities that share a tie shall ensure Tie Line MW metering is telemetered to both control centers, and emanates from a common, agreed-upon source using common primary metering equipment. Balancing Authorities shall ensure that megawatt-hour data is telemetered or reported at the end of each hour. |  | BA | BA | [23 empty] | 2008-04-15 |  |  |  | 121000000 | NPCC-ON |  | NPCC-US
1 | 79780003701 | Each Balancing Authority shall provide redundant and independent frequency metering equipment that shall automatically activate upon detection of failure of the primary source. This overall installation shall provide a minimum availability of 99.95%. |  | BA | BA | [23 empty] | 2008-04-15 |  |  |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780003702 | Balancing Authorities with a high voltage direct current (HVDC) link to another Balancing Authority connected asynchronously to their Interconnection may choose to omit the Interchange Schedule related to the HVDC link from the ACE equation if it is modeled as internal generation or load. |  | BA | BA | [23 empty] | 2008-04-15 |  |  |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780003705 | Maintenance and testing intervals and their basis. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2011-09-26 |  | 2012-03-13 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780003707 | Evidence Protection System devices were maintained and tested within the defined intervals. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2011-09-26 |  | 2012-03-13 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780003718 | The Balancing Authority may change its Frequency Bias Setting, and the method used to determine the setting, whenever any of the factors used to determine the current bias value change. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2009-06-28 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780003721 | The Balancing Authority may use a fixed Frequency Bias value which is based on a fixed, straight-line function of Tie Line deviation versus Frequency Deviation. The Balancing Authority shall determine the fixed value by observing and averaging the Frequency Response for several Disturbances during on-peak hours. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2009-06-28 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780003723 | Fixed schedules for Jointly Owned Units mandate that Balancing Authority (A) that contains the Jointly Owned Unit must incorporate the respective share of the unit governor droop response for any Balancing Authorities that have fixed schedules (B and C). See the diagram below. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2009-06-28 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780003724 | Balancing Authorities that do not serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of its estimated maximum generation level in the coming year per 0.1 Hz change. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2009-06-28 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780003787 | Changes in real output capabilities. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-10-20 |  | 2012-09-12 |  |  |  | 141000000 | NPCC-ON |  | NPCC-US
1 | 79780003789 | Changes in transmission facility status. |  | TOP | [18 empty] | TOP |  |  |  | 2011-10-20 |  | 2012-09-12 |  |  |  | 161000000 | NPCC-ON |  | NPCC-US
1 | 79780003811 | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780003822 | For a generator outage, the Generator Operator shall notify and coordinate with the Transmission Operator. The Transmission Operator shall notify the Reliability Coordinator and other affected Transmission Operators, and coordinate the impact of removing the Bulk Electric System facility. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-11-21 |  | 2017-03-31 |  |  |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780003836 | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780003840 | Communications protocols to be used during emergencies. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780003841 | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780003852 | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780003857 | Communications protocols to be used during emergencies. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780003858 | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780003902 | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780003907 | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780003908 | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780003923 | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780003927 | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2011-05-18 |  |  |  | 16100000 | NPCC-ON |  | NPCC-US
1 | 79780003929 | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780003931 | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780003961 | Information describing how the selected methodology has been implemented, in such detail that, given the same information used by the Transmission Operator, the results of the TTC calculations can be validated. |  | TSP | [20 empty] | TSP |  | 2013-09-27 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780003966 | Define if the source used for Available Transfer Capability (ATC) calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation |  | TSP | [20 empty] | TSP |  | 2013-10-01 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 15100000 | NPCC-ON |  | NPCC-US
1 | 79780003973 | Modeling data and topology of its Reliability Coordinator’s area of responsibility. Equivalent representation of radial lines and facilities 161 kV or below is allowed. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780003977 | For TTCs, use the following (as well as any other values and additional parameters as specified in the ATCID): |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780003978 | Expected generation and Transmission outages, additions, and retirements, included as specified in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2013-10-01 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 31100000 | NPCC-ON |  | NPCC-US
1 | 79780003984 | Use all Contingencies meeting the criteria described in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780003988 | At least once within the seven calendar days prior to the specified period for TTCs used in hourly and daily ATC calculations. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780003992 | &lt;p&gt;Determine the incremental Transfer Capability for each ATC Path by increasing generation and/or decreasing load within the source Balancing Authority area and decreasing generation and/or increasing load within the sink Balancing Authority area until either:&lt;br/&gt;- A System Operating Limit is reached on the Transmission Service Provider’s system, or&lt;br/&gt;- A SOL is reached on any other adjacent system in the Transmission model that is not on the study path and the distribution factor is 5% or greater .&lt;/p&gt; &lt;p&gt;Footnote: The Transmission operator may honor distribution factors less than 5% if desired.&lt;/p&gt; &lt;p/&gt; |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780003997 | One calendar day after its determination for TTCs used in hourly and daily ATC calculations. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780004036 | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780004045 | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004047 | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780004049 | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 16100000 | NPCC-ON |  | NPCC-US
1 | 79780004062 | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004066 | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 16100000 | NPCC-ON |  | NPCC-US
1 | 79780004068 | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780004070 | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780004075 | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator, and all other potentially affected Balancing Authorities and Transmission Operators through predetermined communication paths of any condition that could threaten the reliability of its area or when firm load shedding is anticipated. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004078 | Maintenance and testing intervals and their basis. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2012-03-14 |  | 2013-11-24 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004080 | Evidence Protection System devices were maintained and tested within the defined intervals. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2012-03-14 |  | 2013-11-24 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780004090 | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780004092 | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780004096 | Communications protocols to be used during emergencies. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780004118 | Each Generator Operator with generation facilities operating in an Interconnection shall ensure that those generation facilities are included within the metered boundaries of a Balancing Authority Area. |  | GOP | [5 empty] | GOP | [16 empty] | 2012-09-13 |  | 2018-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004119 | Balancing Authorities that share a tie shall ensure Tie Line MW metering is telemetered to both control centers, and emanates from a common, agreed-upon source using common primary metering equipment. Balancing Authorities shall ensure that megawatt-hour data is telemetered or reported at the end of each hour. |  | BA | BA | [21 empty] | 2012-09-13 |  | 2018-12-31 |  |  |  | 121000000 | NPCC-ON |  | NPCC-US
1 | 79780004122 | Each Balancing Authority shall provide redundant and independent frequency metering equipment that shall automatically activate upon detection of failure of the primary source. This overall installation shall provide a minimum availability of 99.95%. |  | BA | BA | [21 empty] | 2012-09-13 |  | 2018-12-31 |  |  |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780004123 | Balancing Authorities with a high voltage direct current (HVDC) link to another Balancing Authority connected asynchronously to their Interconnection may choose to omit the Interchange Schedule related to the HVDC link from the ACE equation if it is modeled as internal generation or load. |  | BA | BA | [21 empty] | 2012-09-13 |  | 2018-12-31 |  |  |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780004133 | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780004136 | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780004142 | Communications protocols to be used during emergencies. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780004163 | Changes in real output capabilities. |  | GOP | [5 empty] | GOP | [16 empty] | 2012-09-13 |  | 2017-03-31 |  |  |  | 141000000 | NPCC-ON |  | NPCC-US
1 | 79780004165 | Changes in transmission facility status. |  | TOP | [18 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  |  | 161000000 | NPCC-ON |  | NPCC-US
1 | 79780004187 | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004197 | Loading all available generating capacity. |  | BA | BA | [21 empty] | 2012-09-13 |  | 2017-03-31 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780004204 | Manually shed firm load without delay to return its ACE to zero; and |  | BA | BA | [21 empty] | 2012-09-13 |  | 2017-03-31 |  |  |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780004205 | The deficient Load-Serving Entity shall request its Reliability Coordinator to initiate an Energy Emergency Alert in accordance with Attachment 1-EOP-002 “Energy Emergency Alerts.” |  | LSE | [7 empty] | LSE | [14 empty] | 2012-09-13 |  | 2017-03-31 |  |  |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780004218 | Incorporate the NPIRs into their operating analyses of the electric system. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP | M4.1 The NPIRs have been incorporated into the current operating analysis of the electric system. (Requirement 4.1) | 2013-04-01 |  | 2015-12-31 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780004222 | Administrative elements: |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2014-01-21 |  |  |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780004227 | Definitions of key terms used in the agreement. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2014-01-21 |  |  |  | 91100000 | NPCC-ON |  | NPCC-US
1 | 79780004230 | Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the agreement. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 92100000 | NPCC-ON |  | NPCC-US
1 | 79780004232 | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 93100000 | NPCC-ON |  | NPCC-US
1 | 79780004239 | Provisions for communications between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of terms. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 94100000 | NPCC-ON |  | NPCC-US
1 | 79780004253 | Incorporate the NPIRs into their operating analyses of the electric system. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780004257 | Administrative elements: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780004285 | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. |  | GOP | [5 empty] | GOP | [16 empty] | 2013-04-01 |  | 2015-05-28 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780004288 | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. |  | GOP | [5 empty] | GOP | [16 empty] | 2013-04-01 |  | 2015-05-28 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780004290 | Each Generator Operator shall notify its Transmission Operator in advance of changes in generation or operating conditions that could require changes in the Transmission Operator’s Protection Systems. |  | GOP | [5 empty] | GOP | [16 empty] | 2013-04-01 |  | 2015-05-28 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780004293 | Maintenance and testing intervals and their basis. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2013-11-25 |  | 2021-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004295 | Evidence Protection System devices were maintained and tested within the defined intervals. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2013-11-25 |  | 2021-03-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780004319 | Each Transmission Operator shall maintain a list of generators in its area that are exempt from following a voltage or Reactive Power schedule. |  | TOP | [18 empty] | TOP |  |  |  | 2013-06-20 |  | 2014-09-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780004324 | When notified of the loss of an automatic voltage regulator control, the Transmission Operator shall direct the Generator Operator to maintain or change either its voltage schedule or its Reactive Power schedule. |  | TOP | [18 empty] | TOP |  |  |  | 2013-06-20 |  | 2014-09-30 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780004328 | Each Transmission Operator shall disperse and locate the reactive resources so that the resources can be applied effectively and quickly when Contingencies occur. |  | TOP | [18 empty] | TOP |  |  |  | 2013-06-20 |  | 2014-09-30 |  |  |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780004337 | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004342 | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 12100000 | NPCC-ON |  | NPCC-US
1 | 79780004345 | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780004360 | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. |  | GOP | [5 empty] | GOP | [18 empty] | 2016-01-26 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780004368 | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:&lt;br/&gt;&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780004373 | The proper use of Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:&lt;br/&gt;&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 22100000 | NPCC-ON |  | NPCC-US
1 | 79780004375 | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:&lt;br/&gt;&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780004377 | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:&lt;br/&gt;&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780004384 | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2014-02-03 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780004389 | The proper use of Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 22100000 | NPCC-ON |  | NPCC-US
1 | 79780004391 | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2014-02-03 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780004393 | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2014-02-03 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780004400 | When a generator’s automatic voltage regulator is out of service, the Generator Operator shall use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2013-07-01 |  | 2014-09-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780004403 | A status or capability change on any generator Reactive Power resource, including the status of each automatic voltage regulator and power system stabilizer and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2013-07-01 |  | 2014-09-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780004406 | For generator step-up transformers and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: |  | GO | [22 empty] | 2013-07-01 |  | 2014-09-30 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780004407 | Tap settings. |  | GO | [22 empty] | 2013-07-01 |  | 2014-09-30 |  |  |  | 41100000 | NPCC-ON |  | NPCC-US
1 | 79780004412 | If the Generator Operator can’t comply with the Transmission Operator’s specifications, the Generator Operator shall notify the Transmission Operator and shall provide the technical justification. |  | GOP | [5 empty] | GOP | [16 empty] | 2013-07-01 |  | 2014-09-30 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780004443 | A Balancing Authority may elect to fulfill its Contingency Reserve obligations by participating as a member of a Reserve Sharing Group. In such cases, the Reserve Sharing Group shall have the same responsibilities and obligations as each Balancing Authority with respect to monitoring and meeting the requirements of Standard BAL-002. |  | RSG | [16 empty] | RSG | [7 empty] | 2017-02-17 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004447 | The minimum reserve requirement for the group. |  | RRO, RSG | [14 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780004450 | As a minimum, the Balancing Authority or Reserve Sharing Group shall carry at least enough Contingency Reserve to cover the most severe single contingency. All Balancing Authorities and Reserve Sharing Groups shall review, no less frequently than annually, their probable contingencies to determine their prospective most severe single contingencies. |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2017-02-17 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780004452 | A Balancing Authority shall return its ACE to zero if its ACE just prior to the Reportable Disturbance was positive or equal to zero. For negative initial ACE values just prior to the Disturbance, the Balancing Authority shall return ACE to its pre-Disturbance value. |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2017-02-17 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780004453 | The Reserve Sharing Group reviews group ACE (or equivalent) and demonstrates compliance to the DCS. To be in compliance, the group ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. |  | RSG | [16 empty] | RSG | [7 empty] | 2017-02-17 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780004455 | The Contingency Reserve Restoration Period begins at the end of the Disturbance Recovery Period. |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2017-02-17 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780004463 | Each Generator Operator shall inform its Host Balancing Authority and the Transmission Operator of all generation resources available for use. |  | GOP | [5 empty] | GOP | [18 empty] | 2015-03-18 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004559 | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780004560 | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004565 | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 12100000 | NPCC-ON |  | NPCC-US
1 | 79780004586 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  | M2. The Planning Authority and Transmission Planner shall have evidence it reported&lt;br/&gt;documentation of results of its reliability assessments and corrective plans per Reliability&lt;br/&gt;Standard TPL-002-1_R3. |  |  | 2014-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004588 | Cover critical system conditions and study years as deemed appropriate by the entity performing the study. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780004596 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780004600 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780004628 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004632 | Be performed and evaluated only for those Category B contingencies that would produce the more severe System results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780004642 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780004646 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780004653 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004657 | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780004667 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780004671 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780004676 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004679 | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780004693 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004697 | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780004707 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780004711 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780004717 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004720 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780004728 | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780004735 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780004741 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004744 | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780004754 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004763 | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780004798 |  |  | BA | BA | [23 empty] | 2006-05-01 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780004799 |  |  | BA | BA | [23 empty] | 2006-05-01 |  |  |  | 41100000 | NPCC-ON |  | NPCC-US
1 | 79780004809 |  |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004820 |  |  | BA | BA | [23 empty] | 2006-11-01 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780004825 |  |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004829 |  |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 101000000 | NPCC-ON |  | NPCC-US
1 | 79780004838 |  |  | BA | BA | [23 empty] | 2006-11-01 |  |  |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780004845 |  |  | BA | BA | [23 empty] | 2006-11-01 |  |  |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780004855 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780004862 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780004866 |  |  | RC | [11 empty] | RC | [12 empty] | 2007-01-01 |  |  |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780004887 |  |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2007-05-02 |  |  |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780004892 |  |  | TOP | [18 empty] | TOP | [5 empty] | 2007-05-02 |  |  |  | 95100000 | NPCC-ON |  | NPCC-US
1 | 79780004903 |  |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-04-07 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004908 |  |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-08-01 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004909 |  |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-08-01 |  |  |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780004922 |  |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-10-07 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004925 |  |  | BA, PSE | BA | [9 empty] | PSE | [13 empty] | 2007-01-01 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004929 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780004936 |  |  | PSE | [10 empty] | PSE | [13 empty] | 2006-11-01 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004938 |  |  | BA, PSE | BA | [9 empty] | PSE | [13 empty] | 2006-11-01 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780004941 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004947 |  |  | TSP | [20 empty] | TSP |  |  |  | 2007-01-01 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780004954 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780004961 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004962 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780004972 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780004975 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004976 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780004980 |  |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780004986 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780004991 |  |  | PSE | [10 empty] | PSE | [13 empty] | 2007-01-01 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780005026 |  |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780005054 |  |  | RC | [11 empty] | RC | [12 empty] | 2005-08-08 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780005063 |  |  | RC | [11 empty] | RC | [12 empty] | 2006-09-29 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780005072 |  |  | RC | [11 empty] | RC | [12 empty] | 2006-09-29 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780005080 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2006-11-02 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780005081 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2006-11-02 |  |  |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780005088 |  |  | PCPA, RRO | [9 empty] | PA |  |  |  |  | RRO | [9 empty] | 2006-11-02 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780005097 |  |  | GOP | [5 empty] | GOP | [18 empty] | 2007-01-01 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780005100 |  |  | GOP | [5 empty] | GOP | [18 empty] | 2007-01-01 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780005104 |  |  | GOP | [5 empty] | GOP | [18 empty] | 2007-01-01 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780005108 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780005110 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 12100000 | NPCC-ON |  | NPCC-US
1 | 79780005115 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780005122 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 16100000 | NPCC-ON |  | NPCC-US
1 | 79780005129 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2006-05-01 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780005138 |  |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2006-05-01 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780005139 |  |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2006-05-01 |  |  |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780005161 |  |  | GOP | [5 empty] | GOP | [18 empty] | 2007-08-07 |  |  |  | 141000000 | NPCC-ON |  | NPCC-US
1 | 79780005165 |  |  | TOP | [18 empty] | TOP | [5 empty] | 2007-08-07 |  |  |  | 161000000 | NPCC-ON |  | NPCC-US
1 | 79780005184 |  |  | GOP | [5 empty] | GOP | [18 empty] | 2007-01-01 |  |  |  | 141000000 | NPCC-ON |  | NPCC-US
1 | 79780005187 |  |  | TOP | [18 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 161000000 | NPCC-ON |  | NPCC-US
1 | 79780005206 |  |  | TOP | [18 empty] | TOP | [5 empty] | 2005-04-01 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780005213 |  |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780005219 |  |  | GOP | [5 empty] | GOP | [18 empty] | 2007-01-01 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780005238 |  |  | TOP | [18 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780005241 |  |  | GOP | [5 empty] | GOP | [18 empty] | 2007-01-01 |  |  |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780005272 | The cyber security policy addresses the requirements in Standards CIP-002-3 through CIP-009-3, including provision for emergency situations. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780005275 | The senior manager shall be identified by name, title, and date of designation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780005278 | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780005282 | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP-002-3, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780005283 | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780005286 | Personnel shall be identified by name, title, and the information for which they are responsible for authorizing access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | 51100000 | NPCC-ON |  | NPCC-US
1 | 79780005296 | The cyber security policy addresses the requirements in Standards CIP-002-4 through CIP-009-4, including provision for emergency situations. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780005299 | The senior manager shall be identified by name, title, and date of designation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780005302 | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780005306 | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP-002-4, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780005307 | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780005310 | Personnel shall be identified by name, title, and the information for which they are responsible for authorizing access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 51100000 | NPCC-ON |  | NPCC-US
1 | 79780005322 | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780005325 | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780005327 | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780005330 | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780005332 | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780005335 | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-3 Requirement R5. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 51100000 | NPCC-ON |  | NPCC-US
1 | 79780005338 | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 52100000 | NPCC-ON |  | NPCC-US
1 | 79780005341 | Each password shall be a minimum of six characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 53100000 | NPCC-ON |  | NPCC-US
1 | 79780005347 | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780005349 | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780005354 | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780005365 | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780005368 | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780005370 | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780005373 | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780005375 | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780005378 | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-4 Requirement R5. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 51100000 | NPCC-ON |  | NPCC-US
1 | 79780005381 | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 52100000 | NPCC-ON |  | NPCC-US
1 | 79780005384 | Each password shall be a minimum of six characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 53100000 | NPCC-ON |  | NPCC-US
1 | 79780005390 | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780005392 | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780005397 | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780005599 | Be applicable for developing SOLs used in the planning horizon. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780005603 | In the pre-contingency state and with all Facilities in service, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect expected system conditions and shall reflect changes to system topology such as Facility outages. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780005618 | Study model (must include at least the entire Planning Authority Area as well as the critical modeling details from other Planning Authority Areas that would impact the Facility or Facilities under study). |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780005625 | Each adjacent Planning Authority and each Planning Authority that indicated it has a reliability-related need for the methodology. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780005630 | Be applicable for developing SOLs used in the operations horizon. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780005634 | In the pre-contingency state, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect current or expected system conditions and shall reflect changes to system topology such as Facility outages. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780005636 | Single line to ground or 3-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 22100000 | NPCC-ON |  | NPCC-US
1 | 79780005641 | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 23100000 | NPCC-ON |  | NPCC-US
1 | 79780005646 | Study model (must include at least the entire Reliability Coordinator Area as well as the critical modeling details from other Reliability Coordinator Areas that would impact the Facility or Facilities under study.) |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780005649 | This process shall address the need to modify these limits, to modify the list of limits, and to modify the list of associated multiple contingencies. |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 33100000 | NPCC-ON |  | NPCC-US
1 | 79780005655 | Each adjacent Reliability Coordinator and each Reliability Coordinator that indicated it has a reliability-related need for the methodology. |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780005656 | Each adjacent Reliability Coordinator and each Reliability Coordinator that indicated it has a reliability-related need for the methodology. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780005661 | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Remedial Action Schemes) and system loading. |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780005683 | The criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates that are to be considered in Available Flowgate Capability (AFC) calculations. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780005685 | Define if the source used for AFC calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation. |  | TSP | [20 empty] | TSP |  | 2017-04-01 | [5 empty] | 12100000 | NPCC-ON |  | NPCC-US
1 | 79780005690 | Include Flowgates used in the AFC process based, at a minimum, on the following criteria |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780005691 | Results of a first Contingency transfer analysis for ATC Paths internal to a Transmission Operator’s system up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an OTDF of at least 5% and within the Transmission Operator’s system are included as Flowgates. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780005708 | If notified of a change in the Rating by the Transmission Owner that would affect the TFC of a flowgate used in the AFC process, the TFC should be updated within seven calendar days of the notification. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 25100000 | NPCC-ON |  | NPCC-US
1 | 79780005711 | Contains generation Facility Ratings, such as generation maximum and minimum output levels, specified by the Generator Owners of the Facilities within the model. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780005718 | Use the models provided by the Transmission Operator. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780005722 | The impact of firm Network Integration Transmission Service, including the impacts of generation to load, in the model referenced in R5.2 for the Transmission Service Provider’s area, based on: |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780005723 | Load forecast for the time period being calculated, including Native Load and Network Service load |  | TSP | [20 empty] | TSP |  | 2017-04-01 | [5 empty] | 61100000 | NPCC-ON |  | NPCC-US
1 | 79780005726 | Load forecast for the time period being calculated, including Native Load and Network Service load |  | TSP | [20 empty] | TSP |  | 2017-04-01 | [5 empty] | 62100000 | NPCC-ON |  | NPCC-US
1 | 79780005734 | The impact of all confirmed non-firm Point-to-Point Transmission Service expected to be scheduled for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780005744 | For hourly AFC, once per hour. Transmission Service Providers are allowed up to 175 hours per calendar year during which calculations are not required to be performed, despite a change in a calculated value identified in the AFC equation. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 101000000 | NPCC-ON |  | NPCC-US
1 | 79780005751 | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780005753 | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12100000 | NPCC-ON |  | NPCC-US
1 | 79780005760 | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780005763 | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780005765 | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12100000 | NPCC-ON |  | NPCC-US
1 | 79780005772 | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780005780 | Incorporate the NPIRs into their operating analyses of the electric system. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780005788 | Administrative elements: (Retirement approved by FERC effective January 21, 2014.) | [26 empty] | 2014-11-13 |  |  |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780005789 | Definitions of key terms used in the agreement. (Retirement approved by FERC effective January 21, 2014.) | [26 empty] | 2014-11-13 |  |  |  | 91100000 | NPCC-ON |  | NPCC-US
1 | 79780005794 | Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the agreement. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 92100000 | NPCC-ON |  | NPCC-US
1 | 79780005798 | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 93100000 | NPCC-ON |  | NPCC-US
1 | 79780005806 | Provisions for communications between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of terms. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 94100000 | NPCC-ON |  | NPCC-US
1 | 79780005812 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780005815 | Cover critical system conditions and study years as deemed appropriate by the entity performing the study. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780005826 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780005827 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780005833 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780005836 | Be performed and evaluated only for those Category B contingencies that would produce the more severe System results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780005851 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780005852 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780005858 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780005861 | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780005876 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780005877 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780005883 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780005886 | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780005898 | Description of the process for submitting a proposed RAS for Regional Reliability Organization review. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780005917 | Identification of group conducting the assessment and the date the assessment was performed. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780005923 | Design Objectives — Contingencies and system conditions for which the RAS was designed, |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780005934 | RAS identification shall include but is not limited to: |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-01-25 |  | 2021-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780005935 | Relays. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-04-01 |  | 2021-03-31 |  |  |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780005947 | Owner and operator of the UVLS program. | [26 empty] | 2014-11-13 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780005955 | Size and location of customer load, or percent of connected load, to be interrupted. | [26 empty] | 2014-11-13 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780005963 | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. |  | GOP | [5 empty] | GOP | [16 empty] | 2016-01-25 |  | 2015-05-28 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780005966 | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. |  | GOP | [5 empty] | GOP | [16 empty] | 2016-01-25 |  | 2015-05-28 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780005970 | Each Generator Operator shall notify its Transmission Operator in advance of changes in generation or operating conditions that could require changes in the Transmission Operator’s Protection Systems. |  | GOP | [5 empty] | GOP | [16 empty] | 2016-01-25 |  | 2015-05-28 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780006023 | The model utilizes data and assumptions consistent with the time period being studied and that meets the following criteria: |  | TOP | [18 empty] | TOP |  |  | &lt;p&gt;M1.1. Production shall be in the same form and format used by the Transmission Operator to calculate the TTC, as required in R1. (R1)&lt;/p&gt; | 2016-01-25 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006024 | Includes at least: |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780006025 | The Transmission Operator area. Equivalent representation of radial lines and facilities 161kV or below is allowed. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 11110000 | NPCC-ON |  | NPCC-US
1 | 79780006042 | Except where otherwise specified within MOD-029-2, adjust base case generation and Load levels within the updated power flow model to determine the TTC (maximum flow or reliability limit) that can be simulated on the ATC Path while at the same time satisfying all planning criteria contingencies as follows: |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006115 | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-05-29 |  | 2020-09-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006118 | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority.&lt;br/&gt;• Requirement R3.1 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-05-29 |  | 2020-09-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780006122 | Each Generator Operator shall notify its Transmission Operator in advance of changes in generation or operating conditions that could require changes in the Transmission Operator’s Protection Systems. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-05-29 |  | 2020-09-30 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780006160 | Personnel &amp;amp; training (CIP-004); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006169 | Cyber security awareness; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2016-06-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006173 | One or more processes to identify, classify, and respond to Cyber Security Incidents. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.1. An example of evidence may include, but is not limited to, dated documentation of Cyber Security Incident response plan(s) that include the process to identify, classify, and respond to Cyber Security Incidents. | 2014-02-03 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006177 | Test each Cyber Security Incident response plan(s) at least once every 15 calendar months: &lt;br/&gt;• By responding to an actual Reportable Cyber Security Incident; &lt;br/&gt;• With a paper drill or tabletop exercise of a Reportable Cyber Security Incident; or&lt;br/&gt;• With an operational exercise of a Reportable Cyber Security Incident. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.1. Examples of evidence may include, but are not limited to, dated evidence of a lessons-learned report that includes a summary of the test or a compilation of notes, logs, and communication resulting from the test. Types of exercises may include discussion or operations based exercises. | 2017-07-01 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006180 | No later than 90 calendar days after completion of a Cyber Security Incident response plan(s) test or actual Reportable Cyber Security Incident response: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.1. An example of evidence may include, but is not limited to, all of the following:&lt;br/&gt;1. Dated documentation of post incident(s) review meeting notes or follow-up report showing lessons learned associated with the Cyber Security Incident response plan(s) test or actual Reportable Cyber Security Incident response or dated documentation stating there were no lessons learned;&lt;br/&gt;2. Dated and revised Cyber Security Incident response plan showing any changes based on the lessons learned; and&lt;br/&gt;3. Evidence of plan update distribution including, but not limited to:&lt;br/&gt;• Emails; &lt;br/&gt;• USPS or other mail service; &lt;br/&gt;• Electronic distribution system; or &lt;br/&gt;• Training sign-in sheets. | 2014-02-03 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780006181 | 3.1.1. Document any lessons learned or document the absence of any lessons learned; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | 31100000 | NPCC-ON |  | NPCC-US
1 | 79780006185 | Update the Cyber Security Incident response plan(s); and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | 32100000 | NPCC-ON |  | NPCC-US
1 | 79780006187 | Where technically feasible, enable only logical network accessible ports that have been determined to be needed by the Responsible Entity, including port ranges or services where needed to handle dynamic ports. If a device has no provision for disabling or restricting logical ports on the device then those ports that are open are deemed needed. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006189 | A patch management process for tracking, evaluating, and installing cyber security patches for applicable Cyber Assets. The tracking portion shall include the identification of a source or sources that the Responsible Entity tracks for the release of cyber security patches for applicable Cyber Assets that are updateable and for which a patching source exists. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006193 | Deploy method(s) to deter, detect, or prevent malicious code. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780006196 | Log events at the BES Cyber System level (per BES Cyber System capability) or at the Cyber Asset level (per Cyber Asset capability) for identification of, and after-the-fact investigations of, Cyber Security Incidents that includes, as a minimum, each of the following types of events: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780006200 | Have a method(s) to enforce authentication of interactive user access, where technically feasible. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780006210 | Detected malicious code from Part 4.1; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 42100000 | NPCC-ON |  | NPCC-US
1 | 79780006212 | Password length that is, at least, the lesser of eight characters or the maximum length supported by the Cyber Asset; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 55100000 | NPCC-ON |  | NPCC-US
1 | 79780006214 | Method(s) to identify information that meets the definition of BES Cyber System Information. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006216 | Prior to the release for reuse of applicable Cyber Assets that contain BES Cyber System Information (except for reuse within other systems identified in the “Applicable Systems” column), the Responsible Entity shall take action to prevent the unauthorized retrieval of BES Cyber System Information from the Cyber Asset data storage media. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006218 | Develop a baseline configuration, individually or by group, which shall include the following items: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006219 | Operating system(s) (including version) or firmware where no independent operating system exists; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780006227 | Prior to the change, determine required cyber security controls in CIP-005 and CIP-007 that could be impacted by the change; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 14100000 | NPCC-ON |  | NPCC-US
1 | 79780006231 | Prior to implementing any change in the production environment, test the changes in a test environment or test the changes in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration to ensure that required cyber security controls in CIP-005 and CIP-007 are not adversely affected; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 15100000 | NPCC-ON |  | NPCC-US
1 | 79780006233 | Monitor at least once every 35 calendar days for changes to the baseline configuration (as described in Requirement R1, Part 1.1). Document and investigate detected unauthorized changes. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006234 | At least once every 15 calendar months, conduct a paper or active vulnerability assessment. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780006236 | Perform an active vulnerability assessment in a test environment, or perform an active vulnerability assessment in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration of the BES Cyber System in a production environment; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 32100000 | NPCC-ON |  | NPCC-US
1 | 79780006240 | All applicable Cyber Assets connected to a network via a routable protocol shall reside within a defined ESP. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.1 An example of evidence may include, but is not limited to, a list of all ESPs with all uniquely identifiable applicable Cyber Assets connected via a routable protocol within each ESP. | 2014-02-03 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006245 | Utilize an Intermediate System such that the Cyber Asset initiating Interactive Remote Access does not directly access an applicable Cyber Asset. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.1 Examples of evidence may include, but are not limited to, network diagrams or architecture documents. | 2014-02-03 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006248 | Define operational or procedural controls to restrict physical access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 1.1 An example of evidence may include, but is not limited to, documentation that operational or procedural controls exist. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006257 | Require continuous escorted access of visitors (individuals who are provided access but are not authorized for unescorted physical access) within each Physical Security Perimeter, except during CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 2.1 An example of evidence may include, but is not limited to, language in a visitor control program that requires continuous escorted access of visitors within Physical Security Perimeters and additional evidence to demonstrate that the process was implemented, such as visitor logs. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006260 | Maintenance and testing of each Physical Access Control System and locally mounted hardware or devices at the Physical Security Perimeter at least once every 24 calendar months to ensure they function properly. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 3.1 An example of evidence may include, but is not limited to, a maintenance and testing program that provides for testing each Physical Access Control System and locally mounted hardware or devices associated with each applicable Physical Security Perimeter at least once every 24 calendar months and additional evidence to demonstrate that this testing was done, such as dated maintenance records, or other documentation showing testing and maintenance has been performed on each applicable device or system at least once every 24 calendar months. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780006261 | Conditions for activation of the recovery plan(s). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006266 | Test each of the recovery plans referenced in Requirement R1 at least once every 15 calendar months:&lt;br/&gt;• By recovering from an actual incident;&lt;br/&gt;• With a paper drill or tabletop exercise; or&lt;br/&gt;• With an operational exercise. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006269 | No later than 90 calendar days after completion of a recovery plan test or actual recovery: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780006270 | Document any lessons learned associated with a recovery plan test or actual recovery or document the absence of any lessons learned; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 31100000 | NPCC-ON |  | NPCC-US
1 | 79780006274 | Update the recovery plan; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 32100000 | NPCC-ON |  | NPCC-US
1 | 79780006276 | Security awareness that, at least once each calendar quarter, reinforces cyber security practices (which may include associated physical security practices) for the Responsible Entity’s personnel who have authorized electronic or authorized unescorted physical access to BES Cyber Systems. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation that the quarterly reinforcement has been provided. Examples of evidence of reinforcement may include, but are not limited to, dated copies of information used to reinforce security awareness, as well as evidence of distribution, such as: &lt;br/&gt;• direct communications (for example, e-mails, memos, computer-based training); or &lt;br/&gt;• indirect communications (for example, posters, intranet, or brochures); or&lt;br/&gt;• management support and reinforcement (for example, presentations or meetings). | 2014-02-03 |  | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006277 | Cyber security policies; | [23 empty] | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. |  |  | 2016-06-30 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780006287 | Training content on: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2014-02-03 |  | 2016-06-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006298 | Process to confirm identity. | [23 empty] | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to confirm identity. |  |  | 2016-06-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780006300 | current residence, regardless of duration; and | [23 empty] | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to perform a seven year criminal history records check. |  |  | 2016-06-30 |  |  |  | 32100000 | NPCC-ON |  | NPCC-US
1 | 79780006305 | Process to authorize based on need, as determined by the Responsible Entity, except for CIP Exceptional Circumstances: | [23 empty] | An example of evidence may include, but is not limited to, dated documentation of the process to authorize electronic access, unescorted physical access in a Physical Security Perimeter, and access to designated storage locations, whether physical or electronic, for BES Cyber System Information. |  |  | 2016-06-30 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780006306 | Electronic access; | [23 empty] | An example of evidence may include, but is not limited to, dated documentation of the process to authorize electronic access, unescorted physical access in a Physical Security Perimeter, and access to designated storage locations, whether physical or electronic, for BES Cyber System Information. |  |  | 2016-06-30 |  |  |  | 41100000 | NPCC-ON |  | NPCC-US
1 | 79780006312 | A process to initiate removal of an individual’s ability for unescorted physical access and Interactive Remote Access upon a termination action, and complete the removals within 24 hours of the termination action (Removal of the ability for access may be different than deletion, disabling, revocation, or removal of all access rights). | [23 empty] | An example of evidence may include, but is not limited to, documentation of all of the following:&lt;br/&gt;1. Dated workflow or sign-off form verifying access removal associated with the termination action; and &lt;br/&gt;2. Logs or other demonstration showing such persons no longer have access. |  |  | 2016-06-30 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780006317 | Identify each of the high impact BES Cyber Systems according to Attachment 1, Section 1, if any, at each asset; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-12-26 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006320 | Review the identifications in Requirement R1 and its parts (and update them if there are changes identified) at least once every 15 calendar months, even if it has no identified items in Requirement R1, and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-12-26 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006322 | The documentation shall contain assumptions used to rate the generator and at least one of the following:&lt;br/&gt;• Design or construction information such as design criteria, ratings provided by equipment manufacturers, equipment drawings and/or specifications, engineering analyses, method(s) consistent with industry standards (e.g. ANSI and IEEE), or an established engineering practice that has been verified by testing or engineering analysis.&lt;br/&gt;• Operational information such as commissioning test results, performance testing or historical performance records, any of which may be supplemented by engineering analyses. |  | GO | [22 empty] | 2011-11-17 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006324 | The methodology used to establish the Ratings of the equipment that comprises the Facility(ies) shall be consistent with at least one of the following:&lt;br/&gt;• Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating.&lt;br/&gt;• One or more industry standards developed through an open process such as Institute of Electrical and Electronic Engineers (IEEE) or International Council on Large Electric Systems (CIGRE).&lt;br/&gt;• A practice that has been verified by testing, performance history or engineering analysis. |  | GO | [22 empty] | 2011-11-17 | [5 empty] | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006326 | Equipment Rating standard(s) used in development of this methodology. |  | GO | [22 empty] | 2013-01-01 | [5 empty] | 22100000 | NPCC-ON |  | NPCC-US
1 | 79780006332 | The scope of equipment addressed shall include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | GO | [22 empty] | 2013-01-01 | [5 empty] | 24100000 | NPCC-ON |  | NPCC-US
1 | 79780006334 | The methodology used to establish the Ratings of the equipment that comprises the Facility shall be consistent with at least one of the following:&lt;br/&gt;• Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating.&lt;br/&gt;• One or more industry standards developed through an open process such as Institute of Electrical and Electronics Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). &lt;br/&gt;• A practice that has been verified by testing, performance history or engineering analysis. |  | TO | [22 empty] | 2011-11-17 | [5 empty] | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780006336 | Equipment Rating standard(s) used in development of this methodology. |  | TO | [22 empty] | 2013-01-01 | [5 empty] | 32100000 | NPCC-ON |  | NPCC-US
1 | 79780006342 | The scope of equipment addressed shall include, but not be limited to, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | TO | [22 empty] | 2013-01-01 | [5 empty] | 34100000 | NPCC-ON |  | NPCC-US
1 | 79780006344 | As scheduled by the requesting entities: |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-11-17 | [5 empty] | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780006345 | Facility Ratings |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-01-01 | [5 empty] | 81100000 | NPCC-ON |  | NPCC-US
1 | 79780006348 | Identity of the existing next most limiting equipment of the Facility |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-01-01 | [5 empty] | 82100000 | NPCC-ON |  | NPCC-US
1 | 79780006350 | Maintain a list of circuits subject to PRC-023-2 per application of Attachment B, including identification of the first calendar year in which any criterion in Attachment B applies. |  | PCPA | [9 empty] | PA | [12 empty] | 2014-01-01 |  | 2014-09-30 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780006353 | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-04-02 |  | 2017-04-01 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006354 | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-11-19 |  | 2017-04-01 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006358 | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-11-19 |  | 2017-04-01 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006359 | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-04-02 |  | 2017-04-01 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780006372 | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [19 empty] | 2015-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006380 | Subsequent risk assessments shall be performed:&lt;br/&gt;• At least once every 30 calendar months for a Transmission Owner that has identified in its previous risk assessment (as verified according to Requirement R2) one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection; or &lt;br/&gt;• At least once every 60 calendar months for a Transmission Owner that has not identified in its previous risk assessment (as verified according to Requirement R2) any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection. |  | TO | [22 empty] | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:&lt;br/&gt;4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an &amp;quot;aggregate weighted value&amp;quot; exceeding 3000 according to the table below. The &amp;quot;aggregate weighted value&amp;quot; for a single station or substation is determined by summing the &amp;quot;weight value per line&amp;quot; shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;Voltage Value of a Line Weight Value per Line&lt;br/&gt;less than 200 kV (not applicable) (not applicable)&lt;br/&gt;200 kV to 299 kV 700&lt;br/&gt;300 kV to 499 kV 1300&lt;br/&gt;500 kV and above 0&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.&lt;br/&gt;4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. &lt;br/&gt;Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006383 | Each Transmission Owner shall select an unaffiliated verifying entity that is either:&lt;br/&gt;• A registered Planning Coordinator, Transmission Planner, or Reliability Coordinator; or&lt;br/&gt;• An entity that has transmission planning or analysis experience. |  | TO | [22 empty] | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:&lt;br/&gt;4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an &amp;quot;aggregate weighted value&amp;quot; exceeding 3000 according to the table below. The &amp;quot;aggregate weighted value&amp;quot; for a single station or substation is determined by summing the &amp;quot;weight value per line&amp;quot; shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;Voltage Value of a Line Weight Value per Line&lt;br/&gt;less than 200 kV (not applicable) (not applicable)&lt;br/&gt;200 kV to 299 kV 700&lt;br/&gt;300 kV to 499 kV 1300&lt;br/&gt;500 kV and above 0&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.&lt;br/&gt;4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. &lt;br/&gt;Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006388 | If a Transmission station or Transmission substation previously identified under Requirement R1 and verified according to Requirement R2 is removed from the identification during a subsequent risk assessment performed according to Requirement R1 or a verification according to Requirement R2, then the Transmission Owner shall, within seven calendar days following the verification or the subsequent risk assessment, notify the Transmission Operator that has operational control of the primary control center of the removal. |  | TO | [22 empty] | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:&lt;br/&gt;4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an &amp;quot;aggregate weighted value&amp;quot; exceeding 3000 according to the table below. The &amp;quot;aggregate weighted value&amp;quot; for a single station or substation is determined by summing the &amp;quot;weight value per line&amp;quot; shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;Voltage Value of a Line Weight Value per Line&lt;br/&gt;less than 200 kV (not applicable) (not applicable)&lt;br/&gt;200 kV to 299 kV 700&lt;br/&gt;300 kV to 499 kV 1300&lt;br/&gt;500 kV and above 0&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.&lt;br/&gt;4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. &lt;br/&gt;Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780006390 | Unique characteristics of the identified and verified Transmission station(s), Transmission substation(s), and primary control center(s); |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:&lt;br/&gt;4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an &amp;quot;aggregate weighted value&amp;quot; exceeding 3000 according to the table below. The &amp;quot;aggregate weighted value&amp;quot; for a single station or substation is determined by summing the &amp;quot;weight value per line&amp;quot; shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;Voltage Value of a Line Weight Value per Line&lt;br/&gt;less than 200 kV (not applicable) (not applicable)&lt;br/&gt;200 kV to 299 kV 700&lt;br/&gt;300 kV to 499 kV 1300&lt;br/&gt;500 kV and above 0&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.&lt;br/&gt;4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. &lt;br/&gt;Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780006394 | Resiliency or security measures designed collectively to deter, detect, delay, assess, communicate, and respond to potential physical threats and vulnerabilities identified during the evaluation conducted in Requirement R4. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:&lt;br/&gt;4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an &amp;quot;aggregate weighted value&amp;quot; exceeding 3000 according to the table below. The &amp;quot;aggregate weighted value&amp;quot; for a single station or substation is determined by summing the &amp;quot;weight value per line&amp;quot; shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;Voltage Value of a Line Weight Value per Line&lt;br/&gt;less than 200 kV (not applicable) (not applicable)&lt;br/&gt;200 kV to 299 kV 700&lt;br/&gt;300 kV to 499 kV 1300&lt;br/&gt;500 kV and above 0&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.&lt;br/&gt;4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. &lt;br/&gt;Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780006400 | Each Transmission Owner and Transmission Operator shall select an unaffiliated third party reviewer from the following:&lt;br/&gt;• An entity or organization with electric industry physical security experience and whose review staff has at least one member who holds either a Certified Protection Professional (CPP) or Physical Security Professional (PSP) certification.&lt;br/&gt;• An entity or organization approved by the ERO.&lt;br/&gt;• A governmental agency with physical security expertise.&lt;br/&gt;• An entity or organization with demonstrated law enforcement, government, or military physical security expertise. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:&lt;br/&gt;4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an &amp;quot;aggregate weighted value&amp;quot; exceeding 3000 according to the table below. The &amp;quot;aggregate weighted value&amp;quot; for a single station or substation is determined by summing the &amp;quot;weight value per line&amp;quot; shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;Voltage Value of a Line Weight Value per Line&lt;br/&gt;less than 200 kV (not applicable) (not applicable)&lt;br/&gt;200 kV to 299 kV 700&lt;br/&gt;300 kV to 499 kV 1300&lt;br/&gt;500 kV and above 0&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.&lt;br/&gt;4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. &lt;br/&gt;Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780006401 | Each Transmission Owner and Transmission Operator shall select an unaffiliated third party reviewer from the following:&lt;br/&gt;• An entity or organization with electric industry physical security experience and whose review staff has at least one member who holds either a Certified Protection Professional (CPP) or Physical Security Professional (PSP) certification.&lt;br/&gt;• An entity or organization approved by the ERO.&lt;br/&gt;• A governmental agency with physical security expertise.&lt;br/&gt;• An entity or organization with demonstrated law enforcement, government, or military physical security expertise. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-02 | [5 empty] | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780006406 | The implementation of the UVLS Program resolves the identified undervoltage issues that led to its development and design. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-11-19 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006411 | Whether its UVLS Program resolved the undervoltage issues associated with the event, and |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-11-19 | [5 empty] | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780006418 | A list of congestion management actions to be implemented, and |  | RC | [11 empty] | RC | [10 empty] | 2011-04-21 |  | 2016-03-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006420 | Notify all Reliability Coordinators in the Eastern Interconnection of the identified TLR level |  | RC | [11 empty] | RC | [10 empty] | 2011-04-21 |  | 2016-03-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780006423 | Each applicable unit’s model shall be verified by the Generator Owner using one or more models acceptable to the Transmission Planner. Verification for individual units less than 20 MVA (gross nameplate rating) in a generating plant (per Section 4.2.1.2, 4.2.2.2, or 4.2.3.2) may be performed using either individual unit or aggregate unit model(s), or both. Each verification shall include the&lt;br/&gt;following: |  | GO | [22 empty] | 2018-07-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following:&lt;br/&gt;4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: &lt;br/&gt;4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).&lt;br/&gt;4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.2 Generation in the Western Interconnection with the following characteristics:&lt;br/&gt;4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).&lt;br/&gt;4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.3 Generation in the ERCOT Interconnection with the following characteristics:&lt;br/&gt;4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).&lt;br/&gt;4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.4 For all Interconnections:&lt;br/&gt;• A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006424 | Documentation demonstrating the applicable unit’s model response matches the recorded response for a voltage excursion from either a staged test or a measured system disturbance, |  | GO | [22 empty] | 2018-07-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following:&lt;br/&gt;4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: &lt;br/&gt;4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).&lt;br/&gt;4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.2 Generation in the Western Interconnection with the following characteristics:&lt;br/&gt;4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).&lt;br/&gt;4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.3 Generation in the ERCOT Interconnection with the following characteristics:&lt;br/&gt;4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).&lt;br/&gt;4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.4 For all Interconnections:&lt;br/&gt;• A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780006430 | The excitation control system or plant volt/var control function model initializes to compute modeling data without error, |  | TP | [19 empty] | TP |  |  | 2014-05-26 |  |  |  | 4.2. Facilities:&lt;br/&gt;For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following:&lt;br/&gt;4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: &lt;br/&gt;4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).&lt;br/&gt;4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.2 Generation in the Western Interconnection with the following characteristics:&lt;br/&gt;4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).&lt;br/&gt;4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.3 Generation in the ERCOT Interconnection with the following characteristics:&lt;br/&gt;4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).&lt;br/&gt;4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.4 For all Interconnections:&lt;br/&gt;• A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780006433 | Each applicable unit’s model shall be verified by the Generator Owner using one or more models acceptable to the Transmission Planner. Verification for individual units rated less than 20 MVA (gross nameplate rating) in a generating plant (per Section 4.2.1.2, 4.2.2.2, or 4.2.3.2) may be performed using either individual unit or aggregate unit model(s) or both. Each verification shall include the following: |  | GO | [22 empty] | 2014-07-01 |  |  |  | 4.2. Facilities&lt;br/&gt;For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred to as an “applicable unit” that meet the following:&lt;br/&gt;4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics:&lt;br/&gt;4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).&lt;br/&gt;4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.2 Generation in the Western Interconnection with the following characteristics:&lt;br/&gt;4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).&lt;br/&gt;4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.3 Generation in the ERCOT Interconnection with the following characteristics:&lt;br/&gt;4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).&lt;br/&gt;4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006434 | &lt;p&gt;Documentation comparing the applicable unit’s MW model response to the recorded MW response for either:&lt;br/&gt;? A frequency excursion from a system disturbance that meets MOD-027 Attachment 1 Note 1 with the applicable unit on-line,&lt;br/&gt;? A speed governor reference change with the applicable unit online, or&lt;br/&gt;? A partial load rejection test,&lt;/p&gt; &lt;p&gt;Footnote: Differences between the control mode tested and the final simulation model must be identified, particularly when analyzing load rejection data. Most controls change gains or have a set point runback which takes effect when the breaker opens. Load or set point controls will also not be in effect once the breaker opens. Some method of accounting for these differences must be presented if the final model is not validated from on-line data under the normal operating conditions under which the model is expected to apply.&lt;/p&gt; &lt;p/&gt; |  | GO | [22 empty] | 2014-07-01 |  |  |  | 4.2. Facilities&lt;br/&gt;For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred to as an “applicable unit” that meet the following:&lt;br/&gt;4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics:&lt;br/&gt;4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).&lt;br/&gt;4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.2 Generation in the Western Interconnection with the following characteristics:&lt;br/&gt;4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).&lt;br/&gt;4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.3 Generation in the ERCOT Interconnection with the following characteristics:&lt;br/&gt;4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).&lt;br/&gt;4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780006439 | The turbine/governor and load control or active power/frequency control function model initializes to compute modeling data without error, |  | TP | [19 empty] | TP |  |  | 2014-05-26 |  |  |  | 4.2. Facilities&lt;br/&gt;For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred to as an “applicable unit” that meet the following:&lt;br/&gt;4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics:&lt;br/&gt;4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).&lt;br/&gt;4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.2 Generation in the Western Interconnection with the following characteristics:&lt;br/&gt;4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).&lt;br/&gt;4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.3 Generation in the ERCOT Interconnection with the following characteristics:&lt;br/&gt;4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).&lt;br/&gt;4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780006442 | Areas of Competency |  | RC | [11 empty] | RC | [9 empty] | M1.1 A list of Real-time operating positions. | 2011-09-15 |  | 2019-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006443 | Resource and demand balancing |  | RC | [11 empty] | RC | [10 empty] | 2012-10-01 |  | 2019-06-30 |  |  |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780006451 | Areas of Competency |  | TOP | [18 empty] | TOP |  |  |  | 2011-09-15 |  | 2019-06-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006452 | Transmission operations |  | TOP | [18 empty] | TOP |  |  |  | 2012-10-01 |  | 2019-06-30 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780006458 | Areas of Competency |  | BA | BA | [21 empty] | 2011-09-15 |  | 2019-06-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780006459 | Resources and demand balancing |  | BA | BA | [21 empty] | 2012-10-01 |  | 2019-06-30 |  |  |  | 31100000 | NPCC-ON |  | NPCC-US
1 | 79780006481 | Less than zero at all times, and |  | BA | BA | [21 empty] | 2014-03-24 |  | 2015-11-12 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780006488 | The location and method of implementation for providing backup functionality for the time it takes to restore the primary control center functionality. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006490 | &lt;p&gt;Tools and applications to ensure that System Operators have situational awareness of the BES.&lt;/p&gt; |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2013-07-01 |  | 2019-03-31 |  |  |  | 12100000 | NPCC-ON |  | NPCC-US
1 | 79780006502 | An update and approval of the Operating Plan for backup functionality shall take place within sixty calendar days of any changes to any part of the Operating Plan described in Requirement R1. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780006503 | The transition time between the simulated loss of primary control center functionality and the time to fully implement the backup functionality. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780006505 | A description of activities designed to mitigate the effects of GMD events on the reliable operation of the interconnected transmission system within the Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2015-04-01 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006507 | Steps or tasks to receive space weather information. |  | TOP | [18 empty] | TOP |  |  |  | 2015-04-01 | [5 empty] | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780006513 | Within its Transmission Operator Area, monitor Facilities and the status of Special Protection Systems, and |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-26 |  | 2018-06-30 |  |  |  | 101000000 | NPCC-ON |  | NPCC-US
1 | 79780006525 | Inform its Planning Coordinator of the need to exceed the stated tolerances or the number of stages as shown in UFLS Attachment C, Table 1 if applicable and |  | DP, DP-UFLS, TO |  | DP | [20 empty] | 2016-01-01 |  | 2020-03-31 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780006529 | Eastern Interconnection – 100 ms |  | DP, DP-UFLS, TO |  | DP | [20 empty] | 2016-01-01 |  | 2020-03-31 |  |  |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780006530 | Design measures to prevent the generating unit from tripping directly or indirectly for underfrequency conditions above the appropriate generator tripping threshold curve in Figure 1. |  | DP-UFLS, GO |  | DP | [20 empty] | 2013-04-29 |  | 2020-03-31 |  |  |  | 151000000 | NPCC-ON |  | NPCC-US
1 | 79780006531 | Set the underfrequency protection to operate at the lowest frequency allowed by the plant design and licensing limitations. |  | DP-UFLS, GO |  | DP | [20 empty] | 2013-04-29 |  | 2020-03-31 |  |  |  | 161000000 | NPCC-ON |  | NPCC-US
1 | 79780006534 | Set the underfrequency protection to operate at as low a frequency as possible in accordance with the plant design and licensing limitations but not greater than 57.8Hz. |  | DP-UFLS, GO |  | DP | [20 empty] | 2013-04-29 |  | 2020-03-31 |  |  |  | 191000000 | NPCC-ON |  | NPCC-US
1 | 79780006537 | For each UFLS relay, including those used for compensatory load shedding, the amount and location of load shed at peak, the corresponding frequency threshold and time delay settings. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2013-04-29 |  | 2020-03-31 |  |  |  | 201000000 | NPCC-ON |  | NPCC-US
1 | 79780006544 | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2014-02-24 |  | 2015-05-28 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006546 | Those islands selected by applying the criteria in Requirement R1, and |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006549 | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-1 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780006552 | Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES |  | PCPA | [9 empty] | PA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  |  | 33100000 | NPCC-ON |  | NPCC-US
1 | 79780006555 | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780006562 | UFLS program, including a schedule for implementation |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 141000000 | NPCC-ON |  | NPCC-US
1 | 79780006565 | Movement of applicable line conductors under their Rating and all Rated Electrical Operating Conditions; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-11-25 |  | 2016-09-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780006567 | Criteria for the selection of the transfers to be assessed. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-01-23 |  | 2020-12-14 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006572 | Distribute to the following prior to the effectiveness of such revisions: |  | PCPA | [9 empty] | PA | [12 empty] | 2012-01-23 |  | 2020-12-14 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006577 | Individual generating unit greater than 50 MVA (gross nameplate rating) directly connected to the BES |  | PCPA | [9 empty] | PA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  |  | 331000 | NPCC-ON |  | NPCC-US
1 | 79780006583 | Those islands selected by applying the criteria in Requirement E.B.1, and |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 210000 | NPCC-ON |  | NPCC-US
1 | 79780006585 | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-1 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 310000 | NPCC-ON |  | NPCC-US
1 | 79780006588 | Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES |  | PCPA | [9 empty] | PA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  |  | 331000 | NPCC-ON |  | NPCC-US
1 | 79780006591 | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 410000 | NPCC-ON |  | NPCC-US
1 | 79780006598 | The performance of the UFLS equipment, E.B. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 2010000 | NPCC-ON |  | NPCC-US
1 | 79780006617 | Maintain a list of circuits subject to PRC-023-3 per application of Attachment B, including identification of the first calendar year in which any criterion in PRC-023-3, Attachment B applies. |  | PCPA | [9 empty] | PA | [12 empty] | 2014-09-22 |  | 2017-03-31 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780006622 | System models shall represent: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-12-23 |  | 2023-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006623 | Existing Facilities |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-01-01 | [5 empty] | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780006629 | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by current annual studies or qualified past studies as indicated in Requirement R2, Part 2.6. Qualifying studies need to include the following conditions: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006630 | System peak Load for either Year One or year two, and for year five. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780006636 | A current study assessing expected System peak Load conditions for one of the years in the Long-Term Transmission Planning Horizon and the rationale for why that year was selected. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 22100000 | NPCC-ON |  | NPCC-US
1 | 79780006639 | When a generator’s AVR is out of service or the generator does not have an AVR, the Generator Operator shall use an alternative method to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2014-08-01 |  | 2015-05-28 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006642 | For generator step-up transformers and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: |  | GO | [22 empty] | 2014-08-01 |  | 2015-05-28 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780006643 | Tap settings. |  | GO | [22 empty] | 2014-10-01 |  | 2015-05-28 |  |  |  | 51100000 | NPCC-ON |  | NPCC-US
1 | 79780006646 | If the Generator Owner cannot comply with the Transmission Operator’s specifications, the Generator Owner shall notify the Transmission Operator and shall provide the technical justification. |  | GO | [22 empty] | 2014-08-01 |  | 2015-05-28 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780006647 | Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. |  | TOP | [18 empty] | TOP |  |  |  | 2014-08-01 |  | 2015-11-12 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006648 | System peak Load for one of the five years. System peak Load levels shall include a Load model which represents the expected dynamic behavior of Loads that could impact the study area, considering the behavior of induction motor Loads. An aggregate System Load model which represents the overall dynamic behavior of the Load is acceptable. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 24100000 | NPCC-ON |  | NPCC-US
1 | 79780006653 | For steady state, short circuit, or Stability analysis: the study shall be five calendar years old or less, unless a technical rationale can be provided to demonstrate that the results of an older study are still valid. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 26100000 | NPCC-ON |  | NPCC-US
1 | 79780006656 | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: &lt;br/&gt;• Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. &lt;br/&gt;• Installation, modification, or removal of Protection Systems or Special Protection Systems &lt;br/&gt;• Installation or modification of automatic generation tripping as a response to a single or multiple Contingency to mitigate Stability performance violations. &lt;br/&gt;• Installation or modification of manual and automatic generation runback/tripping as a response to a single or multiple Contingency to mitigate steady state performance violations. &lt;br/&gt;• Use of Operating Procedures specifying how long they will be needed as part of the Corrective Action Plan. &lt;br/&gt;• Use of rate applications, DSM, new technologies, or other initiatives. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 27100000 | NPCC-ON |  | NPCC-US
1 | 79780006661 | List System deficiencies and the associated actions needed to achieve required System performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 28100000 | NPCC-ON |  | NPCC-US
1 | 79780006663 | Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R3, Part 3.4. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780006666 | Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 33100000 | NPCC-ON |  | NPCC-US
1 | 79780006671 | The Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 34100000 | NPCC-ON |  | NPCC-US
1 | 79780006673 | Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R4, Part 4.4. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780006674 | For planning event P1: No generating unit shall pull out of synchronism. A generator being disconnected from the System by fault clearing action or by a Special Protection System is not considered pulling out of synchronism. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 41100000 | NPCC-ON |  | NPCC-US
1 | 79780006679 | Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 43100000 | NPCC-ON |  | NPCC-US
1 | 79780006680 | Successful high speed (less than one second) reclosing and unsuccessful high speed reclosing into a Fault where high speed reclosing is utilized. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 43110000 | NPCC-ON |  | NPCC-US
1 | 79780006685 | Each Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 44100000 | NPCC-ON |  | NPCC-US
1 | 79780006688 | If a recipient of the Planning Assessment results provides documented comments on the results, the respective Planning Coordinator or Transmission Planner shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780006691 | Generation dispatch, including but not limited to long term planned outages, additions and retirements. |  | PCPA | [9 empty] | PA | [12 empty] | 2013-04-01 |  | 2020-12-14 |  |  |  | 14100000 | NPCC-ON |  | NPCC-US
1 | 79780006698 | Each Planning Coordinator adjacent to the Planning Coordinator’s Planning Coordinator area or overlapping the Planning Coordinator’s area. |  | PCPA | [9 empty] | PA | [12 empty] | 2013-04-01 |  | 2020-12-14 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780006700 | For Confirmed Interchange greater than 250 MW for the last hour, the actual hourly integrated energy deviates from the Confirmed Interchange by more than 10% for that hour and that deviation is expected to persist. |  | PSE | [10 empty] | PSE | [11 empty] | 2015-01-01 | [5 empty] | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006703 | Each Source and Sink Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if it does not expect to be capable of supporting the magnitude of the Interchange, including ramping, throughout the duration of the Arranged Interchange. |  | BA | BA | [21 empty] | 2014-06-30 |  | 2021-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006705 | Each Transmission Service Provider shall deny the Arranged Interchange or curtail Confirmed Interchange if the transmission path (proper connectivity of adjacent Transmission Service Providers) between it and its adjacent Transmission Service Providers is invalid. |  | TSP | [20 empty] | TSP |  | 2014-06-30 |  | 2021-03-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006706 | If a Balancing Authority denies a Reliability Adjustment Arranged Interchange, the Balancing Authority must communicate that fact to its Reliability Coordinator no more than 10 minutes after the denial. |  | BA | BA | [21 empty] | 2014-06-30 |  | 2021-03-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780006707 | The Source Balancing Authority, |  | BA | BA | [21 empty] | 2014-06-30 |  | 2021-03-31 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780006712 | Identical in magnitude to that of the Adjacent Balancing Authority, and |  | BA | BA | [21 empty] | 2014-11-26 |  | 2021-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006714 | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006716 | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006718 | Its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780006724 | Its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780006728 | Its Reliability Coordinator. |  | BA | BA | [21 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780006733 | Its Reliability Coordinator. |  | BA | BA | [21 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780006736 | Its Balancing Authority. |  | DP |  | DP | [20 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780006738 | Its Balancing Authority. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780006740 | Subsequent risk assessments shall be performed:&lt;br/&gt; • At least once every 30 calendar months for a Transmission Owner that has identified in its previous risk assessment (as verified according to Requirement R2) one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection; or &lt;br/&gt;• At least once every 60 calendar months for a Transmission Owner that has not identified in its previous risk assessment (as verified according to Requirement R2) any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection. |  | TO | [22 empty] | 2015-10-01 |  | 2015-10-01 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006742 | Each Transmission Owner shall select an unaffiliated verifying entity that is either:&lt;br/&gt;• A registered Planning Coordinator, Transmission Planner, or Reliability Coordinator; or&lt;br/&gt;• An entity that has transmission planning or analysis experience. |  | TO | [22 empty] | 2015-10-01 |  | 2015-10-01 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006746 | If a Transmission station or Transmission substation previously identified under Requirement R1 and verified according to Requirement R2 is removed from the identification during a subsequent risk assessment performed according to Requirement R1 or a verification according to Requirement R2, then the Transmission Owner shall, within seven calendar days following the verification or the subsequent risk assessment, notify the Transmission Operator that has operational control of the primary control center of the removal. |  | TO | [22 empty] | 2015-10-01 |  | 2015-10-01 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780006747 | Unique characteristics of the identified and verified Transmission station(s), Transmission substation(s), and primary control center(s); |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780006750 | Resiliency or security measures designed collectively to deter, detect, delay, assess, communicate, and respond to potential physical threats and vulnerabilities identified during the evaluation conducted in Requirement R4. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780006754 | Each Transmission Owner and Transmission Operator shall select an unaffiliated third party reviewer from the following:&lt;br/&gt;• An entity or organization with electric industry physical security experience and whose review staff has at least one member who holds either a Certified Protection Professional (CPP) or Physical Security Professional (PSP) certification.&lt;br/&gt;• An entity or organization approved by the ERO.&lt;br/&gt;• A governmental agency with physical security expertise.&lt;br/&gt;• An entity or organization with demonstrated law enforcement, government, or military physical security expertise. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780006758 | generation Facilities; |  | TO | [21 empty] | M1. Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements) that it met all requirements in Requirement R1. | 2014-11-06 |  | 2018-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006761 | Procedures for coordinated studies of new or materially modified existing interconnections and their impacts on affected system(s). |  | TO | [22 empty] | 2014-11-06 |  | 2018-12-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780006763 | Procedures for coordinated studies of new interconnections and their impacts on affected system(s). |  | GO | [22 empty] | 2014-11-06 |  | 2018-12-31 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780006765 | The reliability impact of the new interconnection, or materially modified existing interconnection, on affected system(s); |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2014-11-06 |  | 2021-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006769 | Verify the Real Power capability of its generating units in accordance with Attachment 1. |  | GO | [22 empty] | 2014-05-27 |  |  |  | For the purpose of this standard, the term, “applicable Facility” shall mean any one of the following:&lt;br/&gt;4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.&lt;br/&gt;4.2.2 Synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.&lt;br/&gt;4.2.3 Generating plant/Facility greater than 75 MVA (gross aggregate nameplate rating) directly connected to the Bulk Electric System. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006771 | Verify, in accordance with Attachment 1, (i) the Reactive Power capability of its generating units and (ii) the Reactive Power capability of its synchronous condenser units. |  | GO | [22 empty] | 2014-05-27 |  |  |  | For the purpose of this standard, the term, “applicable Facility” shall mean any one of the following:&lt;br/&gt;4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.&lt;br/&gt;4.2.2 Synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.&lt;br/&gt;4.2.3 Generating plant/Facility greater than 75 MVA (gross aggregate nameplate rating) directly connected to the Bulk Electric System. |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006773 | Verify, in accordance with Attachment 1, the Reactive Power capability of its synchronous condenser units. |  | TO | [22 empty] | 2014-05-27 |  |  |  | For the purpose of this standard, the term, “applicable Facility” shall mean any one of the following:&lt;br/&gt;4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.&lt;br/&gt;4.2.2 Synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.&lt;br/&gt;4.2.3 Generating plant/Facility greater than 75 MVA (gross aggregate nameplate rating) directly connected to the Bulk Electric System. |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780006775 | A list of Transmission Planners, Balancing Authorities, Load Serving Entities, and Distribution Providers that are required to provide the data (“Applicable Entities”). |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2015-04-27 |  | 2016-09-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006778 | Integrated hourly Demands in megawatts for the prior calendar year. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780006784 | Monthly peak hour forecast Total Internal Demands in megawatts for the next two calendar years. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 14100000 | NPCC-ON |  | NPCC-US
1 | 79780006790 | The assumptions and methods used in the development of aggregated Peak Demand and Net Energy for Load forecasts. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 15100000 | NPCC-ON |  | NPCC-US
1 | 79780006795 | If the Applicable Entity does not provide data requested under this requirement because (1) the requesting entity did not demonstrate a reliability need for the data; or (2) providing the data would conflict with the Applicable Entity’s confidentiality, regulatory, or security requirements, the Applicable Entity shall, within 30 calendar days of the written request, provide a written response to the requesting entity specifying the data that is not being provided and on what basis. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2015-04-27 |  | 2016-09-30 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780006796 | The data listed in Attachment 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-07-01 |  |  |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006798 | Data format; |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-07-01 |  |  |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. |  | 12100000 | NPCC-ON |  | NPCC-US
1 | 79780006803 | Provide either updated data or an explanation with a technical basis for maintaining the current data; |  | BA, GO, LSE, RP, TO, TSP | BA |  |  |  | GO |  |  | LSE | [5 empty] | RP |  |  |  | TO |  |  | TSP |  | 2015-07-01 |  |  |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780006805 | Comparison of the performance of the Planning Coordinator’s portion of the existing system in a planning power flow model to actual system behavior, represented by a state estimator case or other Real-time data sources, at least once every 24 calendar months through simulation; |  | PCPA | [9 empty] | PA | [12 empty] | 2014-05-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006809 | Criteria and processes for notifications. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-26 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006814 | Review and update annually with no more than 15 months between reviews. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-26 | [5 empty] | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006817 | Identify applicable roles and reporting responsibilities including: |  | RC | [11 empty] | RC | [10 empty] | 2016-01-26 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006818 | Development and communication of outage schedules. |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780006823 | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses and Real-time monitoring. |  | TOP | [18 empty] | TOP | [5 empty] | 2016-01-26 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006827 | A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. |  | BA | BA | [23 empty] | 2016-01-26 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006831 | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data as deemed necessary by the Transmission Operator. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-26 |  | 2021-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006835 | A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. |  | BA | BA | [21 empty] | 2016-01-26 |  | 2021-03-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006839 | A mutually agreeable format |  | BA, DP, GO, GOP, LSE, TO, TOP | BA | DP |  |  | GO | GOP |  | LSE | [9 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2021-03-31 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780006842 | When a generator’s AVR is out of service or the generator does not have an AVR, the Generator Operator shall use an alternative method to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-05-29 |  | 2017-09-25 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006845 | For generator step-up and auxiliary transformers5 with primary voltages equal to or greater than the generator terminal voltage: |  | GO | [22 empty] | 2015-05-29 |  | 2017-09-25 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780006846 | Tap settings. |  | GO | [22 empty] | 2015-05-29 |  | 2017-09-25 |  |  |  | 51100000 | NPCC-ON |  | NPCC-US
1 | 79780006849 | If the Generator Owner cannot comply with the Transmission Operator’s specifications, the Generator Owner shall notify the Transmission Operator and shall provide the technical justification. |  | GO | [22 empty] | 2015-05-29 |  | 2017-09-25 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780006850 | Roles and responsibilities for activating the Operating Plan(s); |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006852 | Notification to its Reliability Coordinator, to include current and projected conditions, when experiencing an operating Emergency; |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 12100000 | NPCC-ON |  | NPCC-US
1 | 79780006858 | Roles and responsibilities for activating the Operating Plan(s); |  | BA | BA | [21 empty] | 2016-01-25 | [5 empty] | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006860 | Notification to its Reliability Coordinator, to include current and projected conditions when experiencing a Capacity Emergency or Energy Emergency; |  | BA | BA | [21 empty] | 2017-04-01 | [5 empty] | 22100000 | NPCC-ON |  | NPCC-US
1 | 79780006863 | capability and availability; |  | BA | BA | [21 empty] | 2017-04-01 | [5 empty] | 22310000 | NPCC-ON |  | NPCC-US
1 | 79780006873 | Within 30 calendar days of receipt, the Reliability Coordinator shall: |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780006874 | Review each submitted Operating Plan(s) on the basis of compatibility and inter-dependency with other Balancing Authorities’ and Transmission Operators’ Operating Plans; |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 31100000 | NPCC-ON |  | NPCC-US
1 | 79780006877 | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System and Automatic Reclosing Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2015-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006879 | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System and Automatic Reclosing Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-01-25 |  | 2015-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006881 | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [19 empty] | 2015-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006883 | The implementation of the UVLS Program resolves the identified undervoltage issues that led to its development and design. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2017-04-01 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006885 | The UVLS Program resolves the identified undervoltage issues for which the UVLS Program is designed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2017-04-01 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780006887 | Maintain a list of circuits subject to PRC-023-4 per application of Attachment B, including identification of the first calendar year in which any criterion in PRC-023-4, Attachment B applies. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 |  |  |  | 4.2. Circuits:&lt;br/&gt;4.2.1 Circuits Subject to Requirements R1 – R5:&lt;br/&gt;4.2.1.1 Transmission lines operated at 200 kV and above, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads.&lt;br/&gt;4.2.1.2 Transmission lines operated at 100 kV to 200 kV selected by the Planning Coordinator in accordance with Requirement R6.&lt;br/&gt;4.2.1.3 Transmission lines operated below 100 kV that are part of the BES and selected by the Planning Coordinator in accordance with Requirement R6.&lt;br/&gt;4.2.1.4 Transformers with low voltage terminals connected at 200 kV and above.&lt;br/&gt;4.2.1.5 Transformers with low voltage terminals connected at 100 kV to 200 kV selected by the Planning Coordinator in accordance with Requirement R6.&lt;br/&gt;4.2.1.6 Transformers with low voltage terminals connected below 100 kV that are part of the BES and selected by the Planning Coordinator in accordance with Requirement R6.&lt;br/&gt;4.2.2 Circuits Subject to Requirement R6:&lt;br/&gt;4.2.2.1 Transmission lines operated at 100 kV to 200 kV and transformers with low voltage terminals connected at 100 kV to 200 kV, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads.&lt;br/&gt;4.2.2.2 Transmission lines operated below 100 kV and transformers with low voltage terminals connected below 100 kV that are part of the BES, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads. |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780006889 | Within 12 full calendar months of notification of a BES Element pursuant to Requirement R1, determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-1 – Attachment B where an evaluation of that Element’s load-responsive protective relay(s) based on PRC-026-1 – Attachment B criteria has not been performed in the last five calendar years. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2020-01-01 | [5 empty] | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006891 | Incorporate the NPIRs into their operating analyses of the electric system. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2014-11-04 |  | 2021-03-31 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780006898 | Retired. [Note: Part 9.1 was retired under the Paragraph 81 project. The NUC SDT proposes to leave this Part blank to avoid renumbering Requirement parts that would impact existing agreements throughout the industry.] |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2014-11-04 |  | 2021-03-31 |  |  |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780006900 | Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the Agreement. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 92100000 | NPCC-ON |  | NPCC-US
1 | 79780006904 | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 93100000 | NPCC-ON |  | NPCC-US
1 | 79780006912 | Conditions for activation of the recovery plan(s). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.1. An example of evidence may include, but is not limited to, one or more plans that include language identifying conditions for activation of the recovery plan(s). | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006913 | Provisions for communications affecting the NPIRs between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of applicable unique terms |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 94100000 | NPCC-ON |  | NPCC-US
1 | 79780006922 | Test each of the recovery plans referenced in Requirement R1 at least once every 15 calendar months:&lt;br/&gt;• By recovering from an actual incident;&lt;br/&gt;• With a paper drill or tabletop exercise; or&lt;br/&gt;• With an operational exercise. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.1. An example of evidence may include, but is not limited to, dated evidence of a test (by recovering from an actual incident, with a paper drill or tabletop exercise, or with an operational exercise) of the recovery plan at least once every 15 calendar months. For the paper drill or full operational exercise, evidence may include meeting notices, minutes, or other records of exercise findings. | 2017-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006925 | No later than 90 calendar days after completion of a recovery plan test or actual recovery: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.1. An example of evidence may include, but is not limited to, all of the following:&lt;br/&gt;1. Dated documentation of identified deficiencies or lessons learned for each recovery plan test or actual incident recovery or dated documentation stating there were no lessons learned;&lt;br/&gt;2. Dated and revised recovery plan showing any changes based on the lessons learned; and&lt;br/&gt;3. Evidence of plan update distribution including, but not limited to:&lt;br/&gt;• Emails;&lt;br/&gt;• USPS or other mail service;&lt;br/&gt;• Electronic distribution system; or &lt;br/&gt;• Training sign-in sheets. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780006927 | Document any lessons learned associated with a recovery plan test or actual recovery or document the absence of any lessons learned; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 31100000 | NPCC-ON |  | NPCC-US
1 | 79780006930 | Update the recovery plan; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 32100000 | NPCC-ON |  | NPCC-US
1 | 79780006932 | Those islands selected by applying the criteria in Requirement R1, and |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006935 | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-2 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, an |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780006938 | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780006945 | The performance of the UFLS equipment, |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 111000000 | NPCC-ON |  | NPCC-US
1 | 79780006949 | UFLS program, including a schedule for implementation |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 141000000 | NPCC-ON |  | NPCC-US
1 | 79780006953 | For UFLS design assessments performed under Requirement R4 or R5, the Corrective Action Plan shall be developed within the five-year time frame identified in Requirement R4. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 151000000 | NPCC-ON |  | NPCC-US
1 | 79780006955 | Assuming the normal automatic voltage regulator control loop and steady-state system operating conditions, verify the following coordination items for each applicable Facility: |  | GO, TO |  |  |  |  | GO | [17 empty] | 2014-05-27 |  | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006956 | The in-service limiters are set to operate before the Protection System of the applicable Facility in order to avoid disconnecting the generator unnecessarily. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-07-01 |  | 2016-06-30 |  |  |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780006958 | &lt;p&gt;The Generator Owner shall communicate the documented regulatory or equipment limitation, or the removal of a previously documented regulatory or equipment limitation, to its Planning Coordinator and Transmission Planner within 30 calendar days of any of the following:&lt;br/&gt;&lt;br/&gt;• Identification of a regulatory or equipment limitation.&lt;br/&gt;• Repair of the equipment causing the limitation that removes the limitation. &lt;br/&gt;• Replacement of the equipment causing the limitation with equipment that removes the limitation.&lt;br/&gt;• Creation or adjustment of an equipment limitation caused by consumption of the cumulative turbine life-time frequency excursion allowance.&lt;/p&gt; |  | GO | [22 empty] | 2014-05-27 |  | 2016-06-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780006959 | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall create a list of Bulk Electric System (BES) company-specific Real-time reliability-related tasks based on a defined and documented methodology. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2014-06-19 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006960 | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall review, and update if necessary, its list of BES companyspecific Real-time reliability-related tasks identified in part 1.1 each calendar year. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2016-07-01 | [5 empty] | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780006964 | Each Transmission Owner shall create a list of BES company-specific Real-time reliability-related tasks based on a defined and documented methodology. |  | TO | [21 empty] | M2.1 Each Transmission Owner shall have available for inspection its methodology and its BES company-specific Real-time reliability-related task list, with the date of the last review, as specified in Requirement R2 part 2.1. | 2014-06-19 | [5 empty] | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780006965 | Each Transmission Owner shall review, and update if necessary, its list of BES company-specific Real-time reliability-related tasks identified in part 2.1 each calendar year. |  | TO | [22 empty] | 2016-07-01 | [5 empty] | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780006969 | Within six months of a modification or addition of a BES company-specific Realtime reliability-related task, each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner shall verify the capabilities of each of its personnel identified in Requirement R1 or Requirement R2 to perform the new or modified BES company-specific Real-time reliability-related tasks identified in Requirement R1 part 1.1 or Requirement R2 part 2.1. |  | BA, RC, TO, TOP | BA | [10 empty] | RC | [5 empty] | TO | TOP |  |  | M3.1 Each Reliability Coordinator, Balancing Authority, Transmission Operator, or Transmission Owner shall present evidence that it verified the capabilities of applicable personnel to perform new or modified BES company-specific Real-time reliability-related tasks within 6 months of a modification or addition of a BES company-specific Real-time reliability-related task. | 2014-06-19 | [5 empty] | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780006970 | A Reliability Coordinator, Balancing Authority, Transmission Operator, or Transmission Owner that did not previously meet the criteria of Requirement R4, shall comply with Requirement R4 within 12 months of meeting the criteria. |  | BA, RC, TO, TOP | BA | [10 empty] | RC | [5 empty] | TO | TOP |  |  | M4.1 Each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner shall have available for inspection training records that provide evidence that personnel identified in Requirement R1 or Requirement R2 completed training that included the use of simulation technology, as specified in Requirement R4, within 12 months of meeting the criteria of Requirement R4. | 2014-06-19 | [5 empty] | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780006971 | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct an evaluation each calendar year of the training established in Requirement R5 to identify and implement changes to the training. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | M5.1 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection evidence (such as instructor observations, trainee feedback, supervisor feedback, course evaluations, learning assessments, or internal audit results) that it performed an evaluation each calendar year, as specified in Requirement R5 part 5.1. | 2014-06-19 | [5 empty] | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780006972 | Each Generator Operator shall conduct an evaluation each calendar year of the training established in Requirement R6 to identify and implement changes to the training. |  | GOP | [5 empty] | GOP | [15 empty] | M6.1 Each Generator Operator shall have available for inspection evidence (such as instructor observations, trainee feedback, supervisor feedback, course evaluations, learning assessments, or internal audit results) that it performed an evaluation each calendar year, as specified in Requirement R6 part 6.1. | 2014-06-19 | [5 empty] | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780006973 | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System and Automatic Reclosing Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [19 empty] | 2015-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780006975 | For its high impact and medium impact BES Cyber Systems, if any: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007043 | Cyber security awareness; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12100000 | NPCC-ON |  | NPCC-US
1 | 79780007047 | A list of data and information needed by the Reliability Coordinator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data, as deemed necessary by the Reliability Coordinator. |  | RC | [11 empty] | RC | [10 empty] | 2017-01-01 |  | 2021-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007051 | A mutually agreeable format |  | BA, DP, GO, GOP, LSE, RC, TO, TOP | BA | DP |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2021-03-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780007054 | Communications and notifications, including the mutually agreed to conditions under which one Reliability Coordinator notifies other Reliability Coordinators; the process to follow in making those notifications; and the data and information to be exchanged with other Reliability Coordinators. |  | RC | [11 empty] | RC | [12 empty] | 2016-01-26 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007061 | Review and update annually with no more that 15 months between reviews. |  | RC | [11 empty] | RC | [9 empty] | 2.1 Reviewed and updated annually with no more than 15 months between reviews. |  |  | 2016-01-26 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780007064 | Each methodology shall describe the method used to account for the following limitations in both the pre- and post-contingency state: |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007065 | Facility ratings; |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780007071 | The simulation of transfers performed through the adjustment of generation, Load, or both; |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 12100000 | NPCC-ON |  | NPCC-US
1 | 79780007079 | Each Transmission Operator that uses the Flowgate Methodology shall include in its methodology an impact test process for including requested constraints. If a generator to Load transfer in a registered entity’s area or a transfer to a neighboring registered entity impacts the requested constraint by five percent or greater, the requested constraint shall be included in the TFC determination, otherwise the requested constraint is not required to be included. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780007082 | Each methodology shall describe the method used to account for the following elements, provided such elements impact the determination of AFC or ATC: |  | TSP | [20 empty] | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780007083 | The simulation of transfers performed through the adjustment of generation, Load, or both; |  | TSP | [20 empty] | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780007091 | A written response to any request for clarification of its TFC or TTC methodology, ATCID, CBMID, or TRMID. If the request for clarification is contrary to the Transmission Operator’s or Transmission Service Provider’s confidentiality, regulatory, or security requirements then a written response shall be provided explaining the clarifications not provided, on what basis and whether there are any options for resolving any of the confidentiality, regulatory, or security concerns. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780007093 | TRMID; and |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 52100000 | NPCC-ON |  | NPCC-US
1 | 79780007096 | ATCID; and |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 53100000 | NPCC-ON |  | NPCC-US
1 | 79780007098 | In responding to a written request for data on an ongoing basis, the Transmission Service Provider or Transmission Operator shall make available its data on an ongoing basis no later than 45 calendar days from receipt of the written request. Unless otherwise agreed upon, the Transmission Operator or Transmission Service Provider is not required to: |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780007101 | Alter the format in which it maintains or uses the data; or |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 61100000 | NPCC-ON |  | NPCC-US
1 | 79780007103 | Expected generation resource commitment and dispatch |  | BA | BA | [21 empty] | 2016-01-26 | [5 empty] | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780007111 | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780007112 | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 41100000 | NPCC-ON |  | NPCC-US
1 | 79780007116 | If a recipient of the GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 43100000 | NPCC-ON |  | NPCC-US
1 | 79780007117 | The maximum effective GIC value for the worst case geoelectric field orientation for the benchmark GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2019-01-01 |  | 2019-06-30 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780007129 | Be based on the effective GIC flow information provided in Requirement R5; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2021-01-01 |  | 2019-06-30 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780007133 | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: &lt;br/&gt;• Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. &lt;br/&gt;• Installation, modification, or removal of Protection Systems or Special Protection Systems. &lt;br/&gt;• Use of Operating Procedures, specifying how long they will be needed as part of the Corrective Action Plan. &lt;br/&gt;• Use of Demand-Side Management, new technologies, or other initiatives. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780007136 | If a recipient of the Corrective Action Plan provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 73100000 | NPCC-ON |  | NPCC-US
1 | 79780007137 | Assuming the normal automatic voltage regulator control loop and steady-state system operating conditions, verify the following coordination items for each applicable Facility: |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-07-01 |  |  |  | 4.2. Facilities&lt;br/&gt;For the purpose of this standard, the term, “applicable Facility” shall mean any one of the following:&lt;br/&gt;4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.&lt;br/&gt;4.2.2 Individual synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.&lt;br/&gt;4.2.3 Generating plant/ Facility consisting of one or more units that are connected to the Bulk Electric System at a common bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.3.1 This includes individual generating units of the dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition where voltage regulating control for the facility is performed solely at the individual generating unit of the dispersed power producing resources. &lt;br/&gt;4.2.4 Any generator, regardless of size, that is a blackstart unit material to and designated as part of a Transmission Operator’s restoration plan. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007138 | The in-service limiters are set to operate before the Protection System of the applicable Facility in order to avoid disconnecting the generator unnecessarily. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-07-01 |  |  |  | 4.2. Facilities&lt;br/&gt;For the purpose of this standard, the term, “applicable Facility” shall mean any one of the following:&lt;br/&gt;4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.&lt;br/&gt;4.2.2 Individual synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.&lt;br/&gt;4.2.3 Generating plant/ Facility consisting of one or more units that are connected to the Bulk Electric System at a common bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.3.1 This includes individual generating units of the dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition where voltage regulating control for the facility is performed solely at the individual generating unit of the dispersed power producing resources. &lt;br/&gt;4.2.4 Any generator, regardless of size, that is a blackstart unit material to and designated as part of a Transmission Operator’s restoration plan. |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780007140 | The Generator Owner shall communicate the documented regulatory or equipment limitation, or the removal of a previously documented regulatory or equipment limitation, to its Planning Coordinator and Transmission Planner within 30 calendar days of any of the following:&lt;br/&gt;&lt;br/&gt;• Identification of a regulatory or equipment limitation.&lt;br/&gt;• Repair of the equipment causing the limitation that removes the limitation. &lt;br/&gt;• Replacement of the equipment causing the limitation with equipment that removes the limitation.&lt;br/&gt;• Creation or adjustment of an equipment limitation caused by consumption of the cumulative turbine life-time frequency excursion allowance. |  | GO | [22 empty] | 2016-07-01 |  | 2022-09-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780007141 | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-05-13 |  | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007144 | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-05-13 |  | 2016-06-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780007145 | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-07-01 |  | 2016-06-30 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780007149 | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and |  | GO, TO |  |  |  |  | GO | [17 empty] | 2015-05-29 |  | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007152 | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-05-29 |  | 2016-06-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780007153 | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2016-06-30 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780007157 | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-05-29 |  | 2016-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007159 | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-01-25 |  | 2015-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007163 | Identify BES buses for which sequence of events recording (SER) and fault recording (FR) data is required by using the methodology in PRC-002-2, Attachment 1. |  | TO | [22 empty] | 2015-11-24 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007166 | Phase-to-neutral voltage for each phase of each specified BES bus. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780007168 | Transformers that have a low-side operating voltage of 100kV or above. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 32100000 | NPCC-ON |  | NPCC-US
1 | 79780007170 | A single record or multiple records that include:&lt;br/&gt;• A pre-trigger record length of at least two cycles and a total record length of at least 30-cycles for the same trigger point, or&lt;br/&gt;• At least two cycles of the pre-trigger data, the first three cycles of the post-trigger data, and the final cycle of the fault as seen by the fault recorder. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780007173 | Neutral (residual) overcurrent. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 43100000 | NPCC-ON |  | NPCC-US
1 | 79780007175 | Identify BES Elements for which dynamic Disturbance recording (DDR) data is required, including the following: |  | PCPA, RC | [9 empty] | PA |  | RC | [10 empty] | 2015-11-24 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780007176 | Generating resource(s) with: |  | PCPA, RC | [9 empty] | PA |  | RC | [10 empty] | 2016-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 51100000 | NPCC-ON |  | NPCC-US
1 | 79780007177 | Gross individual nameplate rating greater than or equal to 500 MVA. |  | PCPA, RC | [9 empty] | PA |  | RC | [10 empty] | 2016-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 51110000 | NPCC-ON |  | NPCC-US
1 | 79780007184 | One BES Element; and |  | PCPA, RC | [9 empty] | PA |  | RC | [10 empty] | 2016-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 52100000 | NPCC-ON |  | NPCC-US
1 | 79780007188 | One phase-to-neutral or positive sequence voltage. |  | TO | [22 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780007192 | One phase-to-neutral, phase-to-phase, or positive sequence voltage at either the generator step-up transformer (GSU) high-side or low-side voltage level. |  | GO | [22 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780007196 | Triggered record lengths of at least three minutes. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780007198 | Input sampling rate of at least 960 samples per second. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780007200 | Synchronization to Coordinated Universal Time (UTC) with or without a local time offset. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 101000000 | NPCC-ON |  | NPCC-US
1 | 79780007202 | Data will be retrievable for the period of 10-calendar days, inclusive of the day the data was recorded. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 111000000 | NPCC-ON |  | NPCC-US
1 | 79780007207 | Security awareness that, at least once each calendar quarter, reinforces cyber security practices (which may include associated physical security practices) for the Responsible Entity’s personnel who have authorized electronic or authorized unescorted physical access to BES Cyber Systems. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.1 An example of evidence may include, but is not limited to, documentation that the quarterly reinforcement has been provided. Examples of evidence of reinforcement may include, but are not limited to, dated copies of information used to reinforce security awareness, as well as evidence of distribution, such as: &lt;br/&gt;• direct communications (for example, e-mails, memos, computer-based training); or &lt;br/&gt;• indirect communications (for example, posters, intranet, or brochures); or&lt;br/&gt;• management support and reinforcement (for example, presentations or meetings). | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007208 | Training content on: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.1 Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780007209 | Cyber security policies; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780007219 | Develop a baseline configuration, individually or by group, which shall include the following items: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.1. Examples of evidence may include, but are not limited to: &lt;br/&gt;• A spreadsheet identifying the required items of the baseline configuration for each Cyber Asset, individually or by group; or&lt;br/&gt;• A record in an asset management system that identifies the required items of the baseline configuration for each Cyber Asset, individually or by group. | 2016-03-31 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007220 | Operating system(s) (including version) or firmware where no independent operating system exists; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780007228 | Prior to the change, determine required cyber security controls in CIP-005 and CIP-007 that could be impacted by the change; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 14100000 | NPCC-ON |  | NPCC-US
1 | 79780007232 | Prior to implementing any change in the production environment, test the changes in a test environment or test the changes in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration to ensure that required cyber security controls in CIP-005 and CIP-007 are not adversely affected; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 15100000 | NPCC-ON |  | NPCC-US
1 | 79780007234 | Monitor at least once every 35 calendar days for changes to the baseline configuration (as described in Requirement R1, Part 1.1). Document and investigate detected unauthorized changes. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.1. An example of evidence may include, but is not limited to, logs from a system that is monitoring the configuration along with records of investigation for any unauthorized changes that were detected. | 2016-08-05 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780007235 | At least once every 15 calendar months, conduct a paper or active vulnerability assessment. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.1. Examples of evidence may include, but are not limited to: &lt;br/&gt;• A document listing the date of the assessment (performed at least once every 15 calendar months), the controls assessed for each BES Cyber System along with the method of assessment; or&lt;br/&gt;• A document listing the date of the assessment and the output of any tools used to perform the assessment. | 2017-07-01 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780007237 | Perform an active vulnerability assessment in a test environment, or perform an active vulnerability assessment in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration of the BES Cyber System in a production environment; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2018-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 32100000 | NPCC-ON |  | NPCC-US
1 | 79780007241 | Method(s) to identify information that meets the definition of BES Cyber System Information. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.1. Examples of acceptable evidence include, but are not limited to: &lt;br/&gt;• Documented method to identify BES Cyber System Information from entity’s information protection program; or&lt;br/&gt;• Indications on information (e.g., labels or classification) that identify BES Cyber System Information as designated in the entity’s information protection program; or&lt;br/&gt;• Training materials that provide personnel with sufficient knowledge to recognize BES Cyber System Information; or&lt;br/&gt;• Repository or electronic and physical location designated for housing BES Cyber System Information in the entity’s information protection program. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting. &lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-011-2: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007243 | Prior to the release for reuse of applicable Cyber Assets that contain BES Cyber System Information (except for reuse within other systems identified in the “Applicable Systems” column), the Responsible Entity shall take action to prevent the unauthorized retrieval of BES Cyber System Information from the Cyber Asset data storage media. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.1. Examples of acceptable evidence include, but are not limited to: &lt;br/&gt;• Records tracking sanitization actions taken to prevent unauthorized retrieval of BES Cyber System Information such as clearing, purging, or destroying; or &lt;br/&gt;• Records tracking actions such as encrypting, retaining in the Physical Security Perimeter or other methods used to prevent unauthorized retrieval of BES Cyber System Information. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting. &lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-011-2: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780007246 | Process to confirm identity. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.1. An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to confirm identity. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780007258 | Process to authorize based on need, as determined by the Responsible Entity, except for CIP Exceptional Circumstances: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.1. An example of evidence may include, but is not limited to, dated documentation of the process to authorize electronic access, unescorted physical access in a Physical Security Perimeter, and access to designated storage locations, whether physical or electronic, for BES Cyber System Information. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780007259 | Electronic access; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 41100000 | NPCC-ON |  | NPCC-US
1 | 79780007265 | A process to initiate removal of an individual’s ability for unescorted physical access and Interactive Remote Access upon a termination action, and complete the removals within 24 hours of the termination action (Removal of the ability for access may be different than deletion, disabling, revocation, or removal of all access rights) |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.1 An example of evidence may include, but is not limited to, documentation of all of the following:&lt;br/&gt;1. Dated workflow or sign-off form verifying access removal associated with the termination action; and &lt;br/&gt;2. Logs or other demonstration showing such persons no longer have access. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780007286 | Where technically feasible, enable only logical network accessible ports that have been determined to be needed by the Responsible Entity, including port ranges or services where needed to handle dynamic ports. If a device has no provision for disabling or restricting logical ports on the device then those ports that are open are deemed needed. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.1. Examples of evidence may include, but are not limited to:&lt;br/&gt;• Documentation of the need for all enabled ports on all applicable Cyber Assets and Electronic Access Points, individually or by group. &lt;br/&gt;• Listings of the listening ports on the Cyber Assets, individually or by group, from either the device configuration files, command output (such as netstat), or network scans of open ports; or&lt;br/&gt;• Configuration files of host-based firewalls or other device level mechanisms that only allow needed ports and deny all others. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007288 | A patch management process for tracking, evaluating, and installing cyber security patches for applicable Cyber Assets. The tracking portion shall include the identification of a source or sources that the Responsible Entity tracks for the release of cyber security patches for applicable Cyber Assets that are updateable and for which a patching source exists. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.1. An example of evidence may include, but is not limited to, documentation of a patch management process and documentation or lists of sources that are monitored, whether on an individual BES Cyber System or Cyber Asset basis. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780007292 | Deploy method(s) to deter, detect, or prevent malicious code. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.1. An example of evidence may include, but is not limited to, records of the Responsible Entity’s performance of these processes (e.g., through traditional antivirus, system hardening, policies, etc.). | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780007295 | Log events at the BES Cyber System level (per BES Cyber System capability) or at the Cyber Asset level (per Cyber Asset capability) for identification of, and after-the-fact investigations of, Cyber Security Incidents that includes, as a minimum, each of the following types of events: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.1. Examples of evidence may include, but are not limited to, a paper or system generated listing of event types for which the BES Cyber System is capable of detecting and, for generated events, is configured to log. This listing must include the required types of events. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780007302 | Detected successful login attempts; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.1. Examples of evidence may include, but are not limited to, a paper or system generated listing of event types for which the BES Cyber System is capable of detecting and, for generated events, is configured to log. This listing must include the required types of events. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 41100000 | NPCC-ON |  | NPCC-US
1 | 79780007306 | Detected malicious code from Part 4.1; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.2. Examples of evidence may include, but are not limited to, paper or system-generated listing of security events that the Responsible Entity determined necessitate alerts, including paper or system generated list showing how alerts are configured. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 42100000 | NPCC-ON |  | NPCC-US
1 | 79780007310 | Have a method(s) to enforce authentication of interactive user access, where technically feasible. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.1. An example of evidence may include, but is not limited to, documentation describing how access is authenticated. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780007316 | Password length that is, at least, the lesser of eight characters or the maximum length supported by the Cyber Asset; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 55100000 | NPCC-ON |  | NPCC-US
1 | 79780007339 | Define operational or procedural controls to restrict physical access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.1. An example of evidence may include, but is not limited to, documentation that operational or procedural controls exist. | 2016-07-01 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007349 | Require continuous escorted access of visitors (individuals who are provided access but are not authorized for unescorted physical access) within each Physical Security Perimeter, except during CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.1. An example of evidence may include, but is not limited to, language in a visitor control program that requires continuous escorted access of visitors within Physical Security Perimeters and additional evidence to demonstrate that the process was implemented, such as visitor logs. | 2016-07-01 | [5 empty] | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780007352 | Maintenance and testing of each Physical Access Control System and locally mounted hardware or devices at the Physical Security Perimeter at least once every 24 calendar months to ensure they function properly. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M.3.1. An example of evidence may include, but is not limited to, a maintenance and testing program that provides for testing each Physical Access Control System and locally mounted hardware or devices associated with each applicable Physical Security Perimeter at least once every 24 calendar months and additional evidence to demonstrate that this testing was done, such as dated maintenance records, or other documentation showing testing and maintenance has been performed on each applicable device or system at least once every 24 calendar months. | 2017-07-01 | [5 empty] | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780007353 | Three phase-to-neutral voltages. (Common bus-side voltages may be used for lines.) |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780007358 | Each Fault recorder record duration shall be a minimum of one (1) second. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780007361 | Monitored phase overcurrents set at 1.5 pu or less of rated CT secondary current or Protective Relay tripping for all Protection Groups. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 63100000 | NPCC-ON |  | NPCC-US
1 | 79780007365 | Provides a minimum of 1 DDR per 3,000 MW of peak Load. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780007367 | Major Load centers. |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 72100000 | NPCC-ON |  | NPCC-US
1 | 79780007386 | The performance of the UFLS equipment, |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 111000000 | NPCC-ON |  | NPCC-US
1 | 79780007388 | Be provided at all substations and at locations where circuit breaker operation affects continuity of service to radial Loads greater than 300MW, or the operation of which drops 50MVA Nameplate Rating or greater of Generation, or the operation of which creates a Generation/Load island. &lt;br/&gt;Be provided at generating units above 50MVA Nameplate Rating or series of generating units utilizing a control scheme such that the loss of 1 unit results in a loss of greater than 50MVA Nameplate Capacity, and at Generating Plants above 300MVA Name Plate Capacity. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007390 | Transmission and Generator circuit breaker positions |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 12100000 | NPCC-ON |  | NPCC-US
1 | 79780007408 | A minimum recording time of sixty (60) seconds per trigger event. |  | RC | [11 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780007411 | Rate of change of Frequency. |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 93100000 | NPCC-ON |  | NPCC-US
1 | 79780007415 | Line currents for most lines such that normal line maintenance activities do not interfere with DDR functionality. |  | RC | [11 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 101000000 | NPCC-ON |  | NPCC-US
1 | 79780007420 | Maintenance and testing intervals and their basis. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 141000000 | NPCC-ON |  | NPCC-US
1 | 79780007427 | NERC, Regional Entity, Reliability Coordinator. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 151000000 | NPCC-ON |  | NPCC-US
1 | 79780007429 | The data files shall be capable of being viewed, read, and analyzed with a generic COMTRADE analysis tool as per the latest revision of IEEE Standard C37.111. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 161000000 | NPCC-ON |  | NPCC-US
1 | 79780007432 | Type of DME. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 171000000 | NPCC-ON |  | NPCC-US
1 | 79780007441 | The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  |  | 2014-08-01 |  | 2015-11-12 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780007444 | Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances. |  | GOP | [5 empty] | GOP | [16 empty] | 2014-08-01 |  | 2015-11-12 |  |  |  | 2710000 | NPCC-ON |  | NPCC-US
1 | 79780007446 | That can be implemented in time to prevent the identified IROL exceedance. |  | RC | [11 empty] | RC | [10 empty] | 2015-12-04 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007454 | Less than zero at all times, and |  | BA | BA | [21 empty] | 2015-11-13 |  | 2020-11-30 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780007468 | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007470 | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780007472 | Its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780007478 | Personnel and training (CIP-004); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780007487 | Its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780007493 | Its Reliability Coordinator. |  | BA | BA | [21 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780007498 | Its Reliability Coordinator. |  | BA | BA | [21 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780007501 | Its Balancing Authority. |  | DP |  | DP | [20 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780007503 | Its Balancing Authority. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780007507 | Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-25 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007510 | If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-25 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780007512 | The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-25 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780007516 | current residence, regardless of duration; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 32100000 | NPCC-ON |  | NPCC-US
1 | 79780007527 | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-12-04 |  | 2016-06-30 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007530 | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-12-04 |  | 2016-06-30 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780007531 | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-07-01 |  | 2016-06-30 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780007536 | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-12-04 |  | 2017-04-01 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007540 | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-12-04 |  | 2017-04-01 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780007541 | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-07-01 |  | 2017-04-01 |  |  |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780007550 | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-11-19 |  | 2021-03-31 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Protection Systems for BES Elements, with the following exclusions:&lt;br/&gt;4.2.1.1 Non-protective functions that are embedded within a Protection System.&lt;br/&gt;4.2.1.2 Protective functions intended to operate as a control function during switching. &lt;br/&gt;4.2.1.3 Special Protection Systems (SPS).&lt;br/&gt;4.2.1.4 Remedial Action Schemes (RAS).&lt;br/&gt;4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.&lt;br/&gt;4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.&lt;br/&gt;4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007554 | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-11-19 |  | 2021-03-31 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Protection Systems for BES Elements, with the following exclusions:&lt;br/&gt;4.2.1.1 Non-protective functions that are embedded within a Protection System.&lt;br/&gt;4.2.1.2 Protective functions intended to operate as a control function during switching. &lt;br/&gt;4.2.1.3 Special Protection Systems (SPS).&lt;br/&gt;4.2.1.4 Remedial Action Schemes (RAS).&lt;br/&gt;4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.&lt;br/&gt;4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.&lt;br/&gt;4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780007555 | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-04-02 |  | 2021-03-31 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Protection Systems for BES Elements, with the following exclusions:&lt;br/&gt;4.2.1.1 Non-protective functions that are embedded within a Protection System.&lt;br/&gt;4.2.1.2 Protective functions intended to operate as a control function during switching. &lt;br/&gt;4.2.1.3 Special Protection Systems (SPS).&lt;br/&gt;4.2.1.4 Remedial Action Schemes (RAS).&lt;br/&gt;4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.&lt;br/&gt;4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.&lt;br/&gt;4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780007564 | A review and update of short-circuit model data for the BES Elements under study. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.1.3. Distribution Provider (that owns Protection Systems identified in the Facilities section 4.2 below)&lt;br/&gt;4.2. Facilities: Protection Systems installed to detect and isolate Faults on BES Elements. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007567 | Provide the proposed Protection System settings to the owner(s) of the electrically joined Facilities. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.1.3. Distribution Provider (that owns Protection Systems identified in the Facilities section 4.2 below)&lt;br/&gt;4.2. Facilities: Protection Systems installed to detect and isolate Faults on BES Elements. |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780007579 | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-12-18 |  |  |  | 4.2.1 Protection Systems and Sudden Pressure Relaying that are installed for the purpose of detecting Faults on BES Elements (lines, buses, transformers, etc.)&lt;br/&gt;4.2.2 Protection Systems used for underfrequency load-shedding systems installed per ERO underfrequency load-shedding requirements.&lt;br/&gt;4.2.3 Protection Systems used for undervoltage load-shedding systems installed to prevent system voltage collapse or voltage instability for BES reliability.&lt;br/&gt;4.2.4 Protection Systems installed as a Remedial Action Scheme (RAS) for BES reliability.&lt;br/&gt;4.2.5 Protection Systems and Sudden Pressure Relaying for generator Facilities that are part of the BES, except for generators identified through Inclusion I4 of the BES definition, including:&lt;br/&gt;4.2.5.1 Protection Systems that act to trip the generator either directly or via lockout or auxiliary tripping relays.&lt;br/&gt;4.2.5.2 Protection Systems and Sudden Pressure Relaying for generator step-up transformers for generators that are part of the BES.&lt;br/&gt;4.2.5.3 Protection Systems and Sudden Pressure Relaying for station service or excitation transformers connected to the generator bus of generators which are part of the BES, that act to trip the generator either directly or via lockout or tripping auxiliary relays.&lt;br/&gt;4.2.6 Protection Systems and Sudden Pressure Relaying for the following BES generator Facilities for dispersed power producing resources identified through Inclusion I4 of the BES definition:&lt;br/&gt;4.2.6.1 Protection Systems and Sudden Pressure Relaying for Facilities used in aggregating dispersed BES generation from the point where those resources aggregate to greater than 75 MVA to a common point of connection at 100kV or above.&lt;br/&gt;4.2.7 Automatic Reclosing , including:&lt;br/&gt;4.2.7.1 Automatic Reclosing applied on the terminals of Elements connected to the BES bus located at generating plant substations where the total installed gross generating plant capacity is greater than the gross capacity of the largest BES generating unit within the Balancing Authority Area or, if a member of a Reserve Sharing Group, the largest generating unit within the Reserve Sharing Group. &lt;br/&gt;4.2.7.2 Automatic Reclosing applied on the terminals of all BES Elements at substations one bus away from generating plants specified in Section 4.2.7.1 when the substation is less than 10 circuit-miles from the generating plant substation.&lt;br/&gt;4.2.7.3 Automatic Reclosing applied as an integral part of an RAS specified in Section 4.2.4. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007581 | A list of Transmission Planners, Balancing Authorities, Load Serving Entities, and Distribution Providers that are required to provide the data (“Applicable Entities”). |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-02-18 |  | 2021-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007584 | &lt;p&gt;Integrated hourly Demands in megawatts for the prior calendar year.&lt;/p&gt; |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | &lt;p&gt;This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.”&lt;/p&gt; |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780007590 | &lt;p&gt;Monthly peak hour forecast Total Internal Demands in megawatts for the next two calendar years.&lt;/p&gt; |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | &lt;p&gt;This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.”&lt;/p&gt; |  | 14100000 | NPCC-ON |  | NPCC-US
1 | 79780007596 | &lt;p&gt;The assumptions and methods used in the development of aggregated Peak Demand and Net Energy for Load forecasts.&lt;/p&gt; |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | &lt;p&gt;This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.”&lt;/p&gt; |  | 15100000 | NPCC-ON |  | NPCC-US
1 | 79780007601 | If the Applicable Entity does not provide data requested because (1) the requesting entity did not demonstrate a reliability need for the data; or (2) providing the data would conflict with the Applicable Entity’s confidentiality, regulatory, or security requirements, the Applicable Entity shall, within 30 calendar days of the written request, provide a written response to the requesting entity specifying the data that is not being provided and on what basis. |  | BA, DP, LSE, PCPA, RP, TP | BA | DP | [5 empty] | LSE |  | PA |  |  |  | RP | [5 empty] | TP |  |  | 2016-02-18 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780007608 | within the Contingency Event Recovery Period, demonstrate recovery by returning its Reporting ACE to at least the recovery value of:&lt;br/&gt;• zero (if its Pre-Reporting Contingency Event ACE Value was positive or equal to zero); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event, or&lt;br/&gt;• its Pre-Reporting Contingency Event ACE Value (if its Pre-Reporting Contingency Event ACE Value was negative); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | M1. Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | 2017-04-03 |  | 2017-12-31 |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007611 | 1.3.1 the Responsible Entity:&lt;br/&gt;• is a Balancing Authority experiencing a Reliability Coordinator declared Energy Emergency Alert Level or is a Reserve Sharing Group whose member, or members, are experiencing a Reliability Coordinator declared Energy Emergency Alert level, and&lt;br/&gt;• is utilizing its Contingency Reserve to mitigate an operating emergency in accordance with its emergency Operating Plan, and&lt;br/&gt;• has depleted its Contingency Reserve to a level below its Most Severe Single Contingency or, |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2017-12-31 |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780007621 | that is available a minimum of 99.95% for each calendar year; and, |  | BA | BA | [21 empty] | 2017-11-27 | [5 empty] | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780007623 | a common source to provide information to both Balancing Authorities for the scan rate values used in the calculation of Reporting ACE; and, |  | BA | BA | [21 empty] | 2017-11-27 | [5 empty] | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780007626 | &lt;p&gt;generation Facilities&lt;/p&gt; |  | TO | [22 empty] | 2019-01-01 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007629 | Procedures for coordinated studies of new or materially modified existing interconnections and their impacts on affected system(s). |  | TO | [22 empty] | 2019-01-01 | [5 empty] | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780007632 | Procedures for coordinated studies of new interconnections and their impacts on affected system(s). |  | GO | [22 empty] | 2019-01-01 | [5 empty] | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780007639 | An encroachment into the MVCD as shown in FAC-003-Table 2, observed in Real-time, absent a Sustained Outage, (Footnote: If a later confirmation of a Fault by the applicable Transmission Owner or applicable Generator Owner shows that a vegetation encroachment within the MVCD has occurred from vegetation within the ROW, this shall be considered the equivalent of a Real-time observation.) |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:&lt;br/&gt;4.1.1. Applicable Transmission Owners&lt;br/&gt;4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.&lt;br/&gt;4.1.2. Applicable Generator Owners&lt;br/&gt;4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. &lt;br/&gt;4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.2.1. Each overhead transmission line operated at 200kV or higher.&lt;br/&gt;4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.&lt;br/&gt;4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.&lt;br/&gt;4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. &lt;br/&gt;4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:&lt;br/&gt;4.3.1.1. Operated at 200kV or higher; or&lt;br/&gt;4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or&lt;br/&gt;4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007643 | An encroachment into the MVCD, observed in Real-time, absent a Sustained Outage, |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:&lt;br/&gt;4.1.1. Applicable Transmission Owners&lt;br/&gt;4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.&lt;br/&gt;4.1.2. Applicable Generator Owners&lt;br/&gt;4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. &lt;br/&gt;4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.2.1. Each overhead transmission line operated at 200kV or higher.&lt;br/&gt;4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.&lt;br/&gt;4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.&lt;br/&gt;4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. &lt;br/&gt;4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:&lt;br/&gt;4.3.1.1. Operated at 200kV or higher; or&lt;br/&gt;4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or&lt;br/&gt;4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780007647 | Movement of applicable line conductors under their Rating and all Rated Electrical Operating Conditions; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:&lt;br/&gt;4.1.1. Applicable Transmission Owners&lt;br/&gt;4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.&lt;br/&gt;4.1.2. Applicable Generator Owners&lt;br/&gt;4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. &lt;br/&gt;4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.2.1. Each overhead transmission line operated at 200kV or higher.&lt;br/&gt;4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.&lt;br/&gt;4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.&lt;br/&gt;4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. &lt;br/&gt;4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:&lt;br/&gt;4.3.1.1. Operated at 200kV or higher; or&lt;br/&gt;4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or&lt;br/&gt;4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780007649 | Change in expected growth rate/environmental factors |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:&lt;br/&gt;4.1.1. Applicable Transmission Owners&lt;br/&gt;4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.&lt;br/&gt;4.1.2. Applicable Generator Owners&lt;br/&gt;4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. &lt;br/&gt;4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.2.1. Each overhead transmission line operated at 200kV or higher.&lt;br/&gt;4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.&lt;br/&gt;4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.&lt;br/&gt;4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. &lt;br/&gt;4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:&lt;br/&gt;4.3.1.1. Operated at 200kV or higher; or&lt;br/&gt;4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or&lt;br/&gt;4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780007665 | When modeling normal conditions, all Transmission Elements will be modeled at or below 100% of their continuous rating. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780007684 | Those islands selected by applying the criteria in Requirement D.B.1, and |  | PCPA | [9 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 210000 | NPCC-ON |  | NPCC-US
1 | 79780007687 | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-2 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 310000 | NPCC-ON |  | NPCC-US
1 | 79780007690 | Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES |  | PCPA | [9 empty] | PA | [12 empty] | 2015-10-01 |  | 2017-09-30 |  |  |  | 331000 | NPCC-ON |  | NPCC-US
1 | 79780007694 | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 410000 | NPCC-ON |  | NPCC-US
1 | 79780007702 | The performance of the UFLS equipment, |  | PCPA | [9 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 2010000 | NPCC-ON |  | NPCC-US
1 | 79780007712 | Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-11-13 |  | 2017-09-25 |  |  |  | 2710000 | NPCC-ON |  | NPCC-US
1 | 79780007725 | Criteria for evaluating the quality of Real-time data; |  | TOP | [18 empty] | TOP |  |  |  | 2016-09-22 |  | 2018-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007729 | Criteria for evaluating the quality of Real-time data; |  | BA | BA | [21 empty] | 2016-09-22 |  | 2018-03-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780007733 | Criteria for evaluating the quality of analysis used in its Real-time Assessments; |  | TOP | [18 empty] | TOP |  |  |  | 2016-09-22 |  | 2018-03-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780007739 | Criteria for evaluating the quality of Real-time data; |  | RC | [11 empty] | RC | [10 empty] | 2016-09-22 |  | 2018-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007742 | Criteria for evaluating the quality of analysis used in its Real-time Assessments; |  | RC | [11 empty] | RC | [10 empty] | 2016-09-22 |  | 2018-03-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780007750 | Perform an evaluation of each RAS within its planning area to determine whether: |  | PCPA | [9 empty] | PA | [12 empty] | 2026-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780007751 | The RAS mitigates the System condition(s) or Contingency(ies) for which it was designed. |  | PCPA | [9 empty] | PA | [12 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 41100000 | NPCC-ON |  | NPCC-US
1 | 79780007755 | The BES shall remain stable. |  | PCPA | [9 empty] | PA | [12 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 41410000 | NPCC-ON |  | NPCC-US
1 | 79780007771 | Implement the CAP. |  | DP, GO, PCPA, RC, TO |  | DP |  |  | GO |  |  |  |  | PA |  | RC | [10 empty] | 2017-11-27 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780007776 | Require its operating personnel that issue and receive an oral or written Operating Instruction to use the English language, unless agreed to otherwise. An alternate language may be used for internal operations. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2015-06-22 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007782 | Assess adherence to the documented communications protocols in Requirement R1 by its operating personnel that issue and receive Operating Instructions, provide feedback to those operating personnel and take corrective action, as deemed appropriate by the entity, to address deviations from the documented protocols. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2015-06-22 | [5 empty] | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780007784 | Detected successful login attempts; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 41100000 | NPCC-ON |  | NPCC-US
1 | 79780007786 | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2016-10-28 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007789 | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2016-10-28 | [5 empty] | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780007792 | Its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | 2016-10-28 | [5 empty] | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780007799 | Its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | 2016-10-28 | [5 empty] | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780007804 | Its Reliability Coordinator. |  | BA | BA | [21 empty] | 2016-10-28 | [5 empty] | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780007810 | Its Reliability Coordinator. |  | BA | BA | [21 empty] | 2016-10-28 | [5 empty] | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780007814 | Its Balancing Authority. |  | DP |  | DP | [20 empty] | 2016-10-28 | [5 empty] | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780007817 | Its Balancing Authority. |  | GOP | [5 empty] | GOP | [16 empty] | 2016-10-28 | [5 empty] | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780007825 | The UVLS Program resolves the identified undervoltage issues for which the UVLS Program is designed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-11-19 | [5 empty] | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780007844 | Identify each of the high impact BES Cyber Systems according to Attachment 1, Section 1, if any, at each asset; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-12-27 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency load shedding (UFLS) or undervoltage load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-002-5.1a: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007848 | Review the identifications in Requirement R1 and its parts (and update them if there are changes identified) at least once every 15 calendar months, even if it has no identified items in Requirement R1, and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-12-27 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency load shedding (UFLS) or undervoltage load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-002-5.1a: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780007851 | Criteria for evaluating the quality of Real-time data; |  | RC | [11 empty] | RC | [10 empty] | 2018-04-01 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007852 | Criteria for evaluating the quality of Real-time data; |  | RC | [11 empty] | RC | [10 empty] | 2016-12-14 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007857 | Criteria for evaluating the quality of analysis used in its Real-time Assessments; |  | RC | [11 empty] | RC | [10 empty] | 2016-12-14 | [5 empty] | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780007861 | Criteria for evaluating the quality of Real-time data; |  | TOP | [18 empty] | TOP |  |  |  | 2016-12-14 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007865 | Criteria for evaluating the quality of Real-time data; |  | BA | BA | [21 empty] | 2016-12-14 | [5 empty] | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780007870 | &lt;p&gt;Criteria for evaluating the quality of analysis used in its Real-time Assessments;&lt;/p&gt; |  | TOP | [18 empty] | TOP |  |  |  | 2016-12-14 | [5 empty] | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780007887 | The location and method of implementation for providing backup functionality. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007889 | Tools and applications to ensure that System Operators have situational awareness of the BES. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2019-04-01 | [5 empty] | 12100000 | NPCC-ON |  | NPCC-US
1 | 79780007898 | A list of all entities to notify when there is a change in operating locations. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2019-04-01 | [5 empty] | 16100000 | NPCC-ON |  | NPCC-US
1 | 79780007907 | An update and approval of the Operating Plan for backup functionality shall take place within sixty calendar days of any changes to any part of the Operating Plan described in Requirement R1. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780007908 | The transition time between the simulated loss of primary control center functionality and the time to fully implement the backup functionality. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780007912 | A description of the high-level strategy to be employed during restoration events for restoring the Interconnection, including minimum criteria for meeting the objectives of the Reliability Coordinator’s restoration plan. |  | RC | [11 empty] | RC | [10 empty] | 2018-03-26 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007922 | If a Reliability Coordinator finds conflicts between its restoration plans and any of its neighbors, the conflicts shall be resolved within 30 calendar days of receipt of written notification. |  | RC | [11 empty] | RC | [10 empty] | 2018-03-26 | [5 empty] | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780007924 | The Reliability Coordinator shall determine whether the Transmission Operator’s restoration plan is coordinated and compatible with the Reliability Coordinator’s restoration plan and other Transmission Operators’ restoration plans within its Reliability Coordinator Area. The Reliability Coordinator shall provide notification to the Transmission Operator of approval or disapproval, with stated reasons, of the Transmission Operator’s submitted restoration plan within 30 calendar days following the receipt of the restoration plan from the Transmission Operator. |  | RC | [11 empty] | RC | [10 empty] | 2018-03-26 | [5 empty] | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780007927 | The coordination role of the Reliability Coordinator; and |  | RC | [11 empty] | RC | [10 empty] | 2018-03-26 | [5 empty] | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780007930 | Each Reliability Coordinator shall request each Transmission Operator identified in its restoration plan and each Generator Operator identified in the Transmission Operators’ restoration plans to participate in a drill, exercise, or simulation at least once every two calendar years. |  | RC | [11 empty] | RC | [10 empty] | 2018-03-26 | [5 empty] | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780007932 | Strategies for System restoration that are coordinated with its Reliability Coordinator’s high level strategy for restoring the Interconnection. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007944 | Within 90 calendar days after identifying any unplanned permanent BES modifications. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780007948 | The capability of Blackstart Resources to meet the Real and Reactive Power requirements of the Cranking Paths and the dynamic capability to supply initial Loads. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780007952 | The frequency of testing such that each Blackstart Resource is tested at least once every three calendar years. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780007954 | The ability to start the unit when isolated with no support from the BES or when designed to remain energized without connection to the remainder of the System. |  | TOP | [18 empty] | TOP |  |  |  | 2019-04-01 | [5 empty] | 72100000 | NPCC-ON |  | NPCC-US
1 | 79780007958 | System restoration plan including coordination with its Reliability Coordinator and Generator Operators included in the restoration plan. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780007969 | Testing records shall include at a minimum: name of the Blackstart Resource, unit tested, date of the test, duration of the test, time required to start the unit, an indication of any testing requirements not met under Requirement R7. |  | GOP | [5 empty] | GOP | [16 empty] | 2018-03-26 | [5 empty] | 141000000 | NPCC-ON |  | NPCC-US
1 | 79780007971 | System restoration plan including coordination with the Transmission Operator |  | GOP | [5 empty] | GOP | [16 empty] | 2018-03-26 | [5 empty] | 151000000 | NPCC-ON |  | NPCC-US
1 | 79780007986 | For its high impact and medium impact BES Cyber Systems, if any: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2018-06-25 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780007988 | Personnel and training (CIP-004); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780007998 | Cyber security awareness; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12100000 | NPCC-ON |  | NPCC-US
1 | 79780008023 | Monitor Facilities within its Transmission Operator Area; |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-17 |  | 2021-03-31 |  |  |  | 101000000 | NPCC-ON |  | NPCC-US
1 | 79780008043 | within the Contingency Event Recovery Period, demonstrate recovery by returning its Reporting ACE to at least the recovery value of:&lt;br/&gt;• zero (if its Pre-Reporting Contingency Event ACE Value was positive or equal to zero); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event,&lt;br/&gt;or,&lt;br/&gt;• its Pre-Reporting Contingency Event ACE Value (if its Pre-Reporting Contingency Event ACE Value was negative); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2017-10-02 |  | 2019-03-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780008046 | the Responsible Entity:&lt;br/&gt;• is a Balancing Authority experiencing a Reliability Coordinator declared Energy Emergency Alert Level or is a Reserve Sharing Group whose member, or members, are experiencing a Reliability Coordinator declared Energy Emergency Alert level, and&lt;br/&gt;• is utilizing its Contingency Reserve to mitigate an operating emergency in accordance with its emergency Operating Plan, and&lt;br/&gt;• has depleted its Contingency Reserve to a level below its Most Severe Single Contingency&lt;br/&gt;or, |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2018-01-01 |  | 2019-03-31 |  |  |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780008051 | Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. |  | TOP | [18 empty] | TOP |  |  |  | 2017-09-26 |  | 2018-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780008052 | Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. |  | TOP | [18 empty] | TOP |  |  |  | 2017-09-26 |  | 2018-12-31 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780008056 | If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. |  | TOP | [18 empty] | TOP |  |  |  | 2017-09-26 |  | 2018-12-31 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780008058 | The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  |  | 2017-09-26 |  | 2018-12-31 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780008068 | Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances. |  | GOP | [5 empty] | GOP | [16 empty] | 2017-09-26 |  | 2018-12-31 |  |  |  | 2710000 | NPCC-ON |  | NPCC-US
1 | 79780008072 | When a generator’s AVR is out of service or the generator does not have an AVR, the Generator Operator shall use an alternative method to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2017-09-26 | [5 empty] | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780008078 | For generator step-up and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: (Footnote: For dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition, this requirement applies only to those transformers that have at least one winding at a voltage of 100 kV or above.) |  | GO | [22 empty] | 2017-09-26 | [5 empty] | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780008079 | Tap settings. |  | GO | [22 empty] | 2017-09-26 | [5 empty] | 51100000 | NPCC-ON |  | NPCC-US
1 | 79780008084 | If the Generator Owner cannot comply with the Transmission Operator’s specifications, the Generator Owner shall notify the Transmission Operator and shall provide the technical justification. |  | GO | [22 empty] | 2017-09-26 | [5 empty] | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780008086 | One or more process(es) used in planning for the procurement of BES Cyber Systems to identify and assess cyber security risk(s) to the Bulk Electric System from vendor products or services resulting from: (i) procuring and installing vendor equipment and software; and (ii) transitions from one vendor(s) to another vendor(s). |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and&lt;br/&gt;4.1.2.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and&lt;br/&gt;4.2.1.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers&lt;br/&gt;4.2.2.1. All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-013-1:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the identification and categorization process required by CIP-002-5, or any subsequent version of that Reliability Standard. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780008088 | Notification by the vendor of vendor-identified incidents related to the products or services provided to the Responsible Entity that pose cyber security risk to the Responsible Entity; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and&lt;br/&gt;4.1.2.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and&lt;br/&gt;4.2.1.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers&lt;br/&gt;4.2.2.1. All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-013-1:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the identification and categorization process required by CIP-002-5, or any subsequent version of that Reliability Standard. |  | 12100000 | NPCC-ON |  | NPCC-US
1 | 79780008097 | All applicable Cyber Assets connected to a network via a routable protocol shall reside within a defined ESP. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a list of all ESPs with all uniquely identifiable applicable Cyber Assets connected via a routable protocol within each ESP. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-005-6:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780008103 | For all Interactive Remote Access, utilize an Intermediate System such that the Cyber Asset initiating Interactive Remote Access does not directly access an applicable Cyber Asset. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, network diagrams or architecture documents. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-005-6:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780008109 | Develop a baseline configuration, individually or by group, which shall include the following items: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: &lt;br/&gt;• A spreadsheet identifying the required items of the baseline configuration for each Cyber Asset, individually or by group; or&lt;br/&gt;• A record in an asset management system that identifies the required items of the baseline configuration for each Cyber Asset, individually or by group. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780008110 | Operating system(s) (including version) or firmware where no independent operating system exists; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780008118 | Prior to the change, determine required cyber security controls in CIP-005 and CIP-007 that could be impacted by the change; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 14100000 | NPCC-ON |  | NPCC-US
1 | 79780008122 | Prior to implementing any change in the production environment, test the changes in a test environment or test the changes in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration to ensure that required cyber security controls in CIP-005 and CIP-007 are not adversely affected; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 15100000 | NPCC-ON |  | NPCC-US
1 | 79780008125 | Verify the identity of the software source; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 16100000 | NPCC-ON |  | NPCC-US
1 | 79780008128 | Monitor at least once every 35 calendar days for changes to the baseline configuration (as described in Requirement R1, Part 1.1). Document and investigate detected unauthorized changes. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, logs from a system that is monitoring the configuration along with records of investigation for any unauthorized changes that were detected. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780008130 | At least once every 15 calendar months, conduct a paper or active vulnerability assessment. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: &lt;br/&gt;• A document listing the date of the assessment (performed at least once every 15 calendar months), the controls assessed for each BES Cyber System along with the method of assessment; or&lt;br/&gt;• A document listing the date of the assessment and the output of any tools used to perform the assessment. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780008132 | Perform an active vulnerability assessment in a test environment, or perform an active vulnerability assessment in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration of the BES Cyber System in a production environment; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 32100000 | NPCC-ON |  | NPCC-US
1 | 79780008166 | Those islands selected by applying the criteria in Requirement R1, and |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780008170 | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-3 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780008174 | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-3 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780008189 | The performance of the UFLS equipment, |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 111000000 | NPCC-ON |  | NPCC-US
1 | 79780008195 | For UFLS design assessments performed under Requirement R4 or R5, the Corrective Action Plan shall be developed within the five-year time frame identified in Requirement R4. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 151000000 | NPCC-ON |  | NPCC-US
1 | 79780008330 | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780008331 | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  |  | 41100000 | NPCC-ON |  | NPCC-US
1 | 79780008335 | If a recipient of the benchmark GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  |  | 43100000 | NPCC-ON |  | NPCC-US
1 | 79780008337 | The maximum effective GIC value for the worst case geoelectric field orientation for the benchmark GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-01-01 |  | 2019-06-30 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780008340 | Be based on the effective GIC flow information provided in Requirement R5; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2019-06-30 |  |  |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780008345 | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include:&lt;br/&gt;• Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment.&lt;br/&gt;• Installation, modification, or removal of Protection Systems or Remedial Action Schemes.&lt;br/&gt;• Use of Operating Procedures, specifying how long they will be needed as part of the CAP.&lt;br/&gt;• Use of Demand-Side Management, new technologies, or other initiatives. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780008348 | Specify implementation of non-hardware mitigation, if any, within two years of development of the CAP; and |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  |  | 73100000 | NPCC-ON |  | NPCC-US
1 | 79780008351 | Circumstances causing the delay for fully or partially implementing the selected actions in Part 7.1; |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  |  | 74100000 | NPCC-ON |  | NPCC-US
1 | 79780008355 | If a recipient of the CAP provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  |  | 75100000 | NPCC-ON |  | NPCC-US
1 | 79780008357 | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780008358 | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  |  | 81100000 | NPCC-ON |  | NPCC-US
1 | 79780008363 | If a recipient of the supplemental GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  |  | 84100000 | NPCC-ON |  | NPCC-US
1 | 79780008365 | The maximum effective GIC value for the worst case geoelectric field orientation for the supplemental GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2019-01-25 |  | 2019-06-30 |  |  |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780008368 | Be based on the effective GIC flow information provided in Requirement R9; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2019-06-30 |  |  |  | 101000000 | NPCC-ON |  | NPCC-US
1 | 79780008391 | If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. |  | TOP | [18 empty] | TOP |  |  |  | 2014-08-01 |  | 2015-11-12 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780008396 | Areas of Competency |  | RC | [11 empty] | RC | [10 empty] | 2018-11-21 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780008397 | Resource and demand balancing |  | RC | [11 empty] | RC | [10 empty] | 2019-07-01 | [5 empty] | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780008406 | Areas of Competency |  | TOP | [18 empty] | TOP |  |  |  | 2018-11-21 | [5 empty] | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780008407 | Transmission operations |  | TOP | [18 empty] | TOP |  |  |  | 2019-07-01 | [5 empty] | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780008414 | Areas of Competency |  | BA | BA | [21 empty] | 2018-11-21 | [5 empty] | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780008415 | Resources and demand balancing |  | BA | BA | [21 empty] | 2019-07-01 | [5 empty] | 31100000 | NPCC-ON |  | NPCC-US
1 | 79780008423 | within the Contingency Event Recovery Period, demonstrate recovery by returning its Reporting ACE to at least the recovery value of:&lt;br/&gt;• zero (if its Pre-Reporting Contingency Event ACE Value was positive or equal to zero); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event,&lt;br/&gt;or,&lt;br/&gt;• its Pre-Reporting Contingency Event ACE Value (if its Pre-Reporting Contingency Event ACE Value was negative); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2019-04-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780008426 | is (i) a Balancing Authority or (ii) a Reserve Sharing Group with at least one member that:&lt;br/&gt;• is experiencing a Reliability Coordinator declared Energy Emergency Alert Level, and&lt;br/&gt;• is utilizing its Contingency Reserve to mitigate an operating emergency in accordance with its emergency Operating Plan, and&lt;br/&gt;• has depleted its Contingency Reserve to a level below its Most Severe Single Contingency, and&lt;br/&gt;• has, during communications with its Reliability Coordinator in accordance with the Energy Emergency Alert procedures, (i) notified the Reliability Coordinator of the conditions described in the preceding two bullet points preventing the Responsible Entity from complying with Requirement R1 part 1.1, and (ii) provided the Reliability Coordinator with an ACE recovery plan, including target recovery time &lt;br/&gt;or, |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2019-04-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780008430 | Identification of security protection used to mitigate the risks posed by unauthorized disclosure and unauthorized modification of Real-time Assessment and Real-time monitoring data while being transmitted between Control Centers; |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-04-13 |  |  |  | 4.2. Exemptions: The following are exempt from Reliability Standard CIP-012-1:&lt;br/&gt;4.2.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3. A Control Center that transmits to another Control Center Real-time Assessment or Real-time monitoring data pertaining only to the generation resource or Transmission station or substation co-located with the transmitting Control Center. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780008434 | Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. |  | TOP | [18 empty] | TOP |  |  |  | 2018-10-15 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780008440 | The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  | For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. | 2018-10-15 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780008452 | System models shall represent: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-04-13 |  | 2020-06-10 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780008453 | Existing Facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP | [8 empty] | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780008459 | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by current annual studies or qualified past studies as indicated in Requirement R2, Part 2.6. Qualifying studies need to include the following conditions: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-04-13 |  | 2020-06-10 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780008460 | System peak Load for either Year One or year two, and for year five. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP | [8 empty] | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780008466 | A current study assessing expected System peak Load conditions for one of the years in the Long-Term Transmission Planning Horizon and the rationale for why that year was selected. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP | [8 empty] | 22100000 | NPCC-ON |  | NPCC-US
1 | 79780008469 | System peak Load for one of the five years. System peak Load levels shall include a Load model which represents the expected dynamic behavior of Loads that could impact the study area, considering the behavior of induction motor Loads. An aggregate System Load model which represents the overall dynamic behavior of the Load is acceptable. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP | [8 empty] | 24100000 | NPCC-ON |  | NPCC-US
1 | 79780008477 | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: &lt;br/&gt;• Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. &lt;br/&gt;• Installation, modification, or removal of Protection Systems or Remedial Action Schemes. &lt;br/&gt;• Installation or modification of automatic generation tripping as a response to a single or multiple Contingency to mitigate Stability performance violations. &lt;br/&gt;• Installation or modification of manual and automatic generation runback/tripping as a response to a single or multiple Contingency to mitigate steady state performance violations. &lt;br/&gt;• Use of Operating Procedures specifying how long they will be needed as part of the Corrective Action Plan. &lt;br/&gt;• Use of rate applications, DSM, new technologies, or other initiatives. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP | [8 empty] | 27100000 | NPCC-ON |  | NPCC-US
1 | 79780008482 | List System deficiencies and the associated actions needed to achieve required System performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP | [8 empty] | 28100000 | NPCC-ON |  | NPCC-US
1 | 79780008491 | Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R3, Part 3.4. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-04-13 |  | 2020-06-10 |  |  |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780008494 | Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP | [8 empty] | 33100000 | NPCC-ON |  | NPCC-US
1 | 79780008496 | Tripping of generators where simulations show generator bus voltages or high side of the generation step up (GSU) voltages are less than known or assumed minimum generator steady state or ride through voltage limitations. Include in the assessment any assumptions made. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP | [8 empty] | 33110000 | NPCC-ON |  | NPCC-US
1 | 79780008500 | The Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP | [8 empty] | 34100000 | NPCC-ON |  | NPCC-US
1 | 79780008507 | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-3 - Attachment 1A, either for 60 seconds or until a steady-state condition between 59.0 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 11000 | NPCC-ON |  | NPCC-US
1 | 79780008511 | Underfrequency trip settings of individual generating units that are part of Quebec BES plants/facilities that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-3 - Attachment 1A, and |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 110000 | NPCC-ON |  | NPCC-US
1 | 79780008519 | One or more processes to identify, classify, and respond to Cyber Security Incidents. |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, dated documentation of Cyber Security Incident response plan(s) that include the process(es) to identify, classify, and respond to Cyber Security Incidents. | 2019-06-20 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780008521 | &lt;p&gt;That include criteria to evaluate and define attempts to compromise;&lt;/p&gt; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2021-01-01 |  |  |  | &lt;p&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes.&lt;/p&gt; |  | 12100000 | NPCC-ON |  | NPCC-US
1 | 79780008527 | &lt;p&gt;Test each Cyber Security Incident response plan(s) at least once every 15 calendar months: &lt;br/&gt;• By responding to an actual Reportable Cyber Security Incident; &lt;br/&gt;• With a paper drill or tabletop exercise of a Reportable Cyber Security Incident; or&lt;br/&gt;• With an operational exercise of a Reportable Cyber Security Incident.&lt;/p&gt; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | &lt;p&gt;Examples of evidence may include, but are not limited to, dated evidence of a lessons-learned report that includes a summary of the test or a compilation of notes, logs, and communication resulting from the test. Types of exercises may include discussion or operations based exercises.&lt;/p&gt; | 2019-06-20 |  |  |  | &lt;p&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes.&lt;/p&gt; |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780008532 | No later than 90 calendar days after completion of a Cyber Security Incident response plan(s) test or actual Reportable Cyber Security Incident response: |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, all of the following:&lt;br/&gt;1. Dated documentation of post incident(s) review meeting notes or follow-up report showing lessons learned associated with the Cyber Security Incident response plan(s) test or actual Reportable Cyber Security Incident response or dated documentation stating there were no lessons learned;&lt;br/&gt;2. Dated and revised Cyber Security Incident response plan showing any changes based on the lessons learned; and&lt;br/&gt;3. Evidence of plan update distribution including, but not limited to:&lt;br/&gt;• Emails; &lt;br/&gt;• USPS or other mail service; &lt;br/&gt;• Electronic distribution system; or &lt;br/&gt;• Training sign-in sheets. | 2019-06-20 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780008533 | &lt;p&gt;Document any lessons learned or document the absence of any lessons learned;&lt;/p&gt; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2021-01-01 |  |  |  | &lt;p&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes.&lt;/p&gt; |  | 31100000 | NPCC-ON |  | NPCC-US
1 | 79780008537 | Update the Cyber Security Incident response plan(s); and | [24 empty] | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | 32100000 | NPCC-ON |  | NPCC-US
1 | 79780008539 | &lt;p&gt;Initial notifications and updates shall include the following attributes, at a minimum, to the extent known:&lt;/p&gt; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | &lt;p&gt;Examples of evidence may include, but are not limited to, dated documentation of initial notifications and updates to the E-ISAC and NCCIC.&lt;/p&gt; | 2019-06-20 |  |  |  | &lt;p&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes.&lt;/p&gt; |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780008540 | &lt;p&gt;The functional impact;&lt;/p&gt; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2021-01-01 |  |  |  | &lt;p&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes.&lt;/p&gt; |  | 41100000 | NPCC-ON |  | NPCC-US
1 | 79780008552 | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2020-10-05 |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780008553 | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 41100000 | NPCC-ON |  | NPCC-US
1 | 79780008557 | If a recipient of the benchmark GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 43100000 | NPCC-ON |  | NPCC-US
1 | 79780008559 | The maximum effective GIC value for the worst case geoelectric field orientation for the benchmark GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-01-01 |  | 2020-10-05 |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780008565 | Be based on the effective GIC flow information provided in Requirement R5; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2020-10-05 |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780008570 | 7.1. List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include:&lt;br/&gt;• Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment.&lt;br/&gt;• Installation, modification, or removal of Protection Systems or Remedial Action Schemes.&lt;br/&gt;• Use of Operating Procedures, specifying how long they will be needed as part of the CAP.&lt;br/&gt;• Use of Demand-Side Management, new technologies, or other initiatives. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2020-10-05 |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780008575 | Specify implementation of non-hardware mitigation, if any, within two years of development of the CAP; and |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 73100000 | NPCC-ON |  | NPCC-US
1 | 79780008577 | Circumstances causing the delay for fully or partially implementing the selected actions in Part 7.1; |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 74100000 | NPCC-ON |  | NPCC-US
1 | 79780008580 | If a recipient of the CAP provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 75100000 | NPCC-ON |  | NPCC-US
1 | 79780008582 | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2020-10-05 |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780008586 | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 81100000 | NPCC-ON |  | NPCC-US
1 | 79780008588 | If a recipient of the supplemental GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 84100000 | NPCC-ON |  | NPCC-US
1 | 79780008590 | The maximum effective GIC value for the worst case geoelectric field orientation for the supplemental GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-01-01 |  | 2020-10-05 |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780008598 | Be based on the effective GIC flow information provided in Requirement R9; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2020-10-05 |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 101000000 | NPCC-ON |  | NPCC-US
1 | 79780008604 | If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. |  | TOP | [18 empty] | TOP |  |  | For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. | 2019-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780008680 | For its high impact and medium impact BES Cyber Systems, if any: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2019-07-31 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service &lt;br/&gt;&lt;br/&gt;equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780008681 | Personnel and training (CIP-004); | [28 empty] | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service &lt;br/&gt;&lt;br/&gt;equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780008691 | Cyber security awareness; | [28 empty] | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service &lt;br/&gt;&lt;br/&gt;equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12100000 | NPCC-ON |  | NPCC-US
1 | 79780008700 | UFLS program, including a schedule for implementation |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 141000000 | NPCC-ON |  | NPCC-US
1 | 79780008705 | Each Source and Sink Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if it does not expect to be capable of supporting the magnitude of the Interchange, including ramping, throughout the duration of the Arranged Interchange. |  | BA | BA | [21 empty] | 2021-04-01 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780008707 | Each Transmission Service Provider shall deny the Arranged Interchange or curtail Confirmed Interchange if the transmission path (proper connectivity of adjacent Transmission Service Providers) between it and its adjacent Transmission Service Providers is invalid. |  | TSP | [20 empty] | TSP |  | 2021-04-01 | [5 empty] | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780008712 | Identical in magnitude to that of the Adjacent Balancing Authority, and |  | BA | BA | [21 empty] | 2021-04-01 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780008723 | The documentation shall contain assumptions used to rate the generator and at least one of the following:&lt;br/&gt;• Design or construction information such as design criteria, ratings provided by equipment manufacturers, equipment drawings and/or specifications, engineering analyses, method(s) consistent with industry standards (e.g. ANSI and IEEE), or an established engineering practice that has been verified by testing or engineering analysis.&lt;br/&gt;• Operational information such as commissioning test results, performance testing or historical performance records, any of which may be supplemented by engineering analyses. |  | GO | [28 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780008725 | The methodology used to establish the Ratings of the equipment that comprises the Facility(ies) shall be consistent with at least one of the following:&lt;br/&gt;• Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating.&lt;br/&gt;• One or more industry standards developed through an open process such as Institute of Electrical and Electronic Engineers (IEEE) or International Council on Large Electric Systems (CIGRE).&lt;br/&gt;• A practice that has been verified by testing, performance history or engineering analysis. |  | GO | [28 empty] | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780008729 | Equipment Rating standard(s) used in development of this methodology. |  | GO | [28 empty] | 22100000 | NPCC-ON |  | NPCC-US
1 | 79780008733 | The scope of equipment addressed shall include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | GO | [28 empty] | 24100000 | NPCC-ON |  | NPCC-US
1 | 79780008735 | The methodology used to establish the Ratings of the equipment that comprises the Facility shall be consistent with at least one of the following:&lt;br/&gt;• Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating.&lt;br/&gt;• One or more industry standards developed through an open process such as Institute of Electrical and Electronics Engineers (IEEE) or International Council on Large Electric Systems (CIGRE).&lt;br/&gt;• A practice that has been verified by testing, performance history or engineering analysis. |  | TO | [28 empty] | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780008740 | Equipment Rating standard(s) used in development of this methodology. |  | TO | [28 empty] | 32100000 | NPCC-ON |  | NPCC-US
1 | 79780008744 | The scope of equipment addressed shall include, but not be limited to, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | TO | [28 empty] | 34100000 | NPCC-ON |  | NPCC-US
1 | 79780008747 | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Protection Systems for BES Elements, with the following exclusions:&lt;br/&gt;4.2.1.1 Non-protective functions that are embedded within a Protection System.&lt;br/&gt;4.2.1.2 Protective functions intended to operate as a control function during switching. &lt;br/&gt;4.2.1.3 Special Protection Systems (SPS).&lt;br/&gt;4.2.1.4 Remedial Action Schemes (RAS).&lt;br/&gt;4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.&lt;br/&gt;4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.&lt;br/&gt;4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780008751 | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Protection Systems for BES Elements, with the following exclusions:&lt;br/&gt;4.2.1.1 Non-protective functions that are embedded within a Protection System.&lt;br/&gt;4.2.1.2 Protective functions intended to operate as a control function during switching. &lt;br/&gt;4.2.1.3 Special Protection Systems (SPS).&lt;br/&gt;4.2.1.4 Remedial Action Schemes (RAS).&lt;br/&gt;4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.&lt;br/&gt;4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.&lt;br/&gt;4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780008752 | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Protection Systems for BES Elements, with the following exclusions:&lt;br/&gt;4.2.1.1 Non-protective functions that are embedded within a Protection System.&lt;br/&gt;4.2.1.2 Protective functions intended to operate as a control function during switching. &lt;br/&gt;4.2.1.3 Special Protection Systems (SPS).&lt;br/&gt;4.2.1.4 Remedial Action Schemes (RAS).&lt;br/&gt;4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.&lt;br/&gt;4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.&lt;br/&gt;4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 21100000 | NPCC-ON |  | NPCC-US
1 | 79780008772 | Monitor Facilities within its Transmission Operator Area; |  | TOP | [18 empty] | TOP |  |  |  | 2021-04-01 | [5 empty] | 101000000 | NPCC-ON |  | NPCC-US
1 | 79780008800 | Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. |  | TOP | [18 empty] | TOP | [5 empty] | 2020-05-14 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780008804 | If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. |  | TOP | [18 empty] | TOP | [5 empty] | 2020-05-14 |  |  |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780008806 | The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). |  | TOP | [18 empty] | TOP | [5 empty] | 2020-05-14 |  |  |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780008847 | Less than zero at all times, and |  | BA | BA | [21 empty] | 2020-07-15 |  |  |  | Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780008907 | Design measures to prevent the generating unit from tripping directly or indirectly for underfrequency conditions above the appropriate generator tripping threshold curve in Figure 2. | [28 empty] | 4.1.3. Distribution Providers that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators&lt;br/&gt;4.1.4. Transmission Owners that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators |  | 121000000 | NPCC-ON |  | NPCC-US
1 | 79780008909 | Each Generator Owner shall set the underfrequency protection to operate at the lowest frequency allowed by the plant design and licensing limitations. |  | GO | [22 empty] | 2020-02-18 |  |  |  | 4.1.3. Distribution Providers that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators&lt;br/&gt;4.1.4. Transmission Owners that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators |  | 131000000 | NPCC-ON |  | NPCC-US
1 | 79780008913 | Set the underfrequency protection to operate at a frequency setting that is as low as possible in accordance with the plant design and licensing limitations but not greater than 57.8 Hz. |  | GO | [22 empty] | 2020-02-18 |  |  |  | 4.1.3. Distribution Providers that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators&lt;br/&gt;4.1.4. Transmission Owners that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators |  | 161000000 | NPCC-ON |  | NPCC-US
1 | 79780008985 | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780008990 | If a recipient of the benchmark GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 43100000 | NPCC-ON |  | NPCC-US
1 | 79780008992 | The maximum effective GIC value for the worst case geoelectric field orientation for the benchmark GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-03-19 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780008995 | Be based on the effective GIC flow information provided in Requirement R5; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 61000000 | NPCC-ON |  | NPCC-US
1 | 79780009000 | 7.1. List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include:&lt;br/&gt;• Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment.&lt;br/&gt;• Installation, modification, or removal of Protection Systems or Remedial Action Schemes.&lt;br/&gt;• Use of Operating Procedures, specifying how long they will be needed as part of the CAP.&lt;br/&gt;• Use of Demand-Side Management, new technologies, or other initiatives. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 71000000 | NPCC-ON |  | NPCC-US
1 | 79780009003 | Specify implementation of non-hardware mitigation, if any, within two years of development of the CAP; and | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 73100000 | NPCC-ON |  | NPCC-US
1 | 79780009006 | Circumstances causing the delay for fully or partially implementing the selected actions in Part 7.1 and how those circumstances are beyond the control of the responsible entity; | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 74100000 | NPCC-ON |  | NPCC-US
1 | 79780009011 | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 81000000 | NPCC-ON |  | NPCC-US
1 | 79780009017 | If a recipient of the supplemental GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 83100000 | NPCC-ON |  | NPCC-US
1 | 79780009019 | The maximum effective GIC value for the worst case geoelectric field orientation for the supplemental GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-03-19 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780009022 | Be based on the effective GIC flow information provided in Requirement R9; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 101000000 | NPCC-ON |  | NPCC-US
1 | 79780009030 | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include:&lt;br/&gt;• Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment.&lt;br/&gt;• Installation, modification, or removal of Protection Systems or Remedial Action Schemes.&lt;br/&gt;• Use of Operating Procedures, specifying how long they will be needed as part of the CAP.&lt;br/&gt;• Use of Demand-Side Management, new technologies, or other initiatives. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 111000000 | NPCC-ON |  | NPCC-US
1 | 79780009033 | Specify implementation of non-hardware mitigation, if any, within two years of development of the CAP; and | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 113100000 | NPCC-ON |  | NPCC-US
1 | 79780009036 | Circumstances causing the delay for fully or partially implementing the selected actions in Part 11.1 and how those circumstances are beyond the control of the responsible entity; | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 114100000 | NPCC-ON |  | NPCC-US
1 | 79780009058 | The reliability impact of the new interconnection, or materially modified existing interconnection, on affected system(s); |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2021-04-01 |  |  |  | Applicable Generator Owner: Generator Owner with a fully executed Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780009067 | A list of data and information needed by the Reliability Coordinator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data, as deemed necessary by the Reliability Coordinator. |  | RC | [11 empty] | RC | [10 empty] | 2021-04-01 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780009073 | A mutually agreeable format |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2021-04-01 | [5 empty] | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780009077 | A list of Transmission Planners, Balancing Authorities, and Distribution Providers that are required to provide the data (“Applicable Entities”). |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780009080 | Integrated hourly Demands in megawatts for the prior calendar year. | [24 empty] | 2021-04-01 | [5 empty] | 13100000 | NPCC-ON |  | NPCC-US
1 | 79780009086 | Monthly peak hour forecast Total Internal Demands in megawatts for the next two calendar years. | [24 empty] | 2021-04-01 | [5 empty] | 14100000 | NPCC-ON |  | NPCC-US
1 | 79780009100 | If the Applicable Entity does not provide data requested because (1) the requesting entity did not demonstrate a reliability need for the data; or (2) providing the data would conflict with the Applicable Entity’s confidentiality, regulatory, or security requirements, the Applicable Entity shall, within 30 calendar days of the written request, provide a written response to the requesting entity specifying the data that is not being provided and on what basis. |  | BA, DP, PCPA, RP, TP | BA | DP | [7 empty] | PA |  |  |  | RP | [5 empty] | TP |  |  | 2021-04-01 | [5 empty] | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780009102 | Comparison of the performance of the Planning Coordinator’s portion of the existing system in a planning power flow model to actual system behavior, represented by a state estimator case or other Real-time data sources, at least once every 24 calendar months through simulation; |  | PCPA | [9 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780009111 | Incorporate the NPIRs into their operating analyses of the electric system. |  | BA, DP, GO, GOP, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  |  |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780009119 | Retired. [Note: Part 9.1 was retired under the Paragraph 81 project. The NUC SDT proposes to leave this Part blank to avoid renumbering Requirement parts that would impact existing agreements throughout the industry.] |  | BA, DP, GO, GOP, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  |  |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 91000000 | NPCC-ON |  | NPCC-US
1 | 79780009121 | Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the Agreement. | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 92100000 | NPCC-ON |  | NPCC-US
1 | 79780009125 | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 93100000 | NPCC-ON |  | NPCC-US
1 | 79780009133 | Provisions for communications affecting the NPIRs between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of applicable unique terms | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 94100000 | NPCC-ON |  | NPCC-US
1 | 79780009171 | Those islands selected by applying the criteria in Requirement R1, and |  | PCPA | [9 empty] | PA | [16 empty] | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780009175 | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-4 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [16 empty] | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780009179 | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1. |  | PCPA | [9 empty] | PA | [16 empty] | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 41000000 | NPCC-ON |  | NPCC-US
1 | 79780009193 | The performance of the UFLS equipment, |  | PCPA | [9 empty] | PA | [16 empty] | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 111000000 | NPCC-ON |  | NPCC-US
1 | 79780009198 | UFLS program, including a schedule for implementation |  | PCPA | [9 empty] | PA | [16 empty] | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 141000000 | NPCC-ON |  | NPCC-US
1 | 79780009202 | For UFLS design assessments performed under Requirement R4 or R5, the Corrective Action Plan shall be developed within the five-year time frame identified in Requirement R4. |  | PCPA | [9 empty] | PA | [16 empty] | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 151000000 | NPCC-ON |  | NPCC-US
1 | 79780009205 | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data as deemed necessary by the Transmission Operator. |  | TOP | [18 empty] | TOP |  |  |  | 2021-04-01 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780009210 | A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. |  | BA | BA | [21 empty] | 2021-04-01 | [5 empty] | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780009217 | A mutually agreeable format |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  |  | 2021-04-01 | [5 empty] | 51000000 | NPCC-ON |  | NPCC-US
1 | 79780009223 | 3.1. The Generator Owner shall communicate the documented regulatory or equipment limitation, or the removal of a previously documented regulatory or equipment limitation, to its Planning Coordinator and Transmission Planner within 30 calendar days of any of the following:&lt;br/&gt;• Identification of a regulatory or equipment limitation.&lt;br/&gt;• Repair of the equipment causing the limitation that removes the limitation. &lt;br/&gt;• Replacement of the equipment causing the limitation with equipment that removes the limitation.&lt;br/&gt;• Creation or adjustment of an equipment limitation caused by consumption of the cumulative turbine life-time frequency excursion allowance. |  | GO | [22 empty] | 2020-07-09 |  |  |  | 4.1. Functional Entities: &lt;br/&gt;4.1.1 Generator Owners that apply protection listed in Section 4.2.1. &lt;br/&gt;4.1.2 Transmission Owners (in the Quebec Interconnection only) that own a BES generator step-up (GSU) transformer or main power transformer (MPT)1 and apply protection listed in Section 4.2.1. &lt;br/&gt;4.1.3 Planning Coordinators (in the Quebec Interconnection only) &lt;br/&gt;&lt;br/&gt;4.2. Facilities2: &lt;br/&gt;4.2.1 Frequency, voltage, and volts per hertz protection (whether provided by relaying or functions within associated control systems) that respond to electrical signals and: (i) directly trip the generating resource(s); or (ii) provide signals to the generating resource(s) to either trip or cease injecting current; and are applied to the following:&lt;br/&gt;4.2.1.1 BES generating resource(s). 4.2.1.2 BES GSU transformer(s). &lt;br/&gt;4.2.1.3 High side of the generator-connected unit auxiliary transformer3 (UAT) installed on BES generating resource(s). &lt;br/&gt;4.2.1.4 Individual dispersed power producing resource(s) identified in the BES Definition, Inclusion I4. 4.2.1.5 Elements that are designed primarily for the delivery of capacity from the individual dispersed power producing resources identified in the BES Definition, Inclusion I4, to the point where those resources aggregate to greater than 75 MVA. &lt;br/&gt;4.2.1.6 MPT4 of resource(s) identified in the BES Definition, Inclusion I4. &lt;br/&gt;4.2.2 Exemptions: Protection on all auxiliary equipment within the generating Facility. &lt;br/&gt;&lt;br/&gt;1 For the purpose of this standard, the MPT is the power transformer that steps up voltage from the collection system voltage to the nominal transmission/interconnecting system voltage for dispersed power producing resources. &lt;br/&gt;2 It is not required to install or activate the protections described in Facilities Section 4.2. &lt;br/&gt;3 These transformers are variably referred to as station power UAT, or station service transformer(s) used to provide overall auxiliary power to the generating resource(s). This UAT is the transformer connected on the generator bus between the low side of the GSU and the generator terminal. &lt;br/&gt;4 For the purpose of this standard, the MPT is the power transformer that steps up voltage from the collection system voltage to the nominal transmission/interconnecting system voltage for dispersed power producing resources |  | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780009254 | Identify each of the high impact BES Cyber System according to Attachment 1, Section 1, if any, at each asset; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [5 empty] | 2021-02-04 |  |  |  | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780009258 | Review the identifications in Requirement R1 and its parts (and update them if there are changes identified) at least once every 15 calendar months, even if it has no identified items in Requirement R1, and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [5 empty] | 2021-02-04 |  |  |  | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780009296 | System models shall represent: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780009303 | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by current annual studies or qualified past studies as indicated in Requirement R2, Part 2.6. Qualifying studies need to include the following conditions: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780009329 | Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R3, Part 3.4. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780009432 | One or more process(es) used in planning for the procurement of BES Cyber Systems and their associated EACMS and PACS to identify and assess cyber security risk(s) to the Bulk Electric System from vendor products or services resulting from: (i) procuring and installing vendor equipment and software; and (ii) transitions from one vendor(s) to another vendor(s). |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780009451 | All applicable Cyber Assets connected to a network via a routable protocol shall reside within a defined ESP. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780009456 | For all Interactive Remote Access, utilize an Intermediate System such that the Cyber Asset initiating Interactive Remote Access does not directly access an applicable Cyber Asset. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780009461 | Have one or more method(s) to determine authenticated vendor-initiated remote connections. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 31000000 | NPCC-ON |  | NPCC-US
1 | 79780009463 | Develop a baseline configuration, individually or by group, which shall include the following items: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 11000000 | NPCC-ON |  | NPCC-US
1 | 79780009464 | Operating system(s) (including version) or firmware where no independent operating system exists; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 11100000 | NPCC-ON |  | NPCC-US
1 | 79780009482 | Monitor at least once every 35 calendar days for changes to the baseline configuration (as described in Requirement R1, Part 1.1). Document and investigate detected unauthorized changes. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 21000000 | NPCC-ON |  | NPCC-US
1 | 79780009483 | At least once every 15 calendar months, conduct a paper or active vulnerability assessment. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 31000000 | NPCC-ON |  | NPCC-US
1 | RP-2021-04-12-0000001 | The documentation shall contain assumptions used to rate the generator and at least one of the following:• Design or construction information such as design criteria, ratings provided by equipment manufacturers, equipment drawings and/or specifications, engineering analyses, method(s) consistent with industry standards (e.g. ANSI and IEEE), or an established engineering practice that has been verified by testing or engineering analysis.• Operational information such as commissioning test results, performance testing or historical performance records, any of which may be supplemented by engineering analyses. |  | GO | [22 empty] | 2021-10-01 | [5 empty] | 10100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1 | RP-2021-04-12-0000003 | The methodology used to establish the Ratings of the equipment that comprises the Facility(ies) shall be consistent with at least one of the following:• Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating.• One or more industry standards developed through an open process such as Institute of Electrical and Electronic Engineers (IEEE) or International Council on Large Electric Systems (CIGRE).• A practice that has been verified by testing, performance history or engineering analysis. |  | GO | [22 empty] | 2021-10-01 | [5 empty] | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1 | RP-2021-04-12-0000013 | The methodology used to establish the Ratings of the equipment that comprises the Facility shall be consistent with at least one of the following:• Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating.• One or more industry standards developed through an open process such as Institute of Electrical and Electronics Engineers (IEEE) or International Council on Large Electric Systems (CIGRE).• A practice that has been verified by testing, performance history or engineering analysis. |  | GO | [22 empty] | 2021-10-01 | [5 empty] | 30100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1 | RP-2021-04-12-0000023 | As scheduled by the requesting entities: |  | GO | [22 empty] | 2021-10-01 | [5 empty] | 80100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1 | RP-2021-06-14-0000001 | Winter |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  |  | 11111000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1 | RP-2021-06-15-0000028 | Voltage, frequency, and phase angle permit. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  |  | 115001000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 100 | Fixed schedules for Jointly Owned Units mandate that Balancing Authority (A) that contains the Jointly Owned Unit must incorporate the respective share of the unit governor droop response for any Balancing Authorities that have fixed schedules (B and C). See the diagram below. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2009-06-28 |  |  | BAL-003-0b R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1023 | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  | IRO-005-2 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 103 | Balancing Authorities that do not serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of its estimated maximum generation level in the coming year per 0.1 Hz change. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2009-06-28 |  |  | BAL-003-0b R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1050 | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  | IRO-005-3a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1073 | The Interconnection-wide Transmission Loading Relief (TLR) procedure for use in the Eastern Interconnection is provided in Attachment 1-IRO-006-0. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-04-22 |  |  | IRO-006-3 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1081 | The Interconnection-wide Transmission Loading Relief (TLR) procedure for use in the Eastern Interconnection provided in Attachment 1-IRO-006-4. The TLR procedure alone is an inappropriate and ineffective tool to mitigate an IROL violation due to the time required to implement the procedure. Other acceptable and more effective procedures to mitigate actual IROL violations include: reconfiguration, redispatch, or load shedding. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-23 |  | 2009-12-09 |  |  | IRO-006-4 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1099 | List of required data and information needed by the Reliability Coordinator to support Real-Time Monitoring, Operational Planning Analyses, and Real-Time Assessments. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2009-08-05 |  |  | IRO-010-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1106 | These Operating Procedures, Processes, or Plans shall collectively address, as a minimum, the following: |  | RC | [11 empty] | RC | [9 empty] | M1.1 These Operating Procedures, Processes, or Plans shall address: | 2007-06-18 |  | 2017-03-31 |  |  | IRO-014-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1107 | Communications and notifications, including the conditions under which one Reliability Coordinator notifies other Reliability Coordinators; the process to follow in making those notifications; and the data and information to be exchanged with other Reliability Coordinators. |  | RC | [11 empty] | RC | [9 empty] | M1.1.1 Communications and notifications, including the conditions under whichone Reliability Coordinator notifies other Reliability Coordinators; theprocess to follow in making those notifications; and the data andinformation to be exchanged with other Reliability Coordinators. | 2007-06-18 |  | 2017-03-31 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1114 | Agreed to by all the Reliability Coordinators required to take the indicated action(s). |  | RC | [11 empty] | RC | [9 empty] | M2.1 Agreed to by all the Reliability Coordinators required to take the indicated action(s). | 2007-06-18 |  | 2017-03-31 |  |  | IRO-014-1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1117 | A reference to the associated Reliability Coordinator-to-Reliability Coordinator Operating Procedure, Process, or Plan. |  | RC | [11 empty] | RC | [9 empty] | M3.1 Be available to the Reliability Coordinator’s System Operators for Real-time use, | 2007-06-18 |  | 2017-03-31 |  |  | IRO-014-1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1120 | Include version control number or date. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  | IRO-014-1 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1124 | The Reliability Coordinator shall make notifications to other Reliability Coordinators of conditions in its Reliability Coordinator Area that may impact other Reliability Coordinator Areas. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  | IRO-015-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1126 | The frequency of these conference calls shall be agreed upon by all involved Reliability Coordinators and shall be at least weekly. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  | IRO-015-1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1129 | If the involved Reliability Coordinators agree on the problem and the actions to take to prevent or mitigate the system condition, each involved Reliability Coordinator shall implement the agreed-upon solution, and notify the involved Reliability Coordinators of the action(s) taken. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  | IRO-016-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1131 | If time permits, this re-evaluation shall be done before taking corrective actions. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1137 | A narrative explaining how TTC and ATC values are determined. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-001-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1142 | Daily values for current week at least once per day. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 15100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1152 | Hourly values for at least the next 48 hours. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-001-1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1156 | Information describing how the selected methodology (or methodologies) has been implemented, in such detail that, given the same information used by the Transmission Service Provider, the results of the ATC or AFC calculations can be validated. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-001-1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1158 | How confirmed Transmission reservations, expected Interchange and internal counterflow are addressed in firm and non-firm ATC or AFC calculations. |  | TSP | [20 empty] | TSP |  |  |  | 2010-09-16 |  |  |  | 32100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 116 | The Balancing Authority shall offset its frequency schedule by 0.02 Hertz, leaving the Frequency Bias Setting normal; or |  | BA, RC | BA | [10 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-04-01 |  |  | BAL-004-0 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1164 | The criteria used to determine when an outage that is in effect part of a day impacts a daily calculation. |  | TSP | [20 empty] | TSP |  |  |  | 2010-09-16 |  |  |  | 36100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1168 | Each Planning Coordinator associated with the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-001-1 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1178 | Hourly values, once per hour. Transmission Service Providers are allowed up to 175 hours per calendar year during which calculations are not required to be performed, despite a change in a calculated value identified in the ATC equation. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-001-1 R8. | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1182 | The Transmission Service Provider shall make its own current data available, in the format maintained by the Transmission Service Provider, for up to 13 months into the future (subject to confidentiality and security requirements). |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-001-1 R9. | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1183 | If the Transmission Service Provider uses the data requested in its transfer or Flowgate capability calculations, it shall make the data used available |  | TSP | [20 empty] | TSP |  |  |  | 2010-09-16 |  |  |  | 91100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 119 | Balancing Authorities that have reliability concerns with the execution of a Time Error Correction shall notify their Reliability Coordinator and request the termination of a Time Error Correction in progress. |  | BA, RC | BA | [10 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-04-01 |  |  | BAL-004-0 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1191 | The name, telephone number and email address of a contact person to whom concerns are to be addressed. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-003-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1197 | Specify that the method used by each Regional Reliability Organization member to determine its generation reliability requirements as the basis for CBM shall be consistent with its generation planning criteria. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-004-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1209 | The process through which a Load-Serving Entity within a Balancing Authority Area associated with the Transmission Service Provider, or the Resource Planner associated with that Balancing Authority Area, may ensure that its need for Transmission capacity to be set aside as CBM will be reviewed and accommodated by the Transmission Service Provider to the extent Transmission capacity is available. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1215 | Using one or more of the following to determine the GCIR: Loss of Load Expectation (LOLE) studies Loss of Load Probability (LOLP) studies Deterministic risk-analysis studies Reserve margin or resource adequacy requirements established by otherentities, such as municipalities, state commissions, regional transmissionorganizations, independent system operators, Regional ReliabilityOrganizations, or regional entities |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1217 | Using one or more of the following to determine the GCIR: Loss of Load Expectation (LOLE) studies Loss of Load Probability (LOLP) studies Deterministic risk-analysis studies Reserve margin or resource adequacy requirements established by otherentities, such as municipalities, state commissions, regional transmissionorganizations, independent system operators, Regional ReliabilityOrganizations, or regional entities |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 122 | The Balancing Authority shall offset its frequency schedule by 0.02 Hertz, leaving the Frequency Bias Setting normal; or |  | BA, RC | BA | [10 empty] | RC | [12 empty] | 2012-08-16 |  |  | BAL-004-1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1220 | Using one or more of the following to determine the GCIR: Loss of Load Expectation (LOLE) studies; Loss of Load Probability (LOLP) studies; Deterministic risk-analysis studies; Reserve margin or resource adequacy requirements established by other entities, such as municipalities, state commissions, regional transmission organizations, independent system operators, Regional Reliability Organizations, or regional entities |  | LSE | [7 empty] | LSE | [14 empty] | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. | MOD-004-1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1221 | The CBM is available |  | LSE | [7 empty] | LSE | [14 empty] | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1223 | Using one or more of the following to determine the GCIR: Loss of Load Expectation (LOLE) studies; Loss of Load Probability (LOLP) studies; Deterministic risk-analysis studies; Reserve margin or resource adequacy requirements established by other entities, such as municipalities, state commissions, regional transmission organizations, independent system operators, Regional Reliability Organizations, or regional entities |  | RP | [13 empty] | RP | [8 empty] | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. | MOD-004-1 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1226 | Reflect consideration of each of the following if available: Any studies (as described in R3.1) performed by Load-Serving Entities for loads within the Transmission Service Provider’s area; Any studies (as described in R4.1) performed by Resource Planners for loads within the Transmission Service Provider’s area; Any reserve margin or resource adequacy requirements for loads within the Transmission Service Provider’s area established by other entities, such as municipalities, state commissions, regional transmission organizations, independent system operators, Regional Reliability Organizations, or regional entities |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1229 | Reflect consideration of each of the following if available: Any studies (as described in R3.1) performed by Load-Serving Entities for loads within the Transmission Planner’s area; Any studies (as described in R4.1) performed by Resource Planners for loads within the Transmission Planner’s area; Any reserve margin or resource adequacy requirements for loads within the Transmission Planner’s area established by other entities, such as municipalities, state commissions, regional transmission organizations, independent system operators, Regional Reliability Organizations, or regional entities |  | TP | [19 empty] | TP |  |  | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1237 | Indicate the frequency under which the verification review shall be implemented. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-005-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1244 | Require that CBM be used only after the following steps have been taken (as time permits): all non-firm sales have been terminated, Direct-Control Load Management has been implemented, and customer interruptible demands have been interrupted. CBM may be used to reestablish Operating Reserves. |  | TSP | [20 empty] | TSP |  | 2007-06-18 |  | 2009-05-12 |  |  | MOD-006-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1249 | Require that CBM be used only after the following steps have been taken (as time permits): all non-firm sales have been terminated, Direct-Control Load Management has been implemented, and customer interruptible demands have been interrupted. CBM may be used to reestablish Operating Reserves. |  | TSP | [20 empty] | TSP |  | 2009-05-13 |  | 2011-03-31 |  |  | MOD-006-0.1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 125 | Balancing Authorities that have reliability concerns with the execution of a Time Error Correction shall notify their Reliability Coordinator and request the termination of a Time Error Correction in progress. |  | BA, RC | BA | [10 empty] | RC | [12 empty] | 2012-08-16 |  |  | BAL-004-1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1255 | Circumstances. |  | TSP | [20 empty] | TSP |  | 2007-06-18 |  | 2011-03-31 |  |  | MOD-007-0 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1259 | Specify the update frequency of TRM calculations. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-008-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1262 | Aggregate Load forecast error (not included in determining generation reliability requirements). |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 127 | The absolute value of the WECC Automatic Time Error Correction term is limited as follows: Where Lmax is chosen by the Balancing Authority and is bounded as follows: 0.20 * ¦Bi¦ <= Lmax<= L10. L10 is the Balancing Authority CPS2 limit in MW. If the WECC Automatic Time Error Correction term is less than the upper limit, use the calculated WECC Automatic Time Error Correction term. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2014-03-31 |  |  | BAL-004-WECC-01 R1. | 11000000 | WECC-US | [5 empty] | WECC-US
1. | 1274 | Identification of (on each of its respective ATC Paths or Flowgates) each of the following components of uncertainty if used in establishing TRM, and a description of how that component is used to establish a TRM value: Aggregate Load forecast.; Load distribution uncertainty.; Forecast uncertainty in Transmission system topology (including, but not limited to, forced or unplanned outages and maintenance outages).; Allowances for parallel path (loop flow) impacts.; Allowances for simultaneous path interactions.; Variations in generation dispatch (including, but not limited to, forced or unplanned outages, maintenance outages and location of future generation).; Short-term System Operator response (Operating Reserve actions ).; Reserve sharing requirements.; Inertial response and frequency bias. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  |  |  |  | MOD-008-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1277 | Same day and real-time. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 | [5 empty] | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1285 | Indicate the frequency under which the verification review shall be implemented. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-009-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1294 | Bus (substation): name, nominal voltage, electrical demand supplied (consistent with the aggregated and dispersed substation demand data supplied per Reliability Standards MOD-016-0, MOD-017-0, and MOD-020-0 ), and location. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | MOD-011-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1305 | Design data shall be provided for new or refurbished excitation systems (for synchronous generators and synchronous condensers) at least three months prior to the installation date. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | MOD-013-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1306 | If design data is unavailable from the manufacturer 3 months prior to the installation date, estimated or typical manufacturer’s data, based on excitation systems of similar design and characteristics, shall be provided. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1308 | Estimated or typical manufacturer’s dynamics data, based on units of similar design and characteristics, may be submitted when unit-specific dynamics data cannot be obtained. In no case shall other than unit-specific data be reported for generator units installed after 1990. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1317 | The Regional Reliability Organization(s) shall develop Interconnectionspecific dynamics system models for at least two timeframes (present or nearterm model and a future or longer-term model), and additional seasonal and demand level models, as necessary, to analyze the dynamic response of that Interconnection. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | MOD-015-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 132 | Each BA in the Western Interconnection shall use the change in Time Error distributed by the Interconnection Time Monitor. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2014-03-31 |  |  | BAL-004-WECC-01 R4. | 41000000 | WECC-US | [5 empty] | WECC-US
1. | 1320 | The Regional Reliability Organization(s) shall develop Interconnection specific dynamics system models for at least two timeframes (present or near-term model and a future or longer-term model), and additional seasonal and demand level models, as necessary, to analyze the dynamic response of that Interconnection. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | MOD-015-0.1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1323 | The aggregated and dispersed data submittal requirements shall ensure that consistent data is supplied for Reliability Standards TPL-005, TPL-006, MOD-010, MOD-011, MOD-012, MOD-013, MOD-014, MOD-015, MOD-016, MOD-017, MOD-018, MOD-019, MOD-020, and MOD-021. The data submittal requirements shall stipulate that each Load-Serving Entity count its customer Demand once and only once, on an aggregated and dispersed basis, in developing its actual and forecast customer Demand values. |  | PCPA, RRO | [9 empty] | PA |  |  |  |  | RRO | [7 empty] | 2007-06-18 |  | 2009-05-12 |  |  | MOD-016-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1325 | The Regional Reliability Organization shall make this distribution within 30 calendar days of approval. |  | RRO | [14 empty] | RRO | [7 empty] | 2007-06-18 |  | 2009-05-12 |  |  | MOD-016-1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1327 | The Planning Authority shall make this distribution within 30 calendar days of approval. |  | PCPA | [9 empty] | PA | [12 empty] | 2007-06-18 |  | 2009-05-12 |  |  | MOD-016-1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1329 | The aggregated and dispersed data submittal requirements shall ensure that consistent data is supplied for Reliability Standards TPL-005, TPL-006, MOD-010, MOD-011, MOD-012, MOD-013, MOD-014, MOD-015, MOD-016, MOD-017, MOD-018, MOD-019, MOD-020, and MOD-021. The data submittal requirements shall stipulate that each Load-Serving Entity count its customer Demand once and only once, on an aggregated and dispersed basis, in developing its actual and forecast customer Demand values. |  | PCPA, RRO | [9 empty] | PA |  |  |  |  | RRO | [7 empty] | 2009-05-13 |  | 2016-06-30 |  |  | MOD-016-1.1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1331 | The Regional Reliability Organization shall make this distribution within 30 calendar days of approval. |  | RRO | [14 empty] | RRO | [7 empty] | 2009-05-13 |  | 2016-06-30 |  |  | MOD-016-1.1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1333 | The Planning Authority shall make this distribution within 30 calendar days of approval. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-05-13 |  | 2016-06-30 |  |  | MOD-016-1.1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1335 | Integrated hourly demands in megawatts (MW) for the prior year. |  | LSE, PCPA, RP | [7 empty] | LSE |  | PA |  |  |  | RP | [8 empty] | 2007-06-18 |  | 2009-05-12 |  |  | MOD-017-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1340 | Integrated hourly demands in megawatts (MW) for the prior year. |  | LSE, PCPA, RP | [7 empty] | LSE |  | PA |  |  |  | RP | [8 empty] | 2009-05-13 |  | 2016-06-30 |  |  | MOD-017-0.1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1345 | Indicate whether the demand data of nonmember entities within an area or Regional Reliability Organization are included, and |  | LSE, PCPA, RP, TP | [7 empty] | LSE |  | PA |  |  |  | RP | [5 empty] | TP |  |  | 2007-06-18 |  | 2016-06-30 |  |  | MOD-018-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1356 | Generating unit exemption criteria including documentation of those units that are exempt from a portion or all of these procedures. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | MOD-024-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1361 | Seasonal gross and net Real Power generating capabilities. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 15100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1367 | Generating unit exemption criteria including documentation of those units that are exempt from a portion or all of these procedures. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | MOD-025-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 137 | Each Generator Operator with generation facilities operating in an Interconnection shall ensure that those generation facilities are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2008-08-26 |  |  | BAL-005-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1372 | Verified maximum gross and net Reactive Power capability (both lagging and leading) at Seasonal Real Power generating capabilities as reported in accordance with Reliability Standard MOD-024 Requirement 1.5.1. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 15100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1379 | Information describing how the selected methodology has been implemented, in such detail that, given the same information used by the Transmission Operator, the results of the TTC calculations can be validated. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2013-09-30 |  |  | MOD-028-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1384 | Define if the source used for Available Transfer Capability (ATC) calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2013-09-30 |  |  |  | 15100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1391 | Modeling data and topology of its Reliability Coordinator’s area of responsibility. Equivalent representation of radial lines and facilities 161 kV or below is allowed. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | MOD-028-1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1395 | For on-peak and off-peak intra-day and next-day TTCs, use the following (as well as any other values and additional parameters as specified in the ATCID): |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | MOD-028-1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1396 | Expected generation and Transmission outages, additions, and retirements, included as specified in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2013-09-30 |  |  |  | 31100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1400 | Expected generation and Transmission outages, additions, and Retirements, included as specified in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2013-09-30 |  |  |  | 32100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1404 | Use all Contingencies meeting the criteria described in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | MOD-028-1 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1408 | At least once within the seven calendar days prior to the specified period for TTCs used in hourly and daily ATC calculations. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | MOD-028-1 R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1412 | Determine the incremental Transfer Capability for each ATC Path by increasing generation and/or decreasing load within the source Balancing Authority area and decreasing generation and/or increasing load within the sink Balancing Authority area until either: - A System Operating Limit is reached on the Transmission Service Provider’s system, or - A SOL is reached on any other adjacent system in the Transmission model that is not on the study path and the distribution factor is 5% or greater . |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | MOD-028-1 R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1417 | One calendar day after its determination for TTCs used in hourly and daily ATC calculations. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | MOD-028-1 R7. | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1422 | The model utilizes data and assumptions consistent with the time period being studied and that meets the following criteria: |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-029-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1423 | Includes at least: |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1424 | The Transmission Operator area. Equivalent representation of radial lines and facilities 161kV or below is allowed. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 11110000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 143 | Balancing Authorities that share a tie shall ensure Tie Line MW metering is telemetered to both control centers, and emanates from a common, agreed-upon source using common primary metering equipment. Balancing Authorities shall ensure that megawatt-hour data is telemetered or reported at the end of each hour. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2008-08-26 |  |  | BAL-005-0 R12. | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1438 | Except where otherwise specified within MOD-029-1, adjust base case generation and Load levels within the updated power flow model to determine the TTC (maximum flow or reliability limit) that can be simulated on the ATC Path while at the same time satisfying all planning criteria contingencies as follows: |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-029-1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1439 | When modeling normal conditions, all Transmission Elements will be modeled at or below 100% of their continuous rating. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1456 | The criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates that are to be considered in Available Flowgate Capability (AFC) calculations. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | MOD-030-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1458 | Define if the source used for AFC calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1463 | For hourly AFC, once per hour. Transmission Service Providers are allowed up to 175 hours per calendar year during which calculations are not required to be performed, despite a change in a calculated value identified in the AFC equation. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | MOD-030-1 R10. | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1468 | Include Flowgates used in the AFC process based, at a minimum, on the following criteria: |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | MOD-030-1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1469 | Results of a first Contingency transfer analysis for ATC Paths internal to a Transmission Operator’s system up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an OTDF of at least 5% and within the Transmission Operator’s system are included as Flowgates. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1470 | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Special Protection Systems. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 21110000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1473 | Use first Contingency criteria consistent with those first Contignency criteria used in planning of operations for the applicable time periods, including use of Special Protection Systems. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 21210000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1477 | The coordination of the limiting Element/Contingency combination is not already addressed through a different methodology, and -Any generator within the Transmission Service Provider’s area has at least a 5% Power Transfer Distribution Factor (PTDF) or Outage Transfer Distribution Factor (OTDF) impact on the Flowgate when delivered to the aggregate load of its own area, or -A transfer from any Balancing Area within the Transmission Service Provider’s area to a Balancing Area adjacent has at least a 5% PTDF or OTDF impact on the Flowgate. -The Transmission Operator may utilize distribution factors less than 5% if desired. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 21410000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1483 | If notified of a change in the Rating by the Transmission Owner that would affect the TFC of a flowgate used in the AFC process, the TFC should be updated within seven calendar days of the notification. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 25100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1486 | Contains generation Facility Ratings, such as generation maximum and minimum output levels, specified by the Generator Owners of the Facilities within the model. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | MOD-030-1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1493 | Use the models provided by the Transmission Operator. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | MOD-030-1 R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1497 | The impact of firm Network Integration Transmission Service, including the impacts of generation to load, in the model referenced in R5.2 for the Transmission Service Provider’s area, based on: |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | MOD-030-1 R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1498 | Load forecast for the time period being calculated, including Native Load and Network Service load |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 61100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1501 | Load forecast for the time period being calculated, including Native Load and Network Service load |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 62100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1509 | The impact of all confirmed non-firm Point-to-Point Transmission Service expected to be scheduled for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | MOD-030-1 R7. | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1519 | The criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates that are to be considered in Available Flowgate Capability (AFC) calculations. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1521 | Define if the source used for AFC calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1526 | For hourly AFC, once per hour. Transmission Service Providers are allowed up to 175 hours per calendar year during which calculations are not required to be performed, despite a change in a calculated value identified in the AFC equation. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R10. | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1531 | Include Flowgates used in the AFC process based, at a minimum, on the following criteria: |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1532 | Results of a first Contingency transfer analysis for ATC Paths internal to a Transmission Operator’s system up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an OTDF of at least 5% and within the Transmission Operator’s system are included as Flowgates. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1533 | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Special Protection Systems. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21110000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1537 | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Special Protection Systems. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21210000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1542 | The coordination of the limiting Element/Contingency combination is not already addressed through a different methodology, and - Any generator within the Transmission Service Provider’s area has at least a 5% Power Transfer Distribution Factor (PTDF) or Outage Transfer Distribution Factor (OTDF) impact on the Flowgate when delivered to the aggregate load of its own area, or - A transfer from any Balancing Area within the Transmission Service Provider’s area to a Balancing Area adjacent has at least a 5% PTDF or OTDF impact on the Flowgate. - The Transmission Operator may utilize distribution factors less than 5% if desired. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21410000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1548 | If notified of a change in the Rating by the Transmission Owner that would affect the TFC of a flowgate used in the AFC process, the TFC should be updated within seven calendar days of the notification. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 25100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1551 | Contains generation Facility Ratings, such as generation maximum and minimum output levels, specified by the Generator Owners of the Facilities within the model. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1558 | Use the models provided by the Transmission Operator. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1562 | The impact of firm Network Integration Transmission Service, including the impacts of generation to load, in the model referenced in R5.2 for the Transmission Service Provider’s area, based on: |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1563 | Load forecast for the time period being calculated, including Native Load and Network Service load |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 61100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1566 | Load forecast for the time period being calculated, including Native Load and Network Service load |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 62100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1574 | The impact of all confirmed non-firm Point-to-Point Transmission Service expected to be scheduled for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R7. | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 158 | Each Balancing Authority shall provide redundant and independent frequency metering equipment that shall automatically activate upon detection of failure of the primary source. This overall installation shall provide a minimum availability of 99.95%. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2008-08-26 |  |  | BAL-005-0 R8. | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1587 | Incorporate the NPIRs into their operating analyses of the electric system. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2008-11-26 |  | 2010-03-31 |  |  | NUC-001-1 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1595 | Administrative elements: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2008-11-26 |  | 2010-03-31 |  |  | NUC-001-1 R9. | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1596 | Definitions of key terms used in the agreement. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 91100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 160 | Balancing Authorities with a high voltage direct current (HVDC) link to another Balancing Authority connected asynchronously to their Interconnection may choose to omit the Interchange Schedule related to the HVDC link from the ACE equation if it is modeled as internal generation or load. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2008-08-26 |  |  | BAL-005-0 R9. | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1601 | Identification of parameters, limits, configurations, and operatingscenarios included in the NPIRs and, as applicable, procedures forproviding any specific data not provided within the agreement. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 92100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1605 | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 93100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1613 | Provisions for communications between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of terms. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 94100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 162 | Each Generator Operator with generation facilities operating in an Interconnection shall ensure that those generation facilities are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2009-05-13 |  | 2012-09-12 |  |  | BAL-005-0.1b R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1621 | Positions that have the primary responsibility, either directly or through communications with others, for the real-time operation of the interconnected Bulk Electric System. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-03-31 |  |  | PER-002-0 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1624 | A set of training program objectives must be defined, based on NERC and Regional Reliability Organization standards, entity operating procedures, and applicable regulatory requirements. These objectives shall reference the knowledge and competencies needed to apply those standards, procedures, and requirements to normal, emergency, and restoration conditions for the Transmission Operator and Balancing Authority operating positions. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-03-31 |  |  | PER-002-0 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1630 | Positions that have the primary responsibility, either directly or through communications with others, for the real-time operation of the interconnected Bulk Electric System. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2012-09-30 |  |  | PER-003-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1640 | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall create a list of BES company-specific reliability-related tasks performed by its System Operators. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | M1.1 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection its company-specific reliability-related task list, with the date of the last review and/or revision, as specified in R1.1. | 2013-04-01 |  | 2016-06-30 |  |  | PER-005-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1641 | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall update its list of BES company-specific reliability-related tasks performed by its System Operators each calendar year to identify new or modified tasks for inclusion in training. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2013-04-01 |  | 2016-06-30 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1646 | Within six months of a modification of the BES company-specific reliability-related tasks, each Reliability Coordinator, Balancing Authority and Transmission Operator shall verify each of its System Operator’s capabilities to perform the new or modified tasks. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2013-04-01 |  | 2016-06-30 |  |  | PER-005-1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1648 | Each Reliability Coordinator, Balancing Authority and Transmission Operator that has operational authority or control over Facilities with established IROLs or has established operating guides or protection systems to mitigate IROL violations shall provide each System Operator with emergency operations training using simulation technology such as a simulator, virtual technology, or other technology that replicates the operational behavior of the BES during normal and emergency conditions. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2014-04-01 |  | 2016-06-30 |  |  | PER-005-1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1651 | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2013-03-31 |  |  | PRC-001-1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1654 | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2013-03-31 |  |  | PRC-001-1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1658 | Each Generator Operator shall notify its Transmission Operator in advance of changes in generation or operating conditions that could require changes in the Transmission Operator’s protection systems. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2013-03-31 |  |  | PRC-001-1 R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1662 | Location, monitoring and recording requirements, including the following: |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | PRC-002-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1663 | Criteria for equipment location (e.g., by voltage, geographic area, station size, etc.). |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1666 | Location, monitoring and recording requirements, including the following: |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | PRC-002-1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1667 | Criteria for equipment location (e.g., by voltage, geographic area, station size, etc.). |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1670 | Three phase to neutral voltages. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 21310000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1676 | Recording duration requirements. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 22100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 168 | Balancing Authorities that share a tie shall ensure Tie Line MW metering is telemetered to both control centers, and emanates from a common, agreed-upon source using common primary metering equipment. Balancing Authorities shall ensure that megawatt-hour data is telemetered or reported at the end of each hour. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2009-05-13 |  | 2012-09-12 |  |  | BAL-005-0.1b R12. | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1680 | Location, monitoring and recording requirements including the following: |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | PRC-002-1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1681 | Criteria for equipment location giving consideration to the following: - Site(s) in or near major load centers - Site(s) in or near major generation clusters - Site(s) in or near major voltage sensitive areas - Site(s) on both sides of major transmission interfaces- A major transmission junction- Elements associated with Interconnection Reliability Operating Limits - Major EHV interconnections between control areas- Coordination with neighboring regions within the interconnection |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 31100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1684 | Voltage, current and frequency. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 31310000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1687 | Capability for continuous recording for devices installed after January 1, 2009. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 32100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1690 | Criteria for events that require the collection of data from DMEs. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | PRC-002-1 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1699 | The Protection Systems to be reviewed and analyzed for Misoperations (due to theirpotential impact on BES reliability). |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | PRC-003-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1709 | System Operators shall review all tripping of transmission elements and RAS operations to identify apparent Misoperations within 24 hours. |  | GO, TO |  |  |  |  | GO | [16 empty] | M1.1 Transmission Owners and Generation Owners shall have evidence that System Operating personnel reviewed all operations of Protection System and RAS within 24 hours. | 2011-06-27 |  | 2017-03-31 |  |  | PRC-004-WECC-1 R1. | 11000000 | WECC-US | [5 empty] | WECC-US
1. | 1712 | If the Protection System or RAS has a Security-Based Misoperation and two or more Functionally Equivalent Protection Systems (FEPS) or Functionally Equivalent RAS (FERAS) remain in service to ensure Bulk Electric System (BES) reliability, the Transmission Owners or Generator Owners shall remove from service the Protection System or RAS that misoperated within 22 hours following identification of the Misoperation. Repair or replacement of the failed Protection System or RAS is at the Transmission Owners’ and Generator Owners’ discretion. |  | GO, TO |  |  |  |  | GO | [16 empty] | M2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. | 2011-06-27 |  | 2017-03-31 |  |  | PRC-004-WECC-1 R2. | 21000000 | WECC-US | [5 empty] | WECC-US
1. | 1714 | Following identification of the Protection System or RAS Misoperation, Transmission Owners and Generator Owners shall remove from service within 22 hours for repair or modification the Protection System or RAS that misoperated. |  | GO, TO |  |  |  |  | GO | [16 empty] | M2.2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. | 2011-10-01 |  | 2017-03-31 |  |  |  | 22100000 | WECC-US | [5 empty] | WECC-US
1. | 1717 | When a FEPS is not available, the Transmission Owners shall remove the associated Element from service. |  | TO | [21 empty] | M2.3.1 The Transmission Owner shall have evidence that it removed the associated Element from service. | 2011-10-01 |  | 2017-03-31 |  |  |  | 23100000 | WECC-US | [5 empty] | WECC-US
1. | 1719 | The Generator Owners shall adjust generation to a reliable operating level, or |  | GO | [21 empty] | M2.4 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated including documentation that describes the actions taken. | 2011-10-01 |  | 2017-03-31 |  |  |  | 23210000 | WECC-US | [5 empty] | WECC-US
1. | 1722 | Transmission Owners or Generator Owners shall repair or replace any Protection System or RAS that misoperated with FEPS and FERAS within 20 business days of the date of the Misoperation identification, or |  | GO, TO |  |  |  |  | GO | [16 empty] | M2.4.1 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days of the misoperation identification. | 2011-10-01 |  | 2017-03-31 |  |  |  | 24100000 | WECC-US | [5 empty] | WECC-US
1. | 1725 | Identification of a Misoperation of a Protection System and/or RAS, |  | GO, TO |  |  |  |  | GO | [16 empty] | M3.1 Identification of all Protection System and RAS Misoperations and corrective actions taken or planned. | 2011-06-27 |  | 2017-03-31 |  |  | PRC-004-WECC-1 R3. | 31000000 | WECC-US | [5 empty] | WECC-US
1. | 1728 | Maintenance and testing intervals and their basis. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2007-06-18 |  | 2011-09-25 |  |  | PRC-005-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1731 | Evidence Protection System devices were maintained and tested within the defined intervals. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2007-06-18 |  | 2011-09-25 |  |  | PRC-005-1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1734 | Requirements for coordination of UFLS programs within the subregions, Regional Reliability Organization and, where appropriate, among Regional Reliability Organizations. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  | PRC-006-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1736 | Frequency set points. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  |  | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1746 | A review of the frequency set points and timing, and |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  |  | 14100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1756 | A description of the event including initiating conditions. |  | DP, LSE, TO, TOP |  | DP | [5 empty] | LSE | [9 empty] | TO | TOP |  |  |  | 2007-06-18 |  | 2013-09-30 |  |  | PRC-009-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1762 | This assessment shall include, but is not limited to: |  | DP, LSE, TO, TOP |  | DP | [5 empty] | LSE | [9 empty] | TO | TOP |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | PRC-010-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1763 | Coordination of the UVLS programs with other protection and control systems in the Region and with other Regional Reliability Organizations, as appropriate. |  | DP, LSE, TO, TOP |  | DP | [5 empty] | LSE | [9 empty] | TO | TOP |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1768 | The UVLS system identification which shall include but is not limited to: |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2027-03-31 |  |  | PRC-011-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1769 | Relays. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2027-03-31 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1780 | Description of the process for submitting a proposed SPS for Regional Reliability Organization review. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  | PRC-012-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1791 | Design Objectives — Contingencies and system conditions for which the SPS was designed, |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  | PRC-013-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1798 | Identification of group conducting the assessment and the date the assessment was performed. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  | PRC-014-0 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 18 | A Balancing Authority may elect to fulfill its Contingency Reserve obligations by participating as a member of a Reserve Sharing Group. In such cases, the Reserve Sharing Group shall have the same responsibilities and obligations as each Balancing Authority with respect to monitoring and meeting the requirements of Standard BAL-002. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  | BAL-002-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1813 | SPS identification shall include but is not limited to: |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2007-06-18 |  | 2017-03-31 |  |  | PRC-017-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1814 | Relays. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1825 | Internal Clocks in DME devices shall be synchronized to within 2 milliseconds or less of Universal Coordinated Time scale (UTC) |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2022-06-30 |  |  | PRC-018-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1829 | Type of DME (sequence of event recorder, fault recorder, or dynamic disturbance recorder). |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2022-06-30 |  |  | PRC-018-1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 183 | Each Balancing Authority shall provide redundant and independent frequency metering equipment that shall automatically activate upon detection of failure of the primary source. This overall installation shall provide a minimum availability of 99.95%. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2009-05-13 |  | 2012-09-12 |  |  | BAL-005-0.1b R8. | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1840 | Maintenance and testing intervals and their basis. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2022-06-30 |  |  | PRC-018-1 R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1843 | Owner and operator of the UVLS program. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  | PRC-020-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 185 | Balancing Authorities with a high voltage direct current (HVDC) link to another Balancing Authority connected asynchronously to their Interconnection may choose to omit the Interchange Schedule related to the HVDC link from the ACE equation if it is modeled as internal generation or load. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2009-05-13 |  | 2012-09-12 |  |  | BAL-005-0.1b R9. | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1851 | Size and location of customer load, or percent of connected load, to be interrupted. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2017-03-31 |  |  | PRC-021-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1858 | A description of the event including initiating conditions. |  | DP, LSE, TOP |  | DP | [5 empty] | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | PRC-022-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1865 | Set transmission line relays so they do not operate at or below 150% of the highest seasonal Facility Rating of a circuit, for the available defined loading duration nearest 4 hours (expressed in amperes). |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  | PRC-023-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1869 | Set the maximum torque angle (MTA) to 90 degrees or the highest supported by the manufacturer. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  |  | 20300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 187 | Each Generator Operator with generation facilities operating in an Interconnection shall ensure that those generation facilities are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2008-08-27 |  | 2009-05-12 |  |  | BAL-005-0b R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1875 | An infinite source (zero source impedance) with a 1.00 per unit bus voltage at each end of the line. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1885 | The Planning Coordinator shall have a process to determine the facilities that are critical to the reliability of the Bulk Electric System. |  | PCPA | [9 empty] | PA | [12 empty] | 2011-11-17 |  | 2012-06-30 |  |  | PRC-023-1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1886 | This process shall consider input from adjoining Planning Coordinators and affected Reliability Coordinators. |  | PCPA | [9 empty] | PA | [12 empty] | 2011-11-17 |  | 2012-06-30 |  |  |  | 31100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1899 | For a generator outage, the Generator Operator shall notify and coordinate with the Transmission Operator. The Transmission Operator shall notify the Reliability Coordinator and other affected Transmission Operators, and coordinate the impact of removing the Bulk Electric System facility. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-11-20 |  |  | TOP-001-1 R7. | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1909 | Changes in real output capabilities. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2009-12-01 |  |  | TOP-002-2 R14. | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1913 | Changes in transmission facility status. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-12-01 |  |  | TOP-002-2 R16. | 161000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 193 | Balancing Authorities that share a tie shall ensure Tie Line MW metering is telemetered to both control centers, and emanates from a common, agreed-upon source using common primary metering equipment. Balancing Authorities shall ensure that megawatt-hour data is telemetered or reported at the end of each hour. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2008-08-27 |  | 2009-05-12 |  |  | BAL-005-0b R12. | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1932 | Changes in real output capabilities. |  | GOP | [5 empty] | GOP | [16 empty] | 2009-12-02 |  | 2011-10-19 |  |  | TOP-002-2a R14. | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1936 | Changes in transmission facility status. |  | TOP | [18 empty] | TOP |  |  |  | 2009-12-02 |  | 2011-10-19 |  |  | TOP-002-2a R16. | 161000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1950 | Each Generator Operator shall provide outage information daily to its Transmission Operator for scheduled generator outages planned for the next day (any foreseen outage of a generator greater than 50 MW). The Transmission Operator shall establish the outage reporting requirements. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-09-30 |  |  | TOP-003-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1957 | Each Generator Operator shall provide outage information daily to its Transmission Operator for scheduled generator outages planned for the next day (any foreseen outage of a generator greater than 50 MW). The Transmission Operator shall establish the outage reporting requirements. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-05-23 |  | 2017-03-31 |  |  | TOP-003-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1969 | Equipment ratings. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-01-21 |  |  | TOP-004-1 R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1981 | Monitoring and controlling voltage levels and real and reactive power flows. |  | TOP | [18 empty] | TOP |  |  |  | 2009-01-22 |  | 2017-03-31 |  |  | TOP-004-2 R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1986 | Each Reliability Coordinator shall identify the data requirements from the list in Attachment 1-TOP-005-0 “Electric System Reliability Data” and any additional operating information requirements relating to operation of the bulk power system within the Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-05-12 |  |  | TOP-005-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 1991 | Each Reliability Coordinator shall identify the data requirements from the list in Attachment 1-TOP-005-0 “Electric System Reliability Data” and any additional operating information requirements relating to operation of the bulk power system within the Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2009-05-13 |  | 2011-05-25 |  |  | TOP-005-1.1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 20 | The minimum reserve requirement for the group. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  | BAL-002-0 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2004 | Each Generator Operator shall inform its Host Balancing Authority and the Transmission Operator of all generation resources available for use. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2011-09-30 |  |  | TOP-006-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2013 | Each Generator Operator shall inform its Host Balancing Authority and the Transmission Operator of all generation resources available for use. | VSL - SevereThe Generator Operator failed to inform its Host Balancing Authority and the Transmission Operator of all generation resources available for use. | GOP | [5 empty] | GOP | [16 empty] | 2011-05-23 |  | 2017-03-31 |  |  | TOP-006-2 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2027 | If the path SOL decreases within 20 minutes before the start of the hour, the Transmission Operator shall adjust the Net Scheduled Interchange within 30 minutes to the new SOL value. Net Scheduled Interchange exceeding the new SOL during this 30-minute period will not be a violation of R2. |  | TOP | [18 empty] | TOP |  |  |  | 2011-06-27 |  | 2014-06-17 |  |  | TOP-007-WECC-1 R2. | 21000000 | WECC-US | [5 empty] | WECC-US
1. | 2034 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  | TPL-001-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2037 | Cover critical system conditions and study years as deemed appropriate by the entity performing the study. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2048 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  | TPL-001-0 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2049 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2055 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  | TPL-001-0.1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2058 | Cover critical system conditions and study years as deemed appropriate by the entity performing the study. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2069 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  | TPL-001-0.1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2070 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2076 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | TPL-002-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2079 | Be performed and evaluated only for those Category B contingencies that would produce the more severe System results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 208 | Each Balancing Authority shall provide redundant and independent frequency metering equipment that shall automatically activate upon detection of failure of the primary source. This overall installation shall provide a minimum availability of 99.95%. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2008-08-27 |  | 2009-05-12 |  |  | BAL-005-0b R8. | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2094 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | TPL-002-0 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2095 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 210 | Balancing Authorities with a high voltage direct current (HVDC) link to another Balancing Authority connected asynchronously to their Interconnection may choose to omit the Interchange Schedule related to the HVDC link from the ACE equation if it is modeled as internal generation or load. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2008-08-27 |  | 2009-05-12 |  |  | BAL-005-0b R9. | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2101 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | TPL-002-0a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2104 | Be performed and evaluated only for those Category B contingencies that would produce the more severe System results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2119 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | TPL-002-0a R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2120 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2126 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | TPL-003-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2129 | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2144 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | TPL-003-0 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2145 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 215 | Each Balancing Authority, by the end of the next business day, shall agree with its Adjacent Balancing Authorities to: |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  | BAL-006-1 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2151 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | TPL-003-0a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2154 | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 216 | The hourly values of Net Interchange Schedule. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | 41100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2169 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | TPL-003-0a R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2170 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2176 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  | TPL-004-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2179 | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2191 | Current year: |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | TPL-005-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2192 | Winter. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2200 | Security assessments. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | TPL-005-0 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2207 | Electric Demand and Net Energy for Load (actual and projected demands and Net Energy for Load, forecast methodologies, forecast assumptions and uncertainties, and treatment of Demand-Side Management.) |  | RRO | [14 empty] | RRO | [9 empty] | 2009-04-15 |  |  | TPL-006-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2220 | Each Transmission Operator shall maintain a list of generators in its area that are exempt from following a voltage or Reactive Power schedule. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-09-30 |  |  | VAR-001-1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2225 | When notified of the loss of an automatic voltage regulator control, the Transmission Operator shall direct the Generator Operator to maintain or change either its voltage schedule or its Reactive Power schedule. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-09-30 |  |  | VAR-001-1 R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2229 | Each Transmission Operator shall disperse and locate the reactive resources so that the resources can be applied effectively and quickly when Contingencies occur. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-09-30 |  |  | VAR-001-1 R9. | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2236 | Each Transmission Operator shall maintain a list of generators in its area that are exempt from following a voltage or Reactive Power schedule. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-05-21 |  |  | VAR-001-1a R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2241 | When notified of the loss of an automatic voltage regulator control, the Transmission Operator shall direct the Generator Operator to maintain or change either its voltage schedule or its Reactive Power schedule. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-05-21 |  |  | VAR-001-1a R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2245 | Each Transmission Operator shall disperse and locate the reactive resources so that the resources can be applied effectively and quickly when Contingencies occur. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-05-21 |  |  | VAR-001-1a R9. | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2248 | When a generator’s automatic voltage regulator is out of service, the Generator Operator shall use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2008-08-26 |  |  | VAR-002-1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 225 | Each Balancing Authority, by the end of the next business day, shall agree with its Adjacent Balancing Authorities to: |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-03-31 |  |  | BAL-006-1.1 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2251 | A status or capability change on any generator Reactive Power resource, including the status of each automatic voltage regulator and power system stabilizer and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2008-08-26 |  |  | VAR-002-1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2254 | For generator step-up transformers and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: |  | GO | [22 empty] | 2007-06-18 |  | 2008-08-26 |  |  | VAR-002-1 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2255 | Tap settings. |  | GO | [22 empty] | 2007-08-02 |  | 2008-08-26 |  |  |  | 41100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 226 | The hourly values of Net Interchange Schedule. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-03-31 |  |  |  | 41100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2260 | If the Generator Operator can’t comply with the Transmission Operator’s specifications, the Generator Operator shall notify the Transmission Operator and shall provide the technical justification. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2008-08-26 |  |  | VAR-002-1 R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2263 | When a generator’s automatic voltage regulator is out of service, the Generator Operator shall use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2009-05-13 |  | 2010-09-15 |  |  | VAR-002-1.1a R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2266 | A status or capability change on any generator Reactive Power resource, including the status of each automatic voltage regulator and power system stabilizer and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2009-05-13 |  | 2010-09-15 |  |  | VAR-002-1.1a R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2269 | For generator step-up transformers and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: |  | GO | [22 empty] | 2009-05-13 |  | 2010-09-15 |  |  | VAR-002-1.1a R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2270 | Tap settings. |  | GO | [22 empty] | 2009-05-13 |  | 2010-09-15 |  |  |  | 41100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2275 | If the Generator Operator can’t comply with the Transmission Operator’s specifications, the Generator Operator shall notify the Transmission Operator and shall provide the technical justification. |  | GOP | [5 empty] | GOP | [16 empty] | 2009-05-13 |  | 2010-09-15 |  |  | VAR-002-1.1a R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2278 | When a generator’s automatic voltage regulator is out of service, the Generator Operator shall use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2010-09-16 |  | 2013-06-30 |  |  | VAR-002-1.1b R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2281 | A status or capability change on any generator Reactive Power resource, including the status of each automatic voltage regulator and power system stabilizer and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2010-09-16 |  | 2013-06-30 |  |  | VAR-002-1.1b R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2284 | For generator step-up transformers and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: |  | GO | [22 empty] | 2010-09-16 |  | 2013-06-30 |  |  | VAR-002-1.1b R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2285 | Tap settings. |  | GO | [22 empty] | 2010-09-16 |  | 2013-06-30 |  |  |  | 41100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2290 | If the Generator Operator can’t comply with the Transmission Operator’s specifications, the Generator Operator shall notify the Transmission Operator and shall provide the technical justification. |  | GOP | [5 empty] | GOP | [16 empty] | 2010-09-16 |  | 2013-06-30 |  |  | VAR-002-1.1b R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2293 | When a generator’s automatic voltage regulator is out of service, the Generator Operator shall use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2008-08-27 |  | 2009-05-12 |  |  | VAR-002-1a R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2296 | A status or capability change on any generator Reactive Power resource, including the status of each automatic voltage regulator and power system stabilizer and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2008-08-27 |  | 2009-05-12 |  |  | VAR-002-1a R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2299 | For generator step-up transformers and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: |  | GO | [22 empty] | 2008-08-27 |  | 2009-05-12 |  |  | VAR-002-1a R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2300 | Tap settings. |  | GO | [22 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 41100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2305 | If the Generator Operator can’t comply with the Transmission Operator’s specifications, the Generator Operator shall notify the Transmission Operator and shall provide the technical justification. |  | GOP | [5 empty] | GOP | [16 empty] | 2008-08-27 |  | 2009-05-12 |  |  | VAR-002-1a R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2307 | The synchronous generator or synchronous condenser operates for less than five percent of all hours during any calendar quarter. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-06-27 |  | 2015-03-31 |  |  | VAR-002-WECC-1 R1. | 11000000 | WECC-US | [5 empty] | WECC-US
1. | 2319 | The synchronous generator operates for less than five percent of all hours during any calendar quarter. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-06-27 |  | 2015-03-31 |  |  | VAR-501-WECC-1 R1. | 11000000 | WECC-US | [5 empty] | WECC-US
1. | 2335 | The Interconnection-wide Transmission Loading Relief (TLR) procedure for use in the Eastern Interconnection provided in Attachment 1-IRO-006-4. The TLR procedure alone is an inappropriate and ineffective tool to mitigate an IROL violation due to the time required to implement the procedure. Other acceptable and more effective procedures to mitigate actual IROL violations include: reconfiguration, redispatch, or load shedding. |  | RC | [11 empty] | RC | [10 empty] | 2009-12-10 |  | 2011-06-30 |  |  | IRO-006-4.1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2347 | Electric Demand and Net Energy for Load (actual and projected demands and Net Energy for Load, forecast methodologies, forecast assumptions and uncertainties, and treatment of Demand-Side Management.) |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | TPL-006-0.1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2355 | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-002-2 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2357 | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2366 | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-002-2 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2371 | The cyber security policy addresses the requirements in Standards CIP-002-2 through CIP-009-2, including provision for emergency situations. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-003-2 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2375 | The senior manager shall be identified by name, title, and date of designation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-003-2 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2380 | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-003-2 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2384 | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP-002-2, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-003-2 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2388 | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-003-2 R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2389 | Personnel shall be identified by name, title, and the information for which they are responsible for authorizing access. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 51100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2396 | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-004-2 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2398 | The proper use of Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 22100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2404 | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-004-2 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2408 | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-004-2 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2411 | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-005-2 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2418 | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-005-2 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2423 | The processes for access request and authorization. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 25100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2429 | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-005-2 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2432 | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-005-2 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2438 | The Responsible Entity shall ensure that all documentation required by Standard CIP-005-2 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005-2 at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-005-2 R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2442 | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  | CIP-006-2 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 245 | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-002-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2451 | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  | CIP-006-2 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2459 | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  | CIP-006-2 R8. | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2463 | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | CIP-007-2 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2467 | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | CIP-007-2 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 247 | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2471 | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | CIP-007-2 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2474 | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | CIP-007-2 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2477 | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | CIP-007-2 R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2478 | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-2 Requirement R5. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 51100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2482 | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 52100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2486 | Each password shall be a minimum of six characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 53100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2490 | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | CIP-007-2 R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2496 | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | CIP-007-2 R7. | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2500 | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | CIP-007-2 R8. | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2506 | Procedures to characterize and classify events as reportable Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-008-2 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2514 | Specify the required actions in response to events or conditions of varying duration and severity that would activate the recovery plan(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-009-2 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2524 | Incorporate the NPIRs into their operating analyses of the electric system. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  | NUC-001-2 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2532 | Administrative elements: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2014-01-21 |  |  | NUC-001-2 R9. | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2533 | Definitions of key terms used in the agreement. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2014-01-21 |  |  |  | 91100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2538 | Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the agreement. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 92100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2542 | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 93100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2550 | Provisions for communications between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of terms. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 94100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2557 | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  | EOP-001-2 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 256 | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-002-1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2561 | Communications protocols to be used during emergencies. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  | EOP-001-2 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2568 | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  | EOP-001-2 R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2573 | Strategies for system restoration that are coordinated with the Reliability Coordinator’s high level strategy for restoring the Interconnection. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | EOP-005-2 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2583 | System restoration plan including coordination with the Reliability Coordinator and Generator Operators included in the restoration plan. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | EOP-005-2 R10. | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2593 | Testing records shall include at a minimum: name of the Blackstart Resource, unit tested, date of the test, duration of the test, time required to start the unit, an indication of any testing requirements not met under Requirement R9. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-05-23 |  | 2019-03-31 |  |  | EOP-005-2 R16. | 161000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2596 | System restoration plan including coordination with the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-05-23 |  | 2019-03-31 |  |  | EOP-005-2 R17. | 171000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2601 | If there are no changes to the previously submitted restoration plan, the Transmission Operator shall confirm annually on a predetermined schedule to its Reliability Coordinator that it has reviewed its restoration plan and no changes were necessary. (Retirement approved by FERC effective January 21, 2014.) |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | EOP-005-2 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2603 | Each Transmission Operator shall submit its revised restoration plan to its Reliability Coordinator for approval within the same 90 calendar day period. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | EOP-005-2 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2606 | The capability of Blackstart Resources to meet the Real and Reactive Power requirements of the Cranking Paths and the dynamic capability to supply initial Loads. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | EOP-005-2 R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 261 | The cyber security policy addresses the requirements in Standards CIP-002 through CIP-009, including provision for emergency situations. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-003-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2612 | The frequency of testing such that each Blackstart Resource is tested at least once every three calendar years. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | EOP-005-2 R9. | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2614 | The ability to start the unit when isolated with no support from the BES or when designed to remain energized without connection to the remainder of the System. |  | TOP | [18 empty] | TOP |  |  |  | 2013-07-01 |  | 2019-03-31 |  |  |  | 92100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2618 | A description of the high level strategy to be employed during restoration events for restoring the Interconnection including minimum criteria for meeting the objectives of the Reliability Coordinator’s restoration plan. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  | EOP-006-2 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2628 | Each Reliability Coordinator shall request each Transmission Operator identified in its restoration plan and each Generator Operator identified in the Transmission Operators’ restoration plans to participate in a drill, exercise, or simulation at least every two calendar years. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  | EOP-006-2 R10. | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2632 | If the Reliability Coordinator finds conflicts between its restoration plans and any of its neighbors, the conflicts shall be resolved in 30 calendar days. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  | EOP-006-2 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2634 | The Reliability Coordinator shall determine whether the Transmission Operator’s restoration plan is coordinated and compatible with the Reliability Coordinator’s restoration plan and other Transmission Operators’ restoration plans within its Reliability Coordinator Area. The Reliability Coordinator shall approve or disapprove, with stated reasons, the Transmission Operator’s submitted restoration plan within 30 calendar days following the receipt of the restoration plan from the Transmission Operator. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  | EOP-006-2 R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2639 | The coordination role of the Reliability Coordinator. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  | EOP-006-2 R9. | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 265 | The senior manager shall be identified by name, title, business phone, business address, and date of designation. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-003-1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2651 | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | CIP-007-2a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2654 | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | CIP-007-2a R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2656 | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | CIP-007-2a R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2659 | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | CIP-007-2a R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2661 | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | CIP-007-2a R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2664 | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-2 Requirement R5. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 51100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2667 | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 52100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2670 | Each password shall be a minimum of six characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 53100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2676 | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | CIP-007-2a R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2678 | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | CIP-007-2a R7. | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2683 | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | CIP-007-2a R8. | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 269 | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-003-1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2690 | Be applicable for developing SOLs used in the planning horizon. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | FAC-010-2.1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2694 | In the pre-contingency state and with all Facilities in service, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect expected system conditions and shall reflect changes to system topology such as Facility outages. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | FAC-010-2.1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 27 | As a minimum, the Balancing Authority or Reserve Sharing Group shall carry at least enough Contingency Reserve to cover the most severe single contingency. All Balancing Authorities and Reserve Sharing Groups shall review, no less frequently than annually, their probable contingencies to determine their prospective most severe single contingencies. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  | BAL-002-0 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2700 | Single line to ground or three-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 22100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2702 | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 23100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2703 | Planned or controlled interruption of electric supply to customers (load shedding), the planned removal from service of certain generators, and/or the curtailment of contracted Firm (non-recallable reserved) electric power Transfers. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 26100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2708 | Study model (must include at least the entire Planning Authority Area as well as the critical modeling details from other Planning Authority Areas that would impact the Facility or Facilities under study). |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | FAC-010-2.1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2712 | Each adjacent Planning Authority and each Planning Authority that indicated it has a reliability-related need for the methodology. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | FAC-010-2.1 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2714 | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. | CIP-002-3 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2716 | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2725 | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. | CIP-002-3 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 273 | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP-002, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-003-1 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2730 | The cyber security policy addresses the requirements in Standards CIP-002-3 through CIP-009-3, including provision for emergency situations. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | CIP-003-3 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2734 | The senior manager shall be identified by name, title, and date of designation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | CIP-003-3 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2739 | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | CIP-003-3 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2743 | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP-002-3, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | CIP-003-3 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2747 | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | CIP-003-3 R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2748 | Personnel shall be identified by name, title, and the information for which they are responsible for authorizing access. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  |  |  | 51100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2755 | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2012-12-11 |  |  | CIP-004-3 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2757 | The proper use of Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2012-12-11 |  |  |  | 22100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2763 | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2012-12-11 |  |  | CIP-004-3 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2767 | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2012-12-11 |  |  | CIP-004-3 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 277 | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-003-1 R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2770 | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | CIP-005-3 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2777 | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | CIP-005-3 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 278 | Personnel shall be identified by name, title, business phone and the information for which they are responsible for authorizing access. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 51100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2782 | The processes for access request and authorization. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2011-02-01 |  |  |  | 25100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2788 | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | CIP-005-3 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2791 | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | CIP-005-3 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2797 | The Responsible Entity shall ensure that all documentation required by Standard CIP-005-3 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005-3 at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | CIP-005-3 R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2801 | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  | CIP-006-3 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2807 | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-09-30 |  |  |  | 16100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2812 | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  | CIP-006-3 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2820 | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  | CIP-006-3 R8. | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2824 | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-007-3a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2828 | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-007-3a R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2832 | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-007-3a R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2835 | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-007-3a R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2838 | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-007-3a R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2839 | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-3 Requirement R5. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 51100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2843 | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 52100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2847 | Each password shall be a minimum of six characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 53100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 285 | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained within ninety calendar days of such authorization. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-04-07 |  | 2010-03-31 |  |  | CIP-004-1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2851 | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-007-3a R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2857 | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-007-3a R7. | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2861 | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-007-3a R8. | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2867 | Procedures to characterize and classify events as reportable Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | CIP-008-3 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 287 | The proper use of Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 22100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2875 | Specify the required actions in response to events or conditions of varying duration and severity that would activate the recovery plan(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | CIP-009-3 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2893 | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  | CIP-006-2b R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2898 | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  | CIP-006-2b R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2899 | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  | CIP-006-2b R8. | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 29 | A Balancing Authority shall return its ACE to zero if its ACE just prior to the Reportable Disturbance was positive or equal to zero. For negative initial ACE values just prior to the Disturbance, the Balancing Authority shall return ACE to its pre-Disturbance value. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  | BAL-002-0 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2914 | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | CIP-006-2c R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2919 | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | CIP-006-2c R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2920 | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | CIP-006-2c R8. | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 293 | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-004-1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2936 | Processes to ensure and document that all Cyber Assets within an Electronic Security Perimeter also reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1b R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2941 | Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1b R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2942 | Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1b R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2945 | Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1b R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2947 | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1b R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2958 | Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | CIP-006-1c R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2959 | Processes to ensure and document that all Cyber Assets within an Electronic Security Perimeter also reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | CIP-006-1c R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 297 | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-004-1 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2971 | Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | CIP-006-1c R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2973 | Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | CIP-006-1c R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2976 | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | CIP-006-1c R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2989 | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  | CIP-006-3c R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2993 | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  |  | 16100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2995 | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  | CIP-006-3c R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 2997 | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  | CIP-006-3c R8. | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 300 | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | CIP-005-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3010 | Hourly values for at least the next 48 hours. |  | TSP | [20 empty] | TSP | M2.1 - There has been at least 48 hours of hourly values calculated at all times. | 2010-09-16 |  |  |  |  | MOD-001-1a R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3014 | Information describing how the selected methodology (or methodologies) has been implemented, in such detail that, given the same information used by the Transmission Service Provider, the results of the ATC or AFC calculations can be validated. |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  |  |  |  | MOD-001-1a R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3019 | How confirmed Transmission reservations, expected Interchange and internal counterflow are addressed in firm and non-firm ATC or AFC calculations. |  | TSP | [20 empty] | TSP |  | 2011-04-01 | [5 empty] | 32100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3022 | The criteria used to determine when an outage that is in effect part of a day impacts a daily calculation. |  | TSP | [20 empty] | TSP |  | 2011-04-01 | [5 empty] | 36100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3028 | Each Planning Coordinator associated with the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  |  |  |  | MOD-001-1a R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3030 | Hourly values, once per hour. Transmission Service Providers are allowed up to 175 hours per calendar year during which calculations are not required to be performed, despite a change in a calculated value identified in the ATC equation. |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  |  |  |  | MOD-001-1a R8. | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3032 | The Transmission Service Provider shall make its own current data available, in the format maintained by the Transmission Service Provider, for up to 13 months into the future (subject to confidentiality and security requirements). |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  |  |  |  | MOD-001-1a R9. | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3045 | The model utilizes data and assumptions consistent with the time period being studied and that meets the following criteria: |  | TOP | [18 empty] | TOP |  |  | M1.1. Production shall be in the same form and format used by the Transmission Operator to calculate the TTC, as required in R1. | 2010-09-16 |  | 2017-03-31 |  |  | MOD-029-1a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3054 | Includes at least: |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3057 | The Transmission Operator area. Equivalent representation of radial lines and facilities 161kV or below is allowed. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 11110000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3061 | Except where otherwise specified within MOD-029-1, adjust base case generation and Load levels within the updated power flow model to determine the TTC (maximum flow or reliability limit) that can be simulated on the ATC Path while at the same time satisfying all planning criteria contingencies as follows: |  | TOP | [18 empty] | TOP |  |  |  | 2010-09-16 |  | 2017-03-31 |  |  | MOD-029-1a R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3068 | When modeling normal conditions, all Transmission Elements will be modeled at or below 100% of their continuous rating. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 307 | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-005-1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3075 | List of required data and information needed by the Reliability Coordinator to support Real-Time Monitoring, Operational Planning Analyses, and Real-Time Assessments. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2017-03-31 |  |  | IRO-010-1a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 312 | The processes for access request and authorization. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 25100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3160 | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. | CIP-005-3a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3163 | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. | CIP-005-3a R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3171 | The processes for access request and authorization. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. |  | 25100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3174 | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. | CIP-005-3a R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3177 | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. | CIP-005-3a R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 318 | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | CIP-005-1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3180 | The Responsible Entity shall ensure that all documentation required by Standard CIP-005-3 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005-3 at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. | CIP-005-3a R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3184 | A Balancing Authority may elect to fulfill its Contingency Reserve obligations by participating as a member of a Reserve Sharing Group. In such cases, the Reserve Sharing Group shall have the same responsibilities and obligations as each Balancing Authority with respect to monitoring and meeting the requirements of Standard BAL-002. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  | BAL-002-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3186 | The minimum reserve requirement for the group. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  | BAL-002-1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3193 | As a minimum, the Balancing Authority or Reserve Sharing Group shall carry at least enough Contingency Reserve to cover the most severe single contingency. All Balancing Authorities and Reserve Sharing Groups shall review, no less frequently than annually, their probable contingencies to determine their prospective most severe single contingencies. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  | BAL-002-1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3195 | A Balancing Authority shall return its ACE to zero if its ACE just prior to the Reportable Disturbance was positive or equal to zero. For negative initial ACE values just prior to the Disturbance, the Balancing Authority shall return ACE to its pre-Disturbance value. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  | BAL-002-1 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3198 | The Reserve Sharing Group reviews group ACE (or equivalent) and demonstrates compliance to the DCS. To be in compliance, the group ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. or |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  | BAL-002-1 R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 32 | The Reserve Sharing Group reviews group ACE (or equivalent) and demonstrates compliance to the DCS. To be in compliance, the group ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. Or |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  | BAL-002-0 R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3201 | The Contingency Reserve Restoration Period begins at the end of the Disturbance Recovery Period. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  | BAL-002-1 R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3207 | Each Balancing Authority, by the end of the next business day, shall agree with its Adjacent Balancing Authorities to: |  | BA | BA | [21 empty] | 2011-04-01 |  | 2018-12-31 |  |  | BAL-006-2 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3208 | The hourly values of Net Interchange Schedule. |  | BA | BA | [21 empty] | 2011-04-01 |  | 2018-12-31 |  |  |  | 41100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 321 | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-005-1 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3219 | The cyber security policy addresses the requirements in Standards CIP-002-4 through CIP-009-4, including provision for emergency situations. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-003-4 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3223 | The senior manager shall be identified by name, title, and date of designation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-003-4 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3228 | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-003-4 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3232 | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP-002-4, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-003-4 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3236 | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-003-4 R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3237 | Personnel shall be identified by name, title, and the information for which they are responsible for authorizing access. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 51100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3244 | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2012-12-11 |  |  | CIP-004-4 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3246 | The proper use of Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2012-12-11 |  |  |  | 22100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3252 | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2012-12-11 |  |  | CIP-004-4 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3256 | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2012-12-11 |  |  | CIP-004-4 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3259 | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-005-4a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3266 | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-005-4a R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 327 | The Responsible Entity shall ensure that all documentation required by Standard CIP-005 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005 at least annually. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-005-1 R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3271 | The processes for access request and authorization. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 25100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3277 | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-005-4a R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3280 | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-005-4a R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3286 | The Responsible Entity shall ensure that all documentation required by Standard CIP-005-4 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005-4 at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-005-4a R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3290 | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-006-4c R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3296 | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 16100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3301 | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-006-4c R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3309 | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-006-4c R8. | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 331 | Processes to ensure and document that all Cyber Assets within an Electronic Security Perimeter also reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-006-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3313 | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-007-4a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3317 | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-007-4a R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3321 | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-007-4a R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3324 | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-007-4a R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3327 | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-007-4a R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3328 | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-4 Requirement R5. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 51100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3332 | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 52100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3336 | Each password shall be a minimum of six characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 53100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3340 | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-007-4a R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3346 | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-007-4a R7. | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3350 | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-007-4a R8. | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3356 | Procedures to characterize and classify events as reportable Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-008-4 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3364 | Specify the required actions in response to events or conditions of varying duration and severity that would activate the recovery plan(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-009-4 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3376 | Loading all available generating capacity. |  | BA | BA | [21 empty] | 2011-01-10 |  | 2012-09-12 |  |  | EOP-002-3 R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3383 | Manually shed firm load without delay to return its ACE to zero; and |  | BA | BA | [21 empty] | 2011-01-10 |  | 2012-09-12 |  |  | EOP-002-3 R7. | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3387 | The deficient Load-Serving Entity shall request its Reliability Coordinator to initiate an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0. |  | LSE | [7 empty] | LSE | [14 empty] | 2011-01-10 |  | 2012-09-12 |  |  | EOP-002-3 R9. | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3408 | Evaluation of the reliability impact of the new facilities and their connections on the interconnected transmission systems. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [14 empty] | 2011-01-10 |  | 2015-12-31 |  |  | FAC-002-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 341 | Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-006-1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3421 | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  | IRO-005-2a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3453 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | TPL-001-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3456 | Cover critical system conditions and study years as deemed appropriate by the entity performing the study. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 346 | Alarm Systems: Systems that alarm to indicate a door, gate or window has been pened without authorization. These alarms must provide for immediate notificationto personnel responsible for response. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-006-1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3467 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | TPL-001-1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3468 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3474 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | TPL-002-0b R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3477 | Be performed and evaluated only for those Category B contingencies that would produce the more severe System results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 349 | Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-006-1 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3492 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | TPL-002-0b R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3493 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3499 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | TPL-002-1b R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 35 | The Contingency Reserve Restoration Period begins at the end of the Disturbance Recovery Period. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  | BAL-002-0 R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3502 | Be performed and evaluated only for those Category B contingencies that would produce the more severe System results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3517 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | TPL-002-1b R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3518 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3524 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | TPL-003-1a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3527 | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 354 | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | CIP-006-1 R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3542 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | TPL-003-1a R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3543 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3549 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | TPL-004-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3552 | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3567 | The Sending Balancing Authority and Receiving Balancing Authority shall agree on Interchange as received from the Interchange Authority, including: |  | BA | BA | [21 empty] | 2011-04-01 |  | 2014-09-30 |  |  | INT-003-3 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3568 | Interchange Schedule start and end time. |  | BA | BA | [21 empty] | 2011-04-01 |  | 2014-09-30 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 358 | Processes to ensure and document that all Cyber Assets within an Electronic Security Perimeter also reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3592 | Each Reliability Coordinator shall identify the data requirements from the list in Attachment 1-TOP-005-0 “Electric System Reliability Data” and any additional operating information requirements relating to operation of the bulk power system within the Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  | TOP-005-1.1a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3602 | Each Transmission Operator shall maintain a list of generators in its area that are exempt from following a voltage or Reactive Power schedule. |  | TOP | [18 empty] | TOP |  |  |  | 2011-01-10 |  | 2013-12-31 |  |  | VAR-001-2 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3607 | When notified of the loss of an automatic voltage regulator control, the Transmission Operator shall direct the Generator Operator to maintain or change either its voltage schedule or its Reactive Power schedule. |  | TOP | [18 empty] | TOP |  |  |  | 2011-01-10 |  | 2013-12-31 |  |  | VAR-001-2 R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3611 | Each Transmission Operator shall disperse and locate the reactive resources so that the resources can be applied effectively and quickly when Contingencies occur. |  | TOP | [18 empty] | TOP |  |  |  | 2011-01-10 |  | 2013-12-31 |  |  | VAR-001-2 R9. | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3624 | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | CIP-005-1a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3627 | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | CIP-005-1a R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3635 | The processes for access request and authorization. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 25100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3638 | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | CIP-005-1a R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3641 | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | CIP-005-1a R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3644 | The Responsible Entity shall ensure that all documentation required by Standard CIP-005 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005 at least annually. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | CIP-005-1a R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3655 | Access points to the Electronic Security Perimeter(s) shall include any externally connected communication end point (for example, dial-up modems) terminating at any device within the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | CIP-005-2a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3658 | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | CIP-005-2a R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3666 | The processes for access request and authorization. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 25100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3669 | For dial-up accessible Critical Cyber Assets that use non-routable protocols, the Responsible Entity shall implement and document monitoring process(es) at each access point to the dial-up device, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | CIP-005-2a R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3672 | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | CIP-005-2a R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3675 | The Responsible Entity shall ensure that all documentation required by Standard CIP-005-2 reflect current configurations and processes and shall review the documents and procedures referenced in Standard CIP-005-2 at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | CIP-005-2a R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 368 | Card Key: A means of electronic access where the access rights of the card holder are predefined in a computer database. Access rights may differ from one perimeter to another. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1a R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3697 | Each Generator Operator with generation facilities operating in an Interconnection shall ensure that those generation facilities are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP | [5 empty] | 2008-04-15 |  |  | BAL-005-0a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3698 | Balancing Authorities that share a tie shall ensure Tie Line MW metering is telemetered to both control centers, and emanates from a common, agreed-upon source using common primary metering equipment. Balancing Authorities shall ensure that megawatt-hour data is telemetered or reported at the end of each hour. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP | [5 empty] | 2008-04-15 |  |  | BAL-005-0a R12. | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3701 | Each Balancing Authority shall provide redundant and independent frequency metering equipment that shall automatically activate upon detection of failure of the primary source. This overall installation shall provide a minimum availability of 99.95%. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP | [5 empty] | 2008-04-15 |  |  | BAL-005-0a R8. | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3702 | Balancing Authorities with a high voltage direct current (HVDC) link to another Balancing Authority connected asynchronously to their Interconnection may choose to omit the Interchange Schedule related to the HVDC link from the ACE equation if it is modeled as internal generation or load. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP | [5 empty] | 2008-04-15 |  |  | BAL-005-0a R9. | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3705 | Maintenance and testing intervals and their basis. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2011-09-26 |  | 2012-03-13 |  |  | PRC-005-1a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3707 | Evidence Protection System devices were maintained and tested within the defined intervals. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2011-09-26 |  | 2012-03-13 |  |  | PRC-005-1a R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3718 | The Balancing Authority may change its Frequency Bias Setting, and the method used to determine the setting, whenever any of the factors used to determine the current bias value change. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2009-06-28 |  |  | BAL-003-0.1a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3721 | The Balancing Authority may use a fixed Frequency Bias value which is based on a fixed, straight-line function of Tie Line deviation versus Frequency Deviation. The Balancing Authority shall determine the fixed value by observing and averaging the Frequency Response for several Disturbances during on-peak hours. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2009-06-28 |  |  | BAL-003-0.1a R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3723 | Fixed schedules for Jointly Owned Units mandate that Balancing Authority (A) that contains the Jointly Owned Unit must incorporate the respective share of the unit governor droop response for any Balancing Authorities that have fixed schedules (B and C). See the diagram below. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2009-06-28 |  |  | BAL-003-0.1a R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3724 | Balancing Authorities that do not serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of its estimated maximum generation level in the coming year per 0.1 Hz change. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2009-06-28 |  |  | BAL-003-0.1a R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 373 | Alarm Systems: Systems that alarm to indicate a door, gate or window has been opened without authorization. These alarms must provide for immediate notification to personnel responsible for response. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1a R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 376 | Computerized Logging: Electronic logs produced by the Responsible Entity’s selected access control and monitoring method. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1a R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3787 | Changes in real output capabilities. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-10-20 |  | 2012-09-12 |  |  | TOP-002-2b R14. | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3789 | Changes in transmission facility status. |  | TOP | [18 empty] | TOP |  |  |  | 2011-10-20 |  | 2012-09-12 |  |  | TOP-002-2b R16. | 161000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 38 | The greater of the following: |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | · evidence such as Operating Plans or other operator documentation that demonstrate that the entity determines its Most Severe Single Contingency and that Contingency Reserves equal to or greater than its Most Severe Single Contingency are included in this process. |  |  | 2010-11-26 |  |  | BAL-002-WECC-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 381 | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1a R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3811 | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  | IRO-005-3 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3822 | For a generator outage, the Generator Operator shall notify and coordinate with the Transmission Operator. The Transmission Operator shall notify the Reliability Coordinator and other affected Transmission Operators, and coordinate the impact of removing the Bulk Electric System facility. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-11-21 |  | 2017-03-31 |  |  | TOP-001-1a R7. | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3836 | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | EOP-001-0b R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3840 | Communications protocols to be used during emergencies. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | EOP-001-0b R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3841 | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | EOP-001-0b R7. | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 385 | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-04-07 |  | 2010-03-31 |  |  | CIP-007-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3852 | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | EOP-001-2b R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3857 | Communications protocols to be used during emergencies. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | EOP-001-2b R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3858 | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | EOP-001-2b R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 389 | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-007-1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 39 | An amount of reserve equal to the loss of the most severe single contingency; or |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2010-11-26 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3902 | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | CIP-006-2a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3907 | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | CIP-006-2a R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3908 | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | CIP-006-2a R8. | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3923 | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  | CIP-006-3a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3927 | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2011-05-18 |  |  |  | 16100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3929 | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  | CIP-006-3a R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 393 | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-007-1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3931 | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  | CIP-006-3a R8. | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 396 | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure or an acceptance of risk. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | CIP-007-1 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3961 | Information describing how the selected methodology has been implemented, in such detail that, given the same information used by the Transmission Operator, the results of the TTC calculations can be validated. |  | TSP | [20 empty] | TSP |  | 2013-09-27 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | MOD-028-2 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3966 | Define if the source used for Available Transfer Capability (ATC) calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation |  | TSP | [20 empty] | TSP |  | 2013-10-01 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 15100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3973 | Modeling data and topology of its Reliability Coordinator’s area of responsibility. Equivalent representation of radial lines and facilities 161 kV or below is allowed. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | MOD-028-2 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3977 | For TTCs, use the following (as well as any other values and additional parameters as specified in the ATCID): |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | MOD-028-2 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3978 | Expected generation and Transmission outages, additions, and retirements, included as specified in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2013-10-01 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 31100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3984 | Use all Contingencies meeting the criteria described in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | MOD-028-2 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3988 | At least once within the seven calendar days prior to the specified period for TTCs used in hourly and daily ATC calculations. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | MOD-028-2 R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 399 | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-007-1 R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3992 | Determine the incremental Transfer Capability for each ATC Path by increasing generation and/or decreasing load within the source Balancing Authority area and decreasing generation and/or increasing load within the sink Balancing Authority area until either:- A System Operating Limit is reached on the Transmission Service Provider’s system, or- A SOL is reached on any other adjacent system in the Transmission model that is not on the study path and the distribution factor is 5% or greater .Footnote: The Transmission operator may honor distribution factors less than 5% if desired. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | MOD-028-2 R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 3997 | One calendar day after its determination for TTCs used in hourly and daily ATC calculations. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | MOD-028-2 R7. | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 400 | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003 Requirement R5. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 51100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4036 | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-006-3d R8. | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 404 | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 52100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4045 | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-006-3d R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4047 | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-006-3d R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4049 | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 16100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4062 | All Cyber Assets within an Electronic Security Perimeter shall reside within an identified Physical Security Perimeter. Where a completely enclosed (“six-wall”) border cannot be established, the Responsible Entity shall deploy and document alternative measures to control physical access to such Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-006-4d R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4066 | Logs (manual or automated) to document the entry and exit of visitors, including the date and time, to and from Physical Security Perimeters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 16100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4068 | Be protected from unauthorized physical access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-006-4d R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4070 | Testing and maintenance of all physical security mechanisms on a cycle no longer than three years. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-006-4d R8. | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4075 | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator, and all other potentially affected Balancing Authorities and Transmission Operators through predetermined communication paths of any condition that could threaten the reliability of its area or when firm load shedding is anticipated. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2016-06-30 |  |  | COM-002-2a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4078 | Maintenance and testing intervals and their basis. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2012-03-14 |  | 2013-11-24 |  |  | PRC-005-1b R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 408 | Each password shall be a minimum of six characters. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 53100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4080 | Evidence Protection System devices were maintained and tested within the defined intervals. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2012-03-14 |  | 2013-11-24 |  |  | PRC-005-1b R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4090 | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  | EOP-001-2.1b R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4092 | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  | EOP-001-2.1b R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4096 | Communications protocols to be used during emergencies. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  | EOP-001-2.1b R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4118 | Each Generator Operator with generation facilities operating in an Interconnection shall ensure that those generation facilities are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2012-09-13 |  | 2018-12-31 |  |  | BAL-005-0.2b R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4119 | Balancing Authorities that share a tie shall ensure Tie Line MW metering is telemetered to both control centers, and emanates from a common, agreed-upon source using common primary metering equipment. Balancing Authorities shall ensure that megawatt-hour data is telemetered or reported at the end of each hour. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2012-09-13 |  | 2018-12-31 |  |  | BAL-005-0.2b R12. | 121000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 412 | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | CIP-007-1 R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4122 | Each Balancing Authority shall provide redundant and independent frequency metering equipment that shall automatically activate upon detection of failure of the primary source. This overall installation shall provide a minimum availability of 99.95%. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2012-09-13 |  | 2018-12-31 |  |  | BAL-005-0.2b R8. | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4123 | Balancing Authorities with a high voltage direct current (HVDC) link to another Balancing Authority connected asynchronously to their Interconnection may choose to omit the Interchange Schedule related to the HVDC link from the ACE equation if it is modeled as internal generation or load. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2012-09-13 |  | 2018-12-31 |  |  | BAL-005-0.2b R9. | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4133 | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  | EOP-001-0.1b R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4136 | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  | EOP-001-0.1b R7. | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4142 | Communications protocols to be used during emergencies. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  | EOP-001-0.1b R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4163 | Changes in real output capabilities. |  | GOP | [5 empty] | GOP | [16 empty] | 2012-09-13 |  | 2017-03-31 |  |  | TOP-002-2.1b R14. | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4165 | Changes in transmission facility status. |  | TOP | [18 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  | TOP-002-2.1b R16. | 161000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 418 | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-007-1 R7. | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4187 | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  | IRO-005-3.1a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4197 | Loading all available generating capacity. |  | BA | BA | [21 empty] | 2012-09-13 |  | 2017-03-31 |  |  | EOP-002-3.1 R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4204 | Manually shed firm load without delay to return its ACE to zero; and |  | BA | BA | [21 empty] | 2012-09-13 |  | 2017-03-31 |  |  | EOP-002-3.1 R7. | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4205 | The deficient Load-Serving Entity shall request its Reliability Coordinator to initiate an Energy Emergency Alert in accordance with Attachment 1-EOP-002 “Energy Emergency Alerts.” |  | LSE | [7 empty] | LSE | [14 empty] | 2012-09-13 |  | 2017-03-31 |  |  | EOP-002-3.1 R9. | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4218 | Incorporate the NPIRs into their operating analyses of the electric system. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP | M4.1 The NPIRs have been incorporated into the current operating analysis of the electric system. (Requirement 4.1) | 2013-04-01 |  | 2015-12-31 |  |  |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 422 | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-007-1 R8. | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4222 | Administrative elements: |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2014-01-21 |  |  |  | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4227 | Definitions of key terms used in the agreement. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2014-01-21 |  |  |  | 91100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4230 | Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the agreement. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 92100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4232 | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 93100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4239 | Provisions for communications between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of terms. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 94100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4253 | Incorporate the NPIRs into their operating analyses of the electric system. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  | NUC-001-2.1 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4257 | Administrative elements: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  | NUC-001-2.1 R9. | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 428 | Procedures to characterize and classify events as reportable Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-008-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4285 | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. |  | GOP | [5 empty] | GOP | [16 empty] | 2013-04-01 |  | 2015-05-28 |  |  | PRC-001-1.1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4288 | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. |  | GOP | [5 empty] | GOP | [16 empty] | 2013-04-01 |  | 2015-05-28 |  |  | PRC-001-1.1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4290 | Each Generator Operator shall notify its Transmission Operator in advance of changes in generation or operating conditions that could require changes in the Transmission Operator’s Protection Systems. |  | GOP | [5 empty] | GOP | [16 empty] | 2013-04-01 |  | 2015-05-28 |  |  | PRC-001-1.1 R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4293 | Maintenance and testing intervals and their basis. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2013-11-25 |  | 2027-03-31 |  |  | PRC-005-1.1b R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4295 | Evidence Protection System devices were maintained and tested within the defined intervals. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2013-11-25 |  | 2027-03-31 |  |  | PRC-005-1.1b R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4319 | Each Transmission Operator shall maintain a list of generators in its area that are exempt from following a voltage or Reactive Power schedule. |  | TOP | [18 empty] | TOP |  |  |  | 2013-06-20 |  | 2014-09-30 |  |  | VAR-001-3 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4324 | When notified of the loss of an automatic voltage regulator control, the Transmission Operator shall direct the Generator Operator to maintain or change either its voltage schedule or its Reactive Power schedule. |  | TOP | [18 empty] | TOP |  |  |  | 2013-06-20 |  | 2014-09-30 |  |  | VAR-001-3 R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4328 | Each Transmission Operator shall disperse and locate the reactive resources so that the resources can be applied effectively and quickly when Contingencies occur. |  | TOP | [18 empty] | TOP |  |  |  | 2013-06-20 |  | 2014-09-30 |  |  | VAR-001-3 R9. | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4337 | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-002-3a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4342 | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4345 | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-002-3a R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 436 | Specify the required actions in response to events or conditions of varying duration and severity that would activate the recovery plan(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-009-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4360 | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. |  | GOP | [5 empty] | GOP | [18 empty] | 2016-01-26 |  |  | PRC-001-2 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4368 | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-004-3 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4373 | The proper use of Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 22100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4375 | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-004-3 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4377 | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-004-3 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4384 | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2014-02-03 |  |  | CIP-004-4 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4389 | The proper use of Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 22100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4391 | The Responsible Entity shall ensure that each assessment conducted include, at least, identity verification (e.g., Social Security Number verification in the U.S.) and seven-year criminal check. The Responsible Entity may conduct more detailed reviews, as permitted by law and subject to existing collective bargaining unit agreements, depending upon the criticality of the position. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2014-02-03 |  |  | CIP-004-4 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4393 | The Responsible Entity shall review the list(s) of its personnel who have such access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to Critical Cyber Assets, or any change in the access rights of such personnel. The Responsible Entity shall ensure access list(s) for contractors and service vendors are properly maintained. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2014-02-03 |  |  | CIP-004-4 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 44 | Immediately and automatically responds proportionally to frequency deviations, e.g. through the action of a governor or other control systems. |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2010-11-26 |  |  | BAL-002-WECC-1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4400 | When a generator’s automatic voltage regulator is out of service, the Generator Operator shall use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2013-07-01 |  | 2014-09-30 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4403 | A status or capability change on any generator Reactive Power resource, including the status of each automatic voltage regulator and power system stabilizer and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2013-07-01 |  | 2014-09-30 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4406 | For generator step-up transformers and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: |  | GO | [22 empty] | 2013-07-01 |  | 2014-09-30 |  |  |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4407 | Tap settings. |  | GO | [22 empty] | 2013-07-01 |  | 2014-09-30 |  |  |  | 41100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4412 | If the Generator Operator can’t comply with the Transmission Operator’s specifications, the Generator Operator shall notify the Transmission Operator and shall provide the technical justification. |  | GOP | [5 empty] | GOP | [16 empty] | 2013-07-01 |  | 2014-09-30 |  |  |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 443 | Internally. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-05-12 |  |  | COM-001-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4443 | A Balancing Authority may elect to fulfill its Contingency Reserve obligations by participating as a member of a Reserve Sharing Group. In such cases, the Reserve Sharing Group shall have the same responsibilities and obligations as each Balancing Authority with respect to monitoring and meeting the requirements of Standard BAL-002. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  | BAL-002-1a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4447 | The minimum reserve requirement for the group. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  | BAL-002-1a R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4450 | As a minimum, the Balancing Authority or Reserve Sharing Group shall carry at least enough Contingency Reserve to cover the most severe single contingency. All Balancing Authorities and Reserve Sharing Groups shall review, no less frequently than annually, their probable contingencies to determine their prospective most severe single contingencies. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  | BAL-002-1a R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4452 | A Balancing Authority shall return its ACE to zero if its ACE just prior to the Reportable Disturbance was positive or equal to zero. For negative initial ACE values just prior to the Disturbance, the Balancing Authority shall return ACE to its pre-Disturbance value. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  | BAL-002-1a R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4453 | The Reserve Sharing Group reviews group ACE (or equivalent) and demonstrates compliance to the DCS. To be in compliance, the group ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period.or |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  | BAL-002-1a R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4455 | The Contingency Reserve Restoration Period begins at the end of the Disturbance Recovery Period. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  | BAL-002-1a R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4463 | Each Generator Operator shall inform its Host Balancing Authority and the Transmission Operator of all generation resources available for use. |  | GOP | [5 empty] | GOP | [18 empty] | 2015-03-18 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 453 | Internally. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2009-05-13 |  | 2015-09-30 |  |  | COM-001-1.1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4559 | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-002-3a R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4560 | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-002-3a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4565 | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4586 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  | M2. The Planning Authority and Transmission Planner shall have evidence it reporteddocumentation of results of its reliability assessments and corrective plans per ReliabilityStandard TPL-002-1_R3. |  |  | 2014-12-31 |  |  | TPL-001-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4588 | Cover critical system conditions and study years as deemed appropriate by the entity performing the study. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4596 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | TPL-001-1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4600 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4628 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | TPL-002-0b R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 463 | Each Balancing Authority and Transmission Operator shall notify its Reliability Coordinator, and all other potentially affected Balancing Authorities and Transmission Operators through predetermined communication paths of any condition that could threaten the reliability of its area or when firm load shedding is anticipated. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2016-06-30 |  |  | COM-002-2 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4632 | Be performed and evaluated only for those Category B contingencies that would produce the more severe System results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4642 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | TPL-002-0b R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4646 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4653 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | TPL-003-0a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4657 | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4667 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | TPL-003-0a R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4671 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4676 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | TPL-004-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4679 | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 468 | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  | EOP-001-0 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4693 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | TPL-003-0a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4697 | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 47 | Spinning Reserve |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Any Reserve Sharing Group or Balancing Authority utilizing Load other than Interruptible Load shall submit documentation demonstrating that the Reliability Coordinator declared a Capacity and/or Energy Emergency prior to utilizing Load for Contingency Reserves. |  |  | 2010-11-26 |  |  | BAL-002-WECC-1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4707 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | TPL-003-0a R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4711 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4717 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | TPL-003-0a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4720 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | TPL-003-0a R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4728 | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 473 | Communications protocols to be used during emergencies. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  | EOP-001-0 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4735 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4741 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | TPL-004-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4744 | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4754 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | TPL-004-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4763 | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4798 | Each Balancing Authority, by the end of the next business day, shall agree with itsAdjacent Balancing Authorities to: |  | BA | BA | [23 empty] | 2006-05-01 |  |  |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4799 | The hourly values of Net Interchange Schedule. |  | BA | BA | [23 empty] | 2006-05-01 |  |  |  | 41100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 480 | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  | EOP-001-0 R7. | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4809 | Internally. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4820 | The Balancing Authority is unable to purchase capacity or energy to meet its demandand reserve requirements on a day-ahead or hour-by-hour basis. |  | BA | BA | [23 empty] | 2006-11-01 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4825 | Each Balancing Authority and Transmission Operator shall notify its ReliabilityCoordinator, and all other potentially affected Balancing Authorities andTransmission Operators through predetermined communication paths of any conditionthat could threaten the reliability of its area or when firm load shedding is anticipated. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4829 | The deficient Load-Serving Entity shall request its Reliability Coordinator to initiatean Energy Emergency Alert in accordance with Attachment 1-EOP-002-0. |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4838 | Loading all available generating capacity. |  | BA | BA | [23 empty] | 2006-11-01 |  |  |  | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4845 | Manually shed firm load without delay to return its ACE to zero; and |  | BA | BA | [23 empty] | 2006-11-01 |  |  |  | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4855 | Loading all available generating capacity. |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 486 | Develop, maintain, and implement a set of plans to mitigate operating emergencies for insufficient generating capacity. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  | EOP-001-1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4862 | Manually shed firm load without delay to return its ACE to zero; and |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4866 | The deficient Load-Serving Entity shall request its Reliability Coordinator to initiatean Energy Emergency Alert in accordance with Attachment 1-EOP-002-0. |  | RC | [11 empty] | RC | [12 empty] | 2007-01-01 |  |  |  | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4887 | The affected Transmission Operators and Balancing Authorities shall work in conjunction with their Reliability Coordinator(s) to determine the extent and condition of the isolated area(s). |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2007-05-02 |  |  |  | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4892 | Voltage, frequency, and phase angle permit. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-05-02 |  |  |  | 95100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4903 | Inspection requirements. |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-04-07 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4908 | The methodology(ies) used to determine equipment and Facility Rating of the itemslisted for both normal and emergency conditions: |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-08-01 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4909 | Transmission circuits. |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-08-01 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 491 | Communications protocols to be used during emergencies. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  | EOP-001-1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4922 | The Ratings shall be consistent with the entity’s methodology(ies) for determiningFacility Ratings and shall be updated as facility changes occur. |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-10-07 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4925 | All Interchange Transactions that are between Balancing Authority Areas |  | BA, PSE | BA | [9 empty] | PSE | [13 empty] | 2007-01-01 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4929 | If a Purchasing-Selling Entity is not involved in the Transaction, such as delivery from a jointly owned generator. |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4936 | All Dynamic Schedules at the expected average MW profile for each hour. |  | PSE | [10 empty] | PSE | [13 empty] | 2006-11-01 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4938 | If a Purchasing-Selling Entity is not involved in the Interchange, such as delivery from a jointly owned generator. |  | BA, PSE | BA | [9 empty] | PSE | [13 empty] | 2006-11-01 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4941 | Sink and Source Balancing Authority for the Transaction. |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4947 | Valid OASIS reservation number or transmission contract identifier. |  | TSP | [20 empty] | TSP |  |  |  | 2007-01-01 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4954 | Transaction start and end time. |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4961 | The Sending Balancing Authority and Receiving Balancing Authority shall agree on: |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4962 | Interchange Schedule start and end time. |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4972 | The total capacity of both the owned and arranged-for transmission facilities in service for any Transmission Service Provider along the path, or |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4975 | The Sending Balancing Authority and Receiving Balancing Authority shall agree on Interchange as received from the Interchange Authority, including: |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4976 | Interchange Schedule start and end time. |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 498 | The Transmission Operator and Balancing Authority shall establish and maintain reliable communications between interconnected systems. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  | EOP-001-1 R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4980 | Transmission Loading Relief procedure curtailment — Eastern Interconnection. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4986 | When a loss of generation necessitates curtailing Interchange Transactions, the Source Balancing Authority shall coordinate the modifications to the appropriate tags. |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 4991 | The average energy profile in an hour is greater than 250 MW and in that hour the actual hourly integrated energy deviates from the hourly average energy profile indicated on the tag by more than +10%. |  | PSE | [10 empty] | PSE | [13 empty] | 2007-01-01 |  |  |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5026 | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5054 | The Interconnection-wide Transmission Loading Relief (TLR) procedure for use inthe Eastern Interconnection is provided in Attachment 1-IRO-006-0. |  | RC | [11 empty] | RC | [12 empty] | 2005-08-08 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5063 | The Interconnection-wide Transmission Loading Relief (TLR) procedure for use inthe Eastern Interconnection is provided in Attachment 1-IRO-006-0. |  | RC | [11 empty] | RC | [12 empty] | 2006-09-29 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5072 | The Interconnection-wide Transmission Loading Relief (TLR) procedure for usein the Eastern Interconnection is provided in Attachment 1-IRO-006-0. |  | RC | [11 empty] | RC | [12 empty] | 2006-09-29 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 508 | Loading all available generating capacity. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  | EOP-002-2 R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5080 | Unit-specific dynamics data shall be reported for generators and synchronous condensers (including, as appropriate to the model, items such as inertia constant, damping coefficient, saturation parameters, and direct and quadrature axes reactances and time constants), excitation systems, voltage regulators, turbine-governor systems, power system stabilizers, and other associated generation equipment. |  | RRO | [14 empty] | RRO | [9 empty] | 2006-11-02 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5081 | Estimated or typical manufacturer’s dynamics data, based on units of similar design and characteristics, may be submitted when unit-specific dynamics data cannot be obtained. In no case shall other than unit-specific data be reported for generator units installed after 1990. |  | RRO | [14 empty] | RRO | [9 empty] | 2006-11-02 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5088 | The aggregated and dispersed data submittal requirements shall ensure that consistentdata is supplied for Reliability Standards TPL-005-0, TPL-006-0, MOD-010-0, MOD011-0, MOD-012-0, MOD-013-0, MOD-014-0, MOD-015-0, MOD-016, MOD-017-0, MOD-018-0, MOD-019-0, MOD-020-0, and MOD-021-0. |  | PCPA, RRO | [9 empty] | PA |  |  |  |  | RRO | [9 empty] | 2006-11-02 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5097 | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. |  | GOP | [5 empty] | GOP | [18 empty] | 2007-01-01 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5100 | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. |  | GOP | [5 empty] | GOP | [18 empty] | 2007-01-01 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5104 | Each Generator Operator shall notify its Transmission Operator in advance of changes in generation or operating conditions that could require changes in the Transmission Operator’s protection systems. |  | GOP | [5 empty] | GOP | [18 empty] | 2007-01-01 |  |  |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5108 | Type of data recording capability (e.g., sequence-of-event, Fault recording, dynamic Disturbance recording). |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5110 | Recording duration requirements. |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5115 | Voltage. |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5122 | Substations. |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 16100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5129 | Requirements for monitoring and analysis of all transmission protective device misoperations. |  | RRO | [14 empty] | RRO | [9 empty] | 2006-05-01 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5138 | Transmission protection system identification shall include but are not limited to: |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2006-05-01 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5139 | Relays. |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2006-05-01 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 515 | Manually shed firm load without delay to return its ACE to zero; and |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  | EOP-002-2 R7. | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5161 | Changes in real and reactive output capabilities. |  | GOP | [5 empty] | GOP | [18 empty] | 2007-08-07 |  |  |  | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5165 | Changes in transmission facility status |  | TOP | [18 empty] | TOP | [5 empty] | 2007-08-07 |  |  |  | 161000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5184 | Changes in real output capabilities |  | GOP | [5 empty] | GOP | [18 empty] | 2007-01-01 |  |  |  | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5187 | Changes in transmission facility status. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 161000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 519 | The deficient Load-Serving Entity shall request its Reliability Coordinator to initiate an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0. |  | LSE | [7 empty] | LSE | [14 empty] | 2007-06-18 |  | 2009-05-12 |  |  | EOP-002-2 R9. | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5206 | Equipment ratings. |  | TOP | [18 empty] | TOP | [5 empty] | 2005-04-01 |  |  |  | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5213 | Each Reliability Coordinator shall identify the data requirements from the list in Attachment 1-TOP-005-0 “Electric System Reliability Data” and any additional operating information requirements relating to operation of the bulk power system within the Reliability Coordinator Area. |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5219 | Each Generator Operator shall inform its Host Balancing Authority and the Transmission Operator of all generation resources available for use. |  | GOP | [5 empty] | GOP | [18 empty] | 2007-01-01 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5238 | Each Transmission Operator shall disperse and locate the reactive resources so that theresources can be applied effectively and quickly when Contingencies occur. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5241 | When a generator’s voltage regulator is out of service, the Generator Operator shallmaintain the generator field excitation at a level to maintain Interconnection andgenerator stability. |  | GOP | [5 empty] | GOP | [18 empty] | 2007-01-01 |  |  |  | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5272 | The cyber security policy addresses the requirements in Standards CIP-002-3 through CIP-009-3, including provision for emergency situations. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | CIP-003-3 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5275 | The senior manager shall be identified by name, title, and date of designation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | CIP-003-3 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5278 | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | CIP-003-3 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5282 | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP-002-3, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | CIP-003-3 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5283 | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | CIP-003-3 R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5286 | Personnel shall be identified by name, title, and the information for which they are responsible for authorizing access. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | 51100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 529 | Loading all available generating capacity. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-09-30 |  |  | EOP-002-2.1 R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5296 | The cyber security policy addresses the requirements in Standards CIP-002-4 through CIP-009-4, including provision for emergency situations. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-003-4 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5299 | The senior manager shall be identified by name, title, and date of designation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-003-4 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5302 | Exceptions to the Responsible Entity’s cyber security policy must be documented within thirty days of being approved by the senior manager or delegate(s). |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-003-4 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5306 | The Critical Cyber Asset information to be protected shall include, at a minimum and regardless of media type, operational procedures, lists as required in Standard CIP-002-4, network topology or similar diagrams, floor plans of computing centers that contain Critical Cyber Assets, equipment layouts of Critical Cyber Assets, disaster recovery plans, incident response plans, and security configuration information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-003-4 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5307 | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-003-4 R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5310 | Personnel shall be identified by name, title, and the information for which they are responsible for authorizing access. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 51100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5322 | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-007-3a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5325 | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-007-3a R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5327 | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-007-3a R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5330 | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-007-3a R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5332 | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-007-3a R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5335 | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-3 Requirement R5. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 51100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5338 | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 52100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5341 | Each password shall be a minimum of six characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 53100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5347 | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-007-3a R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5349 | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-007-3a R7. | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5354 | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-007-3a R8. | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 536 | Manually shed firm load without delay to return its ACE to zero; and |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-09-30 |  |  | EOP-002-2.1 R7. | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5365 | The Responsible Entity shall create, implement, and maintain cyber security test procedures in a manner that minimizes adverse effects on the production system or its operation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-007-4a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5368 | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-007-4a R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5370 | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-007-4a R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5373 | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-007-4a R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5375 | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-007-4a R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5378 | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-4 Requirement R5. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 51100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5381 | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 52100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5384 | Each password shall be a minimum of six characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 53100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5390 | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-007-4a R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5392 | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-007-4a R7. | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5397 | A document identifying the vulnerability assessment process; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-007-4a R8. | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 54 | The Balancing Authority may change its Frequency Bias Setting, and the method used to determine the setting, whenever any of the factors used to determine the current bias value change. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  | BAL-003-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 540 | The deficient Load-Serving Entity shall request its Reliability Coordinator to initiate an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0. |  | LSE | [7 empty] | LSE | [14 empty] | 2009-05-13 |  | 2011-09-30 |  |  | EOP-002-2.1 R9. | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5439 | If the path SOL decreases within 20 minutes before the start of the hour, the Transmission Operator shall adjust the Net Scheduled Interchange within 30 minutes to the new SOL value. Net Scheduled Interchange exceeding the new SOL during this 30-minute period will not be a violation of R2. |  | TOP | [18 empty] | TOP |  |  | M2.1. Evidence that Net Scheduled Interchange was at or below the new SOL within 30-minutes of when the SOL decreased. | 2014-06-18 |  | 2017-03-10 |  |  | TOP-007-WECC-1 R2. | 21000000 | WECC-US | [5 empty] | WECC-US
1. | 555 | The affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator or Load-Serving Entity shall submit within 24 hours of the disturbance or unusual occurrence either a copy of the report submitted to DOE, or, if no DOE report is required, a copy of the NERC Interconnection Reliability Operating Limit and Preliminary Disturbance Report form. Events that are not identified until some time after they occur shall be reported within 24 hours of being recognized. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-12-31 |  |  | EOP-004-1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5599 | Be applicable for developing SOLs used in the planning horizon. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5615 | Planned or controlled interruption of electric supply to customers (load shedding), the planned removal from service of certain generators, and/or the curtailment of contracted Firm (non-recallable reserved) electric power Transfers. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-04-01 | [5 empty] | 26100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5618 | Study model (must include at least the entire Planning Authority Area as well as the critical modeling details from other Planning Authority Areas that would impact the Facility or Facilities under study). |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5625 | Each adjacent Planning Authority and each Planning Authority that indicated it has a reliability-related need for the methodology. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 563 | The Transmission Operator shall perform this simulation or testing at least once every five years. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | EOP-005-1 R10. | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5630 | Be applicable for developing SOLs used in the operations horizon. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5646 | Study model (must include at least the entire Reliability Coordinator Area as well as the critical modeling details from other Reliability Coordinator Areas that would impact the Facility or Facilities under study.) |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5649 | This process shall address the need to modify these limits, to modify the list of limits, and to modify the list of associated multiple contingencies. |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 33100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 565 | The affected Transmission Operators and Balancing Authorities shall work in conjunction with their Reliability Coordinator(s) to determine the extent and condition of the isolated area(s). |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | EOP-005-1 R11. | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5655 | Each adjacent Reliability Coordinator and each Reliability Coordinator that indicated it has a reliability-related need for the methodology. |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5656 | Each adjacent Reliability Coordinator and each Reliability Coordinator that indicated it has a reliability-related need for the methodology. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5661 | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Remedial Action Schemes) and system loading. |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5683 | The criteria used by the Transmission Operator to identify sets of Transmission Facilities as Flowgates that are to be considered in Available Flowgate Capability (AFC) calculations. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5685 | Define if the source used for AFC calculations is obtained from the source field or the Point of Receipt (POR) field of the transmission reservation. |  | TSP | [20 empty] | TSP |  | 2017-04-01 | [5 empty] | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5690 | Include Flowgates used in the AFC process based, at a minimum, on the following criteria |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5691 | Results of a first Contingency transfer analysis for ATC Paths internal to a Transmission Operator’s system up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an OTDF of at least 5% and within the Transmission Operator’s system are included as Flowgates. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5692 | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Remedial Action Schemes. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 21110000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5696 | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Remedial Action Schemes. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 21210000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 57 | The Balancing Authority may use a fixed Frequency Bias value which is based on a fixed, straight-line function of Tie Line deviation versus Frequency Deviation. The Balancing Authority shall determine the fixed value by observing and averaging the Frequency Response for several Disturbances during on-peak hours. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  | BAL-003-0 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 570 | Voltage, frequency, and phase angle permit. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  |  | 115100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5702 | The coordination of the limiting Element/Contingency combination is not already addressed through a different methodology, and - Any generator within the Transmission Service Provider’s area has at least a 5% Power Transfer Distribution Factor (PTDF) or Outage Transfer Distribution Factor (OTDF) impact on the Flowgate when delivered to the aggregate load of its own area, or - A transfer from any Balancing Area within the Transmission Service Provider’s area to a Balancing Area adjacent has at least a 5% PTDF or OTDF impact on the Flowgate. - The Transmission Operator may utilize distribution factors less than 5% if desired. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 21410000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5708 | If notified of a change in the Rating by the Transmission Owner that would affect the TFC of a flowgate used in the AFC process, the TFC should be updated within seven calendar days of the notification. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 25100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5711 | Contains generation Facility Ratings, such as generation maximum and minimum output levels, specified by the Generator Owners of the Facilities within the model. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5718 | Use the models provided by the Transmission Operator. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5722 | The impact of firm Network Integration Transmission Service, including the impacts of generation to load, in the model referenced in R5.2 for the Transmission Service Provider’s area, based on: |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5723 | Load forecast for the time period being calculated, including Native Load and Network Service load |  | TSP | [20 empty] | TSP |  | 2017-04-01 | [5 empty] | 61100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5726 | Load forecast for the time period being calculated, including Native Load and Network Service load |  | TSP | [20 empty] | TSP |  | 2017-04-01 | [5 empty] | 62100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5734 | The impact of all confirmed non-firm Point-to-Point Transmission Service expected to be scheduled for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5744 | For hourly AFC, once per hour. Transmission Service Providers are allowed up to 175 hours per calendar year during which calculations are not required to be performed, despite a change in a calculated value identified in the AFC equation. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5751 | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5753 | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5760 | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5763 | The Responsible Entity shall maintain documentation describing its risk-based assessment methodology that includes procedures and evaluation criteria. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5765 | Control centers and backup control centers performing the functions of the entities listed in the Applicability section of this standard. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5772 | The Cyber Asset uses a routable protocol to communicate outside the Electronic Security Perimeter; or, |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5780 | Incorporate the NPIRs into their operating analyses of the electric system. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5788 | Administrative elements: (Retirement approved by FERC effective January 21, 2014.) | [26 empty] | 2014-11-13 |  |  |  | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5789 | Definitions of key terms used in the agreement. (Retirement approved by FERC effective January 21, 2014.) | [26 empty] | 2014-11-13 |  |  |  | 91100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5794 | Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the agreement. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 92100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5798 | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 93100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5806 | Provisions for communications between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of terms. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 94100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5812 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5815 | Cover critical system conditions and study years as deemed appropriate by the entity performing the study. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5826 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5827 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5833 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5836 | Be performed and evaluated only for those Category B contingencies that would produce the more severe System results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5851 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5852 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5858 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5861 | Be performed and evaluated only for those Category C contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5876 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5877 | Including a schedule for implementation. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5883 | Be made annually. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5886 | Be performed and evaluated only for those Category D contingencies that would produce the more severe system results or impacts. The rationale for the contingencies selected for evaluation shall be available as supporting information. An explanation of why the remaining simulations would produce less severe system results shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 589 | A requirement to have a database that contains all blackstart generators1 designated for use in an SRP within the respective areas. This database shall be updated on an annual basis. The database shall include the name, location, megawatt capacity, type of unit, latest date of test, and starting method. |  | RRO | [14 empty] | RRO | [7 empty] | 2011-05-23 |  | 2011-05-23 |  |  | EOP-007-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5898 | Description of the process for submitting a proposed RAS for Regional Reliability Organization review. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5917 | Identification of group conducting the assessment and the date the assessment was performed. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 592 | Testing frequency (minimum of one third of the units each year). |  | RRO | [14 empty] | RRO | [9 empty] | 2011-05-23 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5923 | Design Objectives — Contingencies and system conditions for which the RAS was designed, |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5934 | RAS identification shall include but is not limited to: |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-01-25 |  | 2027-03-31 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5935 | Relays. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-04-01 |  | 2027-03-31 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5947 | Owner and operator of the UVLS program. | [26 empty] | 2014-11-13 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5955 | Size and location of customer load, or percent of connected load, to be interrupted. | [26 empty] | 2014-11-13 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5963 | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. |  | GOP | [5 empty] | GOP | [16 empty] | 2016-01-25 |  | 2015-05-28 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5966 | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority. |  | GOP | [5 empty] | GOP | [16 empty] | 2016-01-25 |  | 2015-05-28 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5970 | Each Generator Operator shall notify its Transmission Operator in advance of changes in generation or operating conditions that could require changes in the Transmission Operator’s Protection Systems. |  | GOP | [5 empty] | GOP | [16 empty] | 2016-01-25 |  | 2015-05-28 |  |  |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5975 | If the Protection System or RAS has a Security-Based Misoperation and two or more Functionally Equivalent Protection Systems (FEPS) or Functionally Equivalent RAS (FERAS) remain in service to ensure Bulk Electric System (BES) reliability, the Transmission Owners or Generator Owners shall remove from service the Protection System or RAS that misoperated within 22 hours following identification of the Misoperation. Repair or replacement of the failed Protection System or RAS is at the Transmission Owners’ and Generator Owners’ discretion. |  | GO, TO |  |  |  |  | GO | [16 empty] | M2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation. | 2016-01-25 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf..4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. |  | 21000000 | WECC-US | [5 empty] | WECC-US
1. | 598 | The contingency plan shall not rely on data or voice communication from the primary control facility to be viable. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | EOP-008-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 5986 | System Operators shall review all tripping of transmission elements and RAS operations to identify apparent Misoperations within 24 hours. |  | GO, TO |  |  |  |  | GO | [16 empty] | M1.1 Transmission Owners and Generation Owners shall have evidence that System Operating personnel reviewed all operations of Protection System and RAS within 24 hours. | 2016-01-25 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf..4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. |  | 11000000 | WECC-US | [5 empty] | WECC-US
1. | 5992 | When a FEPS is not available, the Transmission Owners shall remove the associated Element from service. |  | TO | [21 empty] | M2.3.1 The Transmission Owner shall have evidence that it removed the associated Element from service. | 2017-04-01 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf..4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. |  | 23100000 | WECC-US | [5 empty] | WECC-US
1. | 5995 | If the Protection System or RAS has a Dependability-Based Misoperation but has one or more FEPS or FERAS that operated correctly, the associated Element or transmission path may remain in service without removing from service the Protection System or RAS |  | GO, TO |  |  |  |  | GO | [16 empty] | M2.4.1 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days of the misoperation identification. | 2017-04-01 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf..4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. |  | 24100000 | WECC-US | [5 empty] | WECC-US
1. | 5998 | Identification of a Misoperation of a Protection System and/or RAS, | [23 empty] | M3.1 Identification of all Protection System and RAS Misoperations and corrective actions taken or planned. | 2017-04-01 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf..4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. |  | 31000000 | WECC-US | [5 empty] | WECC-US
1. | 6023 | The model utilizes data and assumptions consistent with the time period being studied and that meets the following criteria: |  | TOP | [18 empty] | TOP |  |  | M1.1. Production shall be in the same form and format used by the Transmission Operator to calculate the TTC, as required in R1. (R1) | 2016-01-25 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6024 | Includes at least: |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6025 | The Transmission Operator area. Equivalent representation of radial lines and facilities 161kV or below is allowed. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 11110000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6042 | Except where otherwise specified within MOD-029-2, adjust base case generation and Load levels within the updated power flow model to determine the TTC (maximum flow or reliability limit) that can be simulated on the ATC Path while at the same time satisfying all planning criteria contingencies as follows: |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 609 | Generation facilities, |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  | FAC-001-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 61 | Fixed schedules for Jointly Owned Units mandate that Balancing Authority (A) that contains the Jointly Owned Unit must incorporate the respective share of the unit governor droop response for any Balancing Authorities that have fixed schedules (B and C). See the diagram below. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  | BAL-003-0 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6115 | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-05-29 |  | 2020-09-30 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6118 | Each Generator Operator shall coordinate all new protective systems and all protective system changes with its Transmission Operator and Host Balancing Authority.• Requirement R3.1 is not applicable to the individual generating units of dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-05-29 |  | 2020-09-30 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6122 | Each Generator Operator shall notify its Transmission Operator in advance of changes in generation or operating conditions that could require changes in the Transmission Operator’s Protection Systems. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-05-29 |  | 2020-09-30 |  |  |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 613 | Provide a written summary of its plans to achieve the required system performance as described above throughout the planning horizon: |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  | FAC-001-0 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 614 | Procedures for coordinated joint studies of new facilities and their impacts on the interconnected transmission systems. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6160 | Personnel & training (CIP-004); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6169 | Cyber security awareness; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2016-06-30 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6173 | One or more processes to identify, classify, and respond to Cyber Security Incidents. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.1. An example of evidence may include, but is not limited to, dated documentation of Cyber Security Incident response plan(s) that include the process to identify, classify, and respond to Cyber Security Incidents. | 2014-02-03 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6177 | Test each Cyber Security Incident response plan(s) at least once every 15 calendar months: • By responding to an actual Reportable Cyber Security Incident; • With a paper drill or tabletop exercise of a Reportable Cyber Security Incident; or• With an operational exercise of a Reportable Cyber Security Incident. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.1. Examples of evidence may include, but are not limited to, dated evidence of a lessons-learned report that includes a summary of the test or a compilation of notes, logs, and communication resulting from the test. Types of exercises may include discussion or operations based exercises. | 2017-07-01 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6180 | No later than 90 calendar days after completion of a Cyber Security Incident response plan(s) test or actual Reportable Cyber Security Incident response: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.1. An example of evidence may include, but is not limited to, all of the following:1. Dated documentation of post incident(s) review meeting notes or follow-up report showing lessons learned associated with the Cyber Security Incident response plan(s) test or actual Reportable Cyber Security Incident response or dated documentation stating there were no lessons learned;2. Dated and revised Cyber Security Incident response plan showing any changes based on the lessons learned; and3. Evidence of plan update distribution including, but not limited to:• Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2014-02-03 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6181 | 3.1.1. Document any lessons learned or document the absence of any lessons learned; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | 31100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6185 | Update the Cyber Security Incident response plan(s); and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | 32100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6187 | Where technically feasible, enable only logical network accessible ports that have been determined to be needed by the Responsible Entity, including port ranges or services where needed to handle dynamic ports. If a device has no provision for disabling or restricting logical ports on the device then those ports that are open are deemed needed. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6189 | A patch management process for tracking, evaluating, and installing cyber security patches for applicable Cyber Assets. The tracking portion shall include the identification of a source or sources that the Responsible Entity tracks for the release of cyber security patches for applicable Cyber Assets that are updateable and for which a patching source exists. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6193 | Deploy method(s) to deter, detect, or prevent malicious code. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6196 | Log events at the BES Cyber System level (per BES Cyber System capability) or at the Cyber Asset level (per Cyber Asset capability) for identification of, and after-the-fact investigations of, Cyber Security Incidents that includes, as a minimum, each of the following types of events: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6200 | Have a method(s) to enforce authentication of interactive user access, where technically feasible. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6210 | Detected malicious code from Part 4.1; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 42100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6212 | Password length that is, at least, the lesser of eight characters or the maximum length supported by the Cyber Asset; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 55100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6214 | Method(s) to identify information that meets the definition of BES Cyber System Information. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6216 | Prior to the release for reuse of applicable Cyber Assets that contain BES Cyber System Information (except for reuse within other systems identified in the “Applicable Systems” column), the Responsible Entity shall take action to prevent the unauthorized retrieval of BES Cyber System Information from the Cyber Asset data storage media. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6218 | Develop a baseline configuration, individually or by group, which shall include the following items: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6219 | Operating system(s) (including version) or firmware where no independent operating system exists; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6227 | Prior to the change, determine required cyber security controls in CIP-005 and CIP-007 that could be impacted by the change; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 14100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6231 | Prior to implementing any change in the production environment, test the changes in a test environment or test the changes in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration to ensure that required cyber security controls in CIP-005 and CIP-007 are not adversely affected; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 15100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6233 | Monitor at least once every 35 calendar days for changes to the baseline configuration (as described in Requirement R1, Part 1.1). Document and investigate detected unauthorized changes. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6234 | At least once every 15 calendar months, conduct a paper or active vulnerability assessment. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6236 | Perform an active vulnerability assessment in a test environment, or perform an active vulnerability assessment in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration of the BES Cyber System in a production environment; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 32100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6240 | All applicable Cyber Assets connected to a network via a routable protocol shall reside within a defined ESP. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.1 An example of evidence may include, but is not limited to, a list of all ESPs with all uniquely identifiable applicable Cyber Assets connected via a routable protocol within each ESP. | 2014-02-03 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6245 | Utilize an Intermediate System such that the Cyber Asset initiating Interactive Remote Access does not directly access an applicable Cyber Asset. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.1 Examples of evidence may include, but are not limited to, network diagrams or architecture documents. | 2014-02-03 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6248 | Define operational or procedural controls to restrict physical access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 1.1 An example of evidence may include, but is not limited to, documentation that operational or procedural controls exist. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6257 | Require continuous escorted access of visitors (individuals who are provided access but are not authorized for unescorted physical access) within each Physical Security Perimeter, except during CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 2.1 An example of evidence may include, but is not limited to, language in a visitor control program that requires continuous escorted access of visitors within Physical Security Perimeters and additional evidence to demonstrate that the process was implemented, such as visitor logs. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6260 | Maintenance and testing of each Physical Access Control System and locally mounted hardware or devices at the Physical Security Perimeter at least once every 24 calendar months to ensure they function properly. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 3.1 An example of evidence may include, but is not limited to, a maintenance and testing program that provides for testing each Physical Access Control System and locally mounted hardware or devices associated with each applicable Physical Security Perimeter at least once every 24 calendar months and additional evidence to demonstrate that this testing was done, such as dated maintenance records, or other documentation showing testing and maintenance has been performed on each applicable device or system at least once every 24 calendar months. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6261 | Conditions for activation of the recovery plan(s). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6266 | Test each of the recovery plans referenced in Requirement R1 at least once every 15 calendar months:• By recovering from an actual incident;• With a paper drill or tabletop exercise; or• With an operational exercise. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6269 | No later than 90 calendar days after completion of a recovery plan test or actual recovery: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6270 | Document any lessons learned associated with a recovery plan test or actual recovery or document the absence of any lessons learned; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 31100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6274 | Update the recovery plan; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 32100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6276 | Security awareness that, at least once each calendar quarter, reinforces cyber security practices (which may include associated physical security practices) for the Responsible Entity’s personnel who have authorized electronic or authorized unescorted physical access to BES Cyber Systems. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation that the quarterly reinforcement has been provided. Examples of evidence of reinforcement may include, but are not limited to, dated copies of information used to reinforce security awareness, as well as evidence of distribution, such as: • direct communications (for example, e-mails, memos, computer-based training); or • indirect communications (for example, posters, intranet, or brochures); or• management support and reinforcement (for example, presentations or meetings). | 2014-02-03 |  | 2016-06-30 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6287 | Training content on: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2014-02-03 |  | 2016-06-30 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6298 | Process to confirm identity. | [23 empty] | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to confirm identity. |  |  | 2016-06-30 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6300 | current residence, regardless of duration; and | [23 empty] | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to perform a seven year criminal history records check. |  |  | 2016-06-30 |  |  |  | 32100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6305 | Process to authorize based on need, as determined by the Responsible Entity, except for CIP Exceptional Circumstances: | [23 empty] | An example of evidence may include, but is not limited to, dated documentation of the process to authorize electronic access, unescorted physical access in a Physical Security Perimeter, and access to designated storage locations, whether physical or electronic, for BES Cyber System Information. |  |  | 2016-06-30 |  |  |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6306 | Electronic access; | [23 empty] | An example of evidence may include, but is not limited to, dated documentation of the process to authorize electronic access, unescorted physical access in a Physical Security Perimeter, and access to designated storage locations, whether physical or electronic, for BES Cyber System Information. |  |  | 2016-06-30 |  |  |  | 41100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6312 | A process to initiate removal of an individual’s ability for unescorted physical access and Interactive Remote Access upon a termination action, and complete the removals within 24 hours of the termination action (Removal of the ability for access may be different than deletion, disabling, revocation, or removal of all access rights). | [23 empty] | An example of evidence may include, but is not limited to, documentation of all of the following:1. Dated workflow or sign-off form verifying access removal associated with the termination action; and 2. Logs or other demonstration showing such persons no longer have access. |  |  | 2016-06-30 |  |  |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6317 | Identify each of the high impact BES Cyber Systems according to Attachment 1, Section 1, if any, at each asset; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-12-26 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 632 | Evaluation of the reliability impact of the new facilities and their connections on the interconnected transmission systems. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [14 empty] | 2007-06-18 |  | 2011-09-30 |  |  | FAC-002-0 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6320 | Review the identifications in Requirement R1 and its parts (and update them if there are changes identified) at least once every 15 calendar months, even if it has no identified items in Requirement R1, and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-12-26 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6322 | The documentation shall contain assumptions used to rate the generator and at least one of the following:• Design or construction information such as design criteria, ratings provided by equipment manufacturers, equipment drawings and/or specifications, engineering analyses, method(s) consistent with industry standards (e.g. ANSI and IEEE), or an established engineering practice that has been verified by testing or engineering analysis.• Operational information such as commissioning test results, performance testing or historical performance records, any of which may be supplemented by engineering analyses. |  | GO | [22 empty] | 2011-11-17 |  | 2021-09-30 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6326 | Equipment Rating standard(s) used in development of this methodology. |  | GO | [22 empty] | 2013-01-01 |  | 2021-09-30 |  |  |  | 22100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6332 | The scope of equipment addressed shall include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | GO | [22 empty] | 2013-01-01 |  | 2021-09-30 |  |  |  | 24100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6336 | Equipment Rating standard(s) used in development of this methodology. |  | TO | [22 empty] | 2013-01-01 |  | 2021-09-30 |  |  |  | 32100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6342 | The scope of equipment addressed shall include, but not be limited to, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | TO | [22 empty] | 2013-01-01 |  | 2021-09-30 |  |  |  | 34100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6348 | Identity of the existing next most limiting equipment of the Facility |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-01-01 |  | 2021-09-30 |  |  |  | 82100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6350 | Maintain a list of circuits subject to PRC-023-2 per application of Attachment B, including identification of the first calendar year in which any criterion in Attachment B applies. |  | PCPA | [9 empty] | PA | [12 empty] | 2014-01-01 |  | 2014-09-30 |  |  |  | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6353 | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-04-02 |  | 2017-04-01 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6354 | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-11-19 |  | 2017-04-01 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6358 | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-11-19 |  | 2017-04-01 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6359 | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-04-02 |  | 2017-04-01 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6368 | The performance of a combined cycle facility will be determined using an expected performance droop of 5.78%. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [16 empty] | 2014-01-16 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01.4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. |  | 21000000 | TXRE-US |  |  |  |  | TXRE-US
1. | 6372 | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [19 empty] | 2015-12-31 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6388 | If a Transmission station or Transmission substation previously identified under Requirement R1 and verified according to Requirement R2 is removed from the identification during a subsequent risk assessment performed according to Requirement R1 or a verification according to Requirement R2, then the Transmission Owner shall, within seven calendar days following the verification or the subsequent risk assessment, notify the Transmission Operator that has operational control of the primary control center of the removal. |  | TO | [22 empty] | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.Voltage Value of a Line Weight Value per Lineless than 200 kV (not applicable) (not applicable)200 kV to 299 kV 700300 kV to 499 kV 1300500 kV and above 04.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 639 | The TVMP shall define a schedule for and the type (aerial, ground) of ROW vegetation inspections. This schedule should be flexible enough to adjust for changing conditions. The inspection schedule shall be based on the anticipated growth of vegetation and any other environmental or operational factors that could impact the relationship of vegetation to the Transmission Owner’s transmission lines. |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  | FAC-003-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6390 | Unique characteristics of the identified and verified Transmission station(s), Transmission substation(s), and primary control center(s); |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.Voltage Value of a Line Weight Value per Lineless than 200 kV (not applicable) (not applicable)200 kV to 299 kV 700300 kV to 499 kV 1300500 kV and above 04.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6394 | Resiliency or security measures designed collectively to deter, detect, delay, assess, communicate, and respond to potential physical threats and vulnerabilities identified during the evaluation conducted in Requirement R4. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.Voltage Value of a Line Weight Value per Lineless than 200 kV (not applicable) (not applicable)200 kV to 299 kV 700300 kV to 499 kV 1300500 kV and above 04.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 64 | Balancing Authorities that do not serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of its estimated maximum generation level in the coming year per 0.1 Hz change. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  | BAL-003-0 R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6401 | Each Transmission Owner and Transmission Operator shall select an unaffiliated third party reviewer from the following:• An entity or organization with electric industry physical security experience and whose review staff has at least one member who holds either a Certified Protection Professional (CPP) or Physical Security Professional (PSP) certification.• An entity or organization approved by the ERO.• A governmental agency with physical security expertise.• An entity or organization with demonstrated law enforcement, government, or military physical security expertise. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-02 | [5 empty] | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6406 | The implementation of the UVLS Program resolves the identified undervoltage issues that led to its development and design. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-11-19 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 641 | Clearance 1 — The Transmission Owner shall determine and document appropriate clearance distances to be achieved at the time of transmission vegetation management work based upon local conditions and the expected time frame in which the Transmission Owner plans to return for future vegetation management work. Local conditions may include, but are not limited to: operating voltage, appropriate vegetation management techniques, fire risk, reasonably anticipated tree and conductor movement, species types and growth rates, species failure characteristics, local climate and rainfall patterns, line terrain and elevation, location of the vegetation within the span, and worker approach distance requirements. Clearance 1 distances shall be greater than those defined by Clearance 2 below. |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  |  | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6411 | Whether its UVLS Program resolved the undervoltage issues associated with the event, and |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-11-19 | [5 empty] | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6418 | A list of congestion management actions to be implemented, and |  | RC | [11 empty] | RC | [10 empty] | 2011-04-21 |  | 2016-03-31 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US | MRO-US | NPCC-US | RF-US | SERC-US
1. | 6420 | Notify all Reliability Coordinators in the Eastern Interconnection of the identified TLR level |  | RC | [11 empty] | RC | [10 empty] | 2011-04-21 |  | 2016-03-31 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US | MRO-US | NPCC-US | RF-US | SERC-US
1. | 6423 | Each applicable unit’s model shall be verified by the Generator Owner using one or more models acceptable to the Transmission Planner. Verification for individual units less than 20 MVA (gross nameplate rating) in a generating plant (per Section 4.2.1.2, 4.2.2.2, or 4.2.3.2) may be performed using either individual unit or aggregate unit model(s), or both. Each verification shall include thefollowing: |  | GO | [22 empty] | 2018-07-01 |  |  |  | 4.2. Facilities:For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following:4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).4.2.2 Generation in the Western Interconnection with the following characteristics:4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.3 Generation in the ERCOT Interconnection with the following characteristics:4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.4 For all Interconnections:• A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6424 | Documentation demonstrating the applicable unit’s model response matches the recorded response for a voltage excursion from either a staged test or a measured system disturbance, |  | GO | [22 empty] | 2018-07-01 |  |  |  | 4.2. Facilities:For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following:4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).4.2.2 Generation in the Western Interconnection with the following characteristics:4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.3 Generation in the ERCOT Interconnection with the following characteristics:4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.4 For all Interconnections:• A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 643 | Where transmission system transient overvoltage factors are not known, clearances shall be derived from Table 5, IEEE 516-2003, phase-to-ground distances, with appropriate altitude correction factors applied. |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  |  | 12210000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6430 | The excitation control system or plant volt/var control function model initializes to compute modeling data without error, |  | TP | [19 empty] | TP |  |  | 2014-05-26 |  |  |  | 4.2. Facilities:For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following:4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).4.2.2 Generation in the Western Interconnection with the following characteristics:4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.3 Generation in the ERCOT Interconnection with the following characteristics:4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.4 For all Interconnections:• A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. |  | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6433 | Each applicable unit’s model shall be verified by the Generator Owner using one or more models acceptable to the Transmission Planner. Verification for individual units rated less than 20 MVA (gross nameplate rating) in a generating plant (per Section 4.2.1.2, 4.2.2.2, or 4.2.3.2) may be performed using either individual unit or aggregate unit model(s) or both. Each verification shall include the following: |  | GO | [22 empty] | 2014-07-01 |  |  |  | 4.2. FacilitiesFor the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred to as an “applicable unit” that meet the following:4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics:4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).4.2.2 Generation in the Western Interconnection with the following characteristics:4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.3 Generation in the ERCOT Interconnection with the following characteristics:4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6434 | Documentation comparing the applicable unit’s MW model response to the recorded MW response for either:? A frequency excursion from a system disturbance that meets MOD-027 Attachment 1 Note 1 with the applicable unit on-line,? A speed governor reference change with the applicable unit online, or? A partial load rejection test,Footnote: Differences between the control mode tested and the final simulation model must be identified, particularly when analyzing load rejection data. Most controls change gains or have a set point runback which takes effect when the breaker opens. Load or set point controls will also not be in effect once the breaker opens. Some method of accounting for these differences must be presented if the final model is not validated from on-line data under the normal operating conditions under which the model is expected to apply. |  | GO | [22 empty] | 2014-07-01 |  |  |  | 4.2. FacilitiesFor the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred to as an “applicable unit” that meet the following:4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics:4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).4.2.2 Generation in the Western Interconnection with the following characteristics:4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.3 Generation in the ERCOT Interconnection with the following characteristics:4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6439 | The turbine/governor and load control or active power/frequency control function model initializes to compute modeling data without error, |  | TP | [19 empty] | TP |  |  | 2014-05-26 |  |  |  | 4.2. FacilitiesFor the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred to as an “applicable unit” that meet the following:4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics:4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).4.2.2 Generation in the Western Interconnection with the following characteristics:4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.3 Generation in the ERCOT Interconnection with the following characteristics:4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6442 | Areas of Competency |  | RC | [11 empty] | RC | [9 empty] | M1.1 A list of Real-time operating positions. | 2011-09-15 |  | 2019-06-30 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6443 | Resource and demand balancing |  | RC | [11 empty] | RC | [10 empty] | 2012-10-01 |  | 2019-06-30 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6451 | Areas of Competency |  | TOP | [18 empty] | TOP |  |  |  | 2011-09-15 |  | 2019-06-30 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6452 | Transmission operations |  | TOP | [18 empty] | TOP |  |  |  | 2012-10-01 |  | 2019-06-30 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6458 | Areas of Competency |  | BA | BA | [21 empty] | 2011-09-15 |  | 2019-06-30 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6459 | Resources and demand balancing |  | BA | BA | [21 empty] | 2012-10-01 |  | 2019-06-30 |  |  |  | 31100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6465 | Limit Governor deadbands within those listed in Table 6.1, unless directed otherwise by the BA. (see standard for table) | See Standard for calculations | BA, GO, GOP | BA |  |  |  | GO | GOP | [16 empty] | 2014-01-16 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01.4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. |  | 61000000 | TXRE-US |  |  |  |  | TXRE-US
1. | 6468 | The initial Primary Frequency Response performance shall be the ratio of the Actual Primary Frequency Response to the Expected Primary Frequency Response during the initial measurement period following the FME. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [16 empty] | 2014-01-16 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01.4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. |  | 91000000 | TXRE-US |  |  |  |  | TXRE-US
1. | 6472 | The sustained Primary Frequency Response performance shall be the ratio of the Actual Primary Frequency Response to the Expected Primary Frequency Response during the sustained measurement period followingthe FME. |  | GO | [22 empty] | 2014-01-16 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01.4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. |  | 101000000 | TXRE-US |  |  |  |  | TXRE-US
1. | 6475 | The greater of either: • The amount of Contingency Reserve equal to the loss of the most severe single contingency; • The amount of Contingency Reserve equal to the sum of three percent of hourly integrated Load plus three percent of hourly integrated generation. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | 1.1 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates its Contingency Reserve was maintained in accordance with the amounts identified in Requirement R1, Part 1.1, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. Attachment A is a practical illustration showing how the generation amount may be calculated under Requirement R1.• Where Dynamic Schedules are used as part of the generation amount upon which Contingency Reserve is predicated, additional evidence of compliance with Requirement R1, Part 1.1 may include, but is not limited to, documentation showing a reciprocal acknowledgement as to which entity is carrying the reserves. This transfer may be all or some portion of the physical generator and is not limited to the entire physical capability of the generator. • Where Pseudo-Ties are used as part of the generation amount upon which Contingency Reserve is predicated, additional evidence of compliance with Requirement R1, Part 1.1, may include, but is not limited to, documentation accounting for the transfers included in the Pseudo-Ties. | 2014-01-28 |  | 2017-01-23 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity.4.2.1. The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group.4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | 11000000 | WECC-US | [5 empty] | WECC-US
1. | 6479 | Reserve that is immediately and automatically responsive to frequency deviations through the action of a governor or other control system; |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2014-01-28 |  | 2017-01-23 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity.4.2.1. The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group.4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | 21000000 | WECC-US | [5 empty] | WECC-US
1. | 6481 | Less than zero at all times, and |  | BA, FRSG | BA |  |  | FRSG | [12 empty] | RSG | [5 empty] | 2014-03-24 |  | 2015-11-12 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6483 | For load-serving Balancing Authorities, 150% of the previous calendar year’s integrated hourly Peak Demand, |  | BA | BA | [21 empty] | 2013-10-16 |  | 2018-09-30 |  |  |  | 11000000 | WECC-US | [5 empty] | WECC-US
1. | 6485 | PIIhourly, |  | BA | BA | [21 empty] | 2013-10-16 |  | 2018-09-30 |  |  |  | 41000000 | WECC-US | [5 empty] | WECC-US
1. | 6488 | The location and method of implementation for providing backup functionality for the time it takes to restore the primary control center functionality. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6490 | Tools and applications to ensure that System Operators have situational awareness of the BES. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2013-07-01 |  | 2019-03-31 |  |  |  | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6499 | A list of all entities to notify when there is a change in operating locations. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2013-07-01 |  | 2019-03-31 |  |  |  | 16100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 650 | Multiple sustained outages on an individual line, if caused by the same vegetation, shall be reported as one outage regardless of the actual number of outages within a 24-hour period. |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  | FAC-003-1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6502 | An update and approval of the Operating Plan for backup functionality shall take place within sixty calendar days of any changes to any part of the Operating Plan described in Requirement R1. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6503 | The transition time between the simulated loss of primary control center functionality and the time to fully implement the backup functionality. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  |  | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6505 | A description of activities designed to mitigate the effects of GMD events on the reliable operation of the interconnected transmission system within the Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2015-04-01 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6507 | Steps or tasks to receive space weather information. |  | TOP | [18 empty] | TOP |  |  |  | 2015-04-01 | [5 empty] | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6513 | Within its Transmission Operator Area, monitor Facilities and the status of Special Protection Systems, and |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-26 |  | 2018-06-30 |  |  |  | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6525 | Inform its Planning Coordinator of the need to exceed the stated tolerances or the number of stages as shown in UFLS Attachment C, Table 1 if applicable and |  | DP, DP-UFLS, TO |  | DP | [20 empty] | 2016-01-01 |  | 2020-03-31 |  |  |  | 51000000 | NPCC-US |  | NPCC-US
1. | 6529 | Eastern Interconnection – 100 ms |  | DP, DP-UFLS, TO |  | DP | [20 empty] | 2016-01-01 |  | 2020-03-31 |  |  |  | 71000000 | NPCC-US |  | NPCC-US
1. | 6530 | Design measures to prevent the generating unit from tripping directly or indirectly for underfrequency conditions above the appropriate generator tripping threshold curve in Figure 1. |  | DP-UFLS, GO |  | DP | [20 empty] | 2013-04-29 |  | 2020-03-31 |  |  |  | 151000000 | NPCC-US |  | NPCC-US
1. | 6531 | Set the underfrequency protection to operate at the lowest frequency allowed by the plant design and licensing limitations. |  | DP-UFLS, GO |  | DP | [20 empty] | 2013-04-29 |  | 2020-03-31 |  |  |  | 161000000 | NPCC-US |  | NPCC-US
1. | 6534 | Set the underfrequency protection to operate at as low a frequency as possible in accordance with the plant design and licensing limitations but not greater than 57.8Hz. |  | DP-UFLS, GO |  | DP | [20 empty] | 2013-04-29 |  | 2020-03-31 |  |  |  | 191000000 | NPCC-US |  | NPCC-US
1. | 6537 | For each UFLS relay, including those used for compensatory load shedding, the amount and location of load shed at peak, the corresponding frequency threshold and time delay settings. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2013-04-29 |  | 2020-03-31 |  |  |  | 201000000 | NPCC-US |  | NPCC-US
1. | 654 | Category 1 — Grow-ins: Outages caused by vegetation growing into lines from vegetation inside and/or outside of the ROW; |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  |  | 34100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6544 | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2014-02-24 |  | 2015-05-28 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6546 | Those islands selected by applying the criteria in Requirement R1, and |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6549 | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-1 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6552 | Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES |  | PCPA | [9 empty] | PA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  |  | 33100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6555 | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6562 | UFLS program, including a schedule for implementation |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6565 | Movement of applicable line conductors under their Rating and all Rated Electrical Operating Conditions; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-11-25 |  | 2016-09-30 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6567 | Criteria for the selection of the transfers to be assessed. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-01-23 |  | 2020-12-14 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6572 | Distribute to the following prior to the effectiveness of such revisions: |  | PCPA | [9 empty] | PA | [12 empty] | 2012-01-23 |  | 2020-12-14 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6577 | Individual generating unit greater than 50 MVA (gross nameplate rating) directly connected to the BES |  | PCPA | [9 empty] | PA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  |  | 331000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6583 | Those islands selected by applying the criteria in Requirement E.B.1, and |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 210000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6585 | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-1 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 310000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6588 | Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES |  | PCPA | [9 empty] | PA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  |  | 331000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6591 | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 410000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6598 | The performance of the UFLS equipment, E.B. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 2010000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6600 | A Planning Coordinator may adjust island boundaries to differ from subregional boundaries where necessary for the sole purpose of producing a contiguous subregional island more suitable for simulation. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2013-02-25 |  | 2017-12-31 |  |  |  | 11000000 | SERC-US |  |  |  | SERC-US
1. | 6601 | Have the capability of shedding at least 30 percent of the Peak Demand (MW) served from the Planning Coordinator’s transmission system. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2013-02-25 |  | 2017-12-31 |  |  |  | 21000000 | SERC-US |  |  |  | SERC-US
1. | 6605 | This does not apply to UFLS relays with time delay of one second or longer and a higher frequency setpoint applied to prevent the frequency from stalling at less than 60 Hz when recovering from an underfrequency event. |  | PCPA | [9 empty] | PA | [12 empty] | 2014-04-01 |  | 2017-12-31 |  |  |  | 23100000 | SERC-US |  |  |  | SERC-US
1. | 6609 | The percent of load shedding to be implemented shall be based on the actual or estimated distribution substation or feeder demand (including losses) of the UFLS entities at the time coincident with the previous year actual Peak Demand. |  | DP, DP-UFLS, TO |  | DP | [20 empty] | 2015-10-01 |  | 2017-12-31 |  |  |  | 41000000 | SERC-US |  |  |  | SERC-US
1. | 6612 | The percent of load shedding to be implemented shall be based on the actual or estimated distribution substation or feeder demand (including losses) of the UFLS entities at the time coincident with the previous year actual Peak Demand. |  | DP, DP-UFLS, TO |  | DP | [20 empty] | 2015-10-01 |  | 2017-12-31 |  |  |  | 51000000 | SERC-US |  |  |  | SERC-US
1. | 6614 | Underfrequency trip set points (Hz) |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2013-02-25 |  | 2017-12-31 |  |  |  | 71000000 | SERC-US |  |  |  | SERC-US
1. | 6617 | Maintain a list of circuits subject to PRC-023-3 per application of Attachment B, including identification of the first calendar year in which any criterion in PRC-023-3, Attachment B applies. |  | PCPA | [9 empty] | PA | [12 empty] | 2014-09-22 |  | 2017-03-31 |  |  |  | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6619 | Generator protection automatic underfrequency and overfrequency trip set points (Hz). |  | DP-UFLS, GO |  | DP | [20 empty] | 2013-02-25 |  | 2017-12-31 |  |  |  | 81000000 | SERC-US |  |  |  | SERC-US
1. | 6622 | System models shall represent: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-12-23 |  | 2023-06-30 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6623 | Existing Facilities |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-01-01 | [5 empty] | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6629 | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by current annual studies or qualified past studies as indicated in Requirement R2, Part 2.6. Qualifying studies need to include the following conditions: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6630 | System peak Load for either Year One or year two, and for year five. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6636 | A current study assessing expected System peak Load conditions for one of the years in the Long-Term Transmission Planning Horizon and the rationale for why that year was selected. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 22100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6639 | When a generator’s AVR is out of service or the generator does not have an AVR, the Generator Operator shall use an alternative method to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2014-08-01 |  | 2015-05-28 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6642 | For generator step-up transformers and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: |  | GO | [22 empty] | 2014-08-01 |  | 2015-05-28 |  |  |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6643 | Tap settings. |  | GO | [22 empty] | 2014-10-01 |  | 2015-05-28 |  |  |  | 51100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6646 | If the Generator Owner cannot comply with the Transmission Operator’s specifications, the Generator Owner shall notify the Transmission Operator and shall provide the technical justification. |  | GO | [22 empty] | 2014-08-01 |  | 2015-05-28 |  |  |  | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6647 | Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. |  | TOP | [18 empty] | TOP |  |  |  | 2014-08-01 |  | 2015-11-12 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6648 | System peak Load for one of the five years. System peak Load levels shall include a Load model which represents the expected dynamic behavior of Loads that could impact the study area, considering the behavior of induction motor Loads. An aggregate System Load model which represents the overall dynamic behavior of the Load is acceptable. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 24100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6653 | For steady state, short circuit, or Stability analysis: the study shall be five calendar years old or less, unless a technical rationale can be provided to demonstrate that the results of an older study are still valid. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 26100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6656 | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Special Protection Systems • Installation or modification of automatic generation tripping as a response to a single or multiple Contingency to mitigate Stability performance violations. • Installation or modification of manual and automatic generation runback/tripping as a response to a single or multiple Contingency to mitigate steady state performance violations. • Use of Operating Procedures specifying how long they will be needed as part of the Corrective Action Plan. • Use of rate applications, DSM, new technologies, or other initiatives. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 27100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6661 | List System deficiencies and the associated actions needed to achieve required System performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 28100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6663 | Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R3, Part 3.4. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6666 | Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 33100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6668 | Tripping of generators where simulations show generator bus voltages or high side of the generation step up (GSU) voltages are less than known or assumed minimum generator steady state or ride through voltage limitations. Include in the assessment any assumptions made. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 33110000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6671 | The Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 34100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6673 | Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R4, Part 4.4. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6674 | For planning event P1: No generating unit shall pull out of synchronism. A generator being disconnected from the System by fault clearing action or by a Special Protection System is not considered pulling out of synchronism. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 41100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6679 | Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 43100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6680 | Successful high speed (less than one second) reclosing and unsuccessful high speed reclosing into a Fault where high speed reclosing is utilized. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 43110000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6685 | Each Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 44100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6688 | If a recipient of the Planning Assessment results provides documented comments on the results, the respective Planning Coordinator or Transmission Planner shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6691 | Generation dispatch, including but not limited to long term planned outages, additions and retirements. |  | PCPA | [9 empty] | PA | [12 empty] | 2013-04-01 |  | 2020-12-14 |  |  |  | 14100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6698 | Each Planning Coordinator adjacent to the Planning Coordinator’s Planning Coordinator area or overlapping the Planning Coordinator’s area. |  | PCPA | [9 empty] | PA | [12 empty] | 2013-04-01 |  | 2020-12-14 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 67 | The Balancing Authority may change its Frequency Bias Setting, and the method used to determine the setting, whenever any of the factors used to determine the current bias value change. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2015-03-31 |  |  | BAL-003-0.1b R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6700 | For Confirmed Interchange greater than 250 MW for the last hour, the actual hourly integrated energy deviates from the Confirmed Interchange by more than 10% for that hour and that deviation is expected to persist. |  | PSE | [10 empty] | PSE | [11 empty] | 2014-11-26 |  | 2020-12-14 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6703 | Each Source and Sink Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if it does not expect to be capable of supporting the magnitude of the Interchange, including ramping, throughout the duration of the Arranged Interchange. |  | BA | BA | [21 empty] | 2014-06-30 |  | 2021-03-31 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6705 | Each Transmission Service Provider shall deny the Arranged Interchange or curtail Confirmed Interchange if the transmission path (proper connectivity of adjacent Transmission Service Providers) between it and its adjacent Transmission Service Providers is invalid. |  | TSP | [20 empty] | TSP |  | 2014-06-30 |  | 2021-03-31 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6706 | If a Balancing Authority denies a Reliability Adjustment Arranged Interchange, the Balancing Authority must communicate that fact to its Reliability Coordinator no more than 10 minutes after the denial. |  | BA | BA | [21 empty] | 2014-06-30 |  | 2021-03-31 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6707 | The Source Balancing Authority, |  | BA | BA | [21 empty] | 2014-06-30 |  | 2021-03-31 |  |  |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6712 | Identical in magnitude to that of the Adjacent Balancing Authority, and |  | BA | BA | [21 empty] | 2014-11-26 |  | 2021-03-31 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6714 | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6716 | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6718 | Its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6724 | Its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6728 | Its Reliability Coordinator. |  | BA | BA | [21 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6733 | Its Reliability Coordinator. |  | BA | BA | [21 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6736 | Its Balancing Authority. |  | DP |  | DP | [20 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6738 | Its Balancing Authority. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6740 | Subsequent risk assessments shall be performed: • At least once every 30 calendar months for a Transmission Owner that has identified in its previous risk assessment (as verified according to Requirement R2) one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection; or • At least once every 60 calendar months for a Transmission Owner that has not identified in its previous risk assessment (as verified according to Requirement R2) any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in widespread instability, uncontrolled separation, or Cascading within an Interconnection. |  | TO | [22 empty] | 2015-10-01 |  | 2015-10-01 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6742 | Each Transmission Owner shall select an unaffiliated verifying entity that is either:• A registered Planning Coordinator, Transmission Planner, or Reliability Coordinator; or• An entity that has transmission planning or analysis experience. |  | TO | [22 empty] | 2015-10-01 |  | 2015-10-01 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6746 | If a Transmission station or Transmission substation previously identified under Requirement R1 and verified according to Requirement R2 is removed from the identification during a subsequent risk assessment performed according to Requirement R1 or a verification according to Requirement R2, then the Transmission Owner shall, within seven calendar days following the verification or the subsequent risk assessment, notify the Transmission Operator that has operational control of the primary control center of the removal. |  | TO | [22 empty] | 2015-10-01 |  | 2015-10-01 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6747 | Unique characteristics of the identified and verified Transmission station(s), Transmission substation(s), and primary control center(s); |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6750 | Resiliency or security measures designed collectively to deter, detect, delay, assess, communicate, and respond to potential physical threats and vulnerabilities identified during the evaluation conducted in Requirement R4. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6754 | Each Transmission Owner and Transmission Operator shall select an unaffiliated third party reviewer from the following:• An entity or organization with electric industry physical security experience and whose review staff has at least one member who holds either a Certified Protection Professional (CPP) or Physical Security Professional (PSP) certification.• An entity or organization approved by the ERO.• A governmental agency with physical security expertise.• An entity or organization with demonstrated law enforcement, government, or military physical security expertise. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  |  | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6758 | generation Facilities; |  | TO | [21 empty] | M1. Each Transmission Owner shall have evidence (such as dated, documented Facility interconnection requirements) that it met all requirements in Requirement R1. | 2014-11-06 |  | 2018-12-31 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6761 | Procedures for coordinated studies of new or materially modified existing interconnections and their impacts on affected system(s). |  | TO | [22 empty] | 2014-11-06 |  | 2018-12-31 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6763 | Procedures for coordinated studies of new interconnections and their impacts on affected system(s). |  | GO | [22 empty] | 2014-11-06 |  | 2018-12-31 |  |  |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6765 | The reliability impact of the new interconnection, or materially modified existing interconnection, on affected system(s); |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2014-11-06 |  | 2021-03-31 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6769 | Verify the Real Power capability of its generating units in accordance with Attachment 1. |  | GO | [22 empty] | 2014-05-27 |  |  |  | For the purpose of this standard, the term, “applicable Facility” shall mean any one of the following:4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.4.2.2 Synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.4.2.3 Generating plant/Facility greater than 75 MVA (gross aggregate nameplate rating) directly connected to the Bulk Electric System. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6771 | Verify, in accordance with Attachment 1, (i) the Reactive Power capability of its generating units and (ii) the Reactive Power capability of its synchronous condenser units. |  | GO | [22 empty] | 2014-05-27 |  |  |  | For the purpose of this standard, the term, “applicable Facility” shall mean any one of the following:4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.4.2.2 Synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.4.2.3 Generating plant/Facility greater than 75 MVA (gross aggregate nameplate rating) directly connected to the Bulk Electric System. |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6773 | Verify, in accordance with Attachment 1, the Reactive Power capability of its synchronous condenser units. |  | TO | [22 empty] | 2014-05-27 |  |  |  | For the purpose of this standard, the term, “applicable Facility” shall mean any one of the following:4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.4.2.2 Synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.4.2.3 Generating plant/Facility greater than 75 MVA (gross aggregate nameplate rating) directly connected to the Bulk Electric System. |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6775 | A list of Transmission Planners, Balancing Authorities, Load Serving Entities, and Distribution Providers that are required to provide the data (“Applicable Entities”). |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2015-04-27 |  | 2016-09-30 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6778 | Integrated hourly Demands in megawatts for the prior calendar year. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6780 | If the annual peak hour actual Demand varies due to weather-related conditions (e.g., temperature, humidity or wind speed), the Applicable Entity shall also provide the weather normalized annual peak hour actual Demand for the prior calendar year. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 13210000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6784 | Monthly peak hour forecast Total Internal Demands in megawatts for the next two calendar years. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 14100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6790 | The assumptions and methods used in the development of aggregated Peak Demand and Net Energy for Load forecasts. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 15100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6795 | If the Applicable Entity does not provide data requested under this requirement because (1) the requesting entity did not demonstrate a reliability need for the data; or (2) providing the data would conflict with the Applicable Entity’s confidentiality, regulatory, or security requirements, the Applicable Entity shall, within 30 calendar days of the written request, provide a written response to the requesting entity specifying the data that is not being provided and on what basis. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2015-04-27 |  | 2016-09-30 |  |  |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6796 | The data listed in Attachment 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-07-01 |  |  |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6798 | Data format; |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-07-01 |  |  |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. |  | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6803 | Provide either updated data or an explanation with a technical basis for maintaining the current data; |  | BA, GO, LSE, RP, TO, TSP | BA |  |  |  | GO |  |  | LSE | [5 empty] | RP |  |  |  | TO |  |  | TSP |  | 2015-07-01 |  |  |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6805 | Comparison of the performance of the Planning Coordinator’s portion of the existing system in a planning power flow model to actual system behavior, represented by a state estimator case or other Real-time data sources, at least once every 24 calendar months through simulation; |  | PCPA | [9 empty] | PA | [12 empty] | 2014-05-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6809 | Criteria and processes for notifications. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-26 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6814 | Review and update annually with no more than 15 months between reviews. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-26 | [5 empty] | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6817 | Identify applicable roles and reporting responsibilities including: |  | RC | [11 empty] | RC | [10 empty] | 2016-01-26 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6818 | Development and communication of outage schedules. |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6823 | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses and Real-time monitoring. |  | TOP | [18 empty] | TOP | [5 empty] | 2016-01-26 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6827 | A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. |  | BA | BA | [23 empty] | 2016-01-26 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6831 | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data as deemed necessary by the Transmission Operator. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-26 |  | 2021-03-31 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6835 | A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. |  | BA | BA | [21 empty] | 2016-01-26 |  | 2021-03-31 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6839 | A mutually agreeable format |  | BA, DP, GO, GOP, LSE, TO, TOP | BA | DP |  |  | GO | GOP |  | LSE | [9 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2021-03-31 |  |  |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6842 | When a generator’s AVR is out of service or the generator does not have an AVR, the Generator Operator shall use an alternative method to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-05-29 |  | 2017-09-25 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6845 | For generator step-up and auxiliary transformers5 with primary voltages equal to or greater than the generator terminal voltage: |  | GO | [22 empty] | 2015-05-29 |  | 2017-09-25 |  |  |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6846 | Tap settings. |  | GO | [22 empty] | 2015-05-29 |  | 2017-09-25 |  |  |  | 51100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6849 | If the Generator Owner cannot comply with the Transmission Operator’s specifications, the Generator Owner shall notify the Transmission Operator and shall provide the technical justification. |  | GO | [22 empty] | 2015-05-29 |  | 2017-09-25 |  |  |  | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6850 | Roles and responsibilities for activating the Operating Plan(s); |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6852 | Notification to its Reliability Coordinator, to include current and projected conditions, when experiencing an operating Emergency; |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6858 | Roles and responsibilities for activating the Operating Plan(s); |  | BA | BA | [21 empty] | 2016-01-25 | [5 empty] | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 686 | A statement that a Facility Rating shall equal the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2012-12-31 |  |  | FAC-008-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6860 | Notification to its Reliability Coordinator, to include current and projected conditions when experiencing a Capacity Emergency or Energy Emergency; |  | BA | BA | [21 empty] | 2017-04-01 | [5 empty] | 22100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6863 | capability and availability; |  | BA | BA | [21 empty] | 2017-04-01 | [5 empty] | 22310000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6873 | Within 30 calendar days of receipt, the Reliability Coordinator shall: |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6874 | Review each submitted Operating Plan(s) on the basis of compatibility and inter-dependency with other Balancing Authorities’ and Transmission Operators’ Operating Plans; |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 31100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6877 | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System and Automatic Reclosing Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2015-12-31 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6879 | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System and Automatic Reclosing Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-01-25 |  | 2015-12-31 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 688 | The scope of equipment addressed shall include, but not be limited to, generators, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2012-12-31 |  |  |  | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6881 | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [19 empty] | 2015-12-31 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6883 | The implementation of the UVLS Program resolves the identified undervoltage issues that led to its development and design. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2017-04-01 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6885 | The UVLS Program resolves the identified undervoltage issues for which the UVLS Program is designed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2017-04-01 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6887 | Maintain a list of circuits subject to PRC-023-4 per application of Attachment B, including identification of the first calendar year in which any criterion in PRC-023-4, Attachment B applies. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 |  |  |  | 4.2. Circuits:4.2.1 Circuits Subject to Requirements R1 – R5:4.2.1.1 Transmission lines operated at 200 kV and above, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads.4.2.1.2 Transmission lines operated at 100 kV to 200 kV selected by the Planning Coordinator in accordance with Requirement R6.4.2.1.3 Transmission lines operated below 100 kV that are part of the BES and selected by the Planning Coordinator in accordance with Requirement R6.4.2.1.4 Transformers with low voltage terminals connected at 200 kV and above.4.2.1.5 Transformers with low voltage terminals connected at 100 kV to 200 kV selected by the Planning Coordinator in accordance with Requirement R6.4.2.1.6 Transformers with low voltage terminals connected below 100 kV that are part of the BES and selected by the Planning Coordinator in accordance with Requirement R6.4.2.2 Circuits Subject to Requirement R6:4.2.2.1 Transmission lines operated at 100 kV to 200 kV and transformers with low voltage terminals connected at 100 kV to 200 kV, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads.4.2.2.2 Transmission lines operated below 100 kV and transformers with low voltage terminals connected below 100 kV that are part of the BES, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads. |  | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6889 | Within 12 full calendar months of notification of a BES Element pursuant to Requirement R1, determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-1 – Attachment B where an evaluation of that Element’s load-responsive protective relay(s) based on PRC-026-1 – Attachment B criteria has not been performed in the last five calendar years. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2020-01-01 | [5 empty] | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6891 | Incorporate the NPIRs into their operating analyses of the electric system. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2014-11-04 |  | 2021-03-31 |  |  |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6898 | Retired. [Note: Part 9.1 was retired under the Paragraph 81 project. The NUC SDT proposes to leave this Part blank to avoid renumbering Requirement parts that would impact existing agreements throughout the industry.] |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2014-11-04 |  | 2021-03-31 |  |  |  | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6900 | Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the Agreement. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 92100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6904 | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 93100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 691 | Ratings provided by equipment manufacturers. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2012-12-31 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6912 | Conditions for activation of the recovery plan(s). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.1. An example of evidence may include, but is not limited to, one or more plans that include language identifying conditions for activation of the recovery plan(s). | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6913 | Provisions for communications affecting the NPIRs between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of applicable unique terms |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 94100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6922 | Test each of the recovery plans referenced in Requirement R1 at least once every 15 calendar months:• By recovering from an actual incident;• With a paper drill or tabletop exercise; or• With an operational exercise. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.1. An example of evidence may include, but is not limited to, dated evidence of a test (by recovering from an actual incident, with a paper drill or tabletop exercise, or with an operational exercise) of the recovery plan at least once every 15 calendar months. For the paper drill or full operational exercise, evidence may include meeting notices, minutes, or other records of exercise findings. | 2017-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6925 | No later than 90 calendar days after completion of a recovery plan test or actual recovery: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.1. An example of evidence may include, but is not limited to, all of the following:1. Dated documentation of identified deficiencies or lessons learned for each recovery plan test or actual incident recovery or dated documentation stating there were no lessons learned;2. Dated and revised recovery plan showing any changes based on the lessons learned; and3. Evidence of plan update distribution including, but not limited to:• Emails;• USPS or other mail service;• Electronic distribution system; or • Training sign-in sheets. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6927 | Document any lessons learned associated with a recovery plan test or actual recovery or document the absence of any lessons learned; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 31100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6930 | Update the recovery plan; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 32100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6932 | Those islands selected by applying the criteria in Requirement R1, and |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6935 | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-2 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, an |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6938 | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6945 | The performance of the UFLS equipment, |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6949 | UFLS program, including a schedule for implementation |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6953 | For UFLS design assessments performed under Requirement R4 or R5, the Corrective Action Plan shall be developed within the five-year time frame identified in Requirement R4. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 151000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6955 | Assuming the normal automatic voltage regulator control loop and steady-state system operating conditions, verify the following coordination items for each applicable Facility: |  | GO, TO |  |  |  |  | GO | [17 empty] | 2014-05-27 |  | 2016-06-30 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6956 | The in-service limiters are set to operate before the Protection System of the applicable Facility in order to avoid disconnecting the generator unnecessarily. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-07-01 |  | 2016-06-30 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6958 | The Generator Owner shall communicate the documented regulatory or equipment limitation, or the removal of a previously documented regulatory or equipment limitation, to its Planning Coordinator and Transmission Planner within 30 calendar days of any of the following:• Identification of a regulatory or equipment limitation.• Repair of the equipment causing the limitation that removes the limitation. • Replacement of the equipment causing the limitation with equipment that removes the limitation.• Creation or adjustment of an equipment limitation caused by consumption of the cumulative turbine life-time frequency excursion allowance. |  | GO | [22 empty] | 2014-05-27 |  | 2016-06-30 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6959 | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall create a list of Bulk Electric System (BES) company-specific Real-time reliability-related tasks based on a defined and documented methodology. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Reliability Coordinator, Balancing Authority, and Transmission Operatorshall have available for inspection its methodology and its BES companyspecific Real-time reliability-related task list, with the date of the last review,as specified in Requirement R1 part 1.1 and part 1.1.1. | 2014-06-19 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6960 | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall review, and update if necessary, its list of BES companyspecific Real-time reliability-related tasks identified in part 1.1 each calendar year. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2016-07-01 | [5 empty] | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6964 | Each Transmission Owner shall create a list of BES company-specific Real-time reliability-related tasks based on a defined and documented methodology. |  | TO | [21 empty] | M2.1 Each Transmission Owner shall have available for inspection its methodology and its BES company-specific Real-time reliability-related task list, with the date of the last review, as specified in Requirement R2 part 2.1. | 2014-06-19 | [5 empty] | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6965 | Each Transmission Owner shall review, and update if necessary, its list of BES company-specific Real-time reliability-related tasks identified in part 2.1 each calendar year. |  | TO | [22 empty] | 2016-07-01 | [5 empty] | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6969 | Within six months of a modification or addition of a BES company-specific Realtime reliability-related task, each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner shall verify the capabilities of each of its personnel identified in Requirement R1 or Requirement R2 to perform the new or modified BES company-specific Real-time reliability-related tasks identified in Requirement R1 part 1.1 or Requirement R2 part 2.1. |  | BA, RC, TO, TOP | BA | [10 empty] | RC | [5 empty] | TO | TOP |  |  | M3.1 Each Reliability Coordinator, Balancing Authority, Transmission Operator, or Transmission Owner shall present evidence that it verified the capabilities of applicable personnel to perform new or modified BES company-specific Real-time reliability-related tasks within 6 months of a modification or addition of a BES company-specific Real-time reliability-related task. | 2014-06-19 | [5 empty] | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6970 | A Reliability Coordinator, Balancing Authority, Transmission Operator, or Transmission Owner that did not previously meet the criteria of Requirement R4, shall comply with Requirement R4 within 12 months of meeting the criteria. |  | BA, RC, TO, TOP | BA | [10 empty] | RC | [5 empty] | TO | TOP |  |  | M4.1 Each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner shall have available for inspection training records that provide evidence that personnel identified in Requirement R1 or Requirement R2 completed training that included the use of simulation technology, as specified in Requirement R4, within 12 months of meeting the criteria of Requirement R4. | 2014-06-19 | [5 empty] | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6971 | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct an evaluation each calendar year of the training established in Requirement R5 to identify and implement changes to the training. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | M5.1 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection evidence (such as instructor observations, trainee feedback, supervisor feedback, course evaluations, learning assessments, or internal audit results) that it performed an evaluation each calendar year, as specified in Requirement R5 part 5.1. | 2014-06-19 | [5 empty] | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6972 | Each Generator Operator shall conduct an evaluation each calendar year of the training established in Requirement R6 to identify and implement changes to the training. |  | GOP | [5 empty] | GOP | [15 empty] | M6.1 Each Generator Operator shall have available for inspection evidence (such as instructor observations, trainee feedback, supervisor feedback, course evaluations, learning assessments, or internal audit results) that it performed an evaluation each calendar year, as specified in Requirement R6 part 6.1. | 2014-06-19 | [5 empty] | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6973 | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System and Automatic Reclosing Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [19 empty] | 2015-12-31 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 6975 | For its high impact and medium impact BES Cyber Systems, if any: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 70 | The Balancing Authority may use a fixed Frequency Bias value which is based on a fixed, straight-line function of Tie Line deviation versus Frequency Deviation. The Balancing Authority shall determine the fixed value by observing and averaging the Frequency Response for several Disturbances during on-peak hours. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2015-03-31 |  |  | BAL-003-0.1b R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 701 | Be applicable for developing SOLs used in the planning horizon. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-010-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7043 | Cyber security awareness; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7047 | A list of data and information needed by the Reliability Coordinator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data, as deemed necessary by the Reliability Coordinator. |  | RC | [11 empty] | RC | [10 empty] | 2017-01-01 |  | 2021-03-31 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 705 | In the pre-contingency state and with all Facilities in service, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect expected system conditions and shall reflect changes to system topology such as Facility outages. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-05-29 |  | 2009-04-28 |  |  | FAC-010-1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7051 | A mutually agreeable format |  | BA, DP, GO, GOP, LSE, RC, TO, TOP | BA | DP |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2021-03-31 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7054 | Communications and notifications, including the mutually agreed to conditions under which one Reliability Coordinator notifies other Reliability Coordinators; the process to follow in making those notifications; and the data and information to be exchanged with other Reliability Coordinators. |  | RC | [11 empty] | RC | [12 empty] | 2016-01-26 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7061 | Review and update annually with no more that 15 months between reviews. |  | RC | [11 empty] | RC | [9 empty] | 2.1 Reviewed and updated annually with no more than 15 months between reviews. |  |  | 2016-01-26 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7064 | Each methodology shall describe the method used to account for the following limitations in both the pre- and post-contingency state: |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7065 | Facility ratings; |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 707 | Single line to ground or three-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-07-01 |  | 2009-04-28 |  |  |  | 22100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7071 | The simulation of transfers performed through the adjustment of generation, Load, or both; |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7079 | Each Transmission Operator that uses the Flowgate Methodology shall include in its methodology an impact test process for including requested constraints. If a generator to Load transfer in a registered entity’s area or a transfer to a neighboring registered entity impacts the requested constraint by five percent or greater, the requested constraint shall be included in the TFC determination, otherwise the requested constraint is not required to be included. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7082 | Each methodology shall describe the method used to account for the following elements, provided such elements impact the determination of AFC or ATC: |  | TSP | [20 empty] | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7083 | The simulation of transfers performed through the adjustment of generation, Load, or both; |  | TSP | [20 empty] | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7091 | A written response to any request for clarification of its TFC or TTC methodology, ATCID, CBMID, or TRMID. If the request for clarification is contrary to the Transmission Operator’s or Transmission Service Provider’s confidentiality, regulatory, or security requirements then a written response shall be provided explaining the clarifications not provided, on what basis and whether there are any options for resolving any of the confidentiality, regulatory, or security concerns. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7093 | TRMID; and |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 52100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7096 | ATCID; and |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 53100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7098 | In responding to a written request for data on an ongoing basis, the Transmission Service Provider or Transmission Operator shall make available its data on an ongoing basis no later than 45 calendar days from receipt of the written request. Unless otherwise agreed upon, the Transmission Operator or Transmission Service Provider is not required to: |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7101 | Alter the format in which it maintains or uses the data; or |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 61100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7103 | Expected generation resource commitment and dispatch |  | BA | BA | [21 empty] | 2016-01-26 | [5 empty] | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 711 | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-07-01 |  | 2009-04-28 |  |  |  | 23100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7111 | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities:4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7112 | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities:4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 41100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7116 | If a recipient of the GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities:4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 43100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7117 | The maximum effective GIC value for the worst case geoelectric field orientation for the benchmark GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2019-01-01 |  | 2019-06-30 |  | 4.2. Facilities:4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7129 | Be based on the effective GIC flow information provided in Requirement R5; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2021-01-01 |  | 2019-06-30 |  | 4.2. Facilities:4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7133 | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Special Protection Systems. • Use of Operating Procedures, specifying how long they will be needed as part of the Corrective Action Plan. • Use of Demand-Side Management, new technologies, or other initiatives. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities:4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7136 | If a recipient of the Corrective Action Plan provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities:4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 73100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7137 | Assuming the normal automatic voltage regulator control loop and steady-state system operating conditions, verify the following coordination items for each applicable Facility: |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-07-01 |  |  |  | 4.2. FacilitiesFor the purpose of this standard, the term, “applicable Facility” shall mean any one of the following:4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.4.2.2 Individual synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.4.2.3 Generating plant/ Facility consisting of one or more units that are connected to the Bulk Electric System at a common bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.3.1 This includes individual generating units of the dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition where voltage regulating control for the facility is performed solely at the individual generating unit of the dispersed power producing resources. 4.2.4 Any generator, regardless of size, that is a blackstart unit material to and designated as part of a Transmission Operator’s restoration plan. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7138 | The in-service limiters are set to operate before the Protection System of the applicable Facility in order to avoid disconnecting the generator unnecessarily. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-07-01 |  |  |  | 4.2. FacilitiesFor the purpose of this standard, the term, “applicable Facility” shall mean any one of the following:4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.4.2.2 Individual synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.4.2.3 Generating plant/ Facility consisting of one or more units that are connected to the Bulk Electric System at a common bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.3.1 This includes individual generating units of the dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition where voltage regulating control for the facility is performed solely at the individual generating unit of the dispersed power producing resources. 4.2.4 Any generator, regardless of size, that is a blackstart unit material to and designated as part of a Transmission Operator’s restoration plan. |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7140 | The Generator Owner shall communicate the documented regulatory or equipment limitation, or the removal of a previously documented regulatory or equipment limitation, to its Planning Coordinator and Transmission Planner within 30 calendar days of any of the following:• Identification of a regulatory or equipment limitation.• Repair of the equipment causing the limitation that removes the limitation. • Replacement of the equipment causing the limitation with equipment that removes the limitation.• Creation or adjustment of an equipment limitation caused by consumption of the cumulative turbine life-time frequency excursion allowance. |  | GO | [22 empty] | 2016-07-01 |  | 2022-09-30 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7141 | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-05-13 |  | 2016-06-30 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7144 | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-05-13 |  | 2016-06-30 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7145 | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-07-01 |  | 2016-06-30 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7149 | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and |  | GO, TO |  |  |  |  | GO | [17 empty] | 2015-05-29 |  | 2016-06-30 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7152 | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-05-29 |  | 2016-06-30 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7153 | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2016-06-30 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7157 | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-05-29 |  | 2016-12-31 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7159 | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-01-25 |  | 2015-12-31 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 716 | Planned or controlled interruption of electric supply to customers (load shedding), the planned removal from service of certain generators, and/or the curtailment of contracted Firm (non-recallable reserved) electric power Transfers. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-07-01 |  | 2009-04-28 |  |  |  | 25100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7163 | Identify BES buses for which sequence of events recording (SER) and fault recording (FR) data is required by using the methodology in PRC-002-2, Attachment 1. |  | TO | [22 empty] | 2015-11-24 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7166 | Phase-to-neutral voltage for each phase of each specified BES bus. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7168 | Transformers that have a low-side operating voltage of 100kV or above. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 32100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7170 | A single record or multiple records that include:• A pre-trigger record length of at least two cycles and a total record length of at least 30-cycles for the same trigger point, or• At least two cycles of the pre-trigger data, the first three cycles of the post-trigger data, and the final cycle of the fault as seen by the fault recorder. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7173 | Neutral (residual) overcurrent. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 43100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7175 | Identify BES Elements for which dynamic Disturbance recording (DDR) data is required, including the following: |  | PCPA, RC | [9 empty] | PA |  | RC | [10 empty] | 2015-11-24 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7176 | Generating resource(s) with: |  | PCPA, RC | [9 empty] | PA |  | RC | [10 empty] | 2016-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 51100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7177 | Gross individual nameplate rating greater than or equal to 500 MVA. |  | PCPA, RC | [9 empty] | PA |  | RC | [10 empty] | 2016-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 51110000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 718 | Study model (must include at least the entire Planning Authority Area as well as the critical modeling details from other Planning Authority Areas that would impact the Facility or Facilities under study). |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-010-1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7184 | One BES Element; and |  | PCPA, RC | [9 empty] | PA |  | RC | [10 empty] | 2016-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 52100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7188 | One phase-to-neutral or positive sequence voltage. |  | TO | [22 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7192 | One phase-to-neutral, phase-to-phase, or positive sequence voltage at either the generator step-up transformer (GSU) high-side or low-side voltage level. |  | GO | [22 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7196 | Triggered record lengths of at least three minutes. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7198 | Input sampling rate of at least 960 samples per second. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7200 | Synchronization to Coordinated Universal Time (UTC) with or without a local time offset. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7202 | Data will be retrievable for the period of 10-calendar days, inclusive of the day the data was recorded. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7207 | Security awareness that, at least once each calendar quarter, reinforces cyber security practices (which may include associated physical security practices) for the Responsible Entity’s personnel who have authorized electronic or authorized unescorted physical access to BES Cyber Systems. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.1 An example of evidence may include, but is not limited to, documentation that the quarterly reinforcement has been provided. Examples of evidence of reinforcement may include, but are not limited to, dated copies of information used to reinforce security awareness, as well as evidence of distribution, such as: • direct communications (for example, e-mails, memos, computer-based training); or • indirect communications (for example, posters, intranet, or brochures); or• management support and reinforcement (for example, presentations or meetings). | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7208 | Training content on: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.1 Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7209 | Cyber security policies; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7219 | Develop a baseline configuration, individually or by group, which shall include the following items: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.1. Examples of evidence may include, but are not limited to: • A spreadsheet identifying the required items of the baseline configuration for each Cyber Asset, individually or by group; or• A record in an asset management system that identifies the required items of the baseline configuration for each Cyber Asset, individually or by group. | 2016-03-31 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7220 | Operating system(s) (including version) or firmware where no independent operating system exists; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7228 | Prior to the change, determine required cyber security controls in CIP-005 and CIP-007 that could be impacted by the change; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 14100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7232 | Prior to implementing any change in the production environment, test the changes in a test environment or test the changes in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration to ensure that required cyber security controls in CIP-005 and CIP-007 are not adversely affected; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 15100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7234 | Monitor at least once every 35 calendar days for changes to the baseline configuration (as described in Requirement R1, Part 1.1). Document and investigate detected unauthorized changes. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.1. An example of evidence may include, but is not limited to, logs from a system that is monitoring the configuration along with records of investigation for any unauthorized changes that were detected. | 2016-08-05 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7235 | At least once every 15 calendar months, conduct a paper or active vulnerability assessment. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.1. Examples of evidence may include, but are not limited to: • A document listing the date of the assessment (performed at least once every 15 calendar months), the controls assessed for each BES Cyber System along with the method of assessment; or• A document listing the date of the assessment and the output of any tools used to perform the assessment. | 2017-07-01 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7237 | Perform an active vulnerability assessment in a test environment, or perform an active vulnerability assessment in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration of the BES Cyber System in a production environment; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2018-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 32100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7241 | Method(s) to identify information that meets the definition of BES Cyber System Information. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.1. Examples of acceptable evidence include, but are not limited to: • Documented method to identify BES Cyber System Information from entity’s information protection program; or• Indications on information (e.g., labels or classification) that identify BES Cyber System Information as designated in the entity’s information protection program; or• Training materials that provide personnel with sufficient knowledge to recognize BES Cyber System Information; or• Repository or electronic and physical location designated for housing BES Cyber System Information in the entity’s information protection program. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-011-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7243 | Prior to the release for reuse of applicable Cyber Assets that contain BES Cyber System Information (except for reuse within other systems identified in the “Applicable Systems” column), the Responsible Entity shall take action to prevent the unauthorized retrieval of BES Cyber System Information from the Cyber Asset data storage media. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.1. Examples of acceptable evidence include, but are not limited to: • Records tracking sanitization actions taken to prevent unauthorized retrieval of BES Cyber System Information such as clearing, purging, or destroying; or • Records tracking actions such as encrypting, retaining in the Physical Security Perimeter or other methods used to prevent unauthorized retrieval of BES Cyber System Information. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-011-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7246 | Process to confirm identity. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.1. An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to confirm identity. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 725 | Each adjacent Planning Authority and each Planning Authority that indicated it has a reliability-related need for the methodology. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-010-1 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7258 | Process to authorize based on need, as determined by the Responsible Entity, except for CIP Exceptional Circumstances: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.1. An example of evidence may include, but is not limited to, dated documentation of the process to authorize electronic access, unescorted physical access in a Physical Security Perimeter, and access to designated storage locations, whether physical or electronic, for BES Cyber System Information. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7259 | Electronic access; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 41100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7265 | A process to initiate removal of an individual’s ability for unescorted physical access and Interactive Remote Access upon a termination action, and complete the removals within 24 hours of the termination action (Removal of the ability for access may be different than deletion, disabling, revocation, or removal of all access rights) |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.1 An example of evidence may include, but is not limited to, documentation of all of the following:1. Dated workflow or sign-off form verifying access removal associated with the termination action; and 2. Logs or other demonstration showing such persons no longer have access. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7286 | Where technically feasible, enable only logical network accessible ports that have been determined to be needed by the Responsible Entity, including port ranges or services where needed to handle dynamic ports. If a device has no provision for disabling or restricting logical ports on the device then those ports that are open are deemed needed. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.1. Examples of evidence may include, but are not limited to:• Documentation of the need for all enabled ports on all applicable Cyber Assets and Electronic Access Points, individually or by group. • Listings of the listening ports on the Cyber Assets, individually or by group, from either the device configuration files, command output (such as netstat), or network scans of open ports; or• Configuration files of host-based firewalls or other device level mechanisms that only allow needed ports and deny all others. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7288 | A patch management process for tracking, evaluating, and installing cyber security patches for applicable Cyber Assets. The tracking portion shall include the identification of a source or sources that the Responsible Entity tracks for the release of cyber security patches for applicable Cyber Assets that are updateable and for which a patching source exists. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.1. An example of evidence may include, but is not limited to, documentation of a patch management process and documentation or lists of sources that are monitored, whether on an individual BES Cyber System or Cyber Asset basis. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7292 | Deploy method(s) to deter, detect, or prevent malicious code. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.1. An example of evidence may include, but is not limited to, records of the Responsible Entity’s performance of these processes (e.g., through traditional antivirus, system hardening, policies, etc.). | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7295 | Log events at the BES Cyber System level (per BES Cyber System capability) or at the Cyber Asset level (per Cyber Asset capability) for identification of, and after-the-fact investigations of, Cyber Security Incidents that includes, as a minimum, each of the following types of events: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.1. Examples of evidence may include, but are not limited to, a paper or system generated listing of event types for which the BES Cyber System is capable of detecting and, for generated events, is configured to log. This listing must include the required types of events. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 730 | Be applicable for developing SOLs used in the planning horizon. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | FAC-010-2 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7302 | Detected successful login attempts; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.1. Examples of evidence may include, but are not limited to, a paper or system generated listing of event types for which the BES Cyber System is capable of detecting and, for generated events, is configured to log. This listing must include the required types of events. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 41100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7306 | Detected malicious code from Part 4.1; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.2. Examples of evidence may include, but are not limited to, paper or system-generated listing of security events that the Responsible Entity determined necessitate alerts, including paper or system generated list showing how alerts are configured. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 42100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7310 | Have a method(s) to enforce authentication of interactive user access, where technically feasible. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.1. An example of evidence may include, but is not limited to, documentation describing how access is authenticated. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7316 | Password length that is, at least, the lesser of eight characters or the maximum length supported by the Cyber Asset; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 55100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7339 | Define operational or procedural controls to restrict physical access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.1. An example of evidence may include, but is not limited to, documentation that operational or procedural controls exist. | 2016-07-01 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 734 | In the pre-contingency state and with all Facilities in service, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect expected system conditions and shall reflect changes to system topology such as Facility outages. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | FAC-010-2 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7349 | Require continuous escorted access of visitors (individuals who are provided access but are not authorized for unescorted physical access) within each Physical Security Perimeter, except during CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.1. An example of evidence may include, but is not limited to, language in a visitor control program that requires continuous escorted access of visitors within Physical Security Perimeters and additional evidence to demonstrate that the process was implemented, such as visitor logs. | 2016-07-01 | [5 empty] | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7352 | Maintenance and testing of each Physical Access Control System and locally mounted hardware or devices at the Physical Security Perimeter at least once every 24 calendar months to ensure they function properly. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M.3.1. An example of evidence may include, but is not limited to, a maintenance and testing program that provides for testing each Physical Access Control System and locally mounted hardware or devices associated with each applicable Physical Security Perimeter at least once every 24 calendar months and additional evidence to demonstrate that this testing was done, such as dated maintenance records, or other documentation showing testing and maintenance has been performed on each applicable device or system at least once every 24 calendar months. | 2017-07-01 | [5 empty] | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7353 | Three phase-to-neutral voltages. (Common bus-side voltages may be used for lines.) |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 51000000 | NPCC-US |  | NPCC-US
1. | 7358 | Each Fault recorder record duration shall be a minimum of one (1) second. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 61000000 | NPCC-US |  | NPCC-US
1. | 736 | Single line to ground or three-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 22100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7361 | Monitored phase overcurrents set at 1.5 pu or less of rated CT secondary current or Protective Relay tripping for all Protection Groups. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 63100000 | NPCC-US |  | NPCC-US
1. | 7365 | Provides a minimum of 1 DDR per 3,000 MW of peak Load. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 71000000 | NPCC-US |  | NPCC-US
1. | 7367 | Major Load centers. |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 72100000 | NPCC-US |  | NPCC-US
1. | 7386 | The performance of the UFLS equipment, |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7388 | Be provided at all substations and at locations where circuit breaker operation affects continuity of service to radial Loads greater than 300MW, or the operation of which drops 50MVA Nameplate Rating or greater of Generation, or the operation of which creates a Generation/Load island. Be provided at generating units above 50MVA Nameplate Rating or series of generating units utilizing a control scheme such that the loss of 1 unit results in a loss of greater than 50MVA Nameplate Capacity, and at Generating Plants above 300MVA Name Plate Capacity. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 11000000 | NPCC-US |  | NPCC-US
1. | 7390 | Transmission and Generator circuit breaker positions |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 12100000 | NPCC-US |  | NPCC-US
1. | 74 | Fixed schedules for Jointly Owned Units mandate that Balancing Authority (A) that contains the Jointly Owned Unit must incorporate the respective share of the unit governor droop response for any Balancing Authorities that have fixed schedules (B and C). See the diagram below. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2015-03-31 |  |  | BAL-003-0.1b R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 740 | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 23100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7408 | A minimum recording time of sixty (60) seconds per trigger event. |  | RC | [11 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 91000000 | NPCC-US |  | NPCC-US
1. | 7411 | Rate of change of Frequency. |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 93100000 | NPCC-US |  | NPCC-US
1. | 7415 | Line currents for most lines such that normal line maintenance activities do not interfere with DDR functionality. |  | RC | [11 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 101000000 | NPCC-US |  | NPCC-US
1. | 7420 | Maintenance and testing intervals and their basis. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 141000000 | NPCC-US |  | NPCC-US
1. | 7427 | NERC, Regional Entity, Reliability Coordinator. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 151000000 | NPCC-US |  | NPCC-US
1. | 7429 | The data files shall be capable of being viewed, read, and analyzed with a generic COMTRADE analysis tool as per the latest revision of IEEE Standard C37.111. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 161000000 | NPCC-US |  | NPCC-US
1. | 7432 | Type of DME. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 171000000 | NPCC-US |  | NPCC-US
1. | 7441 | The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  |  | 2014-08-01 |  | 2015-11-12 |  |  |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7444 | Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances. |  | GOP | [5 empty] | GOP | [16 empty] | 2014-08-01 |  | 2015-11-12 |  |  |  | 2710000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7446 | That can be implemented in time to prevent the identified IROL exceedance. |  | RC | [11 empty] | RC | [10 empty] | 2015-12-04 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 745 | Planned or controlled interruption of electric supply to customers (load shedding), the planned removal from service of certain generators, and/or the curtailment of contracted Firm (non-recallable reserved) electric power Transfers. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 26100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7454 | Less than zero at all times, and |  | BA, FRSG | BA |  |  | FRSG | [12 empty] | RSG | [5 empty] | 2015-11-13 |  | 2020-11-30 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7468 | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 747 | Study model (must include at least the entire Planning Authority Area as well as the critical modeling details from other Planning Authority Areas that would impact the Facility or Facilities under study). |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | FAC-010-2 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7470 | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7472 | Its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7478 | Personnel and training (CIP-004); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7487 | Its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7493 | Its Reliability Coordinator. |  | BA | BA | [21 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7498 | Its Reliability Coordinator. |  | BA | BA | [21 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7501 | Its Balancing Authority. |  | DP |  | DP | [20 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7503 | Its Balancing Authority. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7507 | Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-25 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7510 | If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-25 |  |  |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7512 | The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-25 |  |  |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7516 | current residence, regardless of duration; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 32100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7527 | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-12-04 |  | 2016-06-30 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7530 | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-12-04 |  | 2016-06-30 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7531 | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-07-01 |  | 2016-06-30 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7536 | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-12-04 |  | 2017-04-01 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 754 | Each adjacent Planning Authority and each Planning Authority that indicated it has a reliability-related need for the methodology. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | FAC-010-2 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7540 | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-12-04 |  | 2017-04-01 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7541 | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-07-01 |  | 2017-04-01 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7550 | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-11-19 |  | 2021-03-31 |  | 4.2. Facilities:4.2.1 Protection Systems for BES Elements, with the following exclusions:4.2.1.1 Non-protective functions that are embedded within a Protection System.4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS).4.2.1.4 Remedial Action Schemes (RAS).4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7554 | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-11-19 |  | 2021-03-31 |  | 4.2. Facilities:4.2.1 Protection Systems for BES Elements, with the following exclusions:4.2.1.1 Non-protective functions that are embedded within a Protection System.4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS).4.2.1.4 Remedial Action Schemes (RAS).4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7555 | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-04-02 |  | 2021-03-31 |  | 4.2. Facilities:4.2.1 Protection Systems for BES Elements, with the following exclusions:4.2.1.1 Non-protective functions that are embedded within a Protection System.4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS).4.2.1.4 Remedial Action Schemes (RAS).4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7564 | A review and update of short-circuit model data for the BES Elements under study. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.1.3. Distribution Provider (that owns Protection Systems identified in the Facilities section 4.2 below)4.2. Facilities: Protection Systems installed to detect and isolate Faults on BES Elements. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7567 | Provide the proposed Protection System settings to the owner(s) of the electrically joined Facilities. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.1.3. Distribution Provider (that owns Protection Systems identified in the Facilities section 4.2 below)4.2. Facilities: Protection Systems installed to detect and isolate Faults on BES Elements. |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7579 | Identify which maintenance method (time-based, performance-based per PRC-005 Attachment A, or a combination) is used to address each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type. All batteries associated with the station dc supply Component Type of a Protection System shall be included in a time-based program as described in Table 1-4 and Table 3. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-12-18 |  |  |  | 4.2.1 Protection Systems and Sudden Pressure Relaying that are installed for the purpose of detecting Faults on BES Elements (lines, buses, transformers, etc.)4.2.2 Protection Systems used for underfrequency load-shedding systems installed per ERO underfrequency load-shedding requirements.4.2.3 Protection Systems used for undervoltage load-shedding systems installed to prevent system voltage collapse or voltage instability for BES reliability.4.2.4 Protection Systems installed as a Remedial Action Scheme (RAS) for BES reliability.4.2.5 Protection Systems and Sudden Pressure Relaying for generator Facilities that are part of the BES, except for generators identified through Inclusion I4 of the BES definition, including:4.2.5.1 Protection Systems that act to trip the generator either directly or via lockout or auxiliary tripping relays.4.2.5.2 Protection Systems and Sudden Pressure Relaying for generator step-up transformers for generators that are part of the BES.4.2.5.3 Protection Systems and Sudden Pressure Relaying for station service or excitation transformers connected to the generator bus of generators which are part of the BES, that act to trip the generator either directly or via lockout or tripping auxiliary relays.4.2.6 Protection Systems and Sudden Pressure Relaying for the following BES generator Facilities for dispersed power producing resources identified through Inclusion I4 of the BES definition:4.2.6.1 Protection Systems and Sudden Pressure Relaying for Facilities used in aggregating dispersed BES generation from the point where those resources aggregate to greater than 75 MVA to a common point of connection at 100kV or above.4.2.7 Automatic Reclosing , including:4.2.7.1 Automatic Reclosing applied on the terminals of Elements connected to the BES bus located at generating plant substations where the total installed gross generating plant capacity is greater than the gross capacity of the largest BES generating unit within the Balancing Authority Area or, if a member of a Reserve Sharing Group, the largest generating unit within the Reserve Sharing Group. 4.2.7.2 Automatic Reclosing applied on the terminals of all BES Elements at substations one bus away from generating plants specified in Section 4.2.7.1 when the substation is less than 10 circuit-miles from the generating plant substation.4.2.7.3 Automatic Reclosing applied as an integral part of an RAS specified in Section 4.2.4. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7581 | A list of Transmission Planners, Balancing Authorities, Load Serving Entities, and Distribution Providers that are required to provide the data (“Applicable Entities”). |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-02-18 |  | 2021-03-31 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7584 | Integrated hourly Demands in megawatts for the prior calendar year. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7586 | If the annual peak hour actual Demand varies due to weather-related conditions (e.g., temperature, humidity or wind speed), the Applicable Entity shall also provide the weather normalized annual peak hour actual Demand for the prior calendar year. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” |  | 13210000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 759 | Be applicable for developing SOLs used in the operations horizon. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-011-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7590 | Monthly peak hour forecast Total Internal Demands in megawatts for the next two calendar years. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” |  | 14100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7596 | The assumptions and methods used in the development of aggregated Peak Demand and Net Energy for Load forecasts. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” |  | 15100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7601 | If the Applicable Entity does not provide data requested because (1) the requesting entity did not demonstrate a reliability need for the data; or (2) providing the data would conflict with the Applicable Entity’s confidentiality, regulatory, or security requirements, the Applicable Entity shall, within 30 calendar days of the written request, provide a written response to the requesting entity specifying the data that is not being provided and on what basis. |  | BA, DP, LSE, PCPA, RP, TP | BA | DP | [5 empty] | LSE |  | PA |  |  |  | RP | [5 empty] | TP |  |  | 2016-02-18 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7608 | within the Contingency Event Recovery Period, demonstrate recovery by returning its Reporting ACE to at least the recovery value of:• zero (if its Pre-Reporting Contingency Event ACE Value was positive or equal to zero); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event, or• its Pre-Reporting Contingency Event ACE Value (if its Pre-Reporting Contingency Event ACE Value was negative); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | M1. Each Responsible Entity shall have, and provide upon request, as evidence, a CR Form 1 with date and time of occurrence to show compliance with Requirement R1. If Requirement R1 part 1.3 applies, then dated documentation that demonstrates compliance with Requirement R1 part 1.3 must also be provided. | 2017-04-03 |  | 2017-12-31 |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7611 | 1.3.1 the Responsible Entity:• is a Balancing Authority experiencing a Reliability Coordinator declared Energy Emergency Alert Level or is a Reserve Sharing Group whose member, or members, are experiencing a Reliability Coordinator declared Energy Emergency Alert level, and• is utilizing its Contingency Reserve to mitigate an operating emergency in accordance with its emergency Operating Plan, and• has depleted its Contingency Reserve to a level below its Most Severe Single Contingency or, |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2017-12-31 |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7621 | that is available a minimum of 99.95% for each calendar year; and, |  | BA | BA | [21 empty] | 2017-11-27 | [5 empty] | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7623 | a common source to provide information to both Balancing Authorities for the scan rate values used in the calculation of Reporting ACE; and, |  | BA | BA | [21 empty] | 2017-11-27 | [5 empty] | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7629 | Procedures for coordinated studies of new or materially modified existing interconnections and their impacts on affected system(s). |  | TO | [22 empty] | 2019-01-01 | [5 empty] | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 763 | In the pre-contingency state, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect current or expected system conditions and shall reflect changes to system topology such as Facility outages. |  | RC | [11 empty] | RC | [10 empty] | 2008-05-29 |  | 2009-04-28 |  |  | FAC-011-1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7632 | Procedures for coordinated studies of new interconnections and their impacts on affected system(s). |  | GO | [22 empty] | 2019-01-01 | [5 empty] | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7639 | An encroachment into the MVCD as shown in FAC-003-Table 2, observed in Real-time, absent a Sustained Outage, (Footnote: If a later confirmation of a Fault by the applicable Transmission Owner or applicable Generator Owner shows that a vegetation encroachment within the MVCD has occurred from vegetation within the ROW, this shall be considered the equivalent of a Real-time observation.) |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:4.1.1. Applicable Transmission Owners4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.4.1.2. Applicable Generator Owners4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.2.1. Each overhead transmission line operated at 200kV or higher.4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:4.3.1.1. Operated at 200kV or higher; or4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7643 | An encroachment into the MVCD, observed in Real-time, absent a Sustained Outage, |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:4.1.1. Applicable Transmission Owners4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.4.1.2. Applicable Generator Owners4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.2.1. Each overhead transmission line operated at 200kV or higher.4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:4.3.1.1. Operated at 200kV or higher; or4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7647 | Movement of applicable line conductors under their Rating and all Rated Electrical Operating Conditions; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:4.1.1. Applicable Transmission Owners4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.4.1.2. Applicable Generator Owners4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.2.1. Each overhead transmission line operated at 200kV or higher.4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:4.3.1.1. Operated at 200kV or higher; or4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 765 | Single line to ground or 3-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. |  | RC | [11 empty] | RC | [10 empty] | 2008-10-01 |  | 2009-04-28 |  |  |  | 22100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7665 | When modeling normal conditions, all Transmission Elements will be modeled at or below 100% of their continuous rating. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7684 | Those islands selected by applying the criteria in Requirement D.B.1, and |  | PCPA | [9 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 210000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7687 | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-2 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 310000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 769 | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. |  | RC | [11 empty] | RC | [10 empty] | 2008-10-01 |  | 2009-04-28 |  |  |  | 23100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7690 | Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES |  | PCPA | [9 empty] | PA | [12 empty] | 2015-10-01 |  | 2017-09-30 |  |  |  | 331000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7694 | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 410000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 77 | Balancing Authorities that do not serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of its estimated maximum generation level in the coming year per 0.1 Hz change. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2015-03-31 |  |  | BAL-003-0.1b R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7702 | The performance of the UFLS equipment, |  | PCPA | [9 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 2010000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7712 | Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-11-13 |  | 2017-09-25 |  |  |  | 2710000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7714 | The synchronous generator or synchronous condenser operates for less than five percent of all hours during any calendar quarter. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2015-03-03 |  | 2018-09-05 |  |  |  | 11000000 | WECC-US | [5 empty] | WECC-US
1. | 7725 | Criteria for evaluating the quality of Real-time data; |  | TOP | [18 empty] | TOP |  |  |  | 2016-09-22 |  | 2018-03-31 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7729 | Criteria for evaluating the quality of Real-time data; |  | BA | BA | [21 empty] | 2016-09-22 |  | 2018-03-31 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7733 | Criteria for evaluating the quality of analysis used in its Real-time Assessments; |  | TOP | [18 empty] | TOP |  |  |  | 2016-09-22 |  | 2018-03-31 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7739 | Criteria for evaluating the quality of Real-time data; |  | RC | [11 empty] | RC | [10 empty] | 2016-09-22 |  | 2018-03-31 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 774 | Study model (must include at least the entire Reliability Coordinator Area as well as the critical modeling details from other Reliability Coordinator Areas that would impact the Facility or Facilities under study.) |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-011-1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7742 | Criteria for evaluating the quality of analysis used in its Real-time Assessments; |  | RC | [11 empty] | RC | [10 empty] | 2016-09-22 |  | 2018-03-31 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7750 | Perform an evaluation of each RAS within its planning area to determine whether: |  | PCPA | [9 empty] | PA | [12 empty] | 2026-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7751 | The RAS mitigates the System condition(s) or Contingency(ies) for which it was designed. |  | PCPA | [9 empty] | PA | [12 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 41100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7755 | The BES shall remain stable. |  | PCPA | [9 empty] | PA | [12 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 41410000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7763 | Participate in analyzing the RAS operational performance to determine whether: |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-11-27 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7764 | The System events and/or conditions appropriately triggered the RAS. |  | PCPA | [9 empty] | PA | [12 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 51100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 777 | This process shall address the need to modify these limits, to modify the list of limits, and to modify the list of associated multiple contingencies. |  | RC | [11 empty] | RC | [10 empty] | 2008-10-01 |  | 2009-04-28 |  |  |  | 33100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7771 | Implement the CAP. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-11-27 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7776 | Require its operating personnel that issue and receive an oral or written Operating Instruction to use the English language, unless agreed to otherwise. An alternate language may be used for internal operations. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2015-06-22 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7782 | Assess adherence to the documented communications protocols in Requirement R1 by its operating personnel that issue and receive Operating Instructions, provide feedback to those operating personnel and take corrective action, as deemed appropriate by the entity, to address deviations from the documented protocols. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2015-06-22 | [5 empty] | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7784 | Detected successful login attempts; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 41100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7786 | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2016-10-28 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7789 | All Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2016-10-28 | [5 empty] | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7792 | Its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | 2016-10-28 | [5 empty] | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7799 | Its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | 2016-10-28 | [5 empty] | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7804 | Its Reliability Coordinator. |  | BA | BA | [21 empty] | 2016-10-28 | [5 empty] | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7810 | Its Reliability Coordinator. |  | BA | BA | [21 empty] | 2016-10-28 | [5 empty] | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7814 | Its Balancing Authority. |  | DP |  | DP | [20 empty] | 2016-10-28 | [5 empty] | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7817 | Its Balancing Authority. |  | GOP | [5 empty] | GOP | [16 empty] | 2016-10-28 | [5 empty] | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7825 | The UVLS Program resolves the identified undervoltage issues for which the UVLS Program is designed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-11-19 | [5 empty] | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7827 | The synchronous generator operates for less than five percent of all hours during any calendar quarter. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-04-01 |  | 2017-06-30 |  |  |  | 11000000 | WECC-US | [5 empty] | WECC-US
1. | 783 | Each adjacent Reliability Coordinator and each Reliability Coordinator that indicated it has a reliability-related need for the methodology. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-011-1 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7841 | The Generator Owners shall adjust generation to a reliable operating level, or |  | GO | [22 empty] | 2017-04-01 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf..4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. |  | 23210000 | WECC-US | [5 empty] | WECC-US
1. | 7844 | Identify each of the high impact BES Cyber Systems according to Attachment 1, Section 1, if any, at each asset; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-12-27 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency load shedding (UFLS) or undervoltage load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-002-5.1a: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7848 | Review the identifications in Requirement R1 and its parts (and update them if there are changes identified) at least once every 15 calendar months, even if it has no identified items in Requirement R1, and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-12-27 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency load shedding (UFLS) or undervoltage load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-002-5.1a: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7851 | Criteria for evaluating the quality of Real-time data; |  | RC | [11 empty] | RC | [10 empty] | 2018-04-01 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7852 | Criteria for evaluating the quality of Real-time data; |  | RC | [11 empty] | RC | [10 empty] | 2016-12-14 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7857 | Criteria for evaluating the quality of analysis used in its Real-time Assessments; |  | RC | [11 empty] | RC | [10 empty] | 2016-12-14 | [5 empty] | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7861 | Criteria for evaluating the quality of Real-time data; |  | TOP | [18 empty] | TOP |  |  |  | 2016-12-14 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7865 | Criteria for evaluating the quality of Real-time data; |  | BA | BA | [21 empty] | 2016-12-14 | [5 empty] | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7870 | Criteria for evaluating the quality of analysis used in its Real-time Assessments; |  | TOP | [18 empty] | TOP |  |  |  | 2016-12-14 | [5 empty] | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7875 | The greater of either: • The amount of Contingency Reserve equal to the loss of the most severe single contingency; • The amount of Contingency Reserve equal to the sum of three percent of hourly integrated Load plus three percent of hourly integrated generation. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Part 1.1. Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates its Contingency Reserve was maintained in accordance with the amounts identified in Requirement R1, Part 1.1, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. Attachment A is a practical illustration showing how the generation amount may be calculated under Requirement R1.• Where Dynamic Schedules are used as part of the generation amount upon which Contingency Reserve is predicated, additional evidence of compliance with Requirement R1, Part 1.1 may include, but is not limited to, documentation showing a reciprocal acknowledgement as to which entity is carrying the reserves. This transfer may be all or some portion of the physical generator and is not limited to the entire physical capability of the generator. • Where Pseudo-Ties are used as part of the generation amount upon which Contingency Reserve is predicated, additional evidence of compliance with Requirement R1, Part 1.1, may include, but is not limited to, documentation accounting for the transfers included in the Pseudo-Ties. | 2017-01-24 |  | 2021-06-27 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity.4.2.1.The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group.4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | 11000000 | WECC-US | [5 empty] | WECC-US
1. | 788 | Be applicable for developing SOLs used in the operations horizon. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | FAC-011-2 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7880 | Reserve that is immediately and automatically responsive to frequency deviations through the action of a governor or other control system; |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2017-01-24 |  | 2021-06-27 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity.4.2.1.The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group.4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | 21000000 | WECC-US | [5 empty] | WECC-US
1. | 7887 | The location and method of implementation for providing backup functionality. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7889 | Tools and applications to ensure that System Operators have situational awareness of the BES. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2019-04-01 | [5 empty] | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7898 | A list of all entities to notify when there is a change in operating locations. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2019-04-01 | [5 empty] | 16100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7907 | An update and approval of the Operating Plan for backup functionality shall take place within sixty calendar days of any changes to any part of the Operating Plan described in Requirement R1. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7908 | The transition time between the simulated loss of primary control center functionality and the time to fully implement the backup functionality. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7912 | A description of the high-level strategy to be employed during restoration events for restoring the Interconnection, including minimum criteria for meeting the objectives of the Reliability Coordinator’s restoration plan. |  | RC | [11 empty] | RC | [10 empty] | 2018-03-26 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 792 | In the pre-contingency state, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect current or expected system conditions and shall reflect changes to system topology such as Facility outages. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | FAC-011-2 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7922 | If a Reliability Coordinator finds conflicts between its restoration plans and any of its neighbors, the conflicts shall be resolved within 30 calendar days of receipt of written notification. |  | RC | [11 empty] | RC | [10 empty] | 2018-03-26 | [5 empty] | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7924 | The Reliability Coordinator shall determine whether the Transmission Operator’s restoration plan is coordinated and compatible with the Reliability Coordinator’s restoration plan and other Transmission Operators’ restoration plans within its Reliability Coordinator Area. The Reliability Coordinator shall provide notification to the Transmission Operator of approval or disapproval, with stated reasons, of the Transmission Operator’s submitted restoration plan within 30 calendar days following the receipt of the restoration plan from the Transmission Operator. |  | RC | [11 empty] | RC | [10 empty] | 2018-03-26 | [5 empty] | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7927 | The coordination role of the Reliability Coordinator; and |  | RC | [11 empty] | RC | [10 empty] | 2018-03-26 | [5 empty] | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7930 | Each Reliability Coordinator shall request each Transmission Operator identified in its restoration plan and each Generator Operator identified in the Transmission Operators’ restoration plans to participate in a drill, exercise, or simulation at least once every two calendar years. |  | RC | [11 empty] | RC | [10 empty] | 2018-03-26 | [5 empty] | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7932 | Strategies for System restoration that are coordinated with its Reliability Coordinator’s high level strategy for restoring the Interconnection. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 794 | Single line to ground or 3-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 22100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7944 | Within 90 calendar days after identifying any unplanned permanent BES modifications. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7948 | The capability of Blackstart Resources to meet the Real and Reactive Power requirements of the Cranking Paths and the dynamic capability to supply initial Loads. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7952 | The frequency of testing such that each Blackstart Resource is tested at least once every three calendar years. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7954 | The ability to start the unit when isolated with no support from the BES or when designed to remain energized without connection to the remainder of the System. |  | TOP | [18 empty] | TOP |  |  |  | 2019-04-01 | [5 empty] | 72100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7958 | System restoration plan including coordination with its Reliability Coordinator and Generator Operators included in the restoration plan. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7969 | Testing records shall include at a minimum: name of the Blackstart Resource, unit tested, date of the test, duration of the test, time required to start the unit, an indication of any testing requirements not met under Requirement R7. |  | GOP | [5 empty] | GOP | [16 empty] | 2018-03-26 | [5 empty] | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7971 | System restoration plan including coordination with the Transmission Operator |  | GOP | [5 empty] | GOP | [16 empty] | 2018-03-26 | [5 empty] | 151000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7977 | PSS shall be set to provide the measured, simulated, or calculated compensated VT/Vref frequency response of the excitation system and synchronous machine such that the phase angle will not exceed ± 30 degrees through the frequency range from 0.2 Hertz to the lesser of 1.0 Hertz or the highest frequency at which the phase of the Vt/Vref frequency response does not exceed 90 degrees. |  | GO | [22 empty] | 2017-04-28 |  | 2017-09-25 |  |  |  | 31000000 | WECC-US | [5 empty] | WECC-US
1. | 79780007763 | Participate in analyzing the RAS operational performance to determine whether: |  | DP, GO, PCPA, RC, TO |  | DP |  |  | GO |  |  |  |  | PA |  | RC | [10 empty] | 2017-11-27 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 51000000 | NPCC-ON |  | NPCC-US
1. | 79780007764 | The System events and/or conditions appropriately triggered the RAS. |  | DP, GO, PCPA, RC, TO |  | DP |  |  | GO |  |  |  |  | PA |  | RC | [10 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 51100000 | NPCC-ON |  | NPCC-US
1. | 798 | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 23100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7986 | For its high impact and medium impact BES Cyber Systems, if any: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2018-06-25 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7988 | Personnel and training (CIP-004); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 7998 | Cyber security awareness; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 80 | The Balancing Authority may change its Frequency Bias Setting, and the method used to determine the setting, whenever any of the factors used to determine the current bias value change. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2009-05-12 |  |  | BAL-003-0a R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8023 | Monitor Facilities within its Transmission Operator Area; |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-17 |  | 2021-03-31 |  |  |  | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 803 | Study model (must include at least the entire Reliability Coordinator Area as well as the critical modeling details from other Reliability Coordinator Areas that would impact the Facility or Facilities under study.) |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | FAC-011-2 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8043 | within the Contingency Event Recovery Period, demonstrate recovery by returning its Reporting ACE to at least the recovery value of:• zero (if its Pre-Reporting Contingency Event ACE Value was positive or equal to zero); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event,or,• its Pre-Reporting Contingency Event ACE Value (if its Pre-Reporting Contingency Event ACE Value was negative); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2017-10-02 |  | 2019-03-31 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8046 | the Responsible Entity:• is a Balancing Authority experiencing a Reliability Coordinator declared Energy Emergency Alert Level or is a Reserve Sharing Group whose member, or members, are experiencing a Reliability Coordinator declared Energy Emergency Alert level, and• is utilizing its Contingency Reserve to mitigate an operating emergency in accordance with its emergency Operating Plan, and• has depleted its Contingency Reserve to a level below its Most Severe Single Contingencyor, |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2018-01-01 |  | 2019-03-31 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8051 | Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. |  | TOP | [18 empty] | TOP |  |  |  | 2017-09-26 |  | 2018-12-31 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8052 | Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. |  | TOP | [18 empty] | TOP |  |  |  | 2017-09-26 |  | 2018-12-31 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8056 | If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. |  | TOP | [18 empty] | TOP |  |  |  | 2017-09-26 |  | 2018-12-31 |  |  |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8058 | The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  |  | 2017-09-26 |  | 2018-12-31 |  |  |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 806 | This process shall address the need to modify these limits, to modify the list of limits, and to modify the list of associated multiple contingencies |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 33100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8068 | Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances. |  | GOP | [5 empty] | GOP | [16 empty] | 2017-09-26 |  | 2018-12-31 |  |  |  | 2710000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8072 | When a generator’s AVR is out of service or the generator does not have an AVR, the Generator Operator shall use an alternative method to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2017-09-26 | [5 empty] | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8078 | For generator step-up and auxiliary transformers with primary voltages equal to or greater than the generator terminal voltage: (Footnote: For dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition, this requirement applies only to those transformers that have at least one winding at a voltage of 100 kV or above.) |  | GO | [22 empty] | 2017-09-26 | [5 empty] | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8084 | If the Generator Owner cannot comply with the Transmission Operator’s specifications, the Generator Owner shall notify the Transmission Operator and shall provide the technical justification. |  | GO | [22 empty] | 2017-09-26 | [5 empty] | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8086 | One or more process(es) used in planning for the procurement of BES Cyber Systems to identify and assess cyber security risk(s) to the Bulk Electric System from vendor products or services resulting from: (i) procuring and installing vendor equipment and software; and (ii) transitions from one vendor(s) to another vendor(s). |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and4.1.2.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and4.2.1.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers4.2.2.1. All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-013-1:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the identification and categorization process required by CIP-002-5, or any subsequent version of that Reliability Standard. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8088 | Notification by the vendor of vendor-identified incidents related to the products or services provided to the Responsible Entity that pose cyber security risk to the Responsible Entity; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and4.1.2.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and4.2.1.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers4.2.2.1. All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-013-1:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the identification and categorization process required by CIP-002-5, or any subsequent version of that Reliability Standard. |  | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8097 | All applicable Cyber Assets connected to a network via a routable protocol shall reside within a defined ESP. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a list of all ESPs with all uniquely identifiable applicable Cyber Assets connected via a routable protocol within each ESP. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-005-6:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8103 | For all Interactive Remote Access, utilize an Intermediate System such that the Cyber Asset initiating Interactive Remote Access does not directly access an applicable Cyber Asset. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, network diagrams or architecture documents. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-005-6:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8109 | Develop a baseline configuration, individually or by group, which shall include the following items: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: • A spreadsheet identifying the required items of the baseline configuration for each Cyber Asset, individually or by group; or• A record in an asset management system that identifies the required items of the baseline configuration for each Cyber Asset, individually or by group. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8110 | Operating system(s) (including version) or firmware where no independent operating system exists; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8118 | Prior to the change, determine required cyber security controls in CIP-005 and CIP-007 that could be impacted by the change; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 14100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 812 | Each adjacent Reliability Coordinator and each Reliability Coordinator that indicated it has a reliability-related need for the methodology. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | FAC-011-2 R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8122 | Prior to implementing any change in the production environment, test the changes in a test environment or test the changes in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration to ensure that required cyber security controls in CIP-005 and CIP-007 are not adversely affected; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 15100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8125 | Verify the identity of the software source; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 16100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8128 | Monitor at least once every 35 calendar days for changes to the baseline configuration (as described in Requirement R1, Part 1.1). Document and investigate detected unauthorized changes. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, logs from a system that is monitoring the configuration along with records of investigation for any unauthorized changes that were detected. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8130 | At least once every 15 calendar months, conduct a paper or active vulnerability assessment. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: • A document listing the date of the assessment (performed at least once every 15 calendar months), the controls assessed for each BES Cyber System along with the method of assessment; or• A document listing the date of the assessment and the output of any tools used to perform the assessment. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8132 | Perform an active vulnerability assessment in a test environment, or perform an active vulnerability assessment in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration of the BES Cyber System in a production environment; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 32100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8138 | A Planning Coordinator may adjust island boundaries to differ from subregional boundaries where necessary for the sole purpose of producing a contiguous subregional island more suitable for simulation. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2017-10-16 | [5 empty] | 11000000 | SERC-US |  |  |  | SERC-US
1. | 8140 | Have the capability of shedding at least 30 percent of the Peak Demand (MW) served from the Planning Coordinator’s transmission system. The Peak Demand may be either summer or winter as determined by the Planning Coordinator. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2017-10-16 | [5 empty] | 21000000 | SERC-US |  |  |  | SERC-US
1. | 8143 | This does not apply to UFLS relays with time delay of one second or longer and a higher frequency setpoint applied to prevent the frequency from stalling at less than 60 Hz when recovering from an underfrequency event. |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 23100000 | SERC-US |  |  |  | SERC-US
1. | 8149 | The percent of load shedding to be implemented shall be based on the actual or estimated substation or feeder demand (including losses) of the UFLS entities at the time coincident with the previous year’s actual Peak Demand in the season specified by the Planning Coordinator in R2. |  | DP, DP-UFLS, TO |  | DP | [20 empty] | 2017-10-16 | [5 empty] | 41000000 | SERC-US |  |  |  | SERC-US
1. | 8153 | The percent of load shedding to be implemented shall be based on the actual or estimated substation or feeder demand (including losses) of the UFLS entities at the time coincident with the previous year actual Peak Demand in the season specified by the Planning Coordinator in R2. |  | DP, DP-UFLS, TO |  | DP | [20 empty] | 2017-10-16 | [5 empty] | 51000000 | SERC-US |  |  |  | SERC-US
1. | 8157 | Underfrequency trip set points (Hz) |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2017-10-16 | [5 empty] | 71000000 | SERC-US |  |  |  | SERC-US
1. | 8161 | Generator protection automatic underfrequency and overfrequency trip set points (Hz). |  | DP-UFLS, GO |  | DP | [20 empty] | 2017-10-16 | [5 empty] | 81000000 | SERC-US |  |  |  | SERC-US
1. | 8166 | Those islands selected by applying the criteria in Requirement R1, and |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 817 | A statement that Transfer Capabilities shall respect all applicable System Operating Limits (SOLs). |  | PCPA, RC | [9 empty] | PA |  | RC | [12 empty] | 2013-03-31 |  |  | FAC-012-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8170 | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-3 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8174 | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-3 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8189 | The performance of the UFLS equipment, |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8195 | For UFLS design assessments performed under Requirement R4 or R5, the Corrective Action Plan shall be developed within the five-year time frame identified in Requirement R4. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 151000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8199 | Those islands selected by applying the criteria in Requirement D.B.1, and |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 210000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 820 | Transmission system topology |  | PCPA, RC | [9 empty] | PA |  | RC | [12 empty] | 2013-03-31 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8202 | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-3 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 310000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8205 | Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 331000 | WECC-US | [5 empty] | WECC-US
1. | 8209 | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-3 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 410000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8217 | The performance of the UFLS equipment, |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 2010000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8221 | Calculate a planning reserve margin that will result in the sum of the probabilities for loss of Load for the integrated peak hour for all days of each planning year analyzed (per R1.2) being equal to 0.1. (This is comparable to a “one day in 10 year” criterion).The annual period over which the LOLE is measured, and the resulting resource requirements are established (June 1st through the following May 31st). |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-16 | [5 empty] | 11000000 | RF-US |  |  | RF-US
1. | 8222 | The utilization of Direct Control Load Management or curtailment of Interruptible Demand shall not contribute to the loss of Load probability. |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 11100000 | RF-US |  |  | RF-US
1. | 8225 | Perform an analysis for Year One. |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 12100000 | RF-US |  |  | RF-US
1. | 8227 | If the analysis is verified, the verification must be supported by current or past studies for the same planning year. |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 12210000 | RF-US |  |  | RF-US
1. | 8230 | Load forecast characteristics: |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 13100000 | RF-US |  |  | RF-US
1. | 8231 | Median (50:50) forecast peak Load. |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 13110000 | RF-US |  |  | RF-US
1. | 8238 | Historic resource performance and any projected changes |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 13210000 | RF-US |  |  | RF-US
1. | 8245 | Criteria for including planned Transmission Facility additions in the analysis |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 13310000 | RF-US |  |  | RF-US
1. | 8248 | Availability and deliverability of fuel. |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 14100000 | RF-US |  |  | RF-US
1. | 825 | Each Adjacent Reliability Coordinator and each Reliability Coordinator that indicated a reliability-related need for the methodology. |  | RC | [11 empty] | RC | [12 empty] | 2013-03-31 |  |  | FAC-012-1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8260 | This documentation shall cover each of the years in Year One through ten. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-16 | [5 empty] | 21000000 | RF-US |  |  | RF-US
1. | 8267 | PSS shall be set to provide the measured, simulated, or calculated compensated Vt/Vref frequency response of the excitation system and synchronous machine such that the phase angle will not exceed ± 30 degrees through the frequency range from 0.2 Hertz to the lesser of 1.0 Hertz or the highest frequency at which the phase of the Vt/Vref frequency response does not exceed 90 degrees. |  | GO | [22 empty] | 2017-09-26 |  |  |  | 5. Facilities: This standard applies to synchronous generators, connected to the Bulk Electric System, that meet the definition of Commercial Operation. |  | 31000000 | WECC-US | [5 empty] | WECC-US
1. | 829 | Each Transmission Planner that works in the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PA | [14 empty] | 2013-03-31 |  |  | FAC-012-1 R3. | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 83 | The Balancing Authority may use a fixed Frequency Bias value which is based on a fixed, straight-line function of Tie Line deviation versus Frequency Deviation. The Balancing Authority shall determine the fixed value by observing and averaging the Frequency Response for several Disturbances during on-peak hours. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2009-05-12 |  |  | BAL-003-0a R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8330 | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8331 | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  |  | 41100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8335 | If a recipient of the benchmark GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  |  | 43100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8337 | The maximum effective GIC value for the worst case geoelectric field orientation for the benchmark GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-01-01 |  | 2019-06-30 |  |  |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8340 | Be based on the effective GIC flow information provided in Requirement R5; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2019-06-30 |  |  |  | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8345 | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include:• Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment.• Installation, modification, or removal of Protection Systems or Remedial Action Schemes.• Use of Operating Procedures, specifying how long they will be needed as part of the CAP.• Use of Demand-Side Management, new technologies, or other initiatives. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  |  | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8348 | Specify implementation of non-hardware mitigation, if any, within two years of development of the CAP; and |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  |  | 73100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 835 | The Reliability Coordinator shall provide its Transfer Capabilities to its associated Regional Reliability Organization(s), to its adjacent Reliability Coordinators, and to the Transmission Operators, Transmission Service Providers and Planning Authorities that work in its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2013-03-31 |  |  | FAC-013-1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8351 | Circumstances causing the delay for fully or partially implementing the selected actions in Part 7.1; |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  |  | 74100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8355 | If a recipient of the CAP provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  |  | 75100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8357 | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  |  | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8358 | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  |  | 81100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8363 | If a recipient of the supplemental GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  |  | 84100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8365 | The maximum effective GIC value for the worst case geoelectric field orientation for the supplemental GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2019-01-25 |  | 2019-06-30 |  |  |  | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8368 | Be based on the effective GIC flow information provided in Requirement R9; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2019-06-30 |  |  |  | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8376 | For load-serving Balancing Authorities, 150% of the previous calendar year’s integrated hourly Peak Demand, |  | BA | BA | [21 empty] | 2018-05-30 | [5 empty] | 11000000 | WECC-US | [5 empty] | WECC-US
1. | 8381 | PIIhourly, |  | BA | BA | [21 empty] | 2018-05-30 | [5 empty] | 41000000 | WECC-US | [5 empty] | WECC-US
1. | 8391 | If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. |  | TOP | [18 empty] | TOP |  |  |  | 2014-08-01 |  | 2015-11-12 |  |  |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8396 | Areas of Competency |  | RC | [11 empty] | RC | [9 empty] | A list of Real-time operating positions. | 2018-11-21 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8397 | Resource and demand balancing |  | RC | [11 empty] | RC | [10 empty] | 2019-07-01 | [5 empty] | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8406 | Areas of Competency |  | TOP | [18 empty] | TOP |  |  |  | 2018-11-21 | [5 empty] | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8407 | Transmission operations |  | TOP | [18 empty] | TOP |  |  |  | 2019-07-01 | [5 empty] | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8414 | Areas of Competency |  | BA | BA | [21 empty] | 2018-11-21 | [5 empty] | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8415 | Resources and demand balancing |  | BA | BA | [21 empty] | 2019-07-01 | [5 empty] | 31100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 842 | The Reliability Coordinator shall provide its SOLs (including the subset of SOLs that are IROLs) to adjacent Reliability Coordinators and Reliability Coordinators who indicate a reliability-related need for those limits, and to the Transmission Operators, Transmission Planners, Transmission Service Providers and Planning Authorities within its Reliability Coordinator Area. For each IROL, the Reliability Coordinator shall provide the following supporting information: |  | RC | [11 empty] | RC | [10 empty] | 2008-05-29 |  | 2009-04-28 |  |  | FAC-014-1 R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8423 | within the Contingency Event Recovery Period, demonstrate recovery by returning its Reporting ACE to at least the recovery value of:• zero (if its Pre-Reporting Contingency Event ACE Value was positive or equal to zero); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event,or,• its Pre-Reporting Contingency Event ACE Value (if its Pre-Reporting Contingency Event ACE Value was negative); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2019-04-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8426 | is (i) a Balancing Authority or (ii) a Reserve Sharing Group with at least one member that:• is experiencing a Reliability Coordinator declared Energy Emergency Alert Level, and• is utilizing its Contingency Reserve to mitigate an operating emergency in accordance with its emergency Operating Plan, and• has depleted its Contingency Reserve to a level below its Most Severe Single Contingency, and• has, during communications with its Reliability Coordinator in accordance with the Energy Emergency Alert procedures, (i) notified the Reliability Coordinator of the conditions described in the preceding two bullet points preventing the Responsible Entity from complying with Requirement R1 part 1.1, and (ii) provided the Reliability Coordinator with an ACE recovery plan, including target recovery time or, |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2019-04-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 843 | Identification and status of the associated Facility (or group of Facilities) that is (are) critical to the derivation of the IROL. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-01 |  | 2009-04-28 |  |  |  | 51100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8430 | Identification of security protection used to mitigate the risks posed by unauthorized disclosure and unauthorized modification of Real-time Assessment and Real-time monitoring data while being transmitted between Control Centers; |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-04-13 |  |  |  | 4.2. Exemptions: The following are exempt from Reliability Standard CIP-012-1:4.2.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.2. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3. A Control Center that transmits to another Control Center Real-time Assessment or Real-time monitoring data pertaining only to the generation resource or Transmission station or substation co-located with the transmitting Control Center. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8434 | Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. |  | TOP | [18 empty] | TOP |  |  |  | 2018-10-15 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8440 | The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  | For part 5.1, the Transmission Operator shall have evidence it provided a voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the applicable Generator Operators, and that the Generator Operator was directed to comply with the schedule in automatic voltage control mode, unless exempted. | 2018-10-15 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8448 | Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances. |  | GOP | [5 empty] | GOP | [16 empty] | 2018-10-15 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | 2610000 | WECC-US | [5 empty] | WECC-US
1. | 8452 | System models shall represent: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-04-13 |  | 2020-06-10 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8453 | Existing Facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8459 | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by current annual studies or qualified past studies as indicated in Requirement R2, Part 2.6. Qualifying studies need to include the following conditions: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-04-13 |  | 2020-06-10 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8460 | System peak Load for either Year One or year two, and for year five. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8466 | A current study assessing expected System peak Load conditions for one of the years in the Long-Term Transmission Planning Horizon and the rationale for why that year was selected. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  |  | 22100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8469 | System peak Load for one of the five years. System peak Load levels shall include a Load model which represents the expected dynamic behavior of Loads that could impact the study area, considering the behavior of induction motor Loads. An aggregate System Load model which represents the overall dynamic behavior of the Load is acceptable. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  |  | 24100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8477 | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Installation or modification of automatic generation tripping as a response to a single or multiple Contingency to mitigate Stability performance violations. • Installation or modification of manual and automatic generation runback/tripping as a response to a single or multiple Contingency to mitigate steady state performance violations. • Use of Operating Procedures specifying how long they will be needed as part of the Corrective Action Plan. • Use of rate applications, DSM, new technologies, or other initiatives. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  |  | 27100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8482 | List System deficiencies and the associated actions needed to achieve required System performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  |  | 28100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8491 | Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R3, Part 3.4. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-04-13 |  | 2020-06-10 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8494 | Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  |  | 33100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8496 | Tripping of generators where simulations show generator bus voltages or high side of the generation step up (GSU) voltages are less than known or assumed minimum generator steady state or ride through voltage limitations. Include in the assessment any assumptions made. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  |  | 33110000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8500 | The Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  |  | 34100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8507 | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-3 - Attachment 1A, either for 60 seconds or until a steady-state condition between 59.0 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 11000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 851 | The Planning Authority shall provide this list of multiple contingencies and the associated stability limits to the Reliability Coordinators that monitor the facilities associated with these contingencies and limits. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-014-1 R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8511 | Underfrequency trip settings of individual generating units that are part of Quebec BES plants/facilities that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-3 - Attachment 1A, and |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 110000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8519 | One or more processes to identify, classify, and respond to Cyber Security Incidents. |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, dated documentation of Cyber Security Incident response plan(s) that include the process(es) to identify, classify, and respond to Cyber Security Incidents. | 2019-06-20 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8521 | That include criteria to evaluate and define attempts to compromise; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8527 | Test each Cyber Security Incident response plan(s) at least once every 15 calendar months: • By responding to an actual Reportable Cyber Security Incident; • With a paper drill or tabletop exercise of a Reportable Cyber Security Incident; or• With an operational exercise of a Reportable Cyber Security Incident. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated evidence of a lessons-learned report that includes a summary of the test or a compilation of notes, logs, and communication resulting from the test. Types of exercises may include discussion or operations based exercises. | 2019-06-20 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8532 | No later than 90 calendar days after completion of a Cyber Security Incident response plan(s) test or actual Reportable Cyber Security Incident response: |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, all of the following:1. Dated documentation of post incident(s) review meeting notes or follow-up report showing lessons learned associated with the Cyber Security Incident response plan(s) test or actual Reportable Cyber Security Incident response or dated documentation stating there were no lessons learned;2. Dated and revised Cyber Security Incident response plan showing any changes based on the lessons learned; and3. Evidence of plan update distribution including, but not limited to:• Emails; • USPS or other mail service; • Electronic distribution system; or • Training sign-in sheets. | 2019-06-20 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8533 | Document any lessons learned or document the absence of any lessons learned; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | 31100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8537 | Update the Cyber Security Incident response plan(s); and | [24 empty] | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | 32100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8539 | Initial notifications and updates shall include the following attributes, at a minimum, to the extent known: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of initial notifications and updates to the E-ISAC and NCCIC. | 2019-06-20 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8540 | The functional impact; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | 41100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8552 | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2020-10-05 |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8553 | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 41100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8557 | If a recipient of the benchmark GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 43100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8559 | The maximum effective GIC value for the worst case geoelectric field orientation for the benchmark GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-01-01 |  | 2020-10-05 |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8565 | Be based on the effective GIC flow information provided in Requirement R5; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2020-10-05 |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8570 | 7.1. List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include:• Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment.• Installation, modification, or removal of Protection Systems or Remedial Action Schemes.• Use of Operating Procedures, specifying how long they will be needed as part of the CAP.• Use of Demand-Side Management, new technologies, or other initiatives. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2020-10-05 |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8575 | Specify implementation of non-hardware mitigation, if any, within two years of development of the CAP; and |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 73100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8577 | Circumstances causing the delay for fully or partially implementing the selected actions in Part 7.1; |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 74100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8580 | If a recipient of the CAP provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 75100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8582 | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2020-10-05 |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8586 | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 81100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8588 | If a recipient of the supplemental GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 84100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8590 | The maximum effective GIC value for the worst case geoelectric field orientation for the supplemental GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-01-01 |  | 2020-10-05 |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8598 | Be based on the effective GIC flow information provided in Requirement R9; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2020-10-05 |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8604 | If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. |  | TOP | [18 empty] | TOP |  |  | For part 4.1, the Transmission Operator shall also have evidence to show that, for each generator in its area that is exempt: 1) from following a voltage or Reactive Power schedule, 2) from having its automatic voltage regulator (AVR) in service or from being in voltage control mode, or 3) from having to make any notifications, the associated Generator Operator was notified of this exemption. | 2019-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8606 | The Responsible Entity shall create, implement, and maintain cyber security testprocedures in a manner that minimizes adverse effects on the production system or its operation. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 11000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC | MRO-US | NPCC-US |  |  |  | WECC-US
1. | 8610 | The Responsible Entity shall enable only those ports and services required for normal and emergency operations. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 21000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC | MRO-US | NPCC-US |  |  |  | WECC-US
1. | 8614 | The Responsible Entity shall document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 31000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC | MRO-US | NPCC-US |  |  |  | WECC-US
1. | 8617 | The Responsible Entity shall document and implement anti-virus and malware prevention tools. In the case where anti-virus software and malware prevention tools are not installed, the Responsible Entity shall document compensating measure(s)applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 41000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC | MRO-US | NPCC-US |  |  |  | WECC-US
1. | 8620 | The Responsible Entity shall ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 51000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC | MRO-US | NPCC-US |  |  |  | WECC-US
1. | 8621 | The Responsible Entity shall ensure that user accounts are implemented as approved by designated personnel. Refer to Standard CIP-003-3 Requirement R5. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 51100000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC | MRO-US | NPCC-US |  |  |  | WECC-US
1. | 8625 | The policy shall include the removal, disabling, or renaming of such accounts where possible. For such accounts that must remain enabled, passwords shall be changed prior to putting any system into service. | [30 empty] | 52100000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC | MRO-US | NPCC-US |  |  |  | WECC-US
1. | 8629 | Each password shall be a minimum of six characters. | [30 empty] | 53100000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC | MRO-US | NPCC-US |  |  |  | WECC-US
1. | 8633 | The Responsible Entity shall implement and document the organizational processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the Electronic Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 61000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC | MRO-US | NPCC-US |  |  |  | WECC-US
1. | 8639 | Prior to the disposal of such assets, the Responsible Entity shall destroy or erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 71000000 | MRO-MB | MRO-US
1. | 8643 | A document identifying the vulnerability assessment process; | [30 empty] | 81000000 | MRO-MB | MRO-US
1. | 8649 | Specify implementation of non-hardware mitigation, if any, within two years of the later of the development of the CAP or receipt of regulatory approvals, if required; and | [24 empty] | 2019-07-01 |  |  |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 731000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC | MRO-US | NPCC-US |  |  |  | WECC-US
1. | 8658 | A method for development, maintenance, and periodic review of a Western Interconnection-wide reference model to serve as the baseline from which Reliability Coordinator’s operational models are derived |  | RC | [11 empty] | RC | [10 empty] | 2019-07-11 |  | 2021-03-31 |  | ApplicabilityAs used in this WECC Regional Variance, Reliability Coordinator is specific to those Reliability Coordinators providing Reliability Coordinator service(s) to entities operating within the Western Interconnection, regardless of where the Reliability Coordinator may be located. |  | 710000 | WECC-US | [5 empty] | WECC-US
1. | 867 | The Planning Authority shall provide this list of multiple contingencies and the associated stability limits to the Reliability Coordinators that monitor the facilities associated with these contingencies and limits. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  |  |  |  | FAC-014-2 R6. | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8672 | A method for development, maintenance, and periodic review of a Western Interconnection-wide reference model to serve as the baseline from which Reliability Coordinator’s operational models are derived; |  | RC | [11 empty] | RC | [10 empty] | 2021-04-01 | [5 empty] | 710000 | WECC-US | [5 empty] | WECC-US
1. | 8680 | For its high impact and medium impact BES Cyber Systems, if any: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8681 | Personnel and training (CIP-004); |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8691 | Cyber security awareness; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 87 | Fixed schedules for Jointly Owned Units mandate that Balancing Authority (A) that contains the Jointly Owned Unit must incorporate the respective share of the unit governor droop response for any Balancing Authorities that have fixed schedules (B and C). See the diagram below. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2009-05-12 |  |  | BAL-003-0a R4. | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 870 | Transmission Owners shall annually review their TMIP and update as required. [Time Horizon: Long-term Planning] |  | TO | [21 empty] | M1.1 Transmission Owners shall have evidence they have annually reviewed their TMIP and updated as needed. | 2011-06-27 |  | 2018-06-30 |  |  | FAC-501-WECC-1 R1. | 11000000 | WECC-US | [5 empty] | WECC-US
1. | 8700 | UFLS program, including a schedule for implementation |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8705 | Each Source and Sink Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if it does not expect to be capable of supporting the magnitude of the Interchange, including ramping, throughout the duration of the Arranged Interchange. |  | BA | BA | [21 empty] | 2021-04-01 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8707 | Each Transmission Service Provider shall deny the Arranged Interchange or curtail Confirmed Interchange if the transmission path (proper connectivity of adjacent Transmission Service Providers) between it and its adjacent Transmission Service Providers is invalid. |  | TSP | [20 empty] | TSP |  | 2021-04-01 | [5 empty] | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8712 | Identical in magnitude to that of the Adjacent Balancing Authority, and |  | BA | BA | [21 empty] | 2021-04-01 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8723 | The documentation shall contain assumptions used to rate the generator and at least one of the following:• Design or construction information such as design criteria, ratings provided by equipment manufacturers, equipment drawings and/or specifications, engineering analyses, method(s) consistent with industry standards (e.g. ANSI and IEEE), or an established engineering practice that has been verified by testing or engineering analysis.• Operational information such as commissioning test results, performance testing or historical performance records, any of which may be supplemented by engineering analyses. |  | GO | [24 empty] | 2021-02-04 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8725 | The methodology used to establish the Ratings of the equipment that comprises the Facility(ies) shall be consistent with at least one of the following:• Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating.• One or more industry standards developed through an open process such as Institute of Electrical and Electronic Engineers (IEEE) or International Council on Large Electric Systems (CIGRE).• A practice that has been verified by testing, performance history or engineering analysis. |  | GO | [24 empty] | 2021-02-04 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8729 | Equipment Rating standard(s) used in development of this methodology. |  | GO | [24 empty] | 2021-02-04 |  |  |  | 22100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8733 | The scope of equipment addressed shall include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | GO | [24 empty] | 2021-02-04 |  |  |  | 24100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8735 | The methodology used to establish the Ratings of the equipment that comprises the Facility shall be consistent with at least one of the following:• Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating.• One or more industry standards developed through an open process such as Institute of Electrical and Electronics Engineers (IEEE) or International Council on Large Electric Systems (CIGRE).• A practice that has been verified by testing, performance history or engineering analysis. |  | TO | [24 empty] | 2021-02-04 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 874 | All Dynamic Schedules at the expected average MW profile for each hour. |  | PSE | [10 empty] | PSE | [11 empty] | 2007-06-18 |  | 2008-08-26 |  |  | INT-001-2 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8740 | Equipment Rating standard(s) used in development of this methodology. |  | TO | [24 empty] | 2021-02-04 |  |  |  | 32100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8744 | The scope of equipment addressed shall include, but not be limited to, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | TO | [24 empty] | 2021-02-04 |  |  |  | 34100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8747 | The BES interrupting device operation was caused by a Protection System or by manual intervention in response to a Protection System failure to operate; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.2. Facilities:4.2.1 Protection Systems for BES Elements, with the following exclusions:4.2.1.1 Non-protective functions that are embedded within a Protection System.4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS).4.2.1.4 Remedial Action Schemes (RAS).4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8751 | For a BES interrupting device operation by a Composite Protection System or by manual intervention in response to a Protection System failure to operate, notification of the operation shall be provided to the other owner(s) that share Misoperation identification responsibility for the Composite Protection System under the following circumstances: |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.2. Facilities:4.2.1 Protection Systems for BES Elements, with the following exclusions:4.2.1.1 Non-protective functions that are embedded within a Protection System.4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS).4.2.1.4 Remedial Action Schemes (RAS).4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8752 | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.2. Facilities:4.2.1 Protection Systems for BES Elements, with the following exclusions:4.2.1.1 Non-protective functions that are embedded within a Protection System.4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS).4.2.1.4 Remedial Action Schemes (RAS).4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 876 | If a Purchasing-Selling Entity is not involved in the Interchange, such as delivery from a jointly owned generator. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  | INT-001-2 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8772 | Monitor Facilities within its Transmission Operator Area; |  | TOP | [18 empty] | TOP |  |  |  | 2021-04-01 | [5 empty] | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 879 | All Dynamic Schedules at the expected average MW profile for each hour. |  | PSE | [10 empty] | PSE | [11 empty] | 2008-08-27 |  | 2014-09-30 |  |  | INT-001-3 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8797 | Each control loop’s design incorporates the AVR’s automatic voltage controlled response to voltage deviations during System Disturbances. |  | GOP | [5 empty] | GOP | [18 empty] | 2020-05-14 |  |  |  | 2610000 | WECC-US | [5 empty] | WECC-US
1. | 8800 | Each Transmission Operator shall provide a copy of the voltage schedules (which is either a range or a target value with an associated tolerance band) to its Reliability Coordinator and adjacent Transmission Operators within 30 calendar days of a request. |  | TOP | [18 empty] | TOP | [5 empty] | 2020-05-14 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8804 | If a Transmission Operator determines that a generator has satisfied the exemption criteria, it shall notify the associated Generator Operator. |  | TOP | [18 empty] | TOP | [5 empty] | 2020-05-14 |  |  |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8806 | The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). |  | TOP | [18 empty] | TOP | [5 empty] | 2020-05-14 |  |  |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 881 | If a Purchasing-Selling Entity is not involved in the Interchange, such as delivery from a jointly owned generator. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2014-09-30 |  |  | INT-001-3 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8839 | The greater of either:• The amount of Contingency Reserve equal to the loss of the most severe single contingency;• The amount of Contingency Reserve equal to the sum of three percent of hourly integrated Load plus three percent of hourly integrated generation. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Part 1.1 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates its Contingency Reserve was maintained in accordance with the amounts identified in Requirement R1, Part 1.1, except within the first sixty minutes following an event requiring the activation of Contingency Reserve. Attachment A is a practical illustration showing how the generation amount may be calculated under Requirement R1.• Where Dynamic Schedules are used as part of the generation amount upon which Contingency Reserve is predicated, additional evidence of compliance with Requirement R1, Part 1.1 may include, but is not limited to, documentation showing a reciprocal acknowledgement as to which entity is carrying the reserves. This transfer may be all or some portion of the physical generator and is not limited to the entire physical capability of the generator. • Where Pseudo-Ties are used as part of the generation amount upon which Contingency Reserve is predicated, additional evidence of compliance with Requirement R1, Part 1.1, may include, but is not limited to, documentation accounting for the transfers included in the Pseudo-Ties. | 2021-06-28 |  |  |  | 4.1.2.1 The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group.4.1.2.2 The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | 11000000 | WECC-US | [5 empty] | WECC-US
1. | 884 | The Sending Balancing Authority and Receiving Balancing Authority shall agree on Interchange as received from the Interchange Authority, including: |  | BA | BA | [21 empty] | 2007-06-18 |  | 2011-03-31 |  |  | INT-003-2 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8847 | Less than zero at all times, and |  | BA, FRSG | BA |  |  | FRSG | [12 empty] | RSG | [5 empty] | 2020-07-15 |  |  |  | Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 885 | Interchange Schedule start and end time. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2011-03-31 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8907 | Design measures to prevent the generating unit from tripping directly or indirectly for underfrequency conditions above the appropriate generator tripping threshold curve in Figure 2. | [28 empty] | 4.1.3. Distribution Providers that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators4.1.4. Transmission Owners that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators |  | 121000000 | NPCC-US |  | NPCC-US
1. | 8909 | Each Generator Owner shall set the underfrequency protection to operate at the lowest frequency allowed by the plant design and licensing limitations. |  | GO | [22 empty] | 2020-02-18 |  |  |  | 4.1.3. Distribution Providers that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators4.1.4. Transmission Owners that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators |  | 131000000 | NPCC-US |  | NPCC-US
1. | 8913 | Set the underfrequency protection to operate at a frequency setting that is as low as possible in accordance with the plant design and licensing limitations but not greater than 57.8 Hz. |  | GO | [22 empty] | 2020-02-18 |  |  |  | 4.1.3. Distribution Providers that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators4.1.4. Transmission Owners that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators |  | 161000000 | NPCC-US |  | NPCC-US
1. | 893 | The average energy profile in an hour is greater than 250 MW and in that hour the actual hourly integrated energy deviates from the hourly average energy profile indicated on the tag by more than +10%. |  | PSE | [10 empty] | PSE | [11 empty] | 2007-06-18 |  | 2008-08-26 |  |  | INT-004-1 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8979 | Specify implementation of non-hardware mitigation, if any, within two years of the later of the development of the CAP or receipt of regulatory approvals, if required; and | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 731000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 898 | The average energy profile in an hour is greater than 250 MW and in that hour the actual hourly integrated energy deviates from the hourly average energy profile indicated on the tag by more than +10%. |  | PSE | [10 empty] | PSE | [11 empty] | 2008-08-27 |  | 2014-09-30 |  |  | INT-004-2 R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8985 | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8990 | If a recipient of the benchmark GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 43100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8992 | The maximum effective GIC value for the worst case geoelectric field orientation for the benchmark GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-03-19 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 8995 | Be based on the effective GIC flow information provided in Requirement R5; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 90 | Balancing Authorities that do not serve native load shall have a monthly average Frequency Bias Setting that is at least 1% of its estimated maximum generation level in the coming year per 0.1 Hz change. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2009-05-12 |  |  | BAL-003-0a R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9000 | 7.1. List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include:• Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment.• Installation, modification, or removal of Protection Systems or Remedial Action Schemes.• Use of Operating Procedures, specifying how long they will be needed as part of the CAP.• Use of Demand-Side Management, new technologies, or other initiatives. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9003 | Specify implementation of non-hardware mitigation, if any, within two years of development of the CAP; and | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 73100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9006 | Circumstances causing the delay for fully or partially implementing the selected actions in Part 7.1 and how those circumstances are beyond the control of the responsible entity; | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 74100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9011 | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9017 | If a recipient of the supplemental GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 83100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9019 | The maximum effective GIC value for the worst case geoelectric field orientation for the supplemental GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-03-19 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 902 | When a Balancing Authority or Reliability Coordinator initiates a Curtailment to Confirmed or Implemented Interchange for reliability, the Interchange Authority shall distribute the Arranged Interchange information for reliability assessment only to the Source Balancing Authority and the Sink Balancing Authority. |  | IA | [6 empty] | IA | [15 empty] | 2007-06-18 |  | 2008-08-26 |  |  | INT-005-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9022 | Be based on the effective GIC flow information provided in Requirement R9; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 101000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9030 | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include:• Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment.• Installation, modification, or removal of Protection Systems or Remedial Action Schemes.• Use of Operating Procedures, specifying how long they will be needed as part of the CAP.• Use of Demand-Side Management, new technologies, or other initiatives. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9033 | Specify implementation of non-hardware mitigation, if any, within two years of development of the CAP; and | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 113100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9036 | Circumstances causing the delay for fully or partially implementing the selected actions in Part 11.1 and how those circumstances are beyond the control of the responsible entity; | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 114100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 904 | When a Balancing Authority or Reliability Coordinator initiates a Curtailment to Confirmed or Implemented Interchange for reliability, the Interchange Authority shall distribute the Arranged Interchange information for reliability assessment only to the Source Balancing Authority and the Sink Balancing Authority. |  | IA | [6 empty] | IA | [15 empty] | 2008-08-27 |  | 2010-06-30 |  |  | INT-005-2 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9043 | Circumstances causing the delay for fully or partially implementing the selected actions in Part 7.1 and how those circumstances are beyond the control of the responsible entity; | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 741000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9047 | If a recipient of the CAP provides documented comments on the CAP, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 751000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9049 | Specify implementation of non-hardware mitigation, if any, within two years of the later of the development of the CAP or receipt of regulatory approvals, if required; and | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 2031000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9052 | Circumstances causing the delay for fully or partially implementing the selected actions in Part 11.1 and how those circumstances are beyond the control of the responsible entity; | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 2041000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9056 | If a recipient of the CAP provides documented comments on the CAP, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 2051000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9058 | The reliability impact of the new interconnection, or materially modified existing interconnection, on affected system(s); |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2021-04-01 |  |  |  | Applicable Generator Owner: Generator Owner with a fully executed Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 906 | When a Balancing Authority or Reliability Coordinator initiates a Curtailment to Confirmed or Implemented Interchange for reliability, the Interchange Authority shall distribute the Arranged Interchange information for reliability assessment only to the Source Balancing Authority and the Sink Balancing Authority. |  | IA | [6 empty] | IA | [15 empty] | 2010-01-25 |  | 2014-09-30 |  |  | INT-005-3 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9067 | A list of data and information needed by the Reliability Coordinator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data, as deemed necessary by the Reliability Coordinator. |  | RC | [11 empty] | RC | [10 empty] | 2021-04-01 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9073 | A mutually agreeable format |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2021-04-01 | [5 empty] | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9077 | A list of Transmission Planners, Balancing Authorities, and Distribution Providers that are required to provide the data (“Applicable Entities”). |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 908 | Each involved Balancing Authority shall evaluate the Arranged Interchange with respect to: |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  | INT-006-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9080 | Integrated hourly Demands in megawatts for the prior calendar year. | [24 empty] | 2021-04-01 | [5 empty] | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9082 | If the annual peak hour actual Demand varies due to weather-related conditions (e.g., temperature, humidity or wind speed), the Applicable Entity shall also provide the weather normalized annual peak hour actual Demand for the prior calendar year. | [24 empty] | 2021-04-01 | [5 empty] | 13210000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9086 | Monthly peak hour forecast Total Internal Demands in megawatts for the next two calendar years. | [24 empty] | 2021-04-01 | [5 empty] | 14100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 909 | Energy profile (ability to support the magnitude of the Interchange). |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9100 | If the Applicable Entity does not provide data requested because (1) the requesting entity did not demonstrate a reliability need for the data; or (2) providing the data would conflict with the Applicable Entity’s confidentiality, regulatory, or security requirements, the Applicable Entity shall, within 30 calendar days of the written request, provide a written response to the requesting entity specifying the data that is not being provided and on what basis. |  | BA, DP, PCPA, RP, TP | BA | DP | [7 empty] | PA |  |  |  | RP | [5 empty] | TP |  |  | 2021-04-01 | [5 empty] | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9102 | Comparison of the performance of the Planning Coordinator’s portion of the existing system in a planning power flow model to actual system behavior, represented by a state estimator case or other Real-time data sources, at least once every 24 calendar months through simulation; |  | PCPA | [9 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9111 | Incorporate the NPIRs into their operating analyses of the electric system. |  | BA, DP, GO, GOP, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  |  |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9119 | Retired. [Note: Part 9.1 was retired under the Paragraph 81 project. The NUC SDT proposes to leave this Part blank to avoid renumbering Requirement parts that would impact existing agreements throughout the industry.] |  | BA, DP, GO, GOP, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  |  |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9121 | Identification of parameters, limits, configurations, and operating scenarios included in the NPIRs and, as applicable, procedures for providing any specific data not provided within the Agreement. | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 92100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9125 | Designation of ownership of electrical facilities at the interface between the electric system and the nuclear plant and responsibilities for operational control coordination and maintenance of these facilities. | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 93100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9133 | Provisions for communications affecting the NPIRs between the Nuclear Plant Generator Operator and Transmission Entities, including communications protocols, notification time requirements, and definitions of applicable unique terms | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 94100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9139 | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-4 - Attachment 1A, either for 60 seconds or until a steady-state condition between 59.0 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 310000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 914 | Each involved Balancing Authority shall evaluate the Arranged Interchange with respect to: |  | BA | BA | [21 empty] | 2008-08-27 |  | 2010-06-30 |  |  | INT-006-2 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9143 | Underfrequency trip settings of individual generating units that are part of Quebec BES plants/facilities that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1A, and |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 410000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9148 | Those islands selected by applying the criteria in Requirement D.B.1, and |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 210000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 915 | Energy profile (ability to support the magnitude of the Interchange). |  | BA | BA | [21 empty] | 2008-08-27 |  | 2010-06-30 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9151 | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-4 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 310000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9154 | Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES | [26 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 331000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9158 | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1. |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 410000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9166 | The performance of the UFLS equipment, |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 2010000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9171 | Those islands selected by applying the criteria in Requirement R1, and |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9175 | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-4 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9179 | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1. |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9193 | The performance of the UFLS equipment, |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 111000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9198 | UFLS program, including a schedule for implementation |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 141000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 920 | Each involved Balancing Authority shall evaluate the Arranged Interchange with respect to: |  | BA | BA | [21 empty] | 2010-01-25 |  | 2014-09-30 |  |  | INT-006-3 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9202 | For UFLS design assessments performed under Requirement R4 or R5, the Corrective Action Plan shall be developed within the five-year time frame identified in Requirement R4. |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 151000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9205 | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data as deemed necessary by the Transmission Operator. |  | TOP | [18 empty] | TOP |  |  |  | 2021-04-01 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 921 | Energy profile (ability to support the magnitude of the Interchange). |  | BA | BA | [21 empty] | 2010-07-01 |  | 2014-09-30 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9210 | A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. |  | BA | BA | [21 empty] | 2021-04-01 | [5 empty] | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9217 | A mutually agreeable format |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  |  | 2021-04-01 | [5 empty] | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9223 | The Generator Owner shall communicate the documented regulatory or equipment limitation, or the removal of a previously documented regulatory or equipment limitation, to its Planning Coordinator and Transmission Planner within 30 calendar days of any of the following:• Identification of a regulatory or equipment limitation.• Repair of the equipment causing the limitation that removes the limitation. • Replacement of the equipment causing the limitation with equipment that removes the limitation.• Creation or adjustment of an equipment limitation caused by consumption of the cumulative turbine life-time frequency excursion allowance. |  | GO | [22 empty] | 2020-07-09 |  |  |  | 4.1. Functional Entities: 4.1.1 Generator Owners that apply protection listed in Section 4.2.1. 4.1.2 Transmission Owners (in the Quebec Interconnection only) that own a BES generator step-up (GSU) transformer or main power transformer (MPT)1 and apply protection listed in Section 4.2.1. 4.1.3 Planning Coordinators (in the Quebec Interconnection only) 4.2. Facilities2: 4.2.1 Frequency, voltage, and volts per hertz protection (whether provided by relaying or functions within associated control systems) that respond to electrical signals and: (i) directly trip the generating resource(s); or (ii) provide signals to the generating resource(s) to either trip or cease injecting current; and are applied to the following:4.2.1.1 BES generating resource(s). 4.2.1.2 BES GSU transformer(s). 4.2.1.3 High side of the generator-connected unit auxiliary transformer3 (UAT) installed on BES generating resource(s). 4.2.1.4 Individual dispersed power producing resource(s) identified in the BES Definition, Inclusion I4. 4.2.1.5 Elements that are designed primarily for the delivery of capacity from the individual dispersed power producing resources identified in the BES Definition, Inclusion I4, to the point where those resources aggregate to greater than 75 MVA. 4.2.1.6 MPT4 of resource(s) identified in the BES Definition, Inclusion I4. 4.2.2 Exemptions: Protection on all auxiliary equipment within the generating Facility. 1 For the purpose of this standard, the MPT is the power transformer that steps up voltage from the collection system voltage to the nominal transmission/interconnecting system voltage for dispersed power producing resources. 2 It is not required to install or activate the protections described in Facilities Section 4.2. 3 These transformers are variably referred to as station power UAT, or station service transformer(s) used to provide overall auxiliary power to the generating resource(s). This UAT is the transformer connected on the generator bus between the low side of the GSU and the generator terminal. 4 For the purpose of this standard, the MPT is the power transformer that steps up voltage from the collection system voltage to the nominal transmission/interconnecting system voltage for dispersed power producing resources |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9229 | The performance of a combined cycle facility will be determined using an expected performance droop of 5.78%., |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [16 empty] | 2020-05-19 |  |  |  | 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL001-TRE-2. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-2. 4.2.3 Any generators that are not required by the Balancing Authority to provide primary frequency response are exempt from this standard. |  | 21000000 | TXRE-US |  |  |  |  | TXRE-US
1. | 9236 | Limit Governor deadbands within those listed in Table 6.1, unless directed otherwise by the Balancing Authority. (see standard for table) |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [16 empty] | 2020-05-19 |  |  |  | 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL001-TRE-2. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-2. 4.2.3 Any generators that are not required by the Balancing Authority to provide primary frequency response are exempt from this standard. |  | 61000000 | TXRE-US |  |  |  |  | TXRE-US
1. | 9242 | The initial Primary Frequency Response performance shall be the ratio of the Actual Primary Frequency Response to the Expected Primary Frequency Response during the initial measurement period following the FME. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [16 empty] | 2020-05-19 |  |  |  | 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL001-TRE-2. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-2. 4.2.3 Any generators that are not required by the Balancing Authority to provide primary frequency response are exempt from this standard. |  | 91000000 | TXRE-US |  |  |  |  | TXRE-US
1. | 9246 | The sustained Primary Frequency Response performance shall be the ratio of the Actual Primary Frequency Response to the Expected Primary Frequency Response during the sustained measurement period followingthe FME. |  | GO | [22 empty] | 2020-05-19 |  |  |  | 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL001-TRE-2. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-2. 4.2.3 Any generators that are not required by the Balancing Authority to provide primary frequency response are exempt from this standard. |  | 101000000 | TXRE-US |  |  |  |  | TXRE-US
1. | 9254 | Identify each of the high impact BES Cyber System according to Attachment 1, Section 1, if any, at each asset; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [5 empty] | 2021-02-04 |  |  |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9258 | Review the identifications in Requirement R1 and its parts (and update them if there are changes identified) at least once every 15 calendar months, even if it has no identified items in Requirement R1, and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [5 empty] | 2021-02-04 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 926 | Source Balancing Authority megawatts equal sink Balancing Authority megawatts (adjusted for losses, if appropriate). |  | IA | [6 empty] | IA | [15 empty] | 2007-06-18 |  | 2014-09-30 |  |  | INT-007-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 929 | Generation source and load sink. |  | IA | [6 empty] | IA | [15 empty] | 2007-06-18 |  | 2014-09-30 |  |  |  | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9296 | System models shall represent: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 93 | The Balancing Authority may change its Frequency Bias Setting, and the method used to determine the setting, whenever any of the factors used to determine the current bias value change. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2009-06-28 |  |  | BAL-003-0b R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9303 | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by current annual studies or qualified past studies as indicated in Requirement R2, Part 2.6. Qualifying studies need to include the following conditions: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9329 | Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R3, Part 3.4. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 935 | For Confirmed Interchange, the Interchange Authority shall also communicate: |  | IA | [6 empty] | IA | [15 empty] | 2007-06-18 |  | 2008-08-26 |  |  | INT-008-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9350 | Those islands selected by applying the criteria in Requirement D.B.1, and |  | PCPA | [9 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 210000 | WECC-US | [5 empty] | WECC-US
1. | 9355 | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-5 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 310000 | WECC-US | [5 empty] | WECC-US
1. | 936 | Start and stop times, ramps, and megawatt profile to Balancing Authorities. |  | IA | [6 empty] | IA | [15 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9366 | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-5 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 410000 | WECC-US | [5 empty] | WECC-US
1. | 9376 | The performance of the UFLS equipment, |  | PCPA | [9 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 2010000 | WECC-US | [5 empty] | WECC-US
1. | 939 | For Confirmed Interchange, the Interchange Authority shall also communicate: |  | IA | [6 empty] | IA | [15 empty] | 2008-08-27 |  | 2010-06-30 |  |  | INT-008-2 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 940 | Start and stop times, ramps, and megawatt profile to Balancing Authorities. |  | IA | [6 empty] | IA | [15 empty] | 2008-08-27 |  | 2010-06-30 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 943 | For Confirmed Interchange, the Interchange Authority shall also communicate: |  | IA | [6 empty] | IA | [15 empty] | 2010-01-25 |  | 2014-09-30 |  |  | INT-008-3 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9432 | One or more process(es) used in planning for the procurement of BES Cyber Systems and their associated EACMS and PACS to identify and assess cyber security risk(s) to the Bulk Electric System from vendor products or services resulting from: (i) procuring and installing vendor equipment and software; and (ii) transitions from one vendor(s) to another vendor(s). |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 944 | Start and stop times, ramps, and megawatt profile to Balancing Authorities. |  | IA | [6 empty] | IA | [15 empty] | 2010-07-01 |  | 2014-09-30 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9451 | All applicable Cyber Assets connected to a network via a routable protocol shall reside within a defined ESP. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9456 | For all Interactive Remote Access, utilize an Intermediate System such that the Cyber Asset initiating Interactive Remote Access does not directly access an applicable Cyber Asset. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9461 | Have one or more method(s) to determine authenticated vendor-initiated remote connections. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9463 | Develop a baseline configuration, individually or by group, which shall include the following items: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9464 | Operating system(s) (including version) or firmware where no independent operating system exists; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9482 | Monitor at least once every 35 calendar days for changes to the baseline configuration (as described in Requirement R1, Part 1.1). Document and investigate detected unauthorized changes. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 9483 | At least once every 15 calendar months, conduct a paper or active vulnerability assessment. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 96 | The Balancing Authority may use a fixed Frequency Bias value which is based on a fixed, straight-line function of Tie Line deviation versus Frequency Deviation. The Balancing Authority shall determine the fixed value by observing and averaging the Frequency Response for several Disturbances during on-peak hours. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2009-06-28 |  |  | BAL-003-0b R2. | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | 996 | Current status of Bulk Electric System elements (transmission or generation including critical auxiliaries such as Automatic Voltage Regulators and Special Protection Systems) and system loading. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  | IRO-005-1 R1. | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-05-26-0000001 | A list of all entities to notify when there is a change in operating locations. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  |  | 16001000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-03-0000001 | When notified of the loss of an automatic voltage regulator control, theTransmission Operator shall direct the Generator Operator to maintain or changeeither its voltage schedule or its Reactive Power schedule. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-09-30 |  |  |  | 60100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-03-0000002 | When notified of the loss of an automatic voltage regulator control, theTransmission Operator shall direct the Generator Operator to maintain or changeeither its voltage schedule or its Reactive Power schedule. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-05-21 |  |  |  | 60100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-03-0000003 | When notified of the loss of an automatic voltage regulator control, theTransmission Operator shall direct the Generator Operator to maintain or changeeither its voltage schedule or its Reactive Power schedule. |  | TOP | [18 empty] | TOP |  |  |  | 2011-10-01 |  | 2013-12-31 |  |  |  | 60100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-03-0000004 | When notified of the loss of an automatic voltage regulator control, theTransmission Operator shall direct the Generator Operator to maintain or changeeither its voltage schedule or its Reactive Power schedule. |  | TOP | [18 empty] | TOP |  |  |  | 2014-01-01 |  | 2014-09-30 |  |  |  | 60100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-03-0000005 | When a generator’s automatic voltage regulator is out of service, the GeneratorOperator shall use an alternative method to control the generator voltage and reactiveoutput to meet the voltage or Reactive Power schedule directed by the TransmissionOperator. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-08-02 |  | 2008-08-26 |  |  |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-03-0000007 | When a generator’s automatic voltage regulator is out of service, the GeneratorOperator shall use an alternative method to control the generator voltage and reactiveoutput to meet the voltage or Reactive Power schedule directed by the TransmissionOperator. |  | GOP | [5 empty] | GOP | [16 empty] | 2009-05-13 |  | 2010-09-15 |  |  |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-03-0000009 | When a generator’s automatic voltage regulator is out of service, the GeneratorOperator shall use an alternative method to control the generator voltage and reactiveoutput to meet the voltage or Reactive Power schedule directed by the TransmissionOperator. |  | GOP | [5 empty] | GOP | [16 empty] | 2010-09-16 |  | 2013-06-30 |  |  |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-03-0000011 | When a generator’s automatic voltage regulator is out of service, the GeneratorOperator shall use an alternative method to control the generator voltage and reactiveoutput to meet the voltage or Reactive Power schedule directed by the TransmissionOperator. |  | GOP | [5 empty] | GOP | [16 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-03-0000013 | When a generator’s automatic voltage regulator is out of service, the GeneratorOperator shall use an alternative method to control the generator voltage and reactive output to meet the voltage or Reactive Power schedule directed by the TransmissionOperator. |  | GOP | [5 empty] | GOP | [16 empty] | 2013-07-01 |  | 2014-09-30 |  |  |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-08-0000001 | A minimum of 10% shall be shed at each UFLS step in accordance with the table below. See standard for table. |  | DP, TO |  | DP | [22 empty] | 2013-11-07 |  |  |  | 10100000 | SPPRE-US
1. | RP-2021-06-08-0000004 | A minimum of one UFLS step with the frequency set point as assigned by the Planning Coordinator. |  | DP, TO |  | DP | [22 empty] | 2013-11-07 |  |  |  | 20100000 | SPPRE-US
1. | RP-2021-06-08-0000008 | Location of installed UFLS equipment |  | DP, TO |  | DP | [22 empty] | 2013-11-07 |  |  |  | 50100000 | SPPRE-US
1. | RP-2021-06-08-0000016 | Location of underfrequency and overfrequency equipment |  | GO | [24 empty] | 2013-11-07 |  |  |  | 60100000 | SPPRE-US
1. | RP-2021-06-08-0000021 | For generating units with operating characteristics that limit the unit’s ability to perform in accordance with R7, the Generator Owner shall provide to the Planning Coordinator technical evidence demonstrating that the unit cannot operate within the specified frequency range without causing equipment damage or violating manufacturer’s published equipment ratings. |  | GO | [24 empty] | 2013-11-07 |  |  |  | 70100000 | SPPRE-US
1. | RP-2021-06-08-0000022 | The Planning Coordinator shall determine if the UFLS program performance is degraded due to the removal of any generation identified in accordance with R7.1 and verified in accordance with R8. |  | PCPA | [9 empty] | PA | [14 empty] | 2013-11-07 |  |  |  | 80100000 | SPPRE-US
1. | RP-2021-06-09-0000004 | For a generator outage, the Generator Operator shall notify and coordinate with theTransmission Operator. The Transmission Operator shall notify the ReliabilityCoordinator and other affected Transmission Operators, and coordinate the impact ofremoving the Bulk Electric System facility. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 70100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-11-0000001 | Transmission Owners shall annually review their TMIP and update as required. |  | TO | [22 empty] | 2011-07-01 |  | 2018-06-30 |  |  |  | 10100000 | WECC-US | [5 empty] | WECC-US
1. | RP-2021-06-14-0000012 | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained within ninety calendar days of such authorization. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-14-0000015 | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2012-12-11 |  |  |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-14-0000018 | This program will ensure that all personnel having such access to Critical Cyber Assets, including contractors and service vendors, are trained prior to their being granted such access except in specified circumstances such as an emergency. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-14-0000020 | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-14-0000023 | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-14-0000026 | These processes and mechanisms shall use an access control model that denies access by default, such that explicit access permissions must be specified. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-15-0000005 | These processes and mechanisms shall use an access control model that denies accessby default, such that explicit access permissions must be specified. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-15-0000037 | Movement of applicable line conductors under their Rating andall Rated Electrical Operating Conditions; |  | TO | [22 empty] | 2014-07-01 |  | 2013-11-25 |  |  |  | 30100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-16-0000001 | The documentation shall contain assumptions used to rate the generator and at least one of the following: • Design or construction information such as design criteria, ratings provided by equipment manufacturers, equipment drawings and/or specifications, engineering analyses, method(s) consistent with industry standards (e.g. ANSI and IEEE), or an established engineering practice that has been verified by testing or engineering analysis. • Operational information such as commissioning test results, performance testing or historical performance records, any of which may be supplemented by engineering analyses. |  | GO | [24 empty] | 2011-05-24 |  |  |  | 10100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-16-0000003 | The methodology used to establish the Ratings of the equipment that comprises the Facility(ies) shall be consistent with at least one of the following:• Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating.• One or more industry standards developed through an open process such as Institute of Electrical and Electronic Engineers (IEEE) or International Council on Large Electric Systems (CIGRE).• A practice that has been verified by testing, performance history or engineering analysis. |  | GO | [24 empty] | 2011-05-24 |  |  |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-16-0000013 | The methodology used to establish the Ratings of the equipment that comprises the Facility shall be consistent with at least one of the following:• Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating.• One or more industry standards developed through an open process such as Institute of Electrical and Electronics Engineers (IEEE) or International Council on Large Electric Systems (CIGRE).• A practice that has been verified by testing, performance history or engineering analysis. |  | TO | [24 empty] | 2011-05-24 |  |  |  | 30100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-16-0000026 | within the Contingency Event Recovery Period, demonstrate recovery by returning its Reporting ACE to at least the recovery value of: • zero (if its Pre-Reporting Contingency Event ACE Value was positive or equal to zero); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event, or, • its Pre-Reporting Contingency Event ACE Value (if its Pre-Reporting Contingency Event ACE Value was negative); however, any Balancing Contingency Event that occurs during the Contingency Event Recovery Period shall reduce the required recovery: (i) beginning at the time of, and (ii) by the magnitude of, such individual Balancing Contingency Event. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2018-01-01 |  | 2019-03-31 |  |  |  | 10100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-16-0000027 | Calculate a planning reserve margin that will result in the sum of the probabilities for loss of Load for the integrated peak hour for all days of each planning year1 analyzed (per R1.2) being equal to 0.1. (This is comparable to a “one day in 10 year” criterion). |  | PCPA | [9 empty] | PA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  |  | 10100000 | RF-US |  |  | RF-US
1. | RP-2021-06-16-0000044 | This documentation shall cover each of the years in Year One through ten. |  | PCPA | [9 empty] | PA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  |  | 20100000 | RF-US |  |  | RF-US
1. | RP-2021-06-17-0000008 | These processes and mechanisms shall use an access control model that denies accessby default, such that explicit access permissions must be specified. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-17-0000012 | Utilize an Intermediate System suchthat the Cyber Asset initiatingInteractive Remote Access does notdirectly access an applicable CyberAsset. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-18-0000001 | Where technically feasible, enable only logical network accessible ports that have been determined to be needed by the Responsible Entity, including port ranges or services where needed to handle dynamic ports. If a device has no provision for disabling or restricting logical ports on the device then those ports that are open are deemed needed. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 10100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-18-0000008 | Develop a baseline configuration,individually or by group, which shallinclude the following items: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 10100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-18-0000015 | Unique characteristics of the identified and verified Transmission station(s),Transmission substation(s), and primary control center(s); |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  |  | 40100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-21-0000004 | Generation Facilities, |  | TO | [22 empty] | 2013-11-25 |  | 2015-12-31 |  |  |  | 10100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-21-0000007 | Provide a written summary of its plans to achieve the required system performance asdescribed in Requirements R1 or R2 throughout the planning horizon: |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-11-25 |  | 2015-12-31 |  |  |  | 30100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-22-0000005 | These Operating Procedures, Processes, or Plans shall collectively address, as aminimum, the following: |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 10100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-22-0000033 | Use the models provided by the Transmission Operator. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 50100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-23-0000005 | Within six months of a modification of the BES company-specific reliability-related tasks, each Reliability Coordinator, Balancing Authority and Transmission Operator shall verify each of its System Operator’s capabilities to perform the new or modified tasks. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2013-04-01 |  | 2016-06-30 |  |  |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-23-0000010 | All transmission lines. |  | TO | [22 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 20100000 | NPCC-US |  | NPCC-US
1. | RP-2021-06-23-0000016 | Three phase-to-neutral voltages. (Common bus-side voltages may be used for lines.) |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 50100000 | NPCC-US |  | NPCC-US
1. | RP-2021-06-23-0000018 | Type of DME. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 170100000 | NPCC-US |  | NPCC-US
1. | RP-2021-06-23-0000032 | Those islands selected by applying the criteria in Requirement R1, and |  | PCPA | [9 empty] | PA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-23-0000035 | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  |  | 40100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-23-0000038 | UFLS program, including a schedule for implementation |  | PCPA | [9 empty] | PA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  |  | 140100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-23-0000040 | Those islands selected by applying the criteria in Requirement R1, and |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-10-01 |  | 2017-09-30 |  |  |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-23-0000041 | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-10-01 |  | 2017-09-30 |  |  |  | 40100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-23-0000044 | UFLS program, including a schedule for implementation |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2015-10-01 |  | 2017-09-30 |  |  |  | 140100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-24-0000001 | Those islands selected by applying the criteria in Requirement R1, and |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-24-0000003 | Underfrequency trip settings of individual generating units greater than 20 MVA(gross nameplate rating) directly connected to the BES that trip above theGenerator Underfrequency Trip Modeling curve in PRC-006-3 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 40100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-24-0000006 | UFLS program, including a schedule for implementation |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 140100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-24-0000008 | Those islands selected by applying the criteria in Requirement R1, and |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-24-0000010 | Underfrequency trip settings of individual generating units greater than 20 MVA(gross nameplate rating) directly connected to the BES that trip above theGenerator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1. |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 40100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-24-0000013 | UFLS program, including a schedule for implementation |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 140100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-24-0000020 | Underfrequency trip set points (Hz) |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2014-04-01 |  | 2017-12-31 |  |  |  | 70100000 | SERC-US |  |  |  | SERC-US
1. | RP-2021-06-24-0000024 | The UVLS Program resolvesthe identified undervoltage issuesfor whichthe UVLS Program is designed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2017-04-01 |  | 2017-04-01 |  |  |  | 30100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-24-0000029 | Within its Transmission Operator Area, monitor Facilities and the status ofSpecial Protection Systems, and |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 |  | 2018-06-30 |  |  |  | 100100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-24-0000054 | If a recipient of the Planning Assessment results provides documentedcomments on the results, the respective Planning Coordinator orTransmission Planner shall provide a documented response to that recipientwithin 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-07-01 |  | 2020-06-10 |  |  |  | 80100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-24-0000055 | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities:4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 40100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-24-0000056 | Be based on the effective GIC flow information provided in Requirement R9; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2019-06-30 |  |  |  | 100100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-24-0000057 | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  |  | 40100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-24-0000059 | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 40100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-24-0000060 | The Transmission Operator shall provide the voltage or Reactive Power schedule (which iseither a range or a target value with an associated tolerance band) to the associated GeneratorOperator and direct the Generator Operator to comply with the schedule in automatic voltagecontrol mode (the AVR is in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  |  | 2014-10-01 |  | 2015-11-12 |  |  |  | 50100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-24-0000063 | The Transmission Operator shall provide the voltage or Reactive Power schedule (which iseither a range or a target value with an associated tolerance band) to the associated GeneratorOperator and direct the Generator Operator to comply with the schedule in automatic voltagecontrol mode (the AVR is in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-25 |  |  |  | 50100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-24-0000066 | The Transmission Operator shall provide the voltage or Reactive Power schedule (which iseither a range or a target value with an associated tolerance band) to the associatedGenerator Operator and direct the Generator Operator to comply with the schedule inautomatic voltage control mode (the AVR is in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  |  | 2017-09-26 |  | 2018-12-31 |  |  |  | 50100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-24-0000069 | The Transmission Operator shall provide the voltage or Reactive Powerschedule (which is either a range or a target value with an associated toleranceband) to the associated Generator Operator and direct the Generator Operatorto comply with the schedule in automatic voltage control mode (the AVR is inservice and controlling voltage). |  | TOP | [18 empty] | TOP | [5 empty] | 2020-05-14 |  |  |  | 50100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-24-0000072 | When a generator’s AVR is out of service or the generator does not have an AVR, theGenerator Operator shall use an alternative method to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the TransmissionOperator. |  | GOP | [5 empty] | GOP | [16 empty] | 2014-10-01 |  | 2015-05-28 |  |  |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-24-0000074 | When a generator’s AVR is out of service or the generator does not have anAVR, the Generator Operator shall use an alternative method to control thegenerator reactive output to meet the voltage or Reactive Power scheduleprovided by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-05-29 |  | 2017-09-25 |  |  |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-24-0000076 | The synchronous generator or synchronous condenser operates for less than fivepercent of all hours during any calendar quarter. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-07-01 |  | 2015-03-31 |  |  |  | 10100000 | WECC-US | [5 empty] | WECC-US
1. | RP-2021-06-24-0000078 | 1.1. Roles and responsibilities for activating the Operating Plan(s); |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 10100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-24-0000088 | Roles and responsibilities for activating the Operating Plan(s); |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-24-0000105 | Within 30 calendar days of receipt, the Reliability Coordinator shall: |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 30100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-24-0000109 | Generating unit(s) freeze protection measures based on geographical location and plant configuration; |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 70100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-24-0000121 | A list of data and information needed by the Reliability Coordinator to support its Operational Planning Analyses, Real-time monitoring, and Real- time Assessments including non-BES data and external network data, as deemed necessary by the Reliability Coordinator. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 10100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-24-0000135 | A mutually agreeable format |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 30100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-24-0000138 | A list of data and information needed by the Transmission Operator to support its Operational Planning Analyses, Real-time monitoring, and Real-time Assessments including non-BES data and external network data as deemed necessary by the Transmission Operator. |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 10100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-24-0000152 | A list of data and information needed by the Balancing Authority to support its analysis functions and Real-time monitoring. |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-24-0000167 | A mutually agreeable format |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 50100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-25-0000001 | The synchronous generator or synchronous condenser operates for less than five percent of all hours during any calendar quarter. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2015-04-01 |  | 2018-09-05 |  |  |  | 10100000 | WECC-US | [5 empty] | WECC-US
1. | RP-2021-06-25-0000008 | The synchronous generator operates for less than five percent of all hours during any calendar quarter. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-07-01 |  | 2015-03-31 |  |  |  | 10100000 | WECC-US | [5 empty] | WECC-US
1. | RP-2021-06-25-0000009 | The synchronous generator operates for less than five percent of all hours during any calendar quarter. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-04-01 |  | 2017-06-30 |  |  |  | 10100000 | WECC-US | [5 empty] | WECC-US
1. | RP-2021-06-29-0000001 | The sustained Primary Frequency Response performance shall be the ratio of the Actual Primary Frequency Response to the Expected Primary Frequency Response during the sustained measurement period following the FME. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [16 empty] | 2014-04-01 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01.4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. |  | 100100000 | TXRE-US |  |  |  |  | TXRE-US
1. | RP-2021-06-29-0000002 | The sustained Primary Frequency Response performance shall be the ratio of theActual Primary Frequency Response to the Expected Primary FrequencyResponse during the sustained measurement period following the FME. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [16 empty] | 2020-07-01 |  |  |  | 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL001-TRE-2. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-2. 4.2.3 Any generators that are not required by the Balancing Authority to provide primary frequency response are exempt from this standard. |  | 100100000 | TXRE-US |  |  |  |  | TXRE-US
1. | RP-2021-06-29-0000003 | within the Contingency Event Recovery Period, demonstrate recovery byreturning its Reporting ACE to at least the recovery value of: zero (if its Pre-Reporting Contingency Event ACE Value was positive orequal to zero); however, any Balancing Contingency Event that occursduring the Contingency Event Recovery Period shall reduce the requiredrecovery: (i) beginning at the time of, and (ii) by the magnitude of, suchindividual Balancing Contingency Event,or, its Pre-Reporting Contingency Event ACE Value (if its Pre-ReportingContingency Event ACE Value was negative); however, any BalancingContingency Event that occurs during the Contingency Event RecoveryPeriod shall reduce the required recovery: (i) beginning at the time of, and(ii) by the magnitude of, such individual Balancing Contingency Event. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2019-04-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | 10100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-29-0000007 | This documentation shall cover each of the years in Year One through ten. |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 20100000 | RF-US |  |  | RF-US
1. | RP-2021-06-30-0000001 | Training content on: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-30-0000010 | Where technically feasible, enable only logical network accessible ports that have been determined to be needed by the Responsible Entity, including port ranges or services where needed to handle dynamic ports. If a device has no provision for disabling or restricting logical ports on the device then those ports that are open are deemed needed. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 10100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-30-0000043 | Subsequent risk assessments shall be performed:• At least once every 30 calendar months for a Transmission Owner that has identified in its previous risk assessment (as verified according to Requirement R2) one or more Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection; or • At least once every 60 calendar months for a Transmission Owner that has not identified in its previous risk assessment (as verified according to Requirement R2) any Transmission stations or Transmission substations that if rendered inoperable or damaged could result in instability, uncontrolled separation, or Cascading within an Interconnection. |  | TO | [22 empty] | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.Voltage Value of a Line Weight Value per Lineless than 200 kV (not applicable) (not applicable)200 kV to 299 kV 700300 kV to 499 kV 1300500 kV and above 04.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 10200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-30-0000044 | Each Transmission Owner shall select an unaffiliated verifying entity that is either:• A registered Planning Coordinator, Transmission Planner, or Reliability Coordinator; or• An entity that has transmission planning or analysis experience. |  | TO | [22 empty] | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.Voltage Value of a Line Weight Value per Lineless than 200 kV (not applicable) (not applicable)200 kV to 299 kV 700300 kV to 499 kV 1300500 kV and above 04.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-06-30-0000045 | Unique characteristics of the identified and verified Transmission station(s), Transmission substation(s), and primary control center(s); |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.Voltage Value of a Line Weight Value per Lineless than 200 kV (not applicable) (not applicable)200 kV to 299 kV 700300 kV to 499 kV 1300500 kV and above 04.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 40100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-01-0000001 | Within 90 calendar days after identifying any unplanned permanent BES modifications. |  | TOP | [18 empty] | TOP |  |  |  | 2019-04-01 | [5 empty] | 40100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-01-0000004 | The transition time between the simulated loss of primary control center functionality and the time to fully implement the backup functionality. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2019-04-01 | [5 empty] | 70100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-01-0000006 | Within 30 calendar days of receipt, the Reliability Coordinator shall: |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 30100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-01-0000008 | generation Facilities; |  | TO | [22 empty] | 2017-11-27 | [5 empty] | 10200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-01-0000009 | Change in expected growth rate/environmental factors |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-10-01 |  |  |  | 4.1. Functional Entities:4.1.1. Applicable Transmission Owners4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.4.1.2. Applicable Generator Owners4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.2.1. Each overhead transmission line operated at 200kV or higher.4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:4.3.1.1. Operated at 200kV or higher; or4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 70600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-01-0000010 | In the pre-contingency state and with all Facilities in service, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect expected system conditions and shall reflect changes to system topology such as Facility outages. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 20400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-01-0000017 | The methodology used to establish the Ratings of the equipment that comprises the Facility(ies) shall be consistent with at least one of the following:• Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating.• One or more industry standards developed through an open process such as Institute of Electrical and Electronic Engineers (IEEE) or International Council on Large Electric Systems (CIGRE).• A practice that has been verified by testing, performance history or engineering analysis. |  | GO | [22 empty] | 2013-01-01 |  | 2021-09-30 |  |  |  | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-01-0000022 | The methodology used to establish the Ratings of the equipment that comprises the Facility shall be consistent with at least one of the following:• Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications such as nameplate rating.• One or more industry standards developed through an open process such as Institute of Electrical and Electronics Engineers (IEEE) or International Council on Large Electric Systems (CIGRE). • A practice that has been verified by testing, performance history or engineering analysis. |  | TO | [22 empty] | 2013-01-01 |  | 2021-09-30 |  |  |  | 30200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-01-0000023 | As scheduled by the requesting entities: |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-01-01 |  | 2021-09-30 |  |  |  | 80200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-02-0000001 | In the pre-contingency state, the BES shall demonstrate transient, dynamic and voltage stability; all Facilities shall be within their Facility Ratings and within their thermal, voltage and stability limits. In the determination of SOLs, the BES condition used shall reflect current or expected system conditions and shall reflect changes to system topology such as Facility outages. |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 20400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-02-0000005 | The Reliability Coordinator shall provide its SOLs (including the subset of SOLs that are IROLs) to adjacent Reliability Coordinators and Reliability Coordinators who indicate a reliability-related need for those limits, and to the Transmission Operators, Transmission Planners, Transmission Service Providers and Planning Authorities within its Reliability Coordinator Area. For each IROL, the Reliability Coordinator shall provide the following supporting information: |  | PCPA, RC, TOP, TP | [9 empty] | PA |  | RC | [6 empty] | TOP | TP |  |  | 2009-04-29 | [5 empty] | 50200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-06-0000001 | The Transmission Service Provider shall make its own current data available,in the format maintained by the Transmission Service Provider, for up to 13months into the future (subject to confidentiality and security requirements). |  | TSP | [20 empty] | TSP |  | 2011-04-01 | [5 empty] | 90100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-06-0000004 | Each of its associated Transmission Operators within 30 calendar days of theirmaking a request for the data. |  | RP | [13 empty] | RP | [8 empty] | 2011-04-01 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 40100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-06-0000006 | Verify the Real Power capability of its generating units in accordance withAttachment 1. |  | GO | [22 empty] | 2016-07-01 |  |  | In those jurisdictions where regulatory approval is required:• Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 By the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities.In those jurisdictions where no regulatory approval is required:• Each responsible entity shall ensure compliance with Requirements R1, and R3 through R6 by the first day of the first calendar quarter following Board of Trustees adoption. | For the purpose of this standard, the term, “applicable Facility” shall mean any one of the following:4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.4.2.2 Synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.4.2.3 Generating plant/Facility greater than 75 MVA (gross aggregate nameplate rating) directly connected to the Bulk Electric System. |  | 10100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-06-0000007 | Verify, in accordance with Attachment 1, (i) the Reactive Power capability of itsgenerating units and (ii) the Reactive Power capability of its synchronouscondenser units. |  | GO | [22 empty] | 2016-07-01 |  |  |  | For the purpose of this standard, the term, “applicable Facility” shall mean any one of the following:4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.4.2.2 Synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.4.2.3 Generating plant/Facility greater than 75 MVA (gross aggregate nameplate rating) directly connected to the Bulk Electric System. |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-06-0000008 | Verify, in accordance with Attachment 1, the Reactive Power capability of itssynchronous condenser units. |  | TO | [22 empty] | 2016-07-01 |  |  | In those jurisdictions where regulatory approval is required:Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities.In those jurisdictions where no regulatory approval is required:Each Generator Owner shall ensure at least 30 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, four years following Board of Trustees adoption.• Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following Board of Trustees adoption.• Each Generator Owner shall ensure at least 100 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, 10 years following Board of Trustees adoption.• Each Generator Owner shall ensure at least 50 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, six years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities.• Each Generator Owner shall ensure at least 100 percent of its applicable unit gross MVA per Interconnection are compliant with Requirement R2 by the first day of the first calendar quarter, 10 years following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities. | For the purpose of this standard, the term, “applicable Facility” shall mean any one of the following:4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.4.2.2 Synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.4.2.3 Generating plant/Facility greater than 75 MVA (gross aggregate nameplate rating) directly connected to the Bulk Electric System. |  | 30100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-06-0000009 | The turbine/governor and load control or active power/frequency control functionmodel initializes to compute modeling data without error, |  | TP | [19 empty] | TP |  |  | 2014-07-01 |  |  | In those jurisdictions where regulatory approval is required:• Each responsible entity shall ensure compliance with Requirements R1, and R3 through R5 by the first day of the first calendar quarter following applicable regulatory approval, or as otherwise made effective pursuant to the laws applicable to such ERO governmental authorities.In those jurisdictions where no regulatory approval is required:• Each responsible entity shall ensure compliance with Requirements R1, and R3 through R5 by the first day of the first calendar quarter following Board of Trustees adoption. | 4.2. FacilitiesFor the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred to as an “applicable unit” that meet the following:4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics:4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).4.2.2 Generation in the Western Interconnection with the following characteristics:4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.3 Generation in the ERCOT Interconnection with the following characteristics:4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). |  | 50100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-07-0000003 | Use all Contingencies meeting the criteria described in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2013-10-01 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 40100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-07-0000024 | Use the models provided by the Transmission Operator. |  | TSP | [20 empty] | TSP |  | 2017-04-01 | [5 empty] | 50100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-08-0000001 | Within six months of a modification or addition of a BES company-specific Realtime reliability-related task, each Reliability Coordinator, Balancing Authority,Transmission Operator, and Transmission Owner shall verify the capabilities ofeach of its personnel identified in Requirement R1 or Requirement R2 to performthe new or modified BES company-specific Real-time reliability-related tasksidentified in Requirement R1 part 1.1 or Requirement R2 part 2.1. |  | BA, RC, TO, TOP | BA | [10 empty] | RC | [5 empty] | TO | TOP |  |  | M3.1 Each Reliability Coordinator, Balancing Authority, Transmission Operator, orTransmission Owner shall present evidence that it verified the capabilities ofapplicable personnel to perform new or modified BES company-specific Realtime reliability-related tasks within 6 months of a modification or addition of aBES company-specific Real-time reliability-related task. | 2016-07-01 | [5 empty] | 30100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-08-0000005 | Triggered record lengths of at least three minutes. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date.Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date.Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 80100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-09-0000001 | Those islands selected by applying the criteria in Requirement R1, and |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2021-04-01 |  |  |  | UFLS entities shall mean all entities that are responsible for the ownership,operation, or control of UFLS equipment as required by the UFLS programestablished by the Planning Coordinators. Such entities may include one ormore of the following: 4.2.1 Transmission Owners4.2.2 Distribution Providers4.2.3 UFLS-Only Distribution Providers4.3. Transmission Owners that own Elements identified in the UFLS programestablished by the Planning Coordinators. |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-09-0000004 | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006-5 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2021-04-01 |  |  |  | UFLS entities shall mean all entities that are responsible for the ownership,operation, or control of UFLS equipment as required by the UFLS programestablished by the Planning Coordinators. Such entities may include one ormore of the following: 4.2.1 Transmission Owners4.2.2 Distribution Providers4.2.3 UFLS-Only Distribution Providers4.3. Transmission Owners that own Elements identified in the UFLS programestablished by the Planning Coordinators. |  | 30100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-09-0000007 | Underfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-5 - Attachment 1. |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2021-04-01 |  |  |  | UFLS entities shall mean all entities that are responsible for the ownership,operation, or control of UFLS equipment as required by the UFLS programestablished by the Planning Coordinators. Such entities may include one ormore of the following: 4.2.1 Transmission Owners4.2.2 Distribution Providers4.2.3 UFLS-Only Distribution Providers4.3. Transmission Owners that own Elements identified in the UFLS programestablished by the Planning Coordinators. |  | 40100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-09-0000014 | The performance of the UFLS equipment, |  | DP, DP-UFLS, TO |  | DP | [20 empty] | 2021-04-01 | [5 empty] | 80100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-09-0000016 | UFLS program, including a schedule for implementation |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2021-04-01 |  |  |  | UFLS entities shall mean all entities that are responsible for the ownership,operation, or control of UFLS equipment as required by the UFLS programestablished by the Planning Coordinators. Such entities may include one ormore of the following: 4.2.1 Transmission Owners4.2.2 Distribution Providers4.2.3 UFLS-Only Distribution Providers4.3. Transmission Owners that own Elements identified in the UFLS programestablished by the Planning Coordinators. |  | 140100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-09-0000019 | For UFLS design assessments performed under Requirement R4 or R5, the Corrective Action Plan shall be developed within the five-year time frame identified in Requirement R4. |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2021-04-01 |  |  |  | UFLS entities shall mean all entities that are responsible for the ownership,operation, or control of UFLS equipment as required by the UFLS programestablished by the Planning Coordinators. Such entities may include one ormore of the following: 4.2.1 Transmission Owners4.2.2 Distribution Providers4.2.3 UFLS-Only Distribution Providers4.3. Transmission Owners that own Elements identified in the UFLS programestablished by the Planning Coordinators. |  | 150100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-09-0000021 | Frequency shall remain above the Underfrequency Performance Characteristic curve in PRC-006 - Attachment 1A, either for 60 seconds or until a steady-state condition between 59.0 Hz and 60.7 Hz is reached, and |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2021-04-01 |  |  |  | UFLS entities shall mean all entities that are responsible for the ownership,operation, or control of UFLS equipment as required by the UFLS programestablished by the Planning Coordinators. Such entities may include one ormore of the following: 4.2.1 Transmission Owners4.2.2 Distribution Providers4.2.3 UFLS-Only Distribution Providers4.3. Transmission Owners that own Elements identified in the UFLS programestablished by the Planning Coordinators. |  | 68030100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-09-0000033 | Underfrequency trip set points(Hz) |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 70100000 | SERC-US |  |  |  | SERC-US
1. | RP-2021-07-09-0000037 | The UVLS Program resolves the identified undervoltage issues for which the UVLS Program is designed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2017-04-02 | [5 empty] | 30100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-09-0000039 | Whether its UVLS Program resolved the undervoltage issues associated with the event, and |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2017-04-02 | [5 empty] | 40100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-09-0000040 | The UVLS system identification which shall include but is not limited to: |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2027-03-31 |  |  |  | 10100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-09-0000044 | Type of DME (sequence of event recorder, fault recorder, or dynamic disturbance recorder). |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2022-06-30 |  100% compliant six months after BOT adoption for already installed DME. 100% compliant six months after installation for DMEs installed to meet Regional Reliability Organization requirements per reliability standard PRC-002 Requirements 1, 2 and 3. |  |  | 30100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-09-0000045 | Within 12 full calendar months of notification of a BES Element pursuant to Requirement R1, determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-1 – Attachment B where an evaluation of that Element’s load-responsive protective relay(s) based on PRC-026-1 – Attachment B criteria has not been performed in the last five calendar years. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2020-01-01 | [5 empty] | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-12-0000032 | Studies shall be performed for planning events to determine whether the BES meets the performance requirements in Table 1 based on the Contingency list created in Requirement R4, Part 4.4. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 40100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-12-0000046 | If a recipient of the Planning Assessment results provides documented comments on the results, the respective Planning Coordinator or Transmission Planner shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 80100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-12-0000050 | Specify implementation of non-hardware mitigation, if any, within two years of the later of the development of the CAP or receipt of regulatory approvals, if required; and |  | GO, PCPA, TO, TP |  |  |  |  | GO |  |  |  |  | PA | [7 empty] | TO |  | TP |  |  | 2020-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 68730100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-12-0000052 | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 40100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-12-0000055 | The study or studies shall include the following conditions: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 80100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-12-0000057 | The Transmission Operator shall provide the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the associated Generator Operator and direct the Generator Operator to comply with the schedule in automatic voltage control mode (the AVR is in service and controlling voltage). |  | TOP | [18 empty] | TOP |  |  |  | 2019-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | 50100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-12-0000060 | When a generator’s AVR is out of service or the generator does not have an AVR, the Generator Operator shall use an alternative method to control the generator reactive output to meet the voltage or Reactive Power schedule provided by the Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2017-09-26 | [5 empty] | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-13-0000001 | Monitor Facilities within its Transmission Operator Area; |  | BA, DP, GOP, TOP | BA | DP |  |  |  | GOP | [12 empty] | TOP | [9 empty] | 100100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-13-0000007 | Require that each BES bus/station have an associated System Voltage Limits, unless its SOL methodology specifically allows the exclusion of BES buses/stations from the requirement to have an associated System Voltage Limit; |  | RC | [11 empty] | RC | [16 empty] | 30100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-13-0000012 | Specify stability performance criteria, including any margins applied. The criteria shall, at a minimum, include the following: |  | RC | [11 empty] | RC | [16 empty] | 40100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-13-0000023 | Specify the following single Contingency events |  | RC | [11 empty] | RC | [16 empty] | 50100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-13-0000027 | System performance for no Contingencies demonstrates the following: |  | RC | [11 empty] | RC | [16 empty] | 60100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-13-0000039 | A requirement that the following SOL exceedances will always be communicated, within a timeframe identified by the Reliability Coordinator. |  | RC | [11 empty] | RC | [16 empty] | 70100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-13-0000048 | A description of how to identify the subset of SOLs that qualify as Interconnection Reliability Operating Limits (IROLs). |  | RC | [11 empty] | RC | [16 empty] | 80100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-13-0000050 | Each Reliability Coordinator that requests and indicates it has a reliability-related need within 30 days of a request. |  | RC | [11 empty] | RC | [16 empty] | 90100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-13-0000056 | Each Planning Coordinator and each Transmission Planner within its Reliability Coordinator Area, the SOLs for its Reliability Coordinator Area (including the subset of SOLs that are IROLs) at least once every twelve calendar months. |  | RC, TOP, TP | [11 empty] | RC | [6 empty] | TOP | TP | [8 empty] | 50100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-13-0000068 | The Corrective Action Plan developed to mitigate the identified instability, including any automatic control or operator-assisted actions (such as Remedial Action Schemes, under voltage load shedding, or any Operating Procedures); |  | RC, TOP, TP | [11 empty] | RC | [6 empty] | TOP | TP | [8 empty] | 70100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-13-0000073 | An encroachment into the MVCD as shown in FAC‐003‐Table 2, observed in Real‐ time, absent a Sustained Outage, Footnote: If a later confirmation of a Fault by the applicable Transmission Owner or applicable Generator Owner shows that a vegetation encroachment within the MVCD has occurred from vegetation within the ROW, this shall be considered the equivalent of a Real‐time observation. |  | GO, TO |  |  |  |  | GO | [23 empty] | 10100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-13-0000077 | Movement of applicable line conductors under their Rating and all Rated Electrical Operating Conditions; |  | GO, TO |  |  |  |  | GO | [23 empty] | 30100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-13-0000079 | Change in expected growth rate/environmental factors |  | GO, TO |  |  |  |  | GO | [23 empty] | 70100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-15-0000001 | Identify BES buses for which sequence of events recording (SER) and fault recording (FR) data is required by using the methodology in PRC-002-3, Attachment 1. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 10100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-15-0000004 | Phase-to-neutral voltage for each phase of each specified BES bus. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 30100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-15-0000008 | A single record or multiple records that include:• A pre-trigger record length of at least two cycles and a total record length of at least 30-cycles for the same trigger point, or• At least two cycles of the pre-trigger data, the first three cycles of the post- trigger data, and the final cycle of the fault as seen by the fault recorder. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 40100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-15-0000013 | Identify BES Elements for which dynamic Disturbance recording (DDR) data is required, including the following: |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 50100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-15-0000026 | One phase-to-neutral or positive sequence voltage. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 60100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-15-0000030 | One phase-to-neutral, phase-to-phase, or positive sequence voltage at either the generator step-up transformer (GSU) high-side or low-side voltage level. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 70100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-15-0000034 | Triggered record lengths of at least three minutes. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 80100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-15-0000036 | Input sampling rate of at least 960 samples per second. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 90100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-15-0000038 | Synchronization to Coordinated Universal Time (UTC) with or without a local time offset. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 100100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-15-0000040 | Data will be retrievable for the period of 10-calendar days, inclusive of the day the data was recorded. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 110100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-15-0000045 | Maintain a list of circuits subject to PRC-023-5 per application of Attachment B, including identification of the first calendar year in which any criterion in PRC-023-5, Attachment B applies. |  | DP, GO, PCPA, TO |  | DP |  |  | GO |  |  |  |  | PA | [18 empty] | 60100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-15-0000047 | Within 12 full calendar months of notification of a BES Element pursuant to Requirement R1, determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-2 – Attachment B where an evaluation of that Element’s load-responsive protective relay(s) based on PRC-026-2 – Attachment B criteria has not been performed in the last five calendar years. |  | GO, PCPA, TO |  |  |  |  | GO |  |  |  |  | PA | [18 empty] | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-07-26-0000004 | Those islands selected by applying the criteria in Requirement D.B.1, and |  | PCPA | [9 empty] | PA | [12 empty] | 2021-04-01 | [6 empty] | WECC-US | [5 empty] | WECC-US
1. | RP-2021-08-12-0000001 | Identify each of the high impact BES Cyber Systems according to Attachment 1, Section 1, if any, at each asset; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2014-02-03 |  |  |  | 10100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-08-12-0000004 | Review the identifications in Requirement R1 and its parts (and update them if there are changes identified) at least once every 15 calendar months, even if it has no identified items in Requirement R1, and |  | BA, GO, GOP, IA, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2014-02-03 |  |  |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-08-13-0000001 | The senior manager shall be identified by name, title, business phone, business address, and date of designation. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-08-13-0000004 | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 50100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-08-13-0000006 | The senior manager shall be identified by name, title, and date of designation. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-08-13-0000009 | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 50100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-08-13-0000011 | The senior manager shall be identified by name, title, and date of designation. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  |  |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-08-13-0000013 | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  |  |  | 50100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-08-13-0000015 | The senior manager shall be identified by name, title, and date of designation. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-08-13-0000017 | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | 50100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-08-13-0000019 | The senior manager shall be identified by name, title, and date of designation. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-08-13-0000021 | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 50100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-08-13-0000023 | The senior manager shall be identified by name, title, and date of designation. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1. | RP-2021-08-13-0000025 | The Responsible Entity shall maintain a list of designated personnel who are responsible for authorizing logical or physical access to protected information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 50100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10 | 79780000615 | Power quality impacts. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 22900000 | NPCC-ON |  | NPCC-US
10 | 79780000997 | Contingency events. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  |  | 20000000 | NPCC-ON |  | NPCC-US
10 | 79780001024 | Contingency events. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  |  | 20000000 | NPCC-ON |  | NPCC-US
10 | 79780001051 | Contingency events. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  |  | 20000000 | NPCC-ON |  | NPCC-US
10 | 79780001198 | Describe the inclusion or exclusion rationale for generation reserve sharing arrangements in the CBM values. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 20000000 | NPCC-ON |  | NPCC-US
10 | 79780001427 | Includes any other modeling requirements or criteria specified in the ATCID. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 12900000 | NPCC-ON |  | NPCC-US
10 | 79780001866 | Set transformer fault protection relays and transmission line relays on transmission lines terminated only with a transformer so that they do not operate at or below the greater of:&lt;br/&gt;- 150% of the applicable maximum transformer nameplate rating (expressed in amperes), including the forced cooled ratings corresponding to all installed supplemental cooling equipment.&lt;br/&gt;- 115% of the highest operator established emergency transformer rating. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  |  | 20000000 | NPCC-ON |  | NPCC-US
10 | 79780002080 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 14900000 | NPCC-ON |  | NPCC-US
10 | 79780002105 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 14900000 | NPCC-ON |  | NPCC-US
10 | 79780002130 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 14900000 | NPCC-ON |  | NPCC-US
10 | 79780002155 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 14900000 | NPCC-ON |  | NPCC-US
10 | 79780003053 | Includes any other modeling requirements or criteria specified in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 12900000 | NPCC-ON |  | NPCC-US
10 | 79780003422 | Contingency events. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  |  | 20000000 | NPCC-ON |  | NPCC-US
10 | 79780003478 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 14900000 | NPCC-ON |  | NPCC-US
10 | 79780003503 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 14900000 | NPCC-ON |  | NPCC-US
10 | 79780003528 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 14900000 | NPCC-ON |  | NPCC-US
10 | 79780003809 | Contingency events. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  |  | 20000000 | NPCC-ON |  | NPCC-US
10 | 79780004185 | Contingency events. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  |  | 20000000 | NPCC-ON |  | NPCC-US
10 | 79780004637 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 14900000 | NPCC-ON |  | NPCC-US
10 | 79780004662 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 14900000 | NPCC-ON |  | NPCC-US
10 | 79780004702 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 14900000 | NPCC-ON |  | NPCC-US
10 | 79780004725 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 14900000 | NPCC-ON |  | NPCC-US
10 | 79780005027 |  |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 20000000 | NPCC-ON |  | NPCC-US
10 | 79780005670 | Contingency events. |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  |  | 20000000 | NPCC-ON |  | NPCC-US
10 | 79780005845 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 14900000 | NPCC-ON |  | NPCC-US
10 | 79780005870 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 14900000 | NPCC-ON |  | NPCC-US
10 | 79780006040 | Includes any other modeling requirements or criteria specified in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 12900000 | NPCC-ON |  | NPCC-US
10 | 79780007348 | Restrict physical access to cabling and other nonprogrammable communication components used for connection between applicable Cyber Assets within the same Electronic Security Perimeter in those instances when such cabling and components are located outside of a Physical Security Perimeter.&lt;br/&gt;Where physical access restrictions to such cabling and components are not implemented, the Responsible Entity shall document and implement one or more of the following: &lt;br/&gt;• encryption of data that transits such cabling and components; or&lt;br/&gt;• monitoring the status of the communication link composed of such cabling and components and issuing an alarm or alert in response to detected communication failures to the personnel identified in the BES Cyber Security Incident response plan within 15 minutes of detection; or&lt;br/&gt;• an equally effective logical protection. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.10 An example of evidence may include, but is not limited to, records of the Responsible Entity’s implementation of the physical access restrictions (e.g., cabling and components secured through conduit or secured cable trays) encryption, monitoring, or equally effective logical protections. | 2016-07-01 | [5 empty] | 20000000 | NPCC-ON |  | NPCC-US
10. | 1024 | Contingency events. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  | IRO-005-2 R1. | 20000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10. | 1051 | Contingency events. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  | IRO-005-3a R1. | 20000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10. | 1198 | Describe the inclusion or exclusion rationale for generation reserve sharing arrangements in the CBM values. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-004-0 R1. | 20000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10. | 1427 | Includes any other modeling requirements or criteria specified in the ATCID. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 12900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10. | 1866 | Set transformer fault protection relays and transmission line relays on transmission lines terminated only with a transformer so that they do not operate at or below the greater of:- 150% of the applicable maximum transformer nameplate rating (expressed in amperes), including the forced cooled ratings corresponding to all installed supplemental cooling equipment.- 115% of the highest operator established emergency transformer rating. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  | PRC-023-1 R1. | 20000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10. | 2080 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 14900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10. | 2105 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 14900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10. | 2130 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 14900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10. | 2155 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 14900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10. | 2308 | If AVR exhibits instability due to operation of a Load Tap Changer (LTC) transformer in the area, the Transmission Operator may authorize the Generator Operator to operate the excitation system in modes other than automatic voltage control until the system configuration changes. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-06-27 |  | 2015-03-31 |  |  | VAR-002-WECC-1 R1. | 20000000 | WECC-US | [5 empty] | WECC-US
10. | 2320 | Due to a component failure, the PSS may be out of service up to 24 months provided the Generator Operator submits documentation identifying the need for time for PSS replacement and to schedule an outage. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-06-27 |  | 2015-03-31 |  |  | VAR-501-WECC-1 R1. | 20000000 | WECC-US | [5 empty] | WECC-US
10. | 3053 | Includes any other modeling requirements or criteria specified in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 12900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10. | 3422 | Contingency events. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  | IRO-005-2a R1. | 20000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10. | 3478 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 14900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10. | 3503 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 14900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10. | 3528 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 14900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10. | 3809 | Contingency events. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  | IRO-005-3 R1. | 20000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10. | 4185 | Contingency events. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  | IRO-005-3.1a R1. | 20000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10. | 4637 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 14900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10. | 4662 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 14900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10. | 4702 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 14900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10. | 4725 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 14900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10. | 5027 | Contingency events. |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 20000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10. | 5670 | Contingency events. |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  |  | 20000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10. | 5845 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 14900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10. | 5870 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 14900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10. | 6040 | Includes any other modeling requirements or criteria specified in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 12900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10. | 615 | Power quality impacts. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 22900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10. | 7348 | Restrict physical access to cabling and other nonprogrammable communication components used for connection between applicable Cyber Assets within the same Electronic Security Perimeter in those instances when such cabling and components are located outside of a Physical Security Perimeter.Where physical access restrictions to such cabling and components are not implemented, the Responsible Entity shall document and implement one or more of the following: • encryption of data that transits such cabling and components; or• monitoring the status of the communication link composed of such cabling and components and issuing an alarm or alert in response to detected communication failures to the personnel identified in the BES Cyber Security Incident response plan within 15 minutes of detection; or• an equally effective logical protection. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.10 An example of evidence may include, but is not limited to, records of the Responsible Entity’s implementation of the physical access restrictions (e.g., cabling and components secured through conduit or secured cable trays) encryption, monitoring, or equally effective logical protections. | 2016-07-01 | [5 empty] | 20000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
10. | 7723 | If AVR exhibits instability due to operation of a Load Tap Changer (LTC) transformer in the area, the Transmission Operator may authorize the Generator Operator to operate the excitation system in modes other than automatic voltage control until the system configuration changes. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2015-03-03 |  | 2018-09-05 |  |  |  | 20000000 | WECC-US | [5 empty] | WECC-US
10. | 7837 | Due to a component failure, the PSS may be out of service up to 24 months provided the Generator Operator submits documentation identifying the need for time for PSS replacement and to schedule an outage. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-04-01 |  | 2017-06-30 |  |  |  | 20000000 | WECC-US | [5 empty] | WECC-US
10. | 997 | Contingency events. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  | IRO-005-1 R1. | 20000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1. | 6277 | Cyber security policies; | [23 empty] | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. |  |  | 2016-06-30 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1. | 6344 | Facility Ratings |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-11-17 |  | 2021-09-30 |  |  |  | 81000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1. | 79780008986 | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 41100000 | NPCC-ON |  | NPCC-US
1.1. | 79780009012 | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 81100000 | NPCC-ON |  | NPCC-US
1.1. | 8079 | Tap settings. |  | GO | [22 empty] | 2017-09-26 | [5 empty] | 51100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1. | 8986 | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 41100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1. | 9012 | System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 81100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1. | RP-2021-04-12-0000026 | Facility Ratings |  | GO | [22 empty] | 2021-10-01 | [5 empty] | 80200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1. | RP-2021-06-08-0000023 | If the Planning Coordinator determines the UFLS program is degraded in accordance with R8.1 and that supplementary load shedding is, therefore, required, the Planning Coordinator shall notify the Generator Owner or UFLS entity(s) in accordance with the following:  Where the Generator Owner is a UFLS Entity and has the required amount of supplementary Load available, the Planning Coordinator shall notify the Generator Owner of Load the entity is required to shed (in addition to that required in accordance with R1 and R2)  Where the Generator Owner is not a UFLS Entity, or does not have the required supplementary Load available for shedding, the Planning Coordinator shall notify any other UFLS Entity(s) within the Planning Coordinator Area of Load the entity(s) is required to shed (in addition to that required in accordance with R1 and R2) |  | PCPA | [9 empty] | PA | [14 empty] | 2013-11-07 |  |  |  | 81100000 | SPPRE-US
1.1. | RP-2021-06-16-0000028 | The utilization of Direct Control Load Management or curtailment of Interruptible Demand shall not contribute to the loss of Load probability. |  | PCPA | [9 empty] | PA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  |  | 11100000 | RF-US |  |  | RF-US
1.1. | RP-2021-06-18-0000009 | Operating system(s) (includingversion) or firmware where noindependent operating systemexists; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1. | RP-2021-06-21-0000008 | Procedures for coordinated joint studies of new Facilities and their impacts on theinterconnected Transmission systems. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-11-25 |  | 2015-12-31 |  |  |  | 31100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1. | RP-2021-06-22-0000025 | When modeling normal conditions, all Transmission Elements willbe modeled at or below 100% of their continuous rating. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1. | RP-2021-06-23-0000003 | Transmission operations |  | TOP | [18 empty] | TOP |  |  |  | 2012-10-01 |  | 2019-06-30 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1. | RP-2021-06-23-0000021 | The BES interrupting device owner shares the Composite Protection System ownership with any other owner; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-04-02 |  | 2017-04-01 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1. | RP-2021-06-24-0000041 | For planning event P1: No generating unit shall pull out ofsynchronism. A generator being disconnected from the System byfault clearing action or by a Remedial Action Scheme is notconsidered pulling out of synchronism. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-07-01 |  | 2020-06-10 |  |  |  | 41100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1. | RP-2021-06-24-0000106 | Review each submitted Operating Plan(s) on the basis of compatibility and inter-dependency with other Balancing Authorities’ and Transmission Operators’ Operating Plans; |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 31100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1. | RP-2021-06-29-0000005 | The utilization of Direct Control Load Management or curtailment ofInterruptible Demand shall not contribute to the loss of Loadprobability. |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 11100000 | RF-US |  |  | RF-US
1.1. | RP-2021-07-02-0000006 | Identification and status of the associated Facility (or group of Facilities) that is (are) critical to the derivation of the IROL. |  | PCPA, RC, TOP, TP | [9 empty] | PA |  | RC | [6 empty] | TOP | TP |  |  | 2009-04-29 | [5 empty] | 50400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1. | RP-2021-07-06-0000002 | If the Transmission Service Provider uses the data requested in itstransfer or Flowgate capability calculations, it shall make the dataused available |  | TSP | [20 empty] | TSP |  | 2011-04-01 | [5 empty] | 90200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1. | RP-2021-07-07-0000013 | When modeling normal conditions, all Transmission Elements will be modeled at or below 100% of their continuous rating. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1. | RP-2021-07-07-0000031 | Transmission operations |  | TOP | [18 empty] | TOP |  |  |  | 2019-07-01 | [5 empty] | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1. | RP-2021-07-09-0000043 | The System events and/or conditions appropriately triggered the RAS. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 51100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1. | RP-2021-07-12-0000001 | Existing Facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 11100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1. | RP-2021-07-12-0000005 | System peak Load for either Year One or year two, and for year five. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 11500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1. | RP-2021-07-12-0000033 | For planning event P1: No generating unit shall pull out of synchronism. A generator being disconnected from the System by fault clearing action or by a Remedial Action Scheme is not considered pulling out of synchronism. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 41100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1. | RP-2021-07-13-0000013 | steady-state voltage stability; |  | RC | [11 empty] | RC | [16 empty] | 41100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1. | RP-2021-07-13-0000024 | Loss of any of the following either by single phase to ground or three phase Fault (whichever is more severe) with Normal Clearing, or without a Fault:· generator;· transmission circuit;· transformer;· shunt device; or· single pole block in a monopolar or bipolar high voltage direct current system. |  | RC | [11 empty] | RC | [16 empty] | 51100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1. | RP-2021-07-13-0000028 | Steady state flow through Facilities are within Normal Ratings; however, Emergency Ratings may be used when System adjustments to return the flow within its Normal Rating could be executed and completed within the specified time duration of those Emergency Ratings. |  | RC | [11 empty] | RC | [16 empty] | 61100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1. | RP-2021-07-13-0000040 | IROL exceedances; |  | RC | [11 empty] | RC | [16 empty] | 71100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1. | RP-2021-07-15-0000014 | Generating resource(s) with: |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 51100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
11 | 79780000616 | Equipment Ratings. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
11 | 79780001867 | For transformer overload protection relays that do not comply with R1.10 set the relays according to one of the following: &lt;br/&gt;- Set the relays to allow the transformer to be operated at an overload level of at least 150% of the maximum applicable nameplate rating, or 115% of the highest operator established emergency transformer rating, whichever is greater. The protection must allow this overload for at least 15 minutes to allow for the operator to take controlled action to relieve the overload.&lt;br/&gt;- Install supervision for the relays using either a top oil or simulated winding hot spot temperature element. The setting should be no less than 100° C for the top oil or 140° C for the winding hot spot temperature . |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  |  | 20100000 | NPCC-ON |  | NPCC-US
11 | 79780002081 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
11 | 79780002106 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
11 | 79780002131 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
11 | 79780002156 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
11 | 79780003479 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
11 | 79780003504 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
11 | 79780003529 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
11 | 79780004641 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
11 | 79780004666 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
11 | 79780004706 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
11 | 79780004723 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
11 | 79780005846 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
11 | 79780005871 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
11. | 1867 | For transformer overload protection relays that do not comply with R1.10 set the relays according to one of the following: - Set the relays to allow the transformer to be operated at an overload level of at least 150% of the maximum applicable nameplate rating, or 115% of the highest operator established emergency transformer rating, whichever is greater. The protection must allow this overload for at least 15 minutes to allow for the operator to take controlled action to relieve the overload.- Install supervision for the relays using either a top oil or simulated winding hot spot temperature element. The setting should be no less than 100° C for the top oil or 140° C for the winding hot spot temperature . |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  | PRC-023-1 R1. | 20100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
11. | 2081 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
11. | 2106 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
11. | 2131 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
11. | 2156 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
11. | 2321 | The synchronous generator has not achieved Commercial Operation. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-06-27 |  | 2015-03-31 |  |  | VAR-501-WECC-1 R1. | 20100000 | WECC-US | [5 empty] | WECC-US
11. | 3479 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
11. | 3504 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
11. | 3529 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
11. | 4641 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
11. | 4666 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
11. | 4706 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
11. | 4723 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
11. | 5846 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
11. | 5871 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
11. | 616 | Equipment Ratings. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
11. | 7839 | The synchronous generator has not achieved Commercial Operation. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-04-01 |  | 2017-06-30 |  |  |  | 20100000 | WECC-US | [5 empty] | WECC-US
1.10. | RP-2021-06-21-0000017 | Power quality impacts. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-11-25 |  | 2015-12-31 |  |  |  | 41000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1.1. | RP-2021-06-22-0000018 | The Transmission Operator area. Equivalentrepresentation of radial lines and facilities 161kV orbelow is allowed. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1.1. | RP-2021-06-22-0000029 | Use first Contingency criteria consistent with those firstContingency criteria used in planning of operations for the applicable time periods, including use of Special ProtectionSystems. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 31100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1.1. | RP-2021-07-07-0000006 | The Transmission Operator area. Equivalent representation of radial lines and facilities 161kV or below is allowed. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 21100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1.1. | RP-2021-07-07-0000019 | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Remedial Action Schemes. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 31100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1.1. | RP-2021-07-15-0000015 | Gross individual nameplate rating greater than or equal to 500 MVA. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 61100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.11. | RP-2021-06-21-0000018 | Equipment Ratings. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-11-25 |  | 2015-12-31 |  |  |  | 41100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.1.2. | RP-2021-07-15-0000016 | Gross individual nameplate rating greater than or equal to 300 MVA where the gross plant/facility aggregate nameplate rating is greater than or equal to 1,000 MVA. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 61200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.12. | RP-2021-06-21-0000019 | Synchronizing of Facilities. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-11-25 |  | 2015-12-31 |  |  |  | 41200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.13. | RP-2021-06-21-0000020 | Maintenance coordination. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-11-25 |  | 2015-12-31 |  |  |  | 41300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.14. | RP-2021-06-21-0000021 | Operational issues (abnormal frequency and voltages). |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-11-25 |  | 2015-12-31 |  |  |  | 41400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.15. | RP-2021-06-21-0000022 | Inspection requirements for existing or new Facilities. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-11-25 |  | 2015-12-31 |  |  |  | 41500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.16. | RP-2021-06-21-0000023 | Communications and procedures during normal and emergency operatingconditions. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-11-25 |  | 2015-12-31 |  |  |  | 41600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | 3036 | If the Transmission Service Provider does not use the data requestedin its transfer or Flowgate capability calculations, but maintains thatdata, it shall make that data available |  | TSP | [20 empty] | TSP |  | 2011-04-01 | [5 empty] | 91100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | 6278 | Physical access controls; | [23 empty] | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. |  |  | 2016-06-30 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | 6345 | Identity of the most limiting equipment of the Facilities |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-01-01 |  | 2021-09-30 |  |  |  | 81100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | 79780008987 | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 41200000 | NPCC-ON |  | NPCC-US
1.2. | 79780009013 | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 81200000 | NPCC-ON |  | NPCC-US
1.2. | 858 | The value of the IROL and its associated Tv. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  |  |  |  | FAC-014-2 R5. | 51000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | 8987 | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 41200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | 9013 | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 81200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | RP-2021-04-12-0000024 | Identity of the most limiting equipment of the Facilities |  | GO | [22 empty] | 2021-10-01 | [5 empty] | 81100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | RP-2021-06-16-0000029 | The planning reserve margin developed from R1.1 shall be expressed as a percentage of the median2 forecast peak Net Internal Demand (planning reserve margin).Note: The median forecast is expected to have a 50% probability of being too high and 50% probability of being too low (50:50). |  | PCPA | [9 empty] | PA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  |  | 11200000 | RF-US |  |  | RF-US
1.2. | RP-2021-06-17-0000005 | Unescorted physical access into a Physical Security Perimeter; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 41200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | RP-2021-06-18-0000004 | Update the Cyber Security Incident response plan based on any documented lessons learned associated with the plan; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-12-31 |  | 1.3 High Impact BES Cyber Systems and their associated:• EACMSMedium Impact BES Cyber Systems and their associated:• EACMS |  | 31200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | RP-2021-06-18-0000006 | Update the recovery plan based on any documented lessons learned associated with the plan; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 31200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | RP-2021-06-21-0000009 | Procedures for notification of new or modified Facilities to others (thoseresponsible for the reliability of the interconnected Transmission systems) assoon as feasible. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-11-25 |  | 2015-12-31 |  |  |  | 31200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | RP-2021-06-22-0000011 | Transmission topology, including, but not limited to, additions and retirements; |  | TSP | [20 empty] | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | RP-2021-06-22-0000026 | When modeling contingencies the system shall demonstratetransient, dynamic and voltage stability, with no TransmissionElement modeled above its Emergency Rating. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | RP-2021-06-22-0000034 | Unit commitment and Dispatch Order, to include all designated networkresources and other resources that are committed or have the legalobligation to run as specified in the Transmission Service Provider'sATCID. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 61200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | RP-2021-06-23-0000001 | Transmission operations |  | RC | [11 empty] | RC | [10 empty] | 2012-10-01 |  | 2019-06-30 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | RP-2021-06-24-0000042 | For planning events P2 through P7: When a generator pulls out ofsynchronism in the simulations, the resulting apparent impedanceswings shall not result in the tripping of any Transmission systemelements other than the generating unit and its directly connectedFacilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-07-01 |  | 2020-06-10 |  |  |  | 41200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | RP-2021-06-24-0000107 | Review each submitted Operating Plan(s) for coordination to avoid risk to Wide Area reliability; and |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 31200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | RP-2021-06-30-0000003 | Unescorted physical access into a Physical Security Perimeter; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 41200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | RP-2021-06-30-0000015 | Update the recovery plan based on any documented lessons learned associated with the plan; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 31200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | RP-2021-06-30-0000021 | Any commercially available or open-source application software (including version) intentionally installed; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | RP-2021-07-07-0000014 | When modeling contingencies the system shall demonstrate transient, dynamic and voltage stability, with no Transmission Element modeled above its Emergency Rating. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | RP-2021-07-07-0000025 | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. |  | TSP | [20 empty] | TSP |  | 2017-04-01 | [5 empty] | 61200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | RP-2021-07-07-0000029 | Transmission operations |  | RC | [11 empty] | RC | [10 empty] | 2019-07-01 | [5 empty] | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | RP-2021-07-12-0000002 | New planned Facilities and changes to existing Facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | RP-2021-07-12-0000007 | System Off-Peak Load for one of the five years. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | RP-2021-07-12-0000034 | For planning events P2 through P7: When a generator pulls out of synchronism in the simulations, the resulting apparent impedance swings shall not result in the tripping of any Transmission system elements other than the generating unit and its directly connected Facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 41200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | RP-2021-07-13-0000014 | transient voltage response; |  | RC | [11 empty] | RC | [16 empty] | 41200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | RP-2021-07-13-0000029 | Steady state voltages are within normal System Voltage Limits; however, emergency System Voltage Limits may be used when System adjustments to return the voltage within its normal System Voltage Limits could be executed and completed within the specified time duration of those emergency System Voltage Limits. |  | RC | [11 empty] | RC | [16 empty] | 61200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | RP-2021-07-13-0000041 | SOL exceedances of stability limits; |  | RC | [11 empty] | RC | [16 empty] | 71200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2. | RP-2021-07-15-0000017 | Any one BES Element that is part of a stability (angular or voltage) related System Operating Limit (SOL). |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 51200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
12 | 79780000617 | Synchronizing of facilities. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 23100000 | NPCC-ON |  | NPCC-US
12 | 79780001868 | When the desired transmission line capability is limited by the requirement to adequately protect the transmission line, set the transmission line distance relays to a maximum of 125% of the apparent impedance (at the impedance angle of the transmission line) subject to the following constraints: |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  |  | 20200000 | NPCC-ON |  | NPCC-US
12 | 79780002082 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 15100000 | NPCC-ON |  | NPCC-US
12 | 79780002107 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 15100000 | NPCC-ON |  | NPCC-US
12 | 79780002132 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 15100000 | NPCC-ON |  | NPCC-US
12 | 79780002157 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 15100000 | NPCC-ON |  | NPCC-US
12 | 79780003480 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 15100000 | NPCC-ON |  | NPCC-US
12 | 79780003505 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 15100000 | NPCC-ON |  | NPCC-US
12 | 79780003530 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 15100000 | NPCC-ON |  | NPCC-US
12 | 79780004636 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 15100000 | NPCC-ON |  | NPCC-US
12 | 79780004661 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 15100000 | NPCC-ON |  | NPCC-US
12 | 79780004701 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 15100000 | NPCC-ON |  | NPCC-US
12 | 79780004724 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 15100000 | NPCC-ON |  | NPCC-US
12 | 79780005847 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 15100000 | NPCC-ON |  | NPCC-US
12 | 79780005872 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 15100000 | NPCC-ON |  | NPCC-US
12. | 1868 | When the desired transmission line capability is limited by the requirement to adequately protect the transmission line, set the transmission line distance relays to a maximum of 125% of the apparent impedance (at the impedance angle of the transmission line) subject to the following constraints: |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  | PRC-023-1 R1. | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
12. | 2082 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 15100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
12. | 2107 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 15100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
12. | 2132 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 15100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
12. | 2157 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 15100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
12. | 2322 | The Transmission Operator directs the Generator Operator to operate the synchronous generator, and the PSS is unavailable for service. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-06-27 |  | 2015-03-31 |  |  | VAR-501-WECC-1 R1. | 20200000 | WECC-US | [5 empty] | WECC-US
12. | 3480 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 15100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
12. | 3505 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 15100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
12. | 3530 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 15100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
12. | 4636 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 15100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
12. | 4661 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 15100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
12. | 4701 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 15100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
12. | 4724 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 15100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
12. | 5847 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 15100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
12. | 5872 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those Demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 15100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
12. | 617 | Synchronizing of facilities. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 23100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
12. | 7840 | The Transmission Operator directs the Generator Operator to operate the synchronous generator, and the PSS is unavailable for service. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-04-01 |  | 2017-06-30 |  |  |  | 20200000 | WECC-US | [5 empty] | WECC-US
12. | RP-2021-06-09-0000001 | When the desired transmission line capability is limited by the requirement toadequately protect the transmission line, set the transmission line distance relays to amaximum of 125% of the apparent impedance (at the impedance angle of thetransmission line) subject to the following constraints: |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2.1. | RP-2021-06-22-0000030 | Use first Contingency criteria consistent with those firstContingency criteria used in planning of operations for theapplicable time periods, including use of Special ProtectionSystems. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 32100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2.1. | RP-2021-07-07-0000020 | Use first Contingency criteria consistent with those first Contingency criteria used in planning of operations for the applicable time periods, including use of Remedial Action Schemes. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 32100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.2.2. | RP-2021-07-07-0000021 | Only the most limiting element in a series configuration needs to be included as a Flowgate. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 32200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.3. | 3034 | If the Transmission Service Provider does not use the data requestedin its transfer or Flowgate capability calculations, and does notmaintain that data, it shall not be required to make that dataavailable |  | TSP | [20 empty] | TSP |  | 2011-04-01 | [5 empty] | 91200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.3. | 6029 | Models all generation (may be either a single generator or multiple generators) that is greater than 20 MVA at the point of interconnection in the studied area. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.3. | 6279 | Electronic access controls; | [23 empty] | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. |  |  | 2016-06-30 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.3. | 6308 | Access to designated storage locations, whether physical or electronic, for BES Cyber System Information. | [23 empty] | An example of evidence may include, but is not limited to, dated documentation of the process to authorize electronic access, unescorted physical access in a Physical Security Perimeter, and access to designated storage locations, whether physical or electronic, for BES Cyber System Information. |  |  | 2016-06-30 |  |  |  | 41300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.3. | 859 | The associated Contingency(ies). |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 | [5 empty] | 51100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.3. | RP-2021-06-15-0000031 | Voltage level and MW and MVAR capacity or demand at point of connection. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.3. | RP-2021-06-21-0000010 | Voltage level and MW and MVAR capacity or demand at point of connection. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-11-25 |  | 2015-12-31 |  |  |  | 31300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.3. | RP-2021-06-22-0000008 | Transient stability limits; |  | TOP | [18 empty] | TOP |  |  |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.3. | RP-2021-06-22-0000027 | Uncontrolled separation shall not occur. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.3. | RP-2021-06-24-0000043 | For planning events P1 through P7: Power oscillations shall exhibitacceptable damping as established by the Planning Coordinator andTransmission Planner. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-07-01 |  | 2020-06-10 |  |  |  | 41300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.3. | RP-2021-06-24-0000108 | Notify each Balancing Authority and Transmission Operator of the results of its review, specifying any time frame for resubmittal of its Operating Plan(s) if revisions are identified. |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 31300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.3. | RP-2021-06-30-0000022 | Any custom software installed; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.3. | RP-2021-07-07-0000015 | Uncontrolled separation shall not occur. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.3. | RP-2021-07-12-0000003 | Real and reactive Load forecasts. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.3. | RP-2021-07-12-0000008 | For each of the studies described in Requirement R2, Parts 2.1.1 and 2.1.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in System response : Real and reactive forecasted Load. Expected transfers. Expected in service dates of new or modified Transmission Facilities. Reactive resource capability. Generation additions, retirements, or other dispatch scenarios. Controllable Loads and Demand Side Management. Duration or timing of known Transmission outages. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.3. | RP-2021-07-12-0000035 | For planning events P1 through P7: Power oscillations shall exhibit acceptable damping as established by the Planning Coordinator and Transmission Planner. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 41300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.3. | RP-2021-07-13-0000015 | angular stability; and |  | RC | [11 empty] | RC | [16 empty] | 41300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.3. | RP-2021-07-13-0000030 | Predetermined stability limits are not exceeded. |  | RC | [11 empty] | RC | [16 empty] | 61300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.3. | RP-2021-07-13-0000042 | Post Contingency SOL exceedances that are identified to have a validated risk of instability, Cascading, and uncontrolled separation; |  | RC | [11 empty] | RC | [16 empty] | 71300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.3. | RP-2021-07-15-0000018 | Each terminal of a high voltage direct current (HVDC) circuit with a nameplate rating greater than or equal to 300 MVA, on the alternating current (AC) portion of the converter. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 51300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
13 | 79780000618 | Maintenance coordination. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 23200000 | NPCC-ON |  | NPCC-US
13 | 79780001872 | Where other situations present practical limitations on circuit capability, set the phase protection relays so they do not operate at or below 115% of such limitations. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  |  | 20300000 | NPCC-ON |  | NPCC-US
13. | 1872 | Where other situations present practical limitations on circuit capability, set the phase protection relays so they do not operate at or below 115% of such limitations. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  | PRC-023-1 R1. | 20300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
13. | 618 | Maintenance coordination. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 23200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
13. | RP-2021-06-09-0000002 | Where other situations present practical limitations on circuit capability, set the phaseprotection relays so they do not operate at or below 115% of such limitations. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  |  | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.3.1. | RP-2021-06-23-0000006 | Three phase to neutral voltages. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 33100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.3.1. | RP-2021-06-23-0000008 | Voltage, current and frequency. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 43100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.3.2. | RP-2021-06-23-0000007 | Three phase currents and neutral currents. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 33200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.4. | 6030 | Models phase shifters in non-regulating mode, unless otherwise specified in the Available Transfer Capability Implementation Document (ATCID). |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 11400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.4. | RP-2021-06-17-0000003 | The visitor control program; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 21400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.4. | RP-2021-06-21-0000011 | Breaker duty and surge protection. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-11-25 |  | 2015-12-31 |  |  |  | 31400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.4. | RP-2021-06-22-0000006 | Voltage control, including the coordination of reactive resources for voltagecontrol. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 11400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.4. | RP-2021-06-22-0000009 | Voltage stability limits; and |  | TOP | [18 empty] | TOP |  |  |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 11400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.4. | RP-2021-06-24-0000030 | When known outage(s) of generation or Transmission Facility(ies) areplanned in the Near-Term Planning Horizon, the impact of selectedknown outages on System performance shall be assessed. Theseknown outage(s) shall be selected for assessment consistent with adocumented outage coordination procedure or technical rationale bythe Planning Coordinator or Transmission Planner. Known outage(s)shall not be excluded solely based upon outage duration. Theassessment shall be performed for the P0 and P1 categoriesidentified in Table 1 with the System peak or Off-Peak conditions thatthe System is expected to experience when the known outage(s) areplanned. This assessment shall include, at a minimum known outagesexpected to produce more severe System impacts on the PlanningCoordinator or Transmission Planner’s portion of the BES. Past orcurrent studies may support the selection of known outage(s), if thestudy(s) has comparable post-Contingency System conditions and configuration such as those following P3 or P6 category events inTable 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-07-01 |  | 2020-06-10 |  |  |  | 21400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.4. | RP-2021-06-30-0000002 | The visitor control program; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.4. | RP-2021-06-30-0000023 | Any logical network accessible ports; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 11400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.4. | RP-2021-07-02-0000004 | The type of limitation represented by the IROL (e.g., voltage collapse, angular stability). |  | PCPA, RC, TOP, TP | [9 empty] | PA |  | RC | [6 empty] | TOP | TP |  |  | 2009-04-29 | [5 empty] | 51200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.4. | RP-2021-07-12-0000004 | Known commitments for Firm Transmission Service and Interchange. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 11400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.4. | RP-2021-07-12-0000009 | When known outage(s) of generation or Transmission Facility(ies) are planned in the Near-Term Planning Horizon, the impact of selected known outages on System performance shall be assessed. These known outage(s) shall be selected for assessment consistent with a documented outage coordination procedure or technical rationale by the Planning Coordinator or Transmission Planner. Known outage(s) shall not be excluded solely based upon outage duration. The assessment shall be performed for the P0 and P1 categories identified in Table 1 with the System peak or Off-Peak conditions that the System is expected to experience when the known outage(s) are planned. This assessment shall include, at a minimum known outages expected to produce more severe System impacts on the Planning Coordinator or Transmission Planner’s portion of the BES. Past or current studies may support the selection of known outage(s), if the study(s) has comparable post-Contingency System conditions and configuration such as those following P3 or P6 category events in Table 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 21400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.4. | RP-2021-07-13-0000016 | System damping. |  | RC | [11 empty] | RC | [16 empty] | 41400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.4. | RP-2021-07-13-0000031 | Instability, Cascading or uncontrolled separation that adversely impact the reliability of the Bulk Electric System does not occur.Footnote: Stability evaluations and assessments of instability, Cascading, and uncontrolled separation can be performed using real-time stability assessments, predetermined stability limits or other offline analysis techniques. |  | RC | [11 empty] | RC | [16 empty] | 61400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.4. | RP-2021-07-13-0000043 | Pre-Contingency SOL exceedances of Facility Ratings; and |  | RC | [11 empty] | RC | [16 empty] | 71400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.4. | RP-2021-07-15-0000019 | One or more BES Elements that are part of an Interconnection Reliability Operating Limit (IROL). |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 51400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
14 | 79780000619 | Operational issues (abnormal frequency and voltages). |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 23300000 | NPCC-ON |  | NPCC-US
14. | 619 | Operational issues (abnormal frequency and voltages). |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 23300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.4.5. | RP-2021-07-09-0000041 | Transient voltage responses shall be within acceptable limits as established by the Transmission Planner and the Planning Coordinator. |  | PCPA | [9 empty] | PA | [12 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 54500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.5. | RP-2021-06-17-0000004 | Handling of BES Cyber SystemInformation and its storage; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 21500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.5. | RP-2021-06-21-0000012 | System protection and coordination. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-11-25 |  | 2015-12-31 |  |  |  | 31500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.5. | RP-2021-06-22-0000019 | Uses Load forecast by Balancing Authority. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 11500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.5. | RP-2021-06-23-0000004 | Voltage and reactive |  | TOP | [18 empty] | TOP |  |  |  | 2012-10-01 |  | 2019-06-30 |  |  |  | 21500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.5. | RP-2021-06-24-0000031 | When an entity’s spare equipment strategy could result in theunavailability of major Transmission equipment that has a lead timeof one year or more (such as a transformer), the impact of thispossible unavailability on System performance shall be assessed.Based upon this assessment, an analysis shall be performed for theP0, P1, and P2 categories identified in Table 1 with the conditionsthat the System is expected to experience during the possibleunavailability of the long lead time equipment. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-07-01 |  | 2020-06-10 |  |  |  | 21500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.5. | RP-2021-06-30-0000024 | Any security patches applied. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 11500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.5. | RP-2021-07-07-0000002 | Unit commitment and dispatch order, to include all designated network resources and other resources that are committed or have the legal obligation to run, (within or out of economic dispatch) as they are expected to run. |  | TOP | [18 empty] | TOP |  |  |  | 2013-10-01 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 31500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.5. | RP-2021-07-07-0000007 | Uses Load forecast by Balancing Authority. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 11500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.5. | RP-2021-07-07-0000032 | Voltage and reactive |  | TOP | [18 empty] | TOP |  |  |  | 2019-07-01 | [5 empty] | 21500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.5. | RP-2021-07-09-0000048 | When an entity’s spare equipment strategy could result in the unavailability of major Transmission equipment that has a lead time of one year or more (such as a transformer), the impact of this possible unavailability on System performance shall be studied. The studies shall be performed for the P0, P1, and P2 categories identified in Table 1 with the conditions that the System is expected to experience during the possible unavailability of the long lead time equipment. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 21500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.5. | RP-2021-07-12-0000006 | Resources (supply or demand side) required for Load. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 11500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.5. | RP-2021-07-12-0000010 | When an entity’s spare equipment strategy could result in the unavailability of major Transmission equipment that has a lead time of one year or more (such as a transformer), the impact of this possible unavailability on System performance shall be assessed. Based upon this assessment, an analysis shall be performed for the P0, P1, and P2 categories identified in Table 1 with the conditions that the System is expected to experience during the possible unavailability of the long lead time equipment. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 21500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.5. | RP-2021-07-13-0000044 | Pre-Contingency SOL exceedances of normal minimum System Voltage Limits. |  | RC | [11 empty] | RC | [16 empty] | 71500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.5. | RP-2021-07-15-0000020 | Any one BES Element within a major voltage sensitive area as defined by an area with an in-service undervoltage load shedding (UVLS) program. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 51500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
15 | 79780000620 | Inspection requirements for existing or new facilities. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 23400000 | NPCC-ON |  | NPCC-US
15. | 620 | Inspection requirements for existing or new facilities. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 23400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.6. | 6282 | Identification of a Cyber Security Incident and initial notifications in accordance with the entity’s incident response plan; | [23 empty] | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. |  |  | 2016-06-30 |  |  |  | 21600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.6. | RP-2021-06-21-0000013 | Metering and telecommunications. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-11-25 |  | 2015-12-31 |  |  |  | 31600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.6. | RP-2021-06-22-0000020 | Uses Transmission Facility additions and retirements. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 11600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.6. | RP-2021-06-23-0000002 | Voltage and reactive |  | RC | [11 empty] | RC | [10 empty] | 2012-10-01 |  | 2019-06-30 |  |  |  | 11600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.6. | RP-2021-07-07-0000008 | Uses Transmission Facility additions and retirements. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 11600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.6. | RP-2021-07-07-0000030 | Voltage and reactive |  | RC | [11 empty] | RC | [10 empty] | 2019-07-01 | [5 empty] | 11600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
16 | 79780000621 | Communications and procedures during normal and emergency operating conditions. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 23500000 | NPCC-ON |  | NPCC-US
16. | 621 | Communications and procedures during normal and emergency operating conditions. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 23500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.7. | 6283 | Recovery plans for BES Cyber Systems; | [23 empty] | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. |  |  | 2016-06-30 |  |  |  | 21700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.7. | RP-2021-06-21-0000014 | Grounding and safety issues. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-11-25 |  | 2015-12-31 |  |  |  | 31700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.7. | RP-2021-06-22-0000021 | Uses Generation Facility additions and retirements. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 11700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.7. | RP-2021-07-07-0000009 | Uses Generation Facility additions and retirements. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 11700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.8. | 6284 | Response to Cyber Security Incidents; and | [23 empty] | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. |  |  | 2016-06-30 |  |  |  | 21800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.8. | RP-2021-06-21-0000015 | Insulation and insulation coordination. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-11-25 |  | 2015-12-31 |  |  |  | 31800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.8. | RP-2021-06-22-0000022 | Uses Special Protection System (SPS) models where currentlyexisting or projected for implementation within the studied timehorizon. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 11800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.8. | RP-2021-07-07-0000010 | Uses Remedial Action Scheme (RAS) models where currently existing or projected for implementation within the studied time horizon. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 11800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.9. | 6285 | Cyber security risks associated with a BES Cyber System’s electronic interconnectivity and interoperability with other Cyber Assets. | [23 empty] | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. |  |  | 2016-06-30 |  |  |  | 21900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.9. | RP-2021-06-15-0000032 | Voltage, Reactive Power, and power factor control. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 21900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
1.9. | RP-2021-06-21-0000016 | Voltage, Reactive Power, and power factor control. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-11-25 |  | 2015-12-31 |  |  |  | 31900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2 | 79780000021 | Its allocation among members. |  | RRO, RSG | [14 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780000030 | The default Disturbance Recovery Period is 15 minutes after the start of a Reportable Disturbance. This period may be adjusted to better suit the needs of an Interconnection based on analysis approved by the NERC Operating Committee. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780000033 | The Reserve Sharing Group reviews each member’s ACE in response to the activation of reserves. To be in compliance, a member’s ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. |  | RSG | [16 empty] | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780000036 | The default Contingency Reserve Restoration Period is 90 minutes. This period may be adjusted to better suit the reliability targets of the Interconnection based on analysis approved by the NERC Operating Committee. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780000055 | Each Balancing Authority shall report its Frequency Bias Setting, and method for determining that setting, to the NERC Operating Committee. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000058 | The Balancing Authority may use a variable (linear or non-linear) bias value, which is based on a variable function of Tie Line deviation to Frequency Deviation. The Balancing Authority shall determine the variable frequency bias value by analyzing Frequency Response as it varies with factors such as load, generation, governor characteristics, and frequency. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780000062 | The Balancing Authorities that have a fixed schedule (B and C) but do not contain the Jointly Owned Unit shall not include their share of the governor droop response in their Frequency Bias Setting. See Standard for Graphic. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780000068 | Each Balancing Authority shall report its Frequency Bias Setting, and method for determining that setting, to the NERC Operating Committee. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2015-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000071 | The Balancing Authority may use a variable (linear or non-linear) bias value, which is based on a variable function of Tie Line deviation to Frequency Deviation. The Balancing Authority shall determine the variable frequency bias value by analyzing Frequency Response as it varies with factors such as load, generation, governor characteristics, and frequency. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2015-03-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780000075 | The Balancing Authorities that have a fixed schedule (B and C) but do not contain the Jointly Owned Unit shall not include their share of the governor droop response in their Frequency Bias Setting. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2015-03-31 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780000081 | Each Balancing Authority shall report its Frequency Bias Setting, and method for determining that setting, to the NERC Operating Committee. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000084 | The Balancing Authority may use a variable (linear or non-linear) bias value, which is based on a variable function of Tie Line deviation to Frequency Deviation. The Balancing Authority shall determine the variable frequency bias value by analyzing Frequency Response as it varies with factors such as load, generation, governor characteristics, and frequency. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780000088 | The Balancing Authorities that have a fixed schedule (B and C) but do not contain the Jointly Owned Unit shall not include their share of the governor droop response in their Frequency Bias Setting. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780000094 | Each Balancing Authority shall report its Frequency Bias Setting, and method for determining that setting, to the NERC Operating Committee. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2009-06-28 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000097 | The Balancing Authority may use a variable (linear or non-linear) bias value, which is based on a variable function of Tie Line deviation to Frequency Deviation. The Balancing Authority shall determine the variable frequency bias value by analyzing Frequency Response as it varies with factors such as load, generation, governor characteristics, and frequency. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2009-06-28 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780000101 | The Balancing Authorities that have a fixed schedule (B and C) but do not contain the Jointly Owned Unit shall not include their share of the governor droop response in their Frequency Bias Setting. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2009-06-28 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780000117 | The Balancing Authority shall offset its Net Interchange Schedule (MW) by an amount equal to the computed bias contribution during a 0.02 Hertz Frequency Deviation (i.e. 20% of the Frequency Bias Setting). |  | BA | BA | [21 empty] | 2007-06-18 |  | 2017-04-01 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780000123 | The Balancing Authority shall offset its Net Interchange Schedule (MW) by an amount equal to the computed bias contribution during a 0.02 Hertz Frequency Deviation (i.e., 20% of the Frequency Bias Setting). |  | BA | BA | [23 empty] | 2012-08-16 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780000138 | Each Transmission Operator with transmission facilities operating in an Interconnection shall ensure that those transmission facilities are included within the metered boundaries of a Balancing Authority Area. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2008-08-26 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000144 | Balancing Authorities shall ensure the power flow and ACE signals that are utilized for calculating Balancing Authority performance or that are transmitted for Regulation Service are not filtered prior to transmission, except for the Anti-aliasing Filters of Tie Lines. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 122000000 | NPCC-ON |  | NPCC-US
2 | 79780000163 | Each Transmission Operator with transmission facilities operating in an Interconnection shall ensure that those transmission facilities are included within the metered boundaries of a Balancing Authority Area. |  | TOP | [18 empty] | TOP |  |  |  | 2009-05-13 |  | 2012-09-12 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000169 | Balancing Authorities shall ensure the power flow and ACE signals that are utilized for calculating Balancing Authority performance or that are transmitted for Regulation Service are not filtered prior to transmission, except for the Anti-aliasing Filters of Tie Lines. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2012-09-12 |  |  |  | 122000000 | NPCC-ON |  | NPCC-US
2 | 79780000188 | Each Transmission Operator with transmission facilities operating in an Interconnection shall ensure that those transmission facilities are included within the metered boundaries of a Balancing Authority Area. |  | TOP | [18 empty] | TOP |  |  |  | 2008-08-27 |  | 2009-05-12 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000194 | Balancing Authorities shall ensure the power flow and ACE signals that are utilized for calculating Balancing Authority performance or that are transmitted for Regulation Service are not filtered prior to transmission, except for the Anti-aliasing Filters of Tie Lines. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 122000000 | NPCC-ON |  | NPCC-US
2 | 79780000217 | The hourly integrated megawatt-hour values of Net Actual Interchange. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | 41200000 | NPCC-ON |  | NPCC-US
2 | 79780000218 | Each Balancing Authority shall use the agreed-to daily and monthly accounting data to compile its monthly accumulated Inadvertent Interchange for the On-Peak and Off-Peak hours of the month. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780000227 | The hourly integrated megawatt-hour values of Net Actual Interchange. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-03-31 |  |  |  | 41200000 | NPCC-ON |  | NPCC-US
2 | 79780000228 | Each Balancing Authority shall use the agreed-to daily and monthly accounting data to compile its monthly accumulated Inadvertent Interchange for the On-Peak and Off-Peak hours of the month. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-03-31 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780000246 | The risk-based assessment shall consider the following assets: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-04-07 |  | 2010-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000248 | Transmission substations that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 12200000 | NPCC-ON |  | NPCC-US
2 | 79780000257 | The Cyber Asset uses a routable protocol within a control center; or, |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780000262 | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000266 | Changes to the senior manager must be documented within thirty calendar days of the effective date. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780000270 | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures, or a statement accepting risk. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780000274 | The Responsible Entity shall classify information to be protected under this program based on the sensitivity of the Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780000279 | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 51200000 | NPCC-ON |  | NPCC-US
2 | 79780000280 | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780000286 | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-04-07 |  | 2010-03-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780000288 | Physical and electronic access controls to Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 22200000 | NPCC-ON |  | NPCC-US
2 | 79780000294 | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780000298 | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-04-07 |  | 2010-03-31 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780000301 | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000308 | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780000313 | The authentication methods. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 25200000 | NPCC-ON |  | NPCC-US
2 | 79780000319 | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780000322 | A review to verify that only ports and services required for operations at these access points are enabled; |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780000328 | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780000332 | Processes to identify all access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000342 | Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780000347 | Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R2.3. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780000350 | Video Recording: Electronic capture of video images of sufficient quality to determine identity. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780000355 | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R6.1. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780000359 | Processes to identify all access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000369 | Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780000374 | Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R2.3. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780000377 | Video Recording: Electronic capture of video images of sufficient quality to determine identity. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780000382 | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R6.1. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780000386 | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000390 | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780000394 | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure or an acceptance of risk. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780000397 | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780000401 | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 51200000 | NPCC-ON |  | NPCC-US
2 | 79780000403 | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780000405 | The Responsible Entity shall identify those individuals with access to shared accounts. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 52200000 | NPCC-ON |  | NPCC-US
2 | 79780000409 | Each password shall consist of a combination of alpha, numeric, and “special” characters. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 53200000 | NPCC-ON |  | NPCC-US
2 | 79780000413 | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780000419 | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780000423 | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  |  | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780000429 | Response actions, including roles and responsibilities of incident response teams, incident handling procedures, and communication plans. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000437 | Define the roles and responsibilities of responders. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000444 | Between the Reliability Coordinator and its Transmission Operators and Balancing Authorities. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000454 | Between the Reliability Coordinator and its Transmission Operators and Balancing Authorities. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2009-05-13 |  | 2015-09-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000469 | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780000474 | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780000481 | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780000487 | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780000492 | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780000499 | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780000509 | Deploying all available operating reserve. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780000516 | Request the Reliability Coordinator to declare an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0 “Energy Emergency Alert Levels.” |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780000520 | The Reliability Coordinator shall submit the report to NERC for posting on the NERC Website, noting the expected total MW that may have its transmission service priority changed. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | 92000000 | NPCC-ON |  | NPCC-US
2 | 79780000530 | Deploying all available operating reserve. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-09-30 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780000537 | Request the Reliability Coordinator to declare an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0 “Energy Emergency Alert Levels.” |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-09-30 |  |  |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780000541 | The Reliability Coordinator shall submit the report to NERC for posting on the NERC Website, noting the expected total MW that may have its transmission service priority changed. |  | RC | [11 empty] | RC | [10 empty] | 2009-05-13 |  | 2011-09-30 |  |  |  | 92000000 | NPCC-ON |  | NPCC-US
2 | 79780000556 | Applicable reporting forms are provided in Attachments 1-EOP-004 and 2-EOP-004. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-12-31 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780000566 | The affected Transmission Operators and Balancing Authorities shall take the necessary actions to restore Bulk Electric System frequency to normal, including adjusting generation, placing additional generators on line, or load shedding. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  |  | 112000000 | NPCC-ON |  | NPCC-US
2 | 79780000571 | The size of the area being reconnected and the capacity of the transmission lines effecting the reconnection and the number of synchronizing points across the system are considered. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  |  | 115200000 | NPCC-ON |  | NPCC-US
2 | 79780000590 | A requirement to demonstrate that blackstart units perform their intended functions as required in the Regional SRP. This requirement can be met through either simulation or testing. The BCP must consider the availability of designated BCP units and initial transmission switching requirements. |  | RRO | [14 empty] | RRO | [7 empty] | 2011-05-23 |  | 2011-05-23 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000593 | Type of test required, including the requirement to start when isolated from the system. |  | RRO | [14 empty] | RRO | [9 empty] | 2011-05-23 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780000599 | The plan shall include procedures and responsibilities for providing basic tie line control and procedures and for maintaining the status of all inter-area schedules, such that there is an hourly accounting of all schedules. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000610 | Transmission facilities, and |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000622 | Procedures for notification of new or modified facilities to others (those responsible for the reliability of the interconnected transmission systems) as soon as feasible. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780000633 | Ensurance of compliance with NERC Reliability Standards and applicable Regional, subregional, Power Pool, and individual system planning criteria and facility connection requirements. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [14 empty] | 2007-06-18 |  | 2011-09-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000640 | The Transmission Owner, in the TVMP, shall identify and document clearances between vegetation and any overhead, ungrounded supply conductors, taking into consideration transmission line voltage, the effects of ambient temperature on conductor sag under maximum design loading, and the effects of wind velocities on conductor sway. Specifically, the Transmission Owner shall establish clearances to be achieved at the time of vegetation management work identified herein as Clearance 1, and shall also establish and maintain a set of clearances identified herein as Clearance 2 to prevent flashover between vegetation and overhead ungrounded supply conductors. |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000642 | Clearance 2 — The Transmission Owner shall determine and document specific radial clearances to be maintained between vegetation and conductors under all rated electrical operating conditions. These minimum clearance distances are necessary to prevent flashover between vegetation and conductors and will vary due to such factors as altitude and operating voltage. These Transmission Owner-specific minimum clearance distances shall be no less than those set forth in the Institute of Electrical and Electronics Engineers (IEEE) Standard 516-2003 (Guide for Maintenance Methods on Energized Power Lines) and as specified in its Section 4.2.2.3, Minimum Air Insulation Distances without Tools in the Air Gap. |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  |  | 12200000 | NPCC-ON |  | NPCC-US
2 | 79780000644 | Where transmission system transient overvoltage factors are known, clearances shall be derived from Table 7, IEEE 516-2003, phase-to-phase voltages, with appropriate altitude correction factors applied. |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  |  | 12220000 | NPCC-ON |  | NPCC-US
2 | 79780000651 | The Transmission Owner is not required to report to the RRO, or the RRO’s designee, certain sustained transmission line outages caused by vegetation: (1) Vegetation-related outages that result from vegetation falling into lines from outside the ROW that result from natural disasters shall not be considered reportable (examples of disasters that could create non-reportable outages include, but are not limited to, earthquakes, fires, tornados, hurricanes, landslides, wind shear, major storms as defined either by the Transmission Owner or an applicable regulatory body, ice storms, and floods), and (2) Vegetation-related outages due to human or animal activity shall not be considered reportable (examples of human or animal activity that could cause a non-reportable outage include, but are not limited to, logging, animal severing tree, vehicle contact with tree, arboricultural activities or horticultural or agricultural activities, or removal or digging of vegetation). |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780000655 | Category 2 — Fall-ins: Outages caused by vegetation falling into lines from inside the ROW; |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  |  | 34200000 | NPCC-ON |  | NPCC-US
2 | 79780000687 | The method by which the Rating (of major BES equipment that comprises a Facility) is determined. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2012-12-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000689 | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2012-12-31 |  |  |  | 12200000 | NPCC-ON |  | NPCC-US
2 | 79780000692 | Design criteria (e.g., including applicable references to industry Rating practices such as manufacturer’s warranty, IEEE, ANSI or other standards). |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2012-12-31 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780000702 | State that SOLs shall not exceed associated Facility Ratings. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000706 | Following the single Contingencies (see footnote in standard) identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading Outages or uncontrolled separation shall not occur. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-05-29 |  | 2009-04-28 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780000708 | Loss of any generator, line, transformer, or shunt device without a Fault. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-07-01 |  | 2009-04-28 |  |  |  | 22200000 | NPCC-ON |  | NPCC-US
2 | 79780000712 | System reconfiguration through manual or automatic control or protection actions. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-07-01 |  | 2009-04-28 |  |  |  | 23200000 | NPCC-ON |  | NPCC-US
2 | 79780000719 | Selection of applicable Contingencies. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780000726 | Each Reliability Coordinator and Transmission Operator that operates any portion of the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780000731 | State that SOLs shall not exceed associated Facility Ratings. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000735 | Following the single Contingencies identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780000737 | Loss of any generator, line, transformer, or shunt device without a Fault. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 22200000 | NPCC-ON |  | NPCC-US
2 | 79780000741 | System reconfiguration through manual or automatic control or protection actions. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 23200000 | NPCC-ON |  | NPCC-US
2 | 79780000748 | Selection of applicable Contingencies. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780000755 | Each Reliability Coordinator and Transmission Operator that operates any portion of the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780000760 | State that SOLs shall not exceed associated Facility Ratings. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000764 | Following the single Contingencies identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading Outages or uncontrolled separation shall not occur. |  | RC | [11 empty] | RC | [10 empty] | 2008-05-29 |  | 2009-04-28 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780000766 | Loss of any generator, line, transformer, or shunt device without a Fault. |  | RC | [11 empty] | RC | [10 empty] | 2008-10-01 |  | 2009-04-28 |  |  |  | 22200000 | NPCC-ON |  | NPCC-US
2 | 79780000770 | Interruption of other network customers, only if the system has already been adjusted, or is being adjusted, following at least one prior outage, or, if the real-time operating conditions are more adverse than anticipated in the corresponding studies, e.g., load greater than studied. |  | RC | [11 empty] | RC | [10 empty] | 2008-10-01 |  | 2009-04-28 |  |  |  | 23200000 | NPCC-ON |  | NPCC-US
2 | 79780000775 | Selection of applicable Contingencies. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780000784 | Each Planning Authority and Transmission Planner that models any portion of the Reliability Coordinator’s Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780000789 | State that SOLs shall not exceed associated Facility Ratings. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000793 | Following the single Contingencies identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780000795 | Loss of any generator, line, transformer, or shunt device without a Fault. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 22200000 | NPCC-ON |  | NPCC-US
2 | 79780000799 | Interruption of other network customers, (a) only if the system has already been adjusted, or is being adjusted, following at least one prior outage, or (b) if the real-time operating conditions are more adverse than anticipated in the corresponding studies |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 23200000 | NPCC-ON |  | NPCC-US
2 | 79780000804 | Selection of applicable Contingencies |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780000813 | Each Planning Authority and Transmission Planner that models any portion of the Reliability Coordinator’s Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780000818 | A definition stating whether the methodology is applicable to the planning horizon or the operating horizon. |  | PCPA, RC | [9 empty] | PA |  | RC | [12 empty] | 2013-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000821 | System demand |  | PCPA, RC | [9 empty] | PA |  | RC | [12 empty] | 2013-03-31 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780000826 | Each Planning Authority and Transmission Planner that models any portion of the Reliability Coordinator’s Reliability Coordinator Area. |  | RC | [11 empty] | RC | [12 empty] | 2013-03-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780000830 | Each Adjacent Planning Authority and each Planning Authority that indicated a reliability-related need for the methodology. |  | PCPA | [9 empty] | PA | [14 empty] | 2013-03-31 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780000836 | The Planning Authority shall provide its Transfer Capabilities to its associated Reliability Coordinator(s) and Regional Reliability Organization(s), and to the Transmission Planners and Transmission Service Provider(s) that work in its Planning Authority Area. |  | PCPA | [9 empty] | PA | [12 empty] | 2007-06-18 |  | 2013-03-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780000844 | The value of the IROL and its associated Tv. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-01 |  | 2009-04-28 |  |  |  | 51200000 | NPCC-ON |  | NPCC-US
2 | 79780000847 | The Transmission Operator shall provide any SOLs it developed to its Reliability Coordinator and to the Transmission Service Providers that share its portion of the Reliability Coordinator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2008-02-08 |  | 2009-04-28 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780000852 | If the Planning Authority does not identify any stability-related multiple contingencies, the Planning Authority shall so notify the Reliability Coordinator. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780000860 | The value of the IROL and its associated Tv. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 | [5 empty] | 51200000 | NPCC-ON |  | NPCC-US
2 | 79780000863 | The Transmission Operator shall provide any SOLs it developed to its Reliability Coordinator and to the Transmission Service Providers that share its portion of the Reliability Coordinator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2009-04-29 | [5 empty] | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780000868 | If the Planning Authority does not identify any stability-related multiple contingencies, the Planning Authority shall so notify the Reliability Coordinator. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 | [5 empty] | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780000877 | For each bilateral Inadvertent Interchange payback. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780000882 | For each bilateral Inadvertent Interchange payback. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2014-09-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780000886 | Energy profile. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2011-03-31 |  |  |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780000887 | If a high voltage direct current (HVDC) tie is on the Scheduling Path, then the Sending Balancing Authorities and Receiving Balancing Authorities shall coordinate the Interchange Schedule with the Transmission Operator of the HVDC tie. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2011-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000894 | The average energy profile in an hour is less than or equal to 250 MW and in that hour the actual hourly integrated energy deviates from the hourly average energy profile indicated on the tag by more than +25 megawatt-hours. |  | PSE | [10 empty] | PSE | [11 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780000899 | The average energy profile in an hour is less than or equal to 250 MW and in that hour the actual hourly integrated energy deviates from the hourly average energy profile indicated on the tag by more than +25 megawatt-hours. |  | PSE | [10 empty] | PSE | [11 empty] | 2008-08-27 |  | 2014-09-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780000910 | Ramp (ability of generation maneuverability to accommodate). |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780000912 | Each involved Transmission Service Provider shall confirm that the transmission service arrangements associated with the Arranged Interchange have adjacent Transmission Service Provider connectivity, are valid and prevailing transmission system limits will not be violated. |  | TSP | [20 empty] | TSP |  | 2007-06-18 |  | 2008-08-26 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000916 | Ramp (ability of generation maneuverability to accommodate). |  | BA | BA | [21 empty] | 2008-08-27 |  | 2010-06-30 |  |  |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780000918 | Each involved Transmission Service Provider shall confirm that the transmission service arrangements associated with the Arranged Interchange have adjacent Transmission Service Provider connectivity, are valid and prevailing transmission system limits will not be violated. |  | TSP | [20 empty] | TSP |  | 2008-08-27 |  | 2010-06-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000922 | Ramp (ability of generation maneuverability to accommodate). |  | BA | BA | [21 empty] | 2010-07-01 |  | 2014-09-30 |  |  |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780000924 | Each involved Transmission Service Provider shall confirm that the transmission service arrangements associated with the Arranged Interchange have adjacent Transmission Service Provider connectivity, are valid and prevailing transmission system limits will not be violated. |  | TSP | [20 empty] | TSP |  | 2010-01-25 |  | 2014-09-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000927 | All reliability entities involved in the Arranged Interchange are currently in the NERC registry. |  | IA | [6 empty] | IA | [15 empty] | 2007-06-18 |  | 2014-09-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780000930 | Megawatt profile. |  | IA | [6 empty] | IA | [15 empty] | 2007-06-18 |  | 2014-09-30 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780000937 | Necessary Interchange information to NERC-identified reliability analysis services. |  | IA | [6 empty] | IA | [15 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780000941 | Necessary Interchange information to NERC-identified reliability analysis services. |  | IA | [6 empty] | IA | [15 empty] | 2008-08-27 |  | 2010-06-30 |  |  |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780000945 | Necessary Interchange information to NERC-identified reliability analysis services. |  | IA | [6 empty] | IA | [15 empty] | 2010-07-01 |  | 2014-09-30 |  |  |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780000998 | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001025 | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001052 | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001074 | The equivalent Interconnection-wide transmission loading relief procedure for use in the Western Interconnection is the “WSCC Unscheduled Flow Mitigation Plan,” provided at: &lt;a href=&quot;http://www.wecc.biz/documents/library/UFAS/UFAS_&quot;&gt;http://www.wecc.biz/documents/library/UFAS/UFAS_&lt;/a&gt; mitigation_plan _rev_2001-clean_8-8-03.pdf. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-04-22 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780001082 | The Interconnection-wide transmission loading relief procedure for use in the Western Interconnection is WECC-IRO-STD-006-0 provided at: ftp://www.nerc.com/pub/sys/all_updl/standards/rrs/IRO-STD-006-&lt;br/&gt;0_17Jan07.pdf. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-23 |  | 2009-12-09 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001100 | Mutually agreeable format. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2009-08-05 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001108 | Energy and capacity shortages. |  | RC | [11 empty] | RC | [9 empty] | M1.1.2 Energy and capacity shortages. | 2007-06-18 |  | 2017-03-31 |  |  |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780001115 | Distributed to all Reliability Coordinators that are required to take the indicated action(s). |  | RC | [11 empty] | RC | [9 empty] | M2.2 Distributed to all Reliability Coordinators that are required to take the indicated&lt;br/&gt;action(s) | 2007-06-18 |  | 2017-03-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780001118 | The agreed-upon actions from the associated Reliability Coordinator-to-Reliability Coordinator Operating Procedure, Process, or Plan. |  | RC | [11 empty] | RC | [9 empty] | M3.2 Include a reference to the associated source document, and Support the agreed-upon actions from the source document. | 2007-06-18 |  | 2017-03-31 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780001121 | Include a distribution list. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780001130 | If the involved Reliability Coordinators cannot agree on the problem(s) each Reliability Coordinator shall re-evaluate the causes of the disagreement (bad data, status, study results, tools, etc.). |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001132 | If time does not permit, then each Reliability Coordinator shall operate as though the problem(s) exist(s) until the conflicting system status is resolved. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 12200000 | NPCC-ON |  | NPCC-US
2 | 79780001138 | An accounting for how the reservations and schedules for firm (non-recallable) and non-firm (recallable) transfers, both within and outside the Transmission Service Provider’s system, are included. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001143 | Daily values for day 8 through the first month at least once per week. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 15200000 | NPCC-ON |  | NPCC-US
2 | 79780001153 | Daily values for at least the next 31 calendar days. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780001157 | A description of the manner in which the Transmission Service Provider will account for counterflows including: |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780001159 | A rationale for that accounting specified in R3.2. |  | TSP | [20 empty] | TSP |  |  |  | 2010-09-16 |  |  |  | 32200000 | NPCC-ON |  | NPCC-US
2 | 79780001165 | The criteria used to determine when an outage that is in effect part of a month impacts a monthly calculation. |  | TSP | [20 empty] | TSP |  |  |  | 2010-09-16 |  |  |  | 36200000 | NPCC-ON |  | NPCC-US
2 | 79780001169 | Each Reliability Coordinator associated with the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780001179 | Daily values, once per day. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780001184 | If the Transmission Service Provider does not use the data requested in its transfer or Flowgate capability calculations, but maintains that data, it shall make that data available. |  | TSP | [20 empty] | TSP |  |  |  | 2010-09-16 |  |  |  | 91200000 | NPCC-ON |  | NPCC-US
2 | 79780001186 | This data shall be made available by the Transmission Provider on the schedule specified by the requestor (but no more frequently than once per hour, unless mutually agreed to by the requester and the provider). |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 92000000 | NPCC-ON |  | NPCC-US
2 | 79780001192 | The amount of time it will take for a response. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001199 | Specify the frequency of calculation of the generation reliability requirement and associated CBM values. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001210 | The procedure and assumptions for establishing CBM for each Available Transfer Capability (ATC) Path or Flowgate. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001216 | The EEA 2 is declared within the Balancing Authority Area of the “energy deficient entity,” and |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 122000000 | NPCC-ON |  | NPCC-US
2 | 79780001221 | Identifying expected import path(s) or source region(s). |  | LSE | [7 empty] | LSE | [14 empty] | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780001224 | Identifying expected import path(s) or source region(s). |  | RP | [13 empty] | RP | [8 empty] | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780001227 | Be allocated as follows: For ATC Paths, based on the expected import paths or source regions provided by Load-Serving Entities or Resource Planners; For Flowgates, based on the expected import paths or source regions provided by Load-Serving Entities or Resource Planners and the distribution factors associated with those paths or regions, as determined by the Transmission Service Provider |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780001230 | Be allocated as follows: For ATC Paths, based on the expected import paths or source regions provided by Load-Serving Entities or Resource Planners; For Flowgates, based on the expected import paths or source regions provided by Load-Serving Entities or Resource Planners and the distribution factors associated with those paths or regions, as determined by the Transmission Planner. |  | TP | [19 empty] | TP |  |  | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780001235 | To any Transmission Service Provider, Reliability Coordinator, Transmission Planner, Resource Planner, or Planning Coordinator within 30 calendar days of their making a request for the data. |  | TP, TSP | [19 empty] | TP | TSP |  | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 92000000 | NPCC-ON |  | NPCC-US
2 | 79780001238 | Require review of the process by which CBM values are updated, and their frequency of update, to ensure that the most current CBM values are available to transmission users. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001245 | Require that CBM shall only be used if the Load-Serving Entity calling for its use is experiencing a generation deficiency and its Transmission Service Provider is also experiencing Transmission Constraints relative to imports of energy on its transmission system. |  | TSP | [20 empty] | TSP |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001250 | Require that CBM shall only be used if the Load-Serving Entity calling for its use is experiencing a generation deficiency and its Transmission Service Provider is also experiencing Transmission Constraints relative to imports of energy on its transmission system. |  | TSP | [20 empty] | TSP |  | 2009-05-13 |  | 2011-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001256 | Duration. |  | TSP | [20 empty] | TSP |  | 2007-06-18 |  | 2011-03-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780001260 | Specify how TRM values are incorporated into Available Transfer Capability calculations. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001263 | Load distribution error. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780001275 | The description of the method used to allocate TRM across ATC Paths or Flowgates. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 | [5 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001278 | Day-ahead and pre-schedule. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 | [5 empty] | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780001286 | Require review of the process by which TRM values are updated, and their frequency of update, to ensure that the most current TRM values are available to transmission users. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001295 | Generating Units (including synchronous condensers, pumped storage, etc.): location, minimum and maximum Ratings (net Real and Reactive Power), regulated bus and voltage set point, and equipment status. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001307 | Unit-specific dynamics data shall be reported for generators and synchronous condensers (including, as appropriate to the model, items such as inertia constant, damping coefficient, saturation parameters, and direct and quadrature axes reactances and time constants), excitation systems, voltage regulators, turbine-governor systems, power system stabilizers, and other associated generation equipment. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001309 | The Interconnection-wide requirements shall specify unit size thresholds for permitting: The use of non-detailed vs. detailed models, The netting of small generating units with bus load, and The combining of multiple generating units at one plant. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 12200000 | NPCC-ON |  | NPCC-US
2 | 79780001336 | Monthly and annual peak hour actual demands in MW and Net Energy for Load in gigawatthours (GWh) for the prior year. |  | LSE, PCPA, RP | [7 empty] | LSE |  | PA |  |  |  | RP | [8 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001341 | Monthly and annual peak hour actual demands in MW and Net Energy for Load in gigawatthours (GWh) for the prior year. |  | LSE, PCPA, RP | [7 empty] | LSE |  | PA |  |  |  | RP | [8 empty] | 2009-05-13 |  | 2016-06-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001346 | Address assumptions, methods, and the manner in which uncertainties are treated in the forecasts of aggregated peak demands and Net Energy for Load. |  | LSE, PCPA, RP, TP | [7 empty] | LSE |  | PA |  |  |  | RP | [5 empty] | TP |  |  | 2007-06-18 |  | 2016-06-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001357 | Criteria for reporting generating unit auxiliary loads. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001362 | Real power requirements of auxiliary loads. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 15200000 | NPCC-ON |  | NPCC-US
2 | 79780001368 | Criteria for reporting generating unit auxiliary loads. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001373 | Verified Reactive Power limitations, such as generator terminal voltage limitations, shorted rotor turns, etc. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 15200000 | NPCC-ON |  | NPCC-US
2 | 79780001380 | A description of the manner in which the Transmission Operator will account for Interchange Schedules in the calculation of TTC. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2013-09-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001385 | Define if the sink used for ATC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2013-09-30 |  |  |  | 15200000 | NPCC-ON |  | NPCC-US
2 | 79780001392 | Modeling data and topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination areas. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780001397 | Load forecast for the applicable period being calculated. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2013-09-30 |  |  |  | 31200000 | NPCC-ON |  | NPCC-US
2 | 79780001399 | For days two through 31 TTCs and for months two through 13 TTCs, use the following (as well as any other values and internal parameters as specified in the ATCID): |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780001401 | Daily load forecast for the days two through 31 TTCs being calculated and monthly forecast for months two through 13 months TTCs being calculated. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2013-09-30 |  |  |  | 32200000 | NPCC-ON |  | NPCC-US
2 | 79780001405 | Respect any contractual allocations of TTC. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780001409 | At least once per calendar month for TTCs used in monthly ATC calculations. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780001413 | If the limit in step R6.1 can not be reached by adjusting any combination of load or generation, then set the incremental Transfer Capability by the results of the case where the maximum adjustments were applied. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780001418 | Seven calendar days after its determination for TTCs used in monthly ATC calculations. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780001428 | Models all system Elements as in-service for the assumed initial conditions. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780001436 | Uses Facility Ratings as provided by the Transmission Owner and Generator Owner |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001440 | When modeling contingencies the system shall demonstrate transient, dynamic and voltage stability, with no Transmission Element modeled above its Emergency Rating. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780001442 | Where it is impossible to actually simulate a reliability-limited flow in a direction counter to prevailing flows (on an alternating current Transmission line), set the TTC for the non-prevailing direction equal to the TTC in the prevailing direction. If the TTC in the prevailing flow direction is dependant on a Special Protection System (SPS), set the TTC for the non-prevailing flow direction equal to the greater of the maximum flow that can be simulated in the non-prevailing flow direction or the maximum TTC that can be achieved in the prevailing flow direction without use of a SPS. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780001457 | The following information on how source and sink for transmission service is accounted for in AFC calculations including: |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001459 | Define if the sink used for AFC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 12200000 | NPCC-ON |  | NPCC-US
2 | 79780001464 | For daily AFC, once per day. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 102000000 | NPCC-ON |  | NPCC-US
2 | 79780001472 | Results of a first Contingency transfer analyses from all adjacent Balancing Authority source and sink (as defined in the ATCID) combinations up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an Outage Transfer Distribution Factor (OTDF) of at least 5% and within the Transmission Operator’s system are included as Flowgates unless the interface between such adjacent Balancing Authorities is accounted for using another ATC methodology. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780001479 | At a minimum, establish the list of Flowgates to create, modify, or delete internal Flowgates definitions at least once per calendar year. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780001487 | Updated at least once per day for AFC calculations for intra-day, next day, and days two through 30. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780001494 | Include in the transmission model expected generation and Transmission outages, additions, and retirements within the scope of the model as specified in the ATCID and in effect during the applicable period of the AFC calculation for the Transmission Service Provider’s area, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780001499 | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 61200000 | NPCC-ON |  | NPCC-US
2 | 79780001500 | The impact of any firm Network Integration Transmission Service, including the impacts of generation to load in the model referenced in R5.2 and has a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed based on:. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780001502 | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 62200000 | NPCC-ON |  | NPCC-US
2 | 79780001510 | The impact of any confirmed non-firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780001520 | The following information on how source and sink for transmission service is accounted for in AFC calculations including: |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001522 | Define if the sink used for AFC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 12200000 | NPCC-ON |  | NPCC-US
2 | 79780001527 | For daily AFC, once per day. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 102000000 | NPCC-ON |  | NPCC-US
2 | 79780001536 | Results of a first Contingency transfer analysis from all adjacent Balancing Authority source and sink (as defined in the ATCID) combinations up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an Outage Transfer Distribution Factor (OTDF) of at least 5% and within the Transmission Operator’s system are included as Flowgates unless the interface between such adjacent Balancing Authorities is accounted for using another ATC methodology. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780001538 | Only the most limiting element in a series configuration needs to be included as a Flowgate. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21220000 | NPCC-ON |  | NPCC-US
2 | 79780001543 | The limiting Element/Contingency combination is included in the requesting Transmission Service Provider’s methodology. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21420000 | NPCC-ON |  | NPCC-US
2 | 79780001544 | At a minimum, establish a list of Flowgates by creating, modifying, or deleting Flowgate definitions at least once per calendar year. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780001552 | Updated at least once per day for AFC calculations for intra-day, next day, and days two through 30. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780001559 | Include in the transmission model expected generation and Transmission outages, additions, and retirements within the scope of the model as specified in the ATCID and in effect during the applicable period of the AFC calculation for the Transmission Service Provider’s area, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780001564 | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 61200000 | NPCC-ON |  | NPCC-US
2 | 79780001565 | The impact of any firm Network Integration Transmission Service, including the impacts of generation to load in the model referenced in R5.2 and has a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed based on:. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780001567 | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 62200000 | NPCC-ON |  | NPCC-US
2 | 79780001575 | The impact of any confirmed non-firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780001588 | Operate the electric system to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2008-11-26 |  | 2010-03-31 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780001597 | Names of the responsible entities, organizational relationships, andresponsibilities related to the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 91200000 | NPCC-ON |  | NPCC-US
2 | 79780001600 | Technical requirements and analysis: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2008-11-26 |  | 2010-03-31 |  |  |  | 92000000 | NPCC-ON |  | NPCC-US
2 | 79780001602 | Identification of facilities, components, and configuration restrictionsthat are essential for meeting the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 92200000 | NPCC-ON |  | NPCC-US
2 | 79780001606 | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 93200000 | NPCC-ON |  | NPCC-US
2 | 79780001614 | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 94200000 | NPCC-ON |  | NPCC-US
2 | 79780001622 | Positions directly responsible for complying with NERC standards. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-03-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780001625 | The training program must include a plan for the initial and continuing training of Transmission Operator and Balancing Authority operating personnel. That plan shall address knowledge and competencies required for reliable system operations. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-03-31 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780001631 | Positions directly responsible for complying with NERC standards. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2012-09-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001642 | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall design and develop learning objectives and training materials based on the task list created in R1.1. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | M1.2 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection its learning objectives and training materials, as specified in R1.2. | 2013-04-01 |  | 2016-06-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001652 | If a protective relay or equipment failure reduces system reliability, the Transmission Operator shall notify its Reliability Coordinator and affected Transmission Operators and Balancing Authorities. The Transmission Operator shall take corrective action as soon as possible. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-03-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780001655 | Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-03-31 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780001659 | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ protection systems. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-03-31 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780001664 | Devices to be monitored. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780001668 | Elements to be monitored at each location. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780001671 | Three phase currents and neutral currents. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 21320000 | NPCC-ON |  | NPCC-US
2 | 79780001675 | Technical requirements, including the following: |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780001677 | Minimum sampling rate of 16 samples per cycle. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 22200000 | NPCC-ON |  | NPCC-US
2 | 79780001682 | Elements and number of phases to be monitored at each location. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 31200000 | NPCC-ON |  | NPCC-US
2 | 79780001685 | Megawatts and megavars. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 31320000 | NPCC-ON |  | NPCC-US
2 | 79780001686 | Technical requirements, including the following: |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780001688 | Each device shall sample data at a rate of at least 960 samples per second and shall record the RMS value of electrical quantities at a rate of at least 6 records per second. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 32200000 | NPCC-ON |  | NPCC-US
2 | 79780001691 | List of entities that must be provided with recorded Disturbance data. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780001700 | Data reporting requirements (periodicity and format) for Misoperations. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001729 | Summary of maintenance and testing procedures. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2007-06-18 |  | 2011-09-25 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001732 | Date each Protection System device was last tested/maintained. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2007-06-18 |  | 2011-09-25 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780001735 | Design details shall include, but are not limited to: |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001737 | Size of corresponding load shedding blocks (% of connected loads.) |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  |  | 12200000 | NPCC-ON |  | NPCC-US
2 | 79780001747 | Dynamic simulation of possible Disturbance that cause the Region or portions of the Region to experience the largest imbalance between Demand (Load) and generation. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  |  | 14200000 | NPCC-ON |  | NPCC-US
2 | 79780001757 | A review of the UFLS set points and tripping times. |  | DP, LSE, TO, TOP |  | DP | [5 empty] | LSE | [9 empty] | TO | TOP |  |  |  | 2007-06-18 |  | 2013-09-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001764 | Simulations that demonstrate that the UVLS programs performance is consistent with Reliability Standards TPL-001-0, TPL-002-0, TPL-003-0 and TPL-004-0. |  | DP, LSE, TO, TOP |  | DP | [5 empty] | LSE | [9 empty] | TO | TOP |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780001770 | Instrument transformers. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2021-03-31 |  |  |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780001773 | Documentation of maintenance and testing intervals and their basis. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2021-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001781 | Requirements to provide data that describes design, operation, and modeling of an SPS. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001792 | Operation — The actions taken by the SPS in response to Disturbance conditions, and |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001799 | Study years, system conditions, and contingencies analyzed in the technical studies on which the assessment is based and when those technical studies were performed. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780001815 | Instrument transformers. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780001818 | Documentation of maintenance and testing intervals and their basis. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001826 | Recorded data from each Disturbance shall be retrievable for ten calendar days.. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2022-06-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001830 | Make and model of equipment. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2022-06-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780001841 | Summary of maintenance and testing procedures. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2022-06-30 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780001844 | Size and location of customer load, or percent of connected load, to be interrupted. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001852 | Corresponding voltage set points and overall scheme clearing times. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001859 | A review of the UVLS set points and tripping times. |  | DP, LSE, TOP |  | DP | [5 empty] | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001870 | Evaluate the relay loadability in amperes at the relay trip point at 0.85 per unit voltage and a power factor angle of 30 degrees. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  |  | 20400000 | NPCC-ON |  | NPCC-US
2 | 79780001873 | Set transmission line relays so they do not operate at or below 115% of the highest seasonal 15-minute Facility Rating2 of a circuit (expressed in amperes). |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001876 | An impedance at each end of the line, which reflects the actual system source impedance with a 1.05 per unit voltage behind each source impedance. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780001887 | The Planning Coordinator shall maintain a current list of facilities determined according to the process described in R3.1. |  | PCPA | [9 empty] | PA | [12 empty] | 2011-11-17 |  | 2012-06-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780001900 | For a transmission facility, the Transmission Operator shall notify and coordinate with its Reliability Coordinator. The Transmission Operator shall notify other affected Transmission Operators, and coordinate the impact of removing the Bulk Electric System facility. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-11-20 |  |  |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780001910 | Automatic Voltage Regulator status and mode setting. (Retired August 1, 2007) |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2009-12-01 |  |  |  | 142000000 | NPCC-ON |  | NPCC-US
2 | 79780001914 | Changes in transmission facility rating. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-12-01 |  |  |  | 162000000 | NPCC-ON |  | NPCC-US
2 | 79780001933 | Automatic Voltage Regulator status and mode setting. (Retired August 1, 2007) |  | GOP | [5 empty] | GOP | [16 empty] | 2009-12-02 |  | 2011-10-19 |  |  |  | 142000000 | NPCC-ON |  | NPCC-US
2 | 79780001937 | Changes in transmission facility rating. |  | TOP | [18 empty] | TOP |  |  |  | 2009-12-02 |  | 2011-10-19 |  |  |  | 162000000 | NPCC-ON |  | NPCC-US
2 | 79780001951 | Each Transmission Operator shall provide outage information daily to its Reliability Coordinator, and to affected Balancing Authorities and Transmission Operators for scheduled generator and bulk transmission outages planned for the next day (any foreseen outage of a transmission line or transformer greater than 100 kV or generator greater than 50 MW) that may collectively cause or contribute to an SOL or IROL violation or a regional operating area limitation. The Reliability Coordinator shall establish the outage reporting requirements. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-09-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001958 | Each Transmission Operator shall provide outage information daily to affected Balancing Authorities and Transmission Operators for scheduled generator and bulk transmission outages planned for the next day (any foreseen outage of a transmission line or transformer greater than 100 kV or generator greater than 50 MW) that may collectively cause or contribute to an SOL or IROL violation or a regional operating area limitation. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2017-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780001970 | Monitoring and controlling voltage levels and real and reactive power flows. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-01-21 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780001982 | Switching transmission elements. |  | TOP | [18 empty] | TOP |  |  |  | 2009-01-22 |  | 2017-03-31 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780002005 | Each Transmission Operator and Balancing Authority shall inform the Reliability Coordinator and other affected Balancing Authorities and Transmission Operators of all generation and transmission resources available for use. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-09-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002014 | Each Transmission Operator and Balancing Authority shall inform the Reliability Coordinator and other affected Balancing Authorities and Transmission Operators of all generation and transmission resources available for use. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2017-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002035 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002038 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780002050 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780002052 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780002056 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002059 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780002071 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780002073 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780002077 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002083 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780002096 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780002098 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780002102 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002108 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780002121 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780002123 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780002127 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002133 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780002146 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780002148 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780002152 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002158 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780002171 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780002173 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780002177 | Be conducted for near-term (years one through five). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002180 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780002193 | Summer. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780002195 | Near-term planning horizons (years one through five). Detailed assessments shall be conducted. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002201 | Operational assessments. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780002208 | Resource Adequacy and supporting information (Regional assessment reports, existing and planned resource data, resource availability and characteristics, and fuel types and requirements.) |  | RRO | [14 empty] | RRO | [9 empty] | 2009-04-15 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002221 | For each generator that is on this exemption list, the Transmission Operator shall notify the associated Generator Owner. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-09-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780002237 | For each generator that is on this exemption list, the Transmission Operator shall notify the associated Generator Owner. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-05-21 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780002249 | When directed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780002252 | A status or capability change on any other Reactive Power resources under the Generator Operator’s control and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780002256 | Available fixed tap ranges. |  | GO | [22 empty] | 2007-08-02 |  | 2008-08-26 |  |  |  | 41200000 | NPCC-ON |  | NPCC-US
2 | 79780002264 | When directed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2009-05-13 |  | 2010-09-15 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780002267 | A status or capability change on any other Reactive Power resources under the Generator Operator’s control and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2009-05-13 |  | 2010-09-15 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780002271 | Available fixed tap ranges. |  | GO | [22 empty] | 2009-05-13 |  | 2010-09-15 |  |  |  | 41200000 | NPCC-ON |  | NPCC-US
2 | 79780002279 | When directed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2010-09-16 |  | 2013-06-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780002282 | A status or capability change on any other Reactive Power resources under the Generator Operator’s control and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2010-09-16 |  | 2013-06-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780002286 | Available fixed tap ranges. |  | GO | [22 empty] | 2010-09-16 |  | 2013-06-30 |  |  |  | 41200000 | NPCC-ON |  | NPCC-US
2 | 79780002294 | When directed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780002297 | A status or capability change on any other Reactive Power resources under the Generator Operator’s control and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780002301 | Available fixed tap ranges. |  | GO | [22 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 41200000 | NPCC-ON |  | NPCC-US
2 | 79780002336 | The Interconnection-wide transmission loading relief procedure for use in the Western Interconnection is the WECC Unscheduled Flow Reduction Procedure provided at: &lt;a href=&quot;http://www.wecc.biz/documents/library/UFAS/UFAS_mitigation_plan_rev_2001-clean_8-8-03.pdf.&quot;&gt;http://www.wecc.biz/documents/library/UFAS/UFAS_mitigation_plan_rev_2001-clean_8-8-03.pdf.&lt;/a&gt; |  | RC | [11 empty] | RC | [10 empty] | 2009-12-10 |  | 2011-06-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002348 | Resource Adequacy and supporting information (Regional assessment reports, existing and planned resource data, resource availability and characteristics, and fuel types and requirements.) |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002356 | The risk-based assessment shall consider the following assets: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002358 | Transmission substations that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 12200000 | NPCC-ON |  | NPCC-US
2 | 79780002367 | The Cyber Asset uses a routable protocol within a control center; or, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780002372 | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002376 | Changes to the senior manager must be documented within thirty calendar days of the effective date. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780002381 | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780002385 | The Responsible Entity shall classify information to be protected under this program based on the sensitivity of the Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780002390 | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 51200000 | NPCC-ON |  | NPCC-US
2 | 79780002391 | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780002397 | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-2, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780002399 | Physical and electronic access controls to Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 22200000 | NPCC-ON |  | NPCC-US
2 | 79780002405 | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780002409 | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780002412 | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002419 | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780002424 | The authentication methods. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 25200000 | NPCC-ON |  | NPCC-US
2 | 79780002430 | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780002433 | A review to verify that only ports and services required for operations at these access points are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780002439 | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780002443 | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002452 | Be afforded the protective measures specified in Standard CIP-003-2; Standard CIP-004-2 Requirement R3; Standard CIP-005-2 Requirements R2 and R3; Standard CIP-006-2 Requirements R4 and R5; Standard CIP-007-2; Standard CIP-008-2; and Standard CIP-009-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780002460 | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  |  | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780002464 | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002468 | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780002472 | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780002475 | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780002479 | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 51200000 | NPCC-ON |  | NPCC-US
2 | 79780002481 | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780002483 | The Responsible Entity shall identify those individuals with access to shared accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 52200000 | NPCC-ON |  | NPCC-US
2 | 79780002487 | Each password shall consist of a combination of alpha, numeric, and “special” characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 53200000 | NPCC-ON |  | NPCC-US
2 | 79780002491 | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780002497 | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780002501 | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  |  | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780002507 | Response actions, including roles and responsibilities of Cyber Security Incident response teams, Cyber Security Incident handling procedures, and communication plans. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002515 | Define the roles and responsibilities of responders. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002525 | Operate the electric system to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780002534 | Names of the responsible entities, organizational relationships, and responsibilities related to the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2014-01-21 |  |  |  | 91200000 | NPCC-ON |  | NPCC-US
2 | 79780002537 | Technical requirements and analysis: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 92000000 | NPCC-ON |  | NPCC-US
2 | 79780002539 | Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 92200000 | NPCC-ON |  | NPCC-US
2 | 79780002543 | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 93200000 | NPCC-ON |  | NPCC-US
2 | 79780002551 | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 94200000 | NPCC-ON |  | NPCC-US
2 | 79780002558 | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780002562 | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780002569 | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780002574 | A description of how all Agreements or mutually agreed upon procedures or protocols for off-site power requirements of nuclear power plants, including priority of restoration, will be fulfilled during System restoration. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002584 | Restoration priorities. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  |  | 102000000 | NPCC-ON |  | NPCC-US
2 | 79780002594 | Each Generator Operator shall provide the blackstart test results within 30 calendar days following a request from its Reliability Coordinator or Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-05-23 |  | 2019-03-31 |  |  |  | 162000000 | NPCC-ON |  | NPCC-US
2 | 79780002597 | The procedures documented in Requirement R14. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-05-23 |  | 2019-03-31 |  |  |  | 172000000 | NPCC-ON |  | NPCC-US
2 | 79780002607 | The location and magnitude of Loads required to control voltages and frequency within acceptable operating limits. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780002613 | A list of required tests including: |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  |  | 92000000 | NPCC-ON |  | NPCC-US
2 | 79780002615 | The ability to energize a bus. If it is not possible to energize a bus during the test, the testing entity must affirm that the unit has the capability to energize a bus such as verifying that the breaker close coil relay can be energized with the voltage and frequency monitor controls disconnected from the synchronizing circuits. |  | TOP | [18 empty] | TOP |  |  |  | 2013-07-01 |  | 2019-03-31 |  |  |  | 92200000 | NPCC-ON |  | NPCC-US
2 | 79780002619 | Operating Processes for restoring the Interconnection. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002640 | Reestablishing the Interconnection. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  |  | 92000000 | NPCC-ON |  | NPCC-US
2 | 79780002652 | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002653 | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780002657 | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780002658 | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780002660 | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780002663 | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 51200000 | NPCC-ON |  | NPCC-US
2 | 79780002668 | The Responsible Entity shall identify those individuals with access to shared accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 52200000 | NPCC-ON |  | NPCC-US
2 | 79780002671 | Each password shall consist of a combination of alpha, numeric, and “special” characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 53200000 | NPCC-ON |  | NPCC-US
2 | 79780002674 | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780002677 | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780002680 | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  |  | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780002691 | State that SOLs shall not exceed associated Facility Ratings. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002693 | Following the single Contingencies identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780002699 | Loss of any generator, line, transformer, or shunt device without a Fault. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 22200000 | NPCC-ON |  | NPCC-US
2 | 79780002701 | System reconfiguration through manual or automatic control or protection actions. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 23200000 | NPCC-ON |  | NPCC-US
2 | 79780002709 | Selection of applicable Contingencies. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780002710 | Each Reliability Coordinator and Transmission Operator that operates any portion of the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780002715 | The risk-based assessment shall consider the following assets: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002717 | Transmission substations that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | 12200000 | NPCC-ON |  | NPCC-US
2 | 79780002726 | The Cyber Asset uses a routable protocol within a control center; or, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780002731 | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002735 | Changes to the senior manager must be documented within thirty calendar days of the effective date. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780002740 | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780002744 | The Responsible Entity shall classify information to be protected under this program based on the sensitivity of the Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780002749 | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  |  |  | 51200000 | NPCC-ON |  | NPCC-US
2 | 79780002750 | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780002756 | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-3, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2012-12-11 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780002758 | Physical and electronic access controls to Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2012-12-11 |  |  |  | 22200000 | NPCC-ON |  | NPCC-US
2 | 79780002764 | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2012-12-11 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780002768 | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2012-12-11 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780002771 | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002778 | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780002783 | The authentication methods. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2011-02-01 |  |  |  | 25200000 | NPCC-ON |  | NPCC-US
2 | 79780002789 | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780002792 | A review to verify that only ports and services required for operations at these access points are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780002798 | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780002802 | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002808 | Continuous escorted access of visitors within the Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-09-30 |  |  |  | 16200000 | NPCC-ON |  | NPCC-US
2 | 79780002813 | Be afforded the protective measures specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirements R4 and R5; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780002821 | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  |  | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780002825 | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002829 | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780002833 | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780002836 | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780002840 | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 51200000 | NPCC-ON |  | NPCC-US
2 | 79780002842 | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780002844 | The Responsible Entity shall identify those individuals with access to shared accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 52200000 | NPCC-ON |  | NPCC-US
2 | 79780002848 | Each password shall consist of a combination of alpha, numeric, and “special” characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 53200000 | NPCC-ON |  | NPCC-US
2 | 79780002852 | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780002858 | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780002862 | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780002868 | Response actions, including roles and responsibilities of Cyber Security Incident response teams, Cyber Security Incident handling procedures, and communication plans. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002876 | Define the roles and responsibilities of responders. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002894 | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002897 | Be afforded the protective measures specified in Standard CIP-003-2; Standard CIP-004-2 Requirement R3; Standard CIP-005-2 Requirements R2 and R3; Standard CIP-006-2 Requirements R4 and R5; Standard CIP-007-2; Standard CIP-008-2; and Standard CIP-009-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780002900 | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  |  | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780002915 | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002918 | Be afforded the protective measures specified in Standard CIP-003-2; Standard CIP-004-2 Requirement R3; Standard CIP-005-2 Requirements R2 and R3; Standard CIP-006-2 Requirements R4 and R5; Standard CIP-007-2; Standard CIP-008-2; and Standard CIP-009-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780002921 | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  |  | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780002935 | Processes to identify all access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002938 | Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780002943 | Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R2.3. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780002944 | Video Recording: Electronic capture of video images of sufficient quality to determine identity. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780002948 | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R6.1. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780002956 | Video Recording: Electronic capture of video images of sufficient quality to determine identity. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780002961 | Processes to identify all access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002970 | Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780002972 | Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R2.3. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780002975 | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R6.1. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780002990 | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780002994 | Continuous escorted access of visitors within the Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  |  | 16200000 | NPCC-ON |  | NPCC-US
2 | 79780002996 | Be afforded the protective measures specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirements R4 and R5; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780002998 | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  |  | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780003009 | Daily values for at least the next 31 calendar days. |  | TSP | [20 empty] | TSP | M2.2 -- There has been at least 31 consecutive calendar days of daily values calculated at all times. | 2010-09-16 | [5 empty] | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780003017 | A description of the manner in which the Transmission Service Provider will account for counterflows including: |  | TSP | [20 empty] | TSP |  | 2010-09-16 | [5 empty] | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780003018 | A rationale for that accounting specified in R3.2. |  | TSP | [20 empty] | TSP |  | 2011-04-01 | [5 empty] | 32200000 | NPCC-ON |  | NPCC-US
2 | 79780003021 | The criteria used to determine when an outage that is in effect part of a month impacts a monthly calculation. |  | TSP | [20 empty] | TSP |  | 2011-04-01 | [5 empty] | 36200000 | NPCC-ON |  | NPCC-US
2 | 79780003027 | Each Reliability Coordinator associated with the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-09-16 | [5 empty] | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780003029 | Daily values, once per day. |  | TSP | [20 empty] | TSP |  | 2010-09-16 | [5 empty] | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780003033 | This data shall be made available by the Transmission Provider on the schedule specified by the requestor (but no more frequently than once per hour, unless mutually agreed to by the requester and the provider). |  | TSP | [20 empty] | TSP |  | 2010-09-16 | [5 empty] | 92000000 | NPCC-ON |  | NPCC-US
2 | 79780003034 | If the Transmission Service Provider does not use the data requested in its transfer or Flowgate capability calculations, but maintains that data, it shall make that data available. |  | TSP | [20 empty] | TSP |  | 2011-04-01 | [5 empty] | 91200000 | NPCC-ON |  | NPCC-US
2 | 79780003046 | Uses Facility Ratings as provided by the Transmission Owner and Generator Owner |  | TOP | [18 empty] | TOP |  |  | M1.2. The Transmission model produced must include the areas listed in R1.1.1 (or an equivalent representation, as described in the requirement) | 2010-09-16 |  | 2017-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780003052 | Models all system Elements as in-service for the assumed initial conditions. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780003066 | Where it is impossible to actually simulate a reliability-limited flow in a direction counter to prevailing flows (on an alternating current Transmission line), set the TTC for the non-prevailing direction equal to the TTC in the prevailing direction. If the TTC in the prevailing flow direction is dependant on a Special Protection System (SPS), set the TTC for the non-prevailing flow direction equal to the greater of the maximum flow that can be simulated in the non-prevailing flow direction or the maximum TTC that can be achieved in the prevailing flow direction without use of a SPS. |  | TOP | [18 empty] | TOP |  |  |  | 2010-09-16 |  | 2017-03-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780003069 | When modeling contingencies the system shall demonstrate transient, dynamic and voltage stability, with no Transmission Element modeled above its Emergency Rating. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780003074 | Mutually agreeable format. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2017-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780003162 | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780003168 | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780003172 | The authentication methods. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | 25200000 | NPCC-ON |  | NPCC-US
2 | 79780003173 | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780003175 | A review to verify that only ports and services required for operations at these access points are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780003181 | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780003187 | Its allocation among members. |  | RRO, RSG | [14 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780003196 | The default Disturbance Recovery Period is 15 minutes after the start of a Reportable Disturbance. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780003199 | The Reserve Sharing Group reviews each member’s ACE in response to the activation of reserves. To be in compliance, a member’s ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. |  | RSG | [16 empty] | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780003202 | The default Contingency Reserve Restoration Period is 90 minutes. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780003209 | The hourly integrated megawatt-hour values of Net Actual Interchange. |  | BA | BA | [21 empty] | 2011-04-01 |  | 2018-12-31 |  |  |  | 41200000 | NPCC-ON |  | NPCC-US
2 | 79780003210 | Each Balancing Authority shall use the agreed-to daily and monthly accounting data to compile its monthly accumulated Inadvertent Interchange for the On-Peak and Off-Peak hours of the month. |  | BA | BA | [21 empty] | 2011-04-01 |  | 2018-12-31 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780003220 | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780003224 | Changes to the senior manager must be documented within thirty calendar days of the effective date. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780003229 | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780003233 | The Responsible Entity shall classify information to be protected under this program based on the sensitivity of the Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780003238 | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 51200000 | NPCC-ON |  | NPCC-US
2 | 79780003239 | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780003245 | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-4, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2012-12-11 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780003247 | Physical and electronic access controls to Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2012-12-11 |  |  |  | 22200000 | NPCC-ON |  | NPCC-US
2 | 79780003253 | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2012-12-11 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780003257 | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2012-12-11 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780003260 | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780003267 | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780003272 | The authentication methods. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 25200000 | NPCC-ON |  | NPCC-US
2 | 79780003278 | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780003281 | A review to verify that only ports and services required for operations at these access points are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780003287 | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780003291 | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780003297 | Continuous escorted access of visitors within the Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 16200000 | NPCC-ON |  | NPCC-US
2 | 79780003302 | Be afforded the protective measures specified in Standard CIP-003-4; Standard CIP-004-4 Requirement R3; Standard CIP-005-4 Requirements R2 and R3; Standard CIP-006-4 Requirements R4 and R5; Standard CIP-007-4; Standard CIP-008-4; and Standard CIP-009-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780003310 | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780003314 | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780003318 | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780003322 | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780003325 | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780003329 | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 51200000 | NPCC-ON |  | NPCC-US
2 | 79780003331 | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780003333 | The Responsible Entity shall identify those individuals with access to shared accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 52200000 | NPCC-ON |  | NPCC-US
2 | 79780003337 | Each password shall consist of a combination of alpha, numeric, and “special” characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 53200000 | NPCC-ON |  | NPCC-US
2 | 79780003341 | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780003347 | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780003351 | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780003357 | Response actions, including roles and responsibilities of Cyber Security Incident response teams, Cyber Security Incident handling procedures, and communication plans. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780003365 | Define the roles and responsibilities of responders. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780003377 | Deploying all available operating reserve. |  | BA | BA | [21 empty] | 2011-01-10 |  | 2012-09-12 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780003384 | Request the Reliability Coordinator to declare an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0 “Energy Emergency Alert Levels.” |  | BA | BA | [21 empty] | 2011-01-10 |  | 2012-09-12 |  |  |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780003388 | The Reliability Coordinator shall submit the report to NERC for posting on the NERC Website, noting the expected total MW that may have its transmission service priority changed. |  | RC | [11 empty] | RC | [10 empty] | 2011-01-10 |  | 2012-09-12 |  |  |  | 92000000 | NPCC-ON |  | NPCC-US
2 | 79780003409 | Ensurance of compliance with NERC Reliability Standards and applicable Regional, subregional, Power Pool, and individual system planning criteria and facility connection requirements. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [14 empty] | 2011-01-10 |  | 2015-12-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780003423 | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780003454 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780003457 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-002-0(i)b_R3. |  |  | 2012-07-06 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780003469 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780003471 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780003475 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780003481 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780003494 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780003496 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780003500 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780003506 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780003519 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780003521 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780003525 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780003531 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780003544 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780003546 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780003550 | Be conducted for near-term (years one through five). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780003553 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780003569 | Energy profile. |  | BA | BA | [21 empty] | 2011-04-01 |  | 2014-09-30 |  |  |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780003570 | If a high voltage direct current (HVDC) tie is on the Scheduling Path, then the Sending Balancing Authorities and Receiving Balancing Authorities shall coordinate the Interchange Schedule with the Transmission Operator of the HVDC tie. |  | BA | BA | [21 empty] | 2011-04-01 |  | 2014-09-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780003603 | For each generator that is on this exemption list, the Transmission Operator shall notify the associated Generator Owner. |  | TOP | [18 empty] | TOP |  |  |  | 2011-01-10 |  | 2013-12-31 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780003626 | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780003632 | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780003636 | The authentication methods. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 25200000 | NPCC-ON |  | NPCC-US
2 | 79780003637 | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780003639 | A review to verify that only ports and services required for operations at these access points are enabled; |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780003645 | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780003657 | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780003663 | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780003667 | The authentication methods. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 25200000 | NPCC-ON |  | NPCC-US
2 | 79780003668 | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780003670 | A review to verify that only ports and services required for operations at these access points are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780003676 | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780003695 | Each Transmission Operator with transmission facilities operating in an Interconnection shall ensure that those transmission facilities are included within the metered boundaries of a Balancing Authority Area. |  | TOP | [18 empty] | TOP | [5 empty] | 2008-04-15 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780003699 | Balancing Authorities shall ensure the power flow and ACE signals that are utilized for calculating Balancing Authority performance or that are transmitted for Regulation Service are not filtered prior to transmission, except for the Anti-aliasing Filters of Tie Lines. |  | BA | BA | [23 empty] | 2008-04-15 |  |  |  | 122000000 | NPCC-ON |  | NPCC-US
2 | 79780003706 | Summary of maintenance and testing procedures. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2011-09-26 |  | 2012-03-13 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780003708 | Date each Protection System device was last tested/maintained. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2011-09-26 |  | 2012-03-13 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780003719 | Each Balancing Authority shall report its Frequency Bias Setting, and method for determining that setting, to the NERC Operating Committee. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2009-06-28 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780003720 | The Balancing Authority may use a variable (linear or non-linear) bias value, which is based on a variable function of Tie Line deviation to Frequency Deviation. The Balancing Authority shall determine the variable frequency bias value by analyzing Frequency Response as it varies with factors such as load, generation, governor characteristics, and frequency. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2009-06-28 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780003722 | The Balancing Authorities that have a fixed schedule (B and C) but do not contain the Jointly Owned Unit shall not include their share of the governor droop response in their Frequency Bias Setting. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2009-06-28 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780003786 | Automatic Voltage Regulator status and mode setting. (Retired August 1, 2007) |  | GOP | [5 empty] | GOP | [16 empty] | 2011-10-20 |  | 2012-09-12 |  |  |  | 142000000 | NPCC-ON |  | NPCC-US
2 | 79780003788 | Changes in transmission facility rating. |  | TOP | [18 empty] | TOP |  |  |  | 2011-10-20 |  | 2012-09-12 |  |  |  | 162000000 | NPCC-ON |  | NPCC-US
2 | 79780003808 | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780003820 | For a transmission facility, the Transmission Operator shall notify and coordinate with its Reliability Coordinator. The Transmission Operator shall notify other affected Transmission Operators, and coordinate the impact of removing the Bulk Electric System facility. |  | TOP | [18 empty] | TOP |  |  |  | 2011-11-21 |  | 2017-03-31 |  |  |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780003834 | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780003837 | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780003842 | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780003851 | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780003854 | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780003859 | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780003903 | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780003906 | Be afforded the protective measures specified in Standard CIP-003-2; Standard CIP-004-2 Requirement R3; Standard CIP-005-2 Requirements R2 and R3; Standard CIP-006-2 Requirements R4 and R5; Standard CIP-007-2; Standard CIP-008-2; and Standard CIP-009-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780003909 | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  |  | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780003924 | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780003928 | Continuous escorted access of visitors within the Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2011-05-18 |  |  |  | 16200000 | NPCC-ON |  | NPCC-US
2 | 79780003930 | Be afforded the protective measures specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirements R4 and R5; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780003932 | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  |  | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780003962 | A description of the manner in which the Transmission Operator will account for Interchange Schedules in the calculation of TTC. |  | TSP | [20 empty] | TSP |  | 2013-09-27 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780003967 | Define if the sink used for ATC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation |  | TSP | [20 empty] | TSP |  | 2013-10-01 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 15200000 | NPCC-ON |  | NPCC-US
2 | 79780003974 | Modeling data and topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination areas. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780003979 | A daily or hourly load forecast for TTCs used in current-day and next-day ATC calculations. |  | TOP | [18 empty] | TOP |  |  |  | 2013-10-01 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 31200000 | NPCC-ON |  | NPCC-US
2 | 79780003985 | Respect any contractual allocations of TTC. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780003989 | At least once per calendar month for TTCs used in monthly ATC calculations. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780003993 | If the limit in step R6.1 can not be reached by adjusting any combination of load or generation, then set the incremental Transfer Capability by the results of the case where the maximum adjustments were applied. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780003998 | Seven calendar days after its determination for TTCs used in monthly ATC calculations. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780004035 | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780004044 | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780004046 | Be afforded the protective measures specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirements R4 and R5; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780004048 | Continuous escorted access of visitors within the Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 16200000 | NPCC-ON |  | NPCC-US
2 | 79780004063 | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780004067 | Continuous escorted access of visitors within the Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 16200000 | NPCC-ON |  | NPCC-US
2 | 79780004069 | Be afforded the protective measures specified in Standard CIP-003-4; Standard CIP-004-4 Requirement R3; Standard CIP-005-4 Requirements R2 and R3; Standard CIP-006-4 Requirements R4 and R5; Standard CIP-007-4; Standard CIP-008-4; and Standard CIP-009-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780004071 | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780004079 | Summary of maintenance and testing procedures. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2012-03-14 |  | 2013-11-24 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780004081 | Date each Protection System device was last tested/maintained. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2012-03-14 |  | 2013-11-24 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780004088 | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780004094 | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780004095 | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780004116 | Each Transmission Operator with transmission facilities operating in an Interconnection shall ensure that those transmission facilities are included within the metered boundaries of a Balancing Authority Area. |  | TOP | [18 empty] | TOP |  |  |  | 2012-09-13 |  | 2018-12-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780004120 | Balancing Authorities shall ensure the power flow and ACE signals that are utilized for calculating Balancing Authority performance or that are transmitted for Regulation Service are not filtered prior to transmission, except for the Anti-aliasing Filters of Tie Lines. |  | BA | BA | [21 empty] | 2012-09-13 |  | 2018-12-31 |  |  |  | 122000000 | NPCC-ON |  | NPCC-US
2 | 79780004135 | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780004139 | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780004143 | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780004164 | Changes in transmission facility rating. |  | TOP | [18 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  |  | 162000000 | NPCC-ON |  | NPCC-US
2 | 79780004184 | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780004202 | Deploying all available operating reserve. |  | BA | BA | [21 empty] | 2012-09-13 |  | 2017-03-31 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780004203 | Request the Reliability Coordinator to declare an Energy Emergency Alert in accordance with Attachment 1-EOP-002 “Energy Emergency Alerts.” |  | BA | BA | [21 empty] | 2012-09-13 |  | 2017-03-31 |  |  |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780004206 | The Reliability Coordinator shall submit the report to NERC for posting on the NERC Website, noting the expected total MW that may have its transmission service priority changed. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  |  | 92000000 | NPCC-ON |  | NPCC-US
2 | 79780004220 | Operate the electric system to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP | M4.2 The electric system was operated to meet the NPIRs. (Requirement 4.2) | 2013-04-01 |  | 2015-12-31 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780004223 | Technical requirements and analysis: |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 92000000 | NPCC-ON |  | NPCC-US
2 | 79780004228 | Names of the responsible entities, organizational relationships, and responsibilities related to the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2014-01-21 |  |  |  | 91200000 | NPCC-ON |  | NPCC-US
2 | 79780004229 | Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 92200000 | NPCC-ON |  | NPCC-US
2 | 79780004235 | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 93200000 | NPCC-ON |  | NPCC-US
2 | 79780004240 | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 94200000 | NPCC-ON |  | NPCC-US
2 | 79780004255 | Operate the electric system to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780004258 | Technical requirements and analysis: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 92000000 | NPCC-ON |  | NPCC-US
2 | 79780004286 | If a protective relay or equipment failure reduces system reliability, the Transmission Operator shall notify its Reliability Coordinator and affected Transmission Operators and Balancing Authorities. The Transmission Operator shall take corrective action as soon as possible. |  | TOP | [18 empty] | TOP |  |  |  | 2013-04-01 |  | 2015-05-28 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780004287 | Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities. |  | TOP | [18 empty] | TOP |  |  |  | 2013-04-01 |  | 2015-05-28 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780004289 | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ Protection Systems. |  | TOP | [18 empty] | TOP |  |  |  | 2013-04-01 |  | 2015-05-28 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780004294 | Summary of maintenance and testing procedures. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2013-11-25 |  | 2021-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780004296 | Date each Protection System device was last tested/maintained. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2013-11-25 |  | 2021-03-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780004320 | For each generator that is on this exemption list, the Transmission Operator shall notify the associated Generator Owner. |  | TOP | [18 empty] | TOP |  |  |  | 2013-06-20 |  | 2014-09-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780004336 | The risk-based assessment shall consider the following assets: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780004341 | Transmission substations that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 12200000 | NPCC-ON |  | NPCC-US
2 | 79780004347 | The Cyber Asset uses a routable protocol within a control center; or, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780004361 | Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities. |  | TOP | [18 empty] | TOP | [5 empty] | 2016-01-26 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780004367 | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-3, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:&lt;br/&gt;&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780004370 | Physical and electronic access controls to Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:&lt;br/&gt;&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 22200000 | NPCC-ON |  | NPCC-US
2 | 79780004374 | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:&lt;br/&gt;&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780004378 | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:&lt;br/&gt;&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780004383 | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-4, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2014-02-03 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780004386 | Physical and electronic access controls to Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 22200000 | NPCC-ON |  | NPCC-US
2 | 79780004390 | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2014-02-03 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780004394 | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2014-02-03 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780004401 | When directed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2013-07-01 |  | 2014-09-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780004404 | A status or capability change on any other Reactive Power resources under the Generator Operator’s control and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2013-07-01 |  | 2014-09-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780004408 | Available fixed tap ranges. |  | GO | [22 empty] | 2013-07-01 |  | 2014-09-30 |  |  |  | 41200000 | NPCC-ON |  | NPCC-US
2 | 79780004448 | Its allocation among members. |  | RRO, RSG | [14 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780004451 | The default Disturbance Recovery Period is 15 minutes after the start of a Reportable Disturbance. |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2017-02-17 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780004454 | The Reserve Sharing Group reviews each member’s ACE in response to the activation of reserves. To be in compliance, a member’s ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. |  | RSG | [16 empty] | RSG | [7 empty] | 2017-02-17 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780004456 | The default Contingency Reserve Restoration Period is 90 minutes. |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2017-02-17 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780004464 | Each Transmission Operator shall inform the Reliability Coordinator and other affected Transmission Operators of all transmission resources available for use. |  | TOP | [18 empty] | TOP | [5 empty] | 2015-03-18 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780004558 | The Cyber Asset uses a routable protocol within a control center; or, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780004561 | The risk-based assessment shall consider the following assets: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780004568 | Transmission substations that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 12200000 | NPCC-ON |  | NPCC-US
2 | 79780004583 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780004591 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780004597 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780004599 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780004626 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780004631 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780004643 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780004645 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780004651 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780004656 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780004668 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780004670 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780004675 | Be conducted for near-term (years one through five). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780004682 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780004691 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780004696 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780004708 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780004710 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780004716 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780004721 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780004729 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780004734 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780004740 | Be conducted for near-term (years one through five). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780004747 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780004757 | Be conducted for near-term (years one through five). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780004762 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780004800 |  |  | BA | BA | [23 empty] | 2006-05-01 |  |  |  | 41200000 | NPCC-ON |  | NPCC-US
2 | 79780004801 |  |  | BA | BA | [23 empty] | 2006-05-01 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780004810 |  |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780004821 |  |  | TOP | [18 empty] | TOP | [5 empty] | 2006-11-01 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780004830 |  |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 102000000 | NPCC-ON |  | NPCC-US
2 | 79780004839 |  |  | BA | BA | [23 empty] | 2006-11-01 |  |  |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780004846 |  |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780004856 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780004863 |  |  | BA, RC | BA | [10 empty] | RC | [12 empty] | 2007-01-01 |  |  |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780004867 |  |  | RC | [11 empty] | RC | [12 empty] | 2007-01-01 |  |  |  | 92000000 | NPCC-ON |  | NPCC-US
2 | 79780004888 |  |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2007-05-02 |  |  |  | 92000000 | NPCC-ON |  | NPCC-US
2 | 79780004893 |  |  | TOP | [18 empty] | TOP | [5 empty] | 2007-05-02 |  |  |  | 95200000 | NPCC-ON |  | NPCC-US
2 | 79780004904 |  |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-04-07 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780004910 |  |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-08-01 |  |  |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780004916 |  |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-08-01 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780004926 |  |  | BA, PSE | BA | [9 empty] | PSE | [13 empty] | 2007-01-01 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780004930 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780004939 |  |  | BA | BA | [23 empty] | 2006-11-01 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780004942 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780004948 |  |  | TSP | [20 empty] | TSP |  |  |  | 2007-01-01 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780004955 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780004963 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780004965 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780004973 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780004977 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780004978 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780004981 |  |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780004987 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780004992 |  |  | PSE | [10 empty] | PSE | [13 empty] | 2007-01-01 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780005028 |  |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780005055 |  |  | RC | [11 empty] | RC | [12 empty] | 2005-08-08 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780005064 |  |  | RC | [11 empty] | RC | [12 empty] | 2006-09-29 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780005073 |  |  | RC | [11 empty] | RC | [12 empty] | 2006-09-29 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780005082 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2006-11-02 |  |  |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780005083 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2006-11-02 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780005098 |  |  | TOP | [18 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780005101 |  |  | TOP | [18 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780005105 |  |  | TOP | [18 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780005109 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780005111 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 12200000 | NPCC-ON |  | NPCC-US
2 | 79780005116 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780005123 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 16200000 | NPCC-ON |  | NPCC-US
2 | 79780005130 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2006-05-01 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780005140 |  |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2006-05-01 |  |  |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780005143 |  |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2006-05-01 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780005162 |  |  | GOP | [5 empty] | GOP | [18 empty] | 2007-08-07 |  |  |  | 142000000 | NPCC-ON |  | NPCC-US
2 | 79780005166 |  |  | TOP | [18 empty] | TOP | [5 empty] | 2007-08-07 |  |  |  | 162000000 | NPCC-ON |  | NPCC-US
2 | 79780005188 |  |  | TOP | [18 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 162000000 | NPCC-ON |  | NPCC-US
2 | 79780005207 |  |  | TOP | [18 empty] | TOP | [5 empty] | 2005-04-01 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780005220 |  |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780005271 | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780005276 | Changes to the senior manager must be documented within thirty calendar days of the effective date. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780005279 | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780005281 | The Responsible Entity shall classify information to be protected under this program based on the sensitivity of the Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780005285 | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780005287 | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | 51200000 | NPCC-ON |  | NPCC-US
2 | 79780005295 | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780005300 | Changes to the senior manager must be documented within thirty calendar days of the effective date. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780005303 | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780005305 | The Responsible Entity shall classify information to be protected under this program based on the sensitivity of the Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780005309 | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780005311 | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 51200000 | NPCC-ON |  | NPCC-US
2 | 79780005323 | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780005324 | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780005328 | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780005329 | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780005331 | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780005334 | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 51200000 | NPCC-ON |  | NPCC-US
2 | 79780005339 | The Responsible Entity shall identify those individuals with access to shared accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 52200000 | NPCC-ON |  | NPCC-US
2 | 79780005342 | Each password shall consist of a combination of alpha, numeric, and “special” characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 53200000 | NPCC-ON |  | NPCC-US
2 | 79780005345 | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780005348 | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780005351 | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780005366 | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780005367 | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780005371 | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780005372 | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780005374 | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780005377 | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 51200000 | NPCC-ON |  | NPCC-US
2 | 79780005382 | The Responsible Entity shall identify those individuals with access to shared accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 52200000 | NPCC-ON |  | NPCC-US
2 | 79780005385 | Each password shall consist of a combination of alpha, numeric, and “special” characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 53200000 | NPCC-ON |  | NPCC-US
2 | 79780005388 | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780005391 | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780005394 | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780005600 | State that SOLs shall not exceed associated Facility Ratings. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780005604 | Following the single Contingencies identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. (Footnote: The Contingencies identified in R2.2.1 through R2.2.3 are the minimum contingencies that must be studied but are not necessarily the only Contingencies that should be studied.) |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780005619 | Selection of applicable Contingencies |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780005626 | Each Reliability Coordinator and Transmission Operator that operates any portion of the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780005631 | State that SOLs shall not exceed associated Facility Ratings. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780005635 | Following the single Contingencies identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. (Footnote: The Contingencies identified in FAC-011 R2.2.1 through R2.2.3 are the minimum contingencies that must be studied but are not necessarily the only Contingencies that should be studied.) |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780005637 | Loss of any generator, line, transformer, or shunt device without a Fault. |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 22200000 | NPCC-ON |  | NPCC-US
2 | 79780005642 | Interruption of other network customers, (a) only if the system has already been adjusted, or is being adjusted, following at least one prior outage, or (b) if the real-time operating conditions are more adverse than anticipated in the corresponding studies |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 23200000 | NPCC-ON |  | NPCC-US
2 | 79780005647 | Selection of applicable Contingencies |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780005657 | Each Planning Authority and Transmission Planner that models any portion of the Reliability Coordinator’s Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780005662 | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780005684 | The following information on how source and sink for transmission service is accounted for in AFC calculations including: |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780005686 | Define if the sink used for AFC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation. |  | TSP | [20 empty] | TSP |  | 2017-04-01 | [5 empty] | 12200000 | NPCC-ON |  | NPCC-US
2 | 79780005695 | Results of a first Contingency transfer analysis from all adjacent Balancing Authority source and sink (as defined in the ATCID) combinations up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an Outage Transfer Distribution Factor (OTDF) of at least 5% and within the Transmission Operator’s system are included as Flowgates unless the interface between such adjacent Balancing Authorities is accounted for using another ATC methodology. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780005697 | Only the most limiting element in a series configuration needs to be included as a Flowgate. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 21220000 | NPCC-ON |  | NPCC-US
2 | 79780005704 | At a minimum, establish a list of Flowgates by creating, modifying, or deleting Flowgate definitions at least once per calendar year. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780005712 | Updated at least once per day for AFC calculations for intra-day, next day, and days two through 30. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780005719 | Include in the transmission model expected generation and Transmission outages, additions, and retirements within the scope of the model as specified in the ATCID and in effect during the applicable period of the AFC calculation for the Transmission Service Provider’s area, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780005724 | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. |  | TSP | [20 empty] | TSP |  | 2017-04-01 | [5 empty] | 61200000 | NPCC-ON |  | NPCC-US
2 | 79780005725 | The impact of any firm Network Integration Transmission Service, including the impacts of generation to load in the model referenced in R5.2 and has a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed based on: (Footnote:A percentage less than that used in the Interconnection-wide congestion management procedure may be utilized.) |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780005727 | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. |  | TSP | [20 empty] | TSP |  | 2017-04-01 | [5 empty] | 62200000 | NPCC-ON |  | NPCC-US
2 | 79780005735 | The impact of any confirmed non-firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780005745 | For daily AFC, once per day. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 102000000 | NPCC-ON |  | NPCC-US
2 | 79780005752 | The risk-based assessment shall consider the following assets: |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780005754 | Transmission substations that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12200000 | NPCC-ON |  | NPCC-US
2 | 79780005761 | The Cyber Asset uses a routable protocol within a control center; or, |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780005764 | The risk-based assessment shall consider the following assets: |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780005766 | Transmission substations that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12200000 | NPCC-ON |  | NPCC-US
2 | 79780005773 | The Cyber Asset uses a routable protocol within a control center; or, |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780005781 | Operate the electric system to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780005790 | Names of the responsible entities, organizational relationships, and responsibilities related to the NPIRs. (Retirement approved by FERC effective January 21, 2014.) | [26 empty] | 2014-11-13 |  |  |  | 91200000 | NPCC-ON |  | NPCC-US
2 | 79780005793 | Technical requirements and analysis: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  |  | 92000000 | NPCC-ON |  | NPCC-US
2 | 79780005795 | Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 92200000 | NPCC-ON |  | NPCC-US
2 | 79780005799 | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 93200000 | NPCC-ON |  | NPCC-US
2 | 79780005807 | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 94200000 | NPCC-ON |  | NPCC-US
2 | 79780005813 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780005816 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780005828 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780005830 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780005834 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780005837 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780005853 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780005855 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780005859 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780005862 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780005878 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780005880 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780005884 | Be conducted for near-term (years one through five). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780005887 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780005899 | Requirements to provide data that describes design, operation, and modeling of a RAS. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780005918 | Study years, system conditions, and contingencies analyzed in the technical studies on which the assessment is based and when those technical studies were performed. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780005924 | Operation — The actions taken by the RAS in response to Disturbance conditions, and |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780005936 | Instrument transformers. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-04-01 |  | 2021-03-31 |  |  |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780005939 | Documentation of maintenance and testing intervals and their basis. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-01-25 |  | 2021-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780005948 | Size and location of customer load, or percent of connected load, to be interrupted. | [26 empty] | 2014-11-13 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780005956 | Corresponding voltage set points and overall scheme clearing times. | [26 empty] | 2014-11-13 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780005964 | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 |  | 2015-05-28 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780005967 | Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 |  | 2015-05-28 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780005971 | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ Protection Systems. |  | TO | [22 empty] | 2017-04-01 |  | 2015-05-28 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780005985 | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ Protection Systems. |  | TO | [22 empty] | 2016-01-25 |  | 2015-05-28 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780006028 | Models all system Elements as in-service for the assumed initial conditions. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780006041 | Uses Facility Ratings as provided by the Transmission Owner and Generator Owner |  | TOP | [18 empty] | TOP |  |  | &lt;p&gt;&lt;br/&gt;M1.2. The Transmission model produced must include the areas listed in R1.1.1 (or an equivalent representation, as described in the requirement) (R1.1)&lt;/p&gt; &lt;p&gt;M1.3. The Transmission model produced must show the use of the modeling parameters stated in R1.1.2 through R1.1.10; except that, no evidence shall be required to prove: 1) utilization of a Remedial Action Scheme where none was included in the model or 2) that no additions or retirements to the generation or Transmission system occurred. (R1.1.2 through R1.1.10)&lt;/p&gt; &lt;p&gt;M1.4. The Transmission Operator must provide evidence that the models used to determine TTC included Facility Ratings as provided by the Transmission Owner and Generator Owner. (R1.2)&lt;/p&gt; | 2016-01-25 | [5 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006116 | If a protective relay or equipment failure reduces system reliability, the Transmission Operator shall notify its Reliability Coordinator and affected Transmission Operators and Balancing Authorities. The Transmission Operator shall take corrective action as soon as possible. |  | TOP | [18 empty] | TOP |  |  |  | 2015-05-29 |  | 2020-09-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006119 | Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities. |  | TOP | [18 empty] | TOP |  |  |  | 2015-05-29 |  | 2020-09-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780006123 | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ Protection Systems. |  | TOP | [18 empty] | TOP |  |  |  | 2015-05-29 |  | 2020-09-30 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780006161 | Electronic Security Perimeters (CIP-005) including Interactive Remote Access; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006170 | Physical security controls; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2016-06-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006174 | One or more processes to determine if an identified Cyber Security Incident is a Reportable Cyber Security Incident and notify the Electricity Sector Information Sharing and Analysis Center (ES-ISAC), unless prohibited by law. Initial notification to the ES-ISAC, which may be only a preliminary notice, shall not exceed one hour from the determination of a Reportable Cyber Security Incident. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.2. Examples of evidence may include, but are not limited to, dated documentation of Cyber Security Incident response plan(s) that provide guidance or thresholds for determining which Cyber Security Incidents are also Reportable Cyber Security Incidents and documentation of initial notices to the Electricity Sector Information Sharing and Analysis Center (ES-ISAC). | 2014-02-03 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006178 | Use the Cyber Security Incident response plan(s) under Requirement R1 when responding to a Reportable Cyber Security Incident or performing an exercise of a Reportable Cyber Security Incident. Document deviations from the plan(s) taken during the response to the incident or exercise. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.2. Examples of evidence may include, but are not limited to, incident reports, logs, and notes that were kept during the incident response process, and follow-up documentation that describes deviations taken from the plan during the incident or exercise. | 2014-02-03 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006182 | Update the Cyber Security Incident response plan based on any documented lessons learned associated with the plan; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | 31200000 | NPCC-ON |  | NPCC-US
2 | 79780006184 | No later than 60 calendar days after a change to the roles or responsibilities, Cyber Security Incident response groups or individuals, or technology that the Responsible Entity determines would impact the ability to execute the plan: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.2. An example of evidence may include, but is not limited to:&lt;br/&gt;1. Dated and revised Cyber Security Incident response plan with changes to the roles or responsibilities, responders or technology; and&lt;br/&gt;2. Evidence of plan update distribution including, but not limited to:&lt;br/&gt;• Emails;&lt;br/&gt;• USPS or other mail service;&lt;br/&gt;• Electronic distribution system; or &lt;br/&gt;• Training sign-in sheets. | 2014-02-03 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780006186 | Notify each person or group with a defined role in the Cyber Security Incident response plan of the updates. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | 32200000 | NPCC-ON |  | NPCC-US
2 | 79780006188 | Protect against the use of unnecessary physical input/output ports used for network connectivity, console commands, or removable media. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006190 | At least once every 35 calendar days, evaluate security patches for applicability that have been released since the last evaluation from the source or sources identified in Part 2.1. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006194 | Mitigate the threat of detected malicious code. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780006197 | Generate alerts for security events that the Responsible Entity determines necessitates an alert, that includes, as a minimum, each of the following types of events (per Cyber Asset or BES Cyber System capability): |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780006201 | Identify and inventory all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780006208 | Detected failed access attempts and failed login attempts; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 41200000 | NPCC-ON |  | NPCC-US
2 | 79780006211 | Detected failure of Part 4.1 event logging. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 42200000 | NPCC-ON |  | NPCC-US
2 | 79780006213 | Minimum password complexity that is the lesser of three or more different types of characters (e.g., uppercase alphabetic, lowercase alphabetic, numeric, non-alphanumeric) or the maximum complexity supported by the Cyber Asset. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 55200000 | NPCC-ON |  | NPCC-US
2 | 79780006215 | Procedure(s) for protecting and securely handling BES Cyber System Information, including storage, transit, and use. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006217 | Prior to the disposal of applicable Cyber Assets that contain BES Cyber System Information, the Responsible Entity shall take action to prevent the unauthorized retrieval of BES Cyber System Information from the Cyber Asset or destroy the data storage media. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006220 | Any commercially available or open-source application software (including version) intentionally installed; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780006224 | Authorize and document changes that deviate from the existing baseline configuration. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006228 | Following the change, verify that required cyber security controls determined in 1.4.1 are not adversely affected; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 14200000 | NPCC-ON |  | NPCC-US
2 | 79780006232 | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 15200000 | NPCC-ON |  | NPCC-US
2 | 79780006235 | Where technically feasible, at least once every 36 calendar months: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780006237 | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 32200000 | NPCC-ON |  | NPCC-US
2 | 79780006241 | All External Routable Connectivity must be through an identified Electronic Access Point (EAP). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.2. An example of evidence may include, but is not limited to, network diagrams showing all external routable communication paths and the identified EAPs. | 2014-02-03 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006246 | For all Interactive Remote Access sessions, utilize encryption that terminates at an Intermediate System. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.2. An example of evidence may include, but is not limited to, architecture documents detailing where encryption initiates and terminates. | 2014-02-03 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006249 | Utilize at least one physical access control to allow unescorted physical access into each applicable Physical Security Perimeter to only those individuals who have authorized unescorted physical access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 1.2 An example of evidence may include, but is not limited to, language in the physical security plan that describes each Physical Security Perimeter and how unescorted physical access is controlled by one or more different methods and proof that unescorted physical access is restricted to only authorized individuals, such as a list of authorized individuals accompanied by access logs. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006258 | Require manual or automated logging of visitor entry into and exit from the Physical Security Perimeter that includes date and time of the initial entry and last exit, the visitor’s name, and the name of an individual point of contact responsible for the visitor, except during CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 2.2 An example of evidence may include, but is not limited to, language in a visitor control program that requires continuous escorted access of visitors within Physical Security Perimeters and additional evidence to demonstrate that the process was implemented, such as dated visitor logs that include the required information. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006262 | Roles and responsibilities of responders. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006267 | Test a representative sample of information used to recover BES Cyber System functionality at least once every 15 calendar months to ensure that the information is useable and is compatible with current configurations.&lt;br/&gt;&lt;br/&gt;An actual recovery that incorporates the information used to recover BES Cyber System functionality substitutes for this test. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006271 | Update the recovery plan based on any documented lessons learned associated with the plan; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 31200000 | NPCC-ON |  | NPCC-US
2 | 79780006273 | Notify each person or group with a defined role in the recovery plan of the updates to the recovery plan based on any documented lessons learned. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780006275 | Notify each person or group with a defined role in the recovery plan of the updates. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 32200000 | NPCC-ON |  | NPCC-US
2 | 79780006278 | Physical access controls; | [23 empty] | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. |  |  | 2016-06-30 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780006286 | Require completion of the training specified in Part 2.1 prior to granting authorized electronic access and authorized unescorted physical access to applicable Cyber Assets, except during CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training records and documentation of when CIP Exceptional Circumstances were invoked. | 2014-02-03 |  | 2016-06-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006299 | Process to perform a seven year criminal history records check as part of each personnel risk assessment that includes: | [23 empty] | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to perform a seven year criminal history records check. |  |  | 2016-06-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780006301 | other locations where, during the seven years immediately prior to the date of the criminal history records check, the subject has resided for six consecutive months or more. If it is not possible to perform a full seven year criminal history records check, conduct as much of the seven year criminal history records check as possible and document the reason the full seven year criminal history records check could not be performed. | [23 empty] | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to perform a seven year criminal history records check. |  |  | 2016-06-30 |  |  |  | 32200000 | NPCC-ON |  | NPCC-US
2 | 79780006307 | Unescorted physical access into a Physical Security Perimeter; and | [23 empty] | An example of evidence may include, but is not limited to, dated documentation of the process to authorize electronic access, unescorted physical access in a Physical Security Perimeter, and access to designated storage locations, whether physical or electronic, for BES Cyber System Information. |  |  | 2016-06-30 |  |  |  | 41200000 | NPCC-ON |  | NPCC-US
2 | 79780006309 | Verify at least once each calendar quarter that individuals with active electronic access or unescorted physical access have authorization records. | [23 empty] | Examples of evidence may include, but are not limited to:&lt;br/&gt;• Dated documentation of the verification between the system generated list of individuals who have been authorized for access (i.e., workflow database) and a system generated list of personnel who have access (i.e., user account listing), or&lt;br/&gt;• Dated documentation of the verification between a list of individuals who have been authorized for access (i.e., authorization forms) and a list of individuals provisioned for access (i.e., provisioning forms or shared account listing). |  |  | 2016-06-30 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780006313 | For reassignments or transfers, revoke the individual’s authorized electronic access to individual accounts and authorized unescorted physical access that the Responsible Entity determines are not necessary by the end of the next calendar day following the date that the Responsible Entity determines that the individual no longer requires retention of that access. | [23 empty] | An example of evidence may include, but is not limited to, documentation of all of the following:&lt;br/&gt;1. Dated workflow or sign-off form showing a review of logical and physical access; and &lt;br/&gt;2. Logs or other demonstration showing such persons no longer have access that the Responsible Entity determines is not necessary. |  |  | 2016-06-30 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780006318 | Identify each of the medium impact BES Cyber Systems according to Attachment 1, Section 2, if any, at each asset; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-12-26 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006321 | Have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 at least once every 15 calendar months, even if it has no identified items in Requirement R1. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-12-26 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006323 | The documentation shall be consistent with the principle that the Facility Ratings do not exceed the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | GO | [22 empty] | 2011-11-17 | [5 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006325 | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R2, Part 2.1 including identification of how each of the following were considered: |  | GO | [22 empty] | 2011-11-17 | [5 empty] | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006327 | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. |  | GO | [22 empty] | 2013-01-01 | [5 empty] | 22200000 | NPCC-ON |  | NPCC-US
2 | 79780006333 | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | GO | [22 empty] | 2013-01-01 | [5 empty] | 24200000 | NPCC-ON |  | NPCC-US
2 | 79780006335 | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R3, Part 3.1 including identification of how each of the following were considered: |  | TO | [22 empty] | 2011-11-17 | [5 empty] | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780006337 | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. |  | TO | [22 empty] | 2013-01-01 | [5 empty] | 32200000 | NPCC-ON |  | NPCC-US
2 | 79780006343 | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | TO | [22 empty] | 2013-01-01 | [5 empty] | 34200000 | NPCC-ON |  | NPCC-US
2 | 79780006346 | Identity of the most limiting equipment of the Facilities |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-01-01 | [5 empty] | 81200000 | NPCC-ON |  | NPCC-US
2 | 79780006347 | Within 30 calendar days (or a later date if specified by the requester), for any requested Facility with a Thermal Rating that limits the use of Facilities under the requester’s authority by causing any of the following: 1) An Interconnection Reliability Operating Limit, 2) A limitation of Total Transfer Capability, 3) An impediment to generator deliverability, or 4) An impediment to service to a major load center: |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-11-17 | [5 empty] | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780006349 | The Thermal Rating for the next most limiting equipment identified in Requirement R8, Part 8.2.1. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-01-01 | [5 empty] | 82200000 | NPCC-ON |  | NPCC-US
2 | 79780006351 | Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. |  | PCPA | [9 empty] | PA | [12 empty] | 2014-01-01 |  | 2014-09-30 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780006355 | The BES interrupting device owner owns all or part of the Composite Protection System; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-11-19 |  | 2017-04-01 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006361 | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-04-02 |  | 2017-04-01 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780006363 | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-11-19 |  | 2017-04-01 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006373 | Include the applicable monitored Component attributes applied to each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-2, and Table 5 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [19 empty] | 2015-12-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006381 | The Transmission Owner shall identify the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment. |  | TO | [22 empty] | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:&lt;br/&gt;4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an &amp;quot;aggregate weighted value&amp;quot; exceeding 3000 according to the table below. The &amp;quot;aggregate weighted value&amp;quot; for a single station or substation is determined by summing the &amp;quot;weight value per line&amp;quot; shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;Voltage Value of a Line Weight Value per Line&lt;br/&gt;less than 200 kV (not applicable) (not applicable)&lt;br/&gt;200 kV to 299 kV 700&lt;br/&gt;300 kV to 499 kV 1300&lt;br/&gt;500 kV and above 0&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.&lt;br/&gt;4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. &lt;br/&gt;Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006384 | The unaffiliated third party verification shall verify the Transmission Owner’s risk assessment performed under Requirement R1, which may include recommendations for the addition or deletion of a Transmission station(s) or Transmission substation(s). The Transmission Owner shall ensure the verification is completed within 90 calendar days following the completion of the Requirement R1 risk assessment. |  | TO | [22 empty] | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:&lt;br/&gt;4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an &amp;quot;aggregate weighted value&amp;quot; exceeding 3000 according to the table below. The &amp;quot;aggregate weighted value&amp;quot; for a single station or substation is determined by summing the &amp;quot;weight value per line&amp;quot; shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;Voltage Value of a Line Weight Value per Line&lt;br/&gt;less than 200 kV (not applicable) (not applicable)&lt;br/&gt;200 kV to 299 kV 700&lt;br/&gt;300 kV to 499 kV 1300&lt;br/&gt;500 kV and above 0&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.&lt;br/&gt;4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. &lt;br/&gt;Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006391 | Prior history of attack on similar facilities taking into account the frequency, geographic proximity, and severity of past physical security related events; and |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:&lt;br/&gt;4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an &amp;quot;aggregate weighted value&amp;quot; exceeding 3000 according to the table below. The &amp;quot;aggregate weighted value&amp;quot; for a single station or substation is determined by summing the &amp;quot;weight value per line&amp;quot; shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;Voltage Value of a Line Weight Value per Line&lt;br/&gt;less than 200 kV (not applicable) (not applicable)&lt;br/&gt;200 kV to 299 kV 700&lt;br/&gt;300 kV to 499 kV 1300&lt;br/&gt;500 kV and above 0&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.&lt;br/&gt;4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. &lt;br/&gt;Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780006395 | Law enforcement contact and coordination information. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:&lt;br/&gt;4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an &amp;quot;aggregate weighted value&amp;quot; exceeding 3000 according to the table below. The &amp;quot;aggregate weighted value&amp;quot; for a single station or substation is determined by summing the &amp;quot;weight value per line&amp;quot; shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;Voltage Value of a Line Weight Value per Line&lt;br/&gt;less than 200 kV (not applicable) (not applicable)&lt;br/&gt;200 kV to 299 kV 700&lt;br/&gt;300 kV to 499 kV 1300&lt;br/&gt;500 kV and above 0&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.&lt;br/&gt;4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. &lt;br/&gt;Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780006402 | The Transmission Owner or Transmission Operator, respectively, shall ensure that the unaffiliated third party review is completed within 90 calendar days of completing the security plan(s) developed in Requirement R5. The unaffiliated third party review may, but is not required to, include recommended changes to the evaluation performed under Requirement R4 or the security plan(s) developed under Requirement R5. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:&lt;br/&gt;4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an &amp;quot;aggregate weighted value&amp;quot; exceeding 3000 according to the table below. The &amp;quot;aggregate weighted value&amp;quot; for a single station or substation is determined by summing the &amp;quot;weight value per line&amp;quot; shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;Voltage Value of a Line Weight Value per Line&lt;br/&gt;less than 200 kV (not applicable) (not applicable)&lt;br/&gt;200 kV to 299 kV 700&lt;br/&gt;300 kV to 499 kV 1300&lt;br/&gt;500 kV and above 0&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.&lt;br/&gt;4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. &lt;br/&gt;Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780006407 | The UVLS Program is integrated through coordination with generator voltage ride-through capabilities and other protection and control systems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage-based load shedding programs. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-11-19 | [5 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006412 | The performance (i.e., operation and non-operation) of the UVLS Program equipment. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-11-19 | [5 empty] | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780006419 | One of the following TLR levels: TLR-1, TLR-2, TLR-3A, TLR-3B, TLR-4, TLR-5A, TLR-5B, TLR-6, TLR-0 |  | RC | [11 empty] | RC | [10 empty] | 2011-04-21 |  | 2016-03-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006421 | Communicate the list of congestion management actions to be implemented to 1.) all Reliability Coordinators in the Eastern Interconnection, and 2.) those Reliability Coordinators in other Interconnections responsible for curtailing Interchange Transactions crossing Interconnection boundaries identified in the list of congestion management actions. |  | RC | [11 empty] | RC | [10 empty] | 2011-04-21 |  | 2016-03-31 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780006425 | Manufacturer, model number (if available), and type of the excitation control system including, but not limited to static, AC brushless, DC rotating, and/or the plant volt/var control function (if installed), |  | GO | [22 empty] | 2018-07-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following:&lt;br/&gt;4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: &lt;br/&gt;4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).&lt;br/&gt;4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.2 Generation in the Western Interconnection with the following characteristics:&lt;br/&gt;4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).&lt;br/&gt;4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.3 Generation in the ERCOT Interconnection with the following characteristics:&lt;br/&gt;4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).&lt;br/&gt;4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.4 For all Interconnections:&lt;br/&gt;• A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780006431 | A no-disturbance simulation results in negligible transients, and |  | TP | [19 empty] | TP |  |  | 2014-05-26 |  |  |  | 4.2. Facilities:&lt;br/&gt;For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following:&lt;br/&gt;4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: &lt;br/&gt;4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).&lt;br/&gt;4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.2 Generation in the Western Interconnection with the following characteristics:&lt;br/&gt;4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).&lt;br/&gt;4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.3 Generation in the ERCOT Interconnection with the following characteristics:&lt;br/&gt;4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).&lt;br/&gt;4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.4 For all Interconnections:&lt;br/&gt;• A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780006435 | &lt;p&gt;Type of governor and load control or active power control/frequency control equipment,&lt;/p&gt; &lt;p&gt;Footnote: Turbine/governor and load control or active power/frequency control:&lt;/p&gt; &lt;p/&gt; |  | GO | [22 empty] | 2014-07-01 |  |  |  | 4.2. Facilities&lt;br/&gt;For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred to as an “applicable unit” that meet the following:&lt;br/&gt;4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics:&lt;br/&gt;4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).&lt;br/&gt;4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.2 Generation in the Western Interconnection with the following characteristics:&lt;br/&gt;4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).&lt;br/&gt;4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.3 Generation in the ERCOT Interconnection with the following characteristics:&lt;br/&gt;4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).&lt;br/&gt;4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780006440 | A no-disturbance simulation results in negligible transients, and |  | TP | [19 empty] | TP |  |  | 2014-05-26 |  |  |  | 4.2. Facilities&lt;br/&gt;For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred to as an “applicable unit” that meet the following:&lt;br/&gt;4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics:&lt;br/&gt;4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).&lt;br/&gt;4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.2 Generation in the Western Interconnection with the following characteristics:&lt;br/&gt;4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).&lt;br/&gt;4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.3 Generation in the ERCOT Interconnection with the following characteristics:&lt;br/&gt;4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).&lt;br/&gt;4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780006444 | Transmission operations |  | RC | [11 empty] | RC | [10 empty] | 2012-10-01 |  | 2019-06-30 |  |  |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780006453 | Emergency preparedness and operations |  | TOP | [18 empty] | TOP |  |  |  | 2012-10-01 |  | 2019-06-30 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780006457 | Certificates:&lt;br/&gt;• Reliability Operator&lt;br/&gt;• Balancing, Interchange and Transmission Operator&lt;br/&gt;• Transmission Operator |  | TOP | [18 empty] | TOP |  |  |  | 2011-09-15 |  | 2019-06-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006460 | Emergency preparedness and operations |  | BA | BA | [21 empty] | 2012-10-01 |  | 2019-06-30 |  |  |  | 31200000 | NPCC-ON |  | NPCC-US
2 | 79780006463 | Certificates&lt;br/&gt;• Reliability Operator&lt;br/&gt;• Balancing, Interchange and Transmission Operator&lt;br/&gt;• Balancing and Interchange Operator |  | BA | BA | [21 empty] | 2012-10-01 |  | 2019-06-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780006464 | Certificates&lt;br/&gt;• Reliability Operator&lt;br/&gt;• Balancing, Interchange and Transmission Operator&lt;br/&gt;• Balancing and Interchange Operator |  | BA | BA | [21 empty] | 2011-09-15 |  | 2019-06-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780006482 | Equal to or more negative than its Frequency Response Obligation when Frequency varies from 60 Hz by more than +/- 0.036 Hz. |  | BA | BA | [21 empty] | 2014-03-24 |  | 2015-11-12 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780006489 | A summary description of the elements required to support the backup functionality. These elements shall include, at a minimum: |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006491 | &lt;p&gt;Data communications.&lt;/p&gt; |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2013-07-01 |  | 2019-03-31 |  |  |  | 12200000 | NPCC-ON |  | NPCC-US
2 | 79780006504 | The backup functionality for a minimum of two continuous hours. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780006506 | A process for the Reliability Coordinator to review the GMD Operating Procedures or Operating Processes of Transmission Operators within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2015-04-01 | [5 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006508 | System Operator actions to be initiated based on predetermined conditions. |  | TOP | [18 empty] | TOP |  |  |  | 2015-04-01 | [5 empty] | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780006514 | Outside its Transmission Operator Area, obtain and utilize status, voltages, and flow data for Facilities and the status of Special Protection Systems. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-26 |  | 2018-06-30 |  |  |  | 102000000 | NPCC-ON |  | NPCC-US
2 | 79780006526 | Provide its Planning Coordinator with a technical study that demonstrates that the Distribution Providers or Transmission Owners specific deviations from the requirements of UFLS Attachment C, Table 1 will not have a significant adverse impact on the bulk power system. |  | DP, DP-UFLS, TO |  | DP | [20 empty] | 2016-01-01 |  | 2020-03-31 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780006532 | Transmit the existing underfrequency settings and any changes to the underfrequency settings along with the technical basis for the settings to the Planning Coordinator. |  | DP-UFLS, GO |  | DP | [20 empty] | 2013-04-29 |  | 2020-03-31 |  |  |  | 162000000 | NPCC-ON |  | NPCC-US
2 | 79780006533 | Design auxiliary system(s) or devices used for the control and protection of auxiliary system(s), necessary for the generating unit operation such that they will not trip the generating unit during underfrequency conditions above the appropriate generator underfrequency trip protection settings threshold curve in Figure 1. |  | DP-UFLS, GO |  | DP | [20 empty] | 2013-04-29 |  | 2020-03-31 |  |  |  | 152000000 | NPCC-ON |  | NPCC-US
2 | 79780006535 | Set the frequency trip setting upper tolerance to no greater than + 0.1 Hz. |  | DP-UFLS, GO |  | DP | [20 empty] | 2013-04-29 |  | 2020-03-31 |  |  |  | 192000000 | NPCC-ON |  | NPCC-US
2 | 79780006538 | The buses at which the Load is modeled in the NPCC library power flow case. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2013-04-29 |  | 2020-03-31 |  |  |  | 202000000 | NPCC-ON |  | NPCC-US
2 | 79780006542 | Québec Interconnection – 200 ms |  | DP, DP-UFLS, TO |  | DP | [20 empty] | 2016-01-01 |  | 2020-03-31 |  |  |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780006545 | Include the applicable monitored Component attributes applied to each Protection System Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, and Table 3 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System Components. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2014-02-24 |  | 2015-05-28 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006547 | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006550 | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-1 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780006553 | Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES |  | PCPA | [9 empty] | PA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  |  | 33200000 | NPCC-ON |  | NPCC-US
2 | 79780006556 | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780006563 | UFLS design assessment |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 142000000 | NPCC-ON |  | NPCC-US
2 | 79780006566 | Inter-relationships between vegetation growth rates, vegetation control methods, and inspection frequency. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-11-25 |  | 2016-09-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780006568 | A statement that the assessment shall respect known System Operating Limits (SOLs). |  | PCPA | [9 empty] | PA | [12 empty] | 2012-01-23 |  | 2020-12-14 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006573 | Distribute to each functional entity that has a reliability-related need for the Transfer Capability methodology and submits a request for that methodology within 30 calendar days of receiving that written request. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-01-23 |  | 2020-12-14 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006578 | Generating plants/facilities greater than 50 MVA (gross aggregate nameplate rating) directly connected to the BES |  | PCPA | [9 empty] | PA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  |  | 332000 | NPCC-ON |  | NPCC-US
2 | 79780006584 | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 220000 | NPCC-ON |  | NPCC-US
2 | 79780006586 | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-1 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 320000 | NPCC-ON |  | NPCC-US
2 | 79780006589 | Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES |  | PCPA | [9 empty] | PA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  |  | 332000 | NPCC-ON |  | NPCC-US
2 | 79780006592 | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 420000 | NPCC-ON |  | NPCC-US
2 | 79780006599 | The effectiveness of the UFLS program |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 2020000 | NPCC-ON |  | NPCC-US
2 | 79780006618 | Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. |  | PCPA | [9 empty] | PA | [12 empty] | 2014-09-22 |  | 2017-03-31 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780006624 | Known outage(s) of generation or Transmission Facility(ies) with a duration of at least six months. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-01-01 | [5 empty] | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780006631 | System Off-Peak Load for one of the five years. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780006635 | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by the following annual current study, supplemented with qualified past studies as indicated in Requirement R2, Part 2.6: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006640 | When instructed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2014-08-01 |  | 2015-05-28 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006644 | Available fixed tap ranges. |  | GO | [22 empty] | 2014-10-01 |  | 2015-05-28 |  |  |  | 51200000 | NPCC-ON |  | NPCC-US
2 | 79780006649 | System Off-Peak Load for one of the five years. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 24200000 | NPCC-ON |  | NPCC-US
2 | 79780006654 | For steady state, short circuit, or Stability analysis: no material changes have occurred to the System represented in the study. Documentation to support the technical rationale for determining material changes shall be included. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 26200000 | NPCC-ON |  | NPCC-US
2 | 79780006657 | Include actions to resolve performance deficiencies identified in multiple sensitivity studies or provide a rationale for why actions were not necessary. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 27200000 | NPCC-ON |  | NPCC-US
2 | 79780006662 | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 28200000 | NPCC-ON |  | NPCC-US
2 | 79780006664 | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R3, Part 3.5. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780006667 | Simulate the expected automatic operation of existing and planned devices designed to provide steady state control of electrical system quantities when such devices impact the study area. These devices may include equipment such as phase-shifting transformers, load tap changing transformers, and switched capacitors and inductors. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 33200000 | NPCC-ON |  | NPCC-US
2 | 79780006675 | For planning events P2 through P7: When a generator pulls out of synchronism in the simulations, the resulting apparent impedance swings shall not result in the tripping of any Transmission system elements other than the generating unit and its directly connected Facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 41200000 | NPCC-ON |  | NPCC-US
2 | 79780006677 | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R4, Part 4.5. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780006681 | Tripping of generators where simulations show generator bus voltages or high side of the GSU voltages are less than known or assumed generator low voltage ride through capability. Include in the assessment any assumptions made. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 43120000 | NPCC-ON |  | NPCC-US
2 | 79780006683 | Simulate the expected automatic operation of existing and planned devices designed to provide dynamic control of electrical system quantities when such devices impact the study area. These devices may include equipment such as generation exciter control and power system stabilizers, static var compensators, power flow controllers, and DC Transmission controllers. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 43200000 | NPCC-ON |  | NPCC-US
2 | 79780006692 | Transmission system topology, including but not limited to long term planned Transmission outages, additions, and retirements. |  | PCPA | [9 empty] | PA | [12 empty] | 2013-04-01 |  | 2020-12-14 |  |  |  | 14200000 | NPCC-ON |  | NPCC-US
2 | 79780006699 | Each Transmission Planner within the Planning Coordinator’s Planning Coordinator area. |  | PCPA | [9 empty] | PA | [12 empty] | 2013-04-01 |  | 2020-12-14 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780006701 | For Confirmed Interchange less than or equal to 250 MW for the last hour, the actual hourly integrated energy deviates from the Confirmed Interchange by more than 25 MW for that hour and that deviation is expected to persist. |  | PSE | [10 empty] | PSE | [11 empty] | 2015-01-01 | [5 empty] | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006704 | Each Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if the Scheduling Path (proper connectivity of Adjacent Balancing Authorities) between it and its Adjacent Balancing Authorities is invalid. |  | BA | BA | [21 empty] | 2014-06-30 |  | 2021-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006708 | Each Intermediate Balancing Authority, |  | BA | BA | [21 empty] | 2014-06-30 |  | 2021-03-31 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780006713 | Opposite in sign or direction to that of the Adjacent Balancing Authority. |  | BA | BA | [21 empty] | 2014-11-26 |  | 2021-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006715 | Each adjacent Reliability Coordinator within the same Interconnection. |  | RC | [11 empty] | RC | [10 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006717 | Each adjacent Reliability Coordinator within the same Interconnection. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006719 | Each Balancing Authority within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780006725 | Each Balancing Authority within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780006729 | Each Transmission Operator that operates Facilities within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780006734 | Each Transmission Operator that operates Facilities within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780006737 | Its Transmission Operator. |  | DP |  | DP | [20 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780006739 | Its Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780006741 | The Transmission Owner shall identify the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment. |  | TO | [22 empty] | 2015-10-01 |  | 2015-10-01 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006743 | The unaffiliated third party verification shall verify the Transmission Owner’s risk assessment performed under Requirement R1, which may include recommendations for the addition or deletion of a Transmission station(s) or Transmission substation(s). The Transmission Owner shall ensure the verification is completed within 90 calendar days following the completion of the Requirement R1 risk assessment. |  | TO | [22 empty] | 2015-10-01 |  | 2015-10-01 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006748 | Prior history of attack on similar facilities taking into account the frequency, geographic proximity, and severity of past physical security related events; and |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780006751 | Law enforcement contact and coordination information. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780006755 | The Transmission Owner or Transmission Operator, respectively, shall ensure that the unaffiliated third party review is completed within 90 calendar days of completing the security plan(s) developed in Requirement R5. The unaffiliated third party review may, but is not required to, include recommended changes to the evaluation performed under Requirement R4 or the security plan(s) developed under Requirement R5. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780006759 | transmission Facilities; and |  | TO | [22 empty] | 2014-11-06 |  | 2018-12-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006762 | Procedures for notifying those responsible for the reliability of affected system(s) of new or materially modified existing interconnections. |  | TO | [22 empty] | 2014-11-06 |  | 2018-12-31 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780006764 | Procedures for notifying those responsible for the reliability of affected system(s) of new interconnections. |  | GO | [22 empty] | 2014-11-06 |  | 2018-12-31 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780006766 | Adherence to applicable NERC Reliability Standards; regional and Transmission Owner planning criteria; and Facility interconnection requirements; |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2014-11-06 |  | 2021-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006770 | Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. |  | GO | [22 empty] | 2014-05-27 |  |  |  | For the purpose of this standard, the term, “applicable Facility” shall mean any one of the following:&lt;br/&gt;4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.&lt;br/&gt;4.2.2 Synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.&lt;br/&gt;4.2.3 Generating plant/Facility greater than 75 MVA (gross aggregate nameplate rating) directly connected to the Bulk Electric System. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006772 | Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. |  | GO | [22 empty] | 2014-05-27 |  |  |  | For the purpose of this standard, the term, “applicable Facility” shall mean any one of the following:&lt;br/&gt;4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.&lt;br/&gt;4.2.2 Synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.&lt;br/&gt;4.2.3 Generating plant/Facility greater than 75 MVA (gross aggregate nameplate rating) directly connected to the Bulk Electric System. |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006774 | Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. |  | TO | [22 empty] | 2014-05-27 |  |  |  | For the purpose of this standard, the term, “applicable Facility” shall mean any one of the following:&lt;br/&gt;4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.&lt;br/&gt;4.2.2 Synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.&lt;br/&gt;4.2.3 Generating plant/Facility greater than 75 MVA (gross aggregate nameplate rating) directly connected to the Bulk Electric System. |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780006776 | A timetable for providing the data. (A minimum of 30 calendar days must be allowed for responding to the request). |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2015-04-27 |  | 2016-09-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006779 | Monthly and annual integrated peak hour Demands in megawatts for the prior calendar year. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780006785 | Monthly forecast Net Energy for Load in gigawatthours for the next two calendar years. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 14200000 | NPCC-ON |  | NPCC-US
2 | 79780006791 | The Demand and energy effects of controllable and dispatchable Demand Side Management under the control or supervision of the System Operator. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 15200000 | NPCC-ON |  | NPCC-US
2 | 79780006797 | Specifications of the following items consistent with procedures for building the Interconnection-wide case(s): |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-07-01 |  |  |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006799 | Level of detail to which equipment shall be modeled; |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-07-01 |  |  |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. |  | 12200000 | NPCC-ON |  | NPCC-US
2 | 79780006804 | Provide the response within 90 calendar days of receipt, unless a longer time period is agreed upon by the notifying Planning Coordinator or Transmission Planner. |  | BA, GO, LSE, RP, TO, TSP | BA |  |  |  | GO |  |  | LSE | [5 empty] | RP |  |  |  | TO |  |  | TSP |  | 2015-07-01 |  |  |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780006806 | Comparison of the performance of the Planning Coordinator’s portion of the existing system in a planning dynamic model to actual system response, through simulation of a dynamic local event, at least once every 24 calendar months (use a dynamic local event that occurs within 24 calendar months of the last dynamic local event used in comparison, and complete each comparison within 24 calendar months of the dynamic local event). If no dynamic local event occurs within the 24 calendar months, use the next dynamic local event that occurs; |  | PCPA | [9 empty] | PA | [12 empty] | 2014-05-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006810 | Energy and capacity shortages. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-26 | [5 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006815 | Obtain written agreement from all of the Reliability Coordinators required to take the indicated action(s) for each update. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-26 | [5 empty] | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006819 | Assignment of coordination responsibilities for outage schedules between Transmission Operator(s) and Balancing Authority(s). |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780006820 | Specify outage submission timing requirements. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-26 | [5 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006824 | A mutually-agreeable format. |  | TOP | [18 empty] | TOP | [5 empty] | 2016-01-26 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006828 | A mutually-agreeable format. |  | BA | BA | [23 empty] | 2016-01-26 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006832 | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-26 |  | 2021-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006836 | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. |  | BA | BA | [21 empty] | 2016-01-26 |  | 2021-03-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006840 | A mutually agreeable process for resolving data conflicts |  | BA, DP, GO, GOP, LSE, TO, TOP | BA | DP |  |  | GO | GOP |  | LSE | [9 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2021-03-31 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780006843 | When instructed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-05-29 |  | 2017-09-25 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006847 | Available fixed tap ranges. |  | GO | [22 empty] | 2015-05-29 |  | 2017-09-25 |  |  |  | 51200000 | NPCC-ON |  | NPCC-US
2 | 79780006851 | Processes to prepare for and mitigate Emergencies including: |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006853 | Cancellation or recall of Transmission and generation outages; |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 12200000 | NPCC-ON |  | NPCC-US
2 | 79780006859 | Processes to prepare for and mitigate Emergencies including: |  | BA | BA | [21 empty] | 2016-01-25 | [5 empty] | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006861 | Requesting an Energy Emergency Alert, per Attachment 1; |  | BA | BA | [21 empty] | 2017-04-01 | [5 empty] | 22200000 | NPCC-ON |  | NPCC-US
2 | 79780006864 | fuel supply and inventory concerns; |  | BA | BA | [21 empty] | 2017-04-01 | [5 empty] | 22320000 | NPCC-ON |  | NPCC-US
2 | 79780006875 | Review each submitted Operating Plan(s) for coordination to avoid risk to Wide Area reliability; and |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 31200000 | NPCC-ON |  | NPCC-US
2 | 79780006878 | Include the applicable monitored Component attributes applied to each Protection System and Automatic Reclosing Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System and Automatic Reclosing Components. |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2015-12-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006880 | Include the applicable monitored Component attributes applied to each Protection System and Automatic Reclosing Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System and Automatic Reclosing Components. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-01-25 |  | 2015-12-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006882 | Include the applicable monitored Component attributes applied to each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-2, and Table 5 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [19 empty] | 2015-12-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006884 | The UVLS Program is integrated through coordination with generator voltage ride-through capabilities and other protection and control systems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage-based load shedding programs. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2017-04-01 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006886 | The UVLS Program is integrated through coordination with generator voltage ride-through capabilities and other protection and control systems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage-based load shedding programs. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2017-04-01 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780006888 | Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 |  |  |  | 4.2. Circuits:&lt;br/&gt;4.2.1 Circuits Subject to Requirements R1 – R5:&lt;br/&gt;4.2.1.1 Transmission lines operated at 200 kV and above, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads.&lt;br/&gt;4.2.1.2 Transmission lines operated at 100 kV to 200 kV selected by the Planning Coordinator in accordance with Requirement R6.&lt;br/&gt;4.2.1.3 Transmission lines operated below 100 kV that are part of the BES and selected by the Planning Coordinator in accordance with Requirement R6.&lt;br/&gt;4.2.1.4 Transformers with low voltage terminals connected at 200 kV and above.&lt;br/&gt;4.2.1.5 Transformers with low voltage terminals connected at 100 kV to 200 kV selected by the Planning Coordinator in accordance with Requirement R6.&lt;br/&gt;4.2.1.6 Transformers with low voltage terminals connected below 100 kV that are part of the BES and selected by the Planning Coordinator in accordance with Requirement R6.&lt;br/&gt;4.2.2 Circuits Subject to Requirement R6:&lt;br/&gt;4.2.2.1 Transmission lines operated at 100 kV to 200 kV and transformers with low voltage terminals connected at 100 kV to 200 kV, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads.&lt;br/&gt;4.2.2.2 Transmission lines operated below 100 kV and transformers with low voltage terminals connected below 100 kV that are part of the BES, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads. |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780006890 | Within 12 full calendar months of becoming aware of a generator, transformer, or transmission line BES Element that tripped in response to a stable or unstable power swing due to the operation of its protective relay(s), determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-1 – Attachment B. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2020-01-01 | [5 empty] | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006892 | Operate the electric system to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2014-11-04 |  | 2021-03-31 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780006899 | Technical requirements and analysis: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2014-11-04 |  | 2021-03-31 |  |  |  | 92000000 | NPCC-ON |  | NPCC-US
2 | 79780006901 | Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 92200000 | NPCC-ON |  | NPCC-US
2 | 79780006905 | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 93200000 | NPCC-ON |  | NPCC-US
2 | 79780006914 | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 94200000 | NPCC-ON |  | NPCC-US
2 | 79780006918 | Roles and responsibilities of responders. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.2. An example of evidence may include, but is not limited to, one or more recovery plans that include language identifying the roles and responsibilities of responders. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006923 | Test a representative sample of information used to recover BES Cyber System functionality at least once every 15 calendar months to ensure that the information is useable and is compatible with current configurations.&lt;br/&gt;&lt;br/&gt;An actual recovery that incorporates the information used to recover BES Cyber System functionality substitutes for this test. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.2. An example of evidence may include, but is not limited to, operational logs or test results with criteria for testing the usability (e.g. sample tape load, browsing tape contents) and compatibility with current system configurations (e.g. manual or automated comparison checkpoints between backup media contents and current configuration). | 2017-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006926 | No later than 60 calendar days after a change to the roles or responsibilities, responders, or technology that the Responsible Entity determines would impact the ability to execute the recovery plan: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.2. An example of evidence may include, but is not limited to, all of the following:&lt;br/&gt;1. Dated and revised recovery plan with changes to the roles or responsibilities, responders, or technology; and&lt;br/&gt;2. Evidence of plan update distribution including, but not limited to:&lt;br/&gt;• Emails;&lt;br/&gt;• USPS or other mail service; &lt;br/&gt;• Electronic distribution system; or&lt;br/&gt;• Training sign-in sheets. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780006928 | Update the recovery plan based on any documented lessons learned associated with the plan; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 31200000 | NPCC-ON |  | NPCC-US
2 | 79780006931 | Notify each person or group with a defined role in the recovery plan of the updates. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 32200000 | NPCC-ON |  | NPCC-US
2 | 79780006933 | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006936 | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-2 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780006939 | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780006946 | The effectiveness of the UFLS program. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 112000000 | NPCC-ON |  | NPCC-US
2 | 79780006950 | UFLS design assessment |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 142000000 | NPCC-ON |  | NPCC-US
2 | 79780006954 | For UFLS design assessments performed under Requirement R12, the Corrective Action Plan shall be developed within the two-year time frame identified in Requirement R12. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 152000000 | NPCC-ON |  | NPCC-US
2 | 79780006957 | The applicable in-service Protection System devices are set to operate to isolate or de-energize equipment in order to limit the extent of damage when operating conditions exceed equipment capabilities or stability limits. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-07-01 |  | 2016-06-30 |  |  |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780006961 | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall design and develop training materials according to its training program, based on the BES company-specific Real-time reliability-related task list created in part 1.1. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | M1.2 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection training materials, as specified in Requirement R1 part 1.2. | 2014-06-19 | [5 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780006966 | Each Transmission Owner shall design and develop training materials according to its training program, based on the BES company-specific Real-time reliabilityrelated task list created in part 2.1. |  | TO | [21 empty] | M2.2 Each Transmission Owner shall have available for inspection training materials, as specified in Requirement R2 part 2.2. | 2014-06-19 | [5 empty] | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780006974 | Include the applicable monitored Component attributes applied to each Protection System and Automatic Reclosing Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System and Automatic Reclosing Components. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [19 empty] | 2015-12-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007042 | For its assets identified in CIP-002 containing low impact BES Cyber Systems, if any: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007044 | Physical security controls; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12200000 | NPCC-ON |  | NPCC-US
2 | 79780007048 | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. |  | RC | [11 empty] | RC | [10 empty] | 2017-01-01 |  | 2021-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007052 | A mutually agreeable process for resolving data conflicts |  | BA, DP, GO, GOP, LSE, RC, TO, TOP | BA | DP |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2021-03-31 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780007055 | Energy and capacity shortages. |  | RC | [11 empty] | RC | [12 empty] | 2016-01-26 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007062 | Obtain written agreement from all of the Reliability Coordinators required to take the indicated action(s) for each update. |  | RC | [11 empty] | RC | [9 empty] | 2.2 Agreed to, in writing, by all the Reliability Coordinators required to take the indicated action(s). |  |  | 2016-01-26 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780007066 | System voltage limits; |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780007070 | Each methodology shall describe the method used to account for each of the following elements, provided such elements impact the determination of TFC or TTC: |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007072 | Transmission topology, including, but not limited to, additions and retirements; |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 12200000 | NPCC-ON |  | NPCC-US
2 | 79780007080 | Each Transmission Operator that uses the Area Interchange or Rated System Path Methodology shall describe in its methodology the process it uses to account for requested constraints that have a five percent or greater distribution factor for a transfer between areas in the TTC determination; otherwise the requested constraint is not required to be included. When testing transfers involving the requesting Transmission Operator’s area, the requested constraint may be excluded. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780007084 | Transmission topology, including, but not limited to, additions and retirements; |  | TSP | [20 empty] | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780007090 | Each Transmission Service Provider that uses the Flowgate Methodology shall, for reliability-related constraints identified in part 1.3, use the AFC determined by the Transmission Service Provider for that constraint. |  | TSP | [20 empty] | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780007092 | If not publicly posted on OASIS or its company website, the Transmission Operator’s effective: |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780007094 | TFC or TTC methodology. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 52200000 | NPCC-ON |  | NPCC-US
2 | 79780007097 | CBMID. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 53200000 | NPCC-ON |  | NPCC-US
2 | 79780007099 | In responding to all other data requests, each Transmission Operator or Transmission Service Provider shall make available the requested data within 45 calendar days of receipt of the written request. Unless otherwise agreed upon, the Transmission Operator or Transmission Service Provider is not required to alter the format in which it maintains or uses the data. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780007102 | Make available the requested data on a more frequent basis than it produces the data and in no event shall it be required to provide the data more frequently than once an hour. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 61200000 | NPCC-ON |  | NPCC-US
2 | 79780007105 | Interchange scheduling |  | BA | BA | [21 empty] | 2016-01-26 | [5 empty] | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780007113 | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 41200000 | NPCC-ON |  | NPCC-US
2 | 79780007114 | The study or studies shall be conducted based on the benchmark GMD event described in Attachment 1 to determine whether the System meets the performance requirements in Table 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780007118 | The effective GIC time series, GIC(t), calculated using the benchmark GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 5.1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2019-01-01 |  | 2019-06-30 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780007130 | Document assumptions used in the analysis; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2021-01-01 |  | 2019-06-30 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780007134 | Be reviewed in subsequent GMD Vulnerability Assessments until it is determined that the System meets the performance requirements contained in Table 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780007139 | The applicable in-service Protection System devices are set to operate to isolate or de-energize equipment in order to limit the extent of damage when operating conditions exceed equipment capabilities or stability limits. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-07-01 |  |  |  | 4.2. Facilities&lt;br/&gt;For the purpose of this standard, the term, “applicable Facility” shall mean any one of the following:&lt;br/&gt;4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.&lt;br/&gt;4.2.2 Individual synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.&lt;br/&gt;4.2.3 Generating plant/ Facility consisting of one or more units that are connected to the Bulk Electric System at a common bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.3.1 This includes individual generating units of the dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition where voltage regulating control for the facility is performed solely at the individual generating unit of the dispersed power producing resources. &lt;br/&gt;4.2.4 Any generator, regardless of size, that is a blackstart unit material to and designated as part of a Transmission Operator’s restoration plan. |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780007142 | The BES interrupting device owner owns all or part of the Composite Protection System; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-05-13 |  | 2016-06-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007146 | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-07-01 |  | 2016-06-30 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780007148 | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-05-13 |  | 2016-06-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780007150 | The BES interrupting device owner owns all or part of the Composite Protection System; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-05-29 |  | 2016-06-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007154 | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2016-06-30 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780007156 | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-05-29 |  | 2016-06-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780007158 | Include the applicable monitored Component attributes applied to each Protection System Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, and Table 3 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System Components. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-05-29 |  | 2016-12-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007161 | Include the applicable monitored Component attributes applied to each Protection System Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, and Table 3 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System Components. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-01-25 |  | 2015-12-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007164 | Notify other owners of BES Elements connected to those BES buses, if any, within 90-calendar days of completion of Part 1.1, that those BES Elements require SER data and/or FR data. |  | TO | [22 empty] | 2015-11-24 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007167 | Each phase current and the residual or neutral current for the following BES Elements: |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780007169 | Transmission Lines. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 32200000 | NPCC-ON |  | NPCC-US
2 | 79780007171 | A minimum recording rate of 16 samples per cycle. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780007174 | Phase undervoltage or overcurrent. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 43200000 | NPCC-ON |  | NPCC-US
2 | 79780007178 | Gross individual nameplate rating greater than or equal to 300 MVA where the gross plant/facility aggregate nameplate rating is greater than or equal to 1,000 MVA. |  | PCPA, RC | [9 empty] | PA |  | RC | [10 empty] | 2016-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 51120000 | NPCC-ON |  | NPCC-US
2 | 79780007179 | Any one BES Element that is part of a stability (angular or voltage) related System Operating Limit (SOL). |  | PCPA, RC | [9 empty] | PA |  | RC | [10 empty] | 2016-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 51200000 | NPCC-ON |  | NPCC-US
2 | 79780007183 | Identify a minimum DDR coverage, inclusive of those BES Elements identified in Part 5.1, of at least: |  | PCPA, RC | [9 empty] | PA |  | RC | [10 empty] | 2015-11-24 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780007185 | One BES Element per 3,000 MW of the Responsible Entity’s historical simultaneous peak System Demand. |  | PCPA, RC | [9 empty] | PA |  | RC | [10 empty] | 2016-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 52200000 | NPCC-ON |  | NPCC-US
2 | 79780007189 | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R6, Part 6.1, or the positive sequence current. |  | TO | [22 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780007193 | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R7, Part 7.1, phase current(s) for any phase-to-phase voltages, or positive sequence current. |  | GO | [22 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780007197 | At least one of the following three triggers: &lt;br/&gt;&lt;br/&gt;• Off nominal frequency trigger set at:&lt;br/&gt; Low High&lt;br/&gt;o Eastern Interconnection &amp;lt;59.75 Hz &amp;gt;61.0 Hz&lt;br/&gt;o Western Interconnection &amp;lt;59.55 Hz &amp;gt;61.0 Hz&lt;br/&gt;o ERCOT Interconnection &amp;lt;59.35 Hz &amp;gt;61.0 Hz&lt;br/&gt;o Hydro-Quebec Interconnection &amp;lt;58.55 Hz &amp;gt;61.5 Hz&lt;br/&gt;&lt;br/&gt;• Rate of change of frequency trigger set at:&lt;br/&gt;o Eastern Interconnection &amp;lt; -0.03125 Hz/sec &amp;gt; 0.125 Hz/sec&lt;br/&gt;o Western Interconnection &amp;lt; -0.05625 Hz/sec &amp;gt; 0.125 Hz/sec&lt;br/&gt;o ERCOT Interconnection &amp;lt; -0.08125 Hz/sec &amp;gt; 0.125 Hz/sec&lt;br/&gt;o Hydro-Quebec Interconnection &amp;lt; -0.18125 Hz/sec &amp;gt; 0.1875 Hz/sec&lt;br/&gt;&lt;br/&gt;• Undervoltage trigger set no lower than 85 percent of normal operating voltage for a duration of 5 seconds. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780007199 | Output recording rate of electrical quantities of at least 30 times per second. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 92000000 | NPCC-ON |  | NPCC-US
2 | 79780007201 | Synchronized device clock accuracy within ± 2 milliseconds of UTC. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 102000000 | NPCC-ON |  | NPCC-US
2 | 79780007203 | Data subject to Part 11.1 will be provided within 30-calendar days of a request unless an extension is granted by the requestor. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 112000000 | NPCC-ON |  | NPCC-US
2 | 79780007210 | Physical access controls; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780007218 | Require completion of the training specified in Part 2.1 prior to granting authorized electronic access and authorized unescorted physical access to applicable Cyber Assets, except during CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.2. Examples of evidence may include, but are not limited to, training records and documentation of when CIP Exceptional Circumstances were invoked. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780007221 | Any commercially available or open-source application software (including version) intentionally installed; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780007225 | Authorize and document changes that deviate from the existing baseline configuration. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.2. Examples of evidence may include, but are not limited to: &lt;br/&gt;• A change request record and associated electronic authorization (performed by the individual or group with the authority to authorize the change) in a change management system for each change; or&lt;br/&gt;• Documentation that the change was performed in accordance with the requirement. | 2016-03-31 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007229 | Following the change, verify that required cyber security controls determined in 1.4.1 are not adversely affected; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 14200000 | NPCC-ON |  | NPCC-US
2 | 79780007233 | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 15200000 | NPCC-ON |  | NPCC-US
2 | 79780007236 | Where technically feasible, at least once every 36 calendar months: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.2. An example of evidence may include, but is not limited to, a document listing the date of the assessment (performed at least once every 36 calendar months), the output of the tools used to perform the assessment, and a list of differences between the production and test environments with descriptions of how any differences were accounted for in conducting the assessment. | 2018-07-01 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780007238 | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2018-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 32200000 | NPCC-ON |  | NPCC-US
2 | 79780007242 | Procedure(s) for protecting and securely handling BES Cyber System Information, including storage, transit, and use. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.2. Examples of acceptable evidence include, but are not limited to: &lt;br/&gt;• Procedures for protecting and securely handling, which include topics such as storage, security during transit, and use of BES Cyber System Information; or &lt;br/&gt;• Records indicating that BES Cyber System Information is handled in a manner consistent with the entity’s documented procedure(s). | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting. &lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-011-2: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007244 | Prior to the disposal of applicable Cyber Assets that contain BES Cyber System Information, the Responsible Entity shall take action to prevent the unauthorized retrieval of BES Cyber System Information from the Cyber Asset or destroy the data storage media. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.2. Examples of acceptable evidence include, but are not limited to: &lt;br/&gt;• Records that indicate that data storage media was destroyed prior to the disposal of an applicable Cyber Asset; or&lt;br/&gt;• Records of actions taken to prevent unauthorized retrieval of BES Cyber System Information prior to the disposal of an applicable Cyber Asset. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting. &lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-011-2: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780007247 | Process to perform a seven year criminal history records check as part of each personnel risk assessment that includes: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.2. An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to perform a seven year criminal history records check. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780007260 | Unescorted physical access into a Physical Security Perimeter; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 41200000 | NPCC-ON |  | NPCC-US
2 | 79780007262 | Verify at least once each calendar quarter that individuals with active electronic access or unescorted physical access have authorization records. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.2. Examples of evidence may include, but are not limited to:&lt;br/&gt;• Dated documentation of the verification between the system generated list of individuals who have been authorized for access (i.e., workflow database) and a system generated list of personnel who have access (i.e., user account listing), or&lt;br/&gt;• Dated documentation of the verification between a list of individuals who have been authorized for access (i.e., authorization forms) and a list of individuals provisioned for access (i.e., provisioning forms or shared account listing). | 2016-10-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780007266 | For reassignments or transfers, revoke the individual’s authorized electronic access to individual accounts and authorized unescorted physical access that the Responsible Entity determines are not necessary by the end of the next calendar day following the date that the Responsible Entity determines that the individual no longer requires retention of that access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.2. An example of evidence may include, but is not limited to, documentation of all of the following:&lt;br/&gt;1. Dated workflow or sign-off form showing a review of logical and physical access; and &lt;br/&gt;2. Logs or other demonstration showing such persons no longer have access that the Responsible Entity determines is not necessary. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780007287 | Protect against the use of unnecessary physical input/output ports used for network connectivity, console commands, or Removable Media. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.2. An example of evidence may include, but is not limited to, documentation showing types of protection of physical input/output ports, either logically through system configuration or physically using a port lock or signage. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007289 | At least once every 35 calendar days, evaluate security patches for applicability that have been released since the last evaluation from the source or sources identified in Part 2.1. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.2. An example of evidence may include, but is not limited to, an evaluation conducted by, referenced by, or on behalf of a Responsible Entity of security-related patches released by the documented sources at least once every 35 calendar days. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780007293 | Mitigate the threat of detected malicious code. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.2. Examples of evidence may include, but are not limited to:&lt;br/&gt;• Records of response processes for malicious code detection&lt;br/&gt;• Records of the performance of these processes when malicious code is detected. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780007303 | Detected failed access attempts and failed login attempts; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.1. Examples of evidence may include, but are not limited to, a paper or system generated listing of event types for which the BES Cyber System is capable of detecting and, for generated events, is configured to log. This listing must include the required types of events. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 41200000 | NPCC-ON |  | NPCC-US
2 | 79780007305 | Generate alerts for security events that the Responsible Entity determines necessitates an alert, that includes, as a minimum, each of the following types of events (per Cyber Asset or BES Cyber System capability): |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.2. Examples of evidence may include, but are not limited to, paper or system-generated listing of security events that the Responsible Entity determined necessitate alerts, including paper or system generated list showing how alerts are configured. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780007307 | Detected failure of Part 4.1 event logging. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.2. Examples of evidence may include, but are not limited to, paper or system-generated listing of security events that the Responsible Entity determined necessitate alerts, including paper or system generated list showing how alerts are configured. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 42200000 | NPCC-ON |  | NPCC-US
2 | 79780007311 | Identify and inventory all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.2. An example of evidence may include, but is not limited to, a listing of accounts by account types showing the enabled or generic account types in use for the BES Cyber System. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780007317 | Minimum password complexity that is the lesser of three or more different types of characters (e.g., uppercase alphabetic, lowercase alphabetic, numeric, non-alphanumeric) or the maximum complexity supported by the Cyber Asset. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 55200000 | NPCC-ON |  | NPCC-US
2 | 79780007340 | Utilize at least one physical access control to allow unescorted physical access into each applicable Physical Security Perimeter to only those individuals who have authorized unescorted physical access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.2. An example of evidence may include, but is not limited to, language in the physical security plan that describes each Physical Security Perimeter and how unescorted physical access is controlled by one or more different methods and proof that unescorted physical access is restricted to only authorized individuals, such as a list of authorized individuals accompanied by access logs. | 2016-07-01 | [5 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007350 | Require manual or automated logging of visitor entry into and exit from the Physical Security Perimeter that includes date and time of the initial entry and last exit, the visitor’s name, and the name of an individual point of contact responsible for the visitor, except during CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.2. An example of evidence may include, but is not limited to, language in a visitor control program that requires continuous escorted access of visitors within Physical Security Perimeters and additional evidence to demonstrate that the process was implemented, such as dated visitor logs that include the required information. | 2016-07-01 | [5 empty] | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780007354 | Three phase currents and neutral currents. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780007359 | Each Fault recorder shall have a minimum recording rate of 16 samples per cycle. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780007362 | Neutral (residual) overcurrent set at 0.2 pu or less of rated CT secondary current. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 63200000 | NPCC-ON |  | NPCC-US
2 | 79780007366 | Records dynamic disturbance information with consideration of the following facilities/locations: |  | RC | [11 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780007387 | The effectiveness of the UFLS program. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 112000000 | NPCC-ON |  | NPCC-US
2 | 79780007389 | Monitor the following at each location listed in 1.1: |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007391 | Protective Relay tripping for all Protection Groups that operate to trip circuit breakers identified in 1.2.1. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 12200000 | NPCC-ON |  | NPCC-US
2 | 79780007402 | Major Generation clusters. |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 72200000 | NPCC-ON |  | NPCC-US
2 | 79780007409 | A minimum data sample rate of 960 samples per second, and a minimum data storage rate for RMS quantities of six (6) data points per second. |  | RC | [11 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 92000000 | NPCC-ON |  | NPCC-US
2 | 79780007412 | Rate of change of Power. |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 93200000 | NPCC-ON |  | NPCC-US
2 | 79780007416 | Bus voltages such that normal bus maintenance activities do not interfere with DDR functionality. |  | RC | [11 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 102000000 | NPCC-ON |  | NPCC-US
2 | 79780007421 | Summary of maintenance and testing procedures. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 142000000 | NPCC-ON |  | NPCC-US
2 | 79780007428 | Request from other Transmission Owners, Generator Owners within NPCC. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 152000000 | NPCC-ON |  | NPCC-US
2 | 79780007430 | Disturbance Data files shall be named in conformance with the latest revision of IEEE Standard C37.232. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 162000000 | NPCC-ON |  | NPCC-US
2 | 79780007433 | Make and model of equipment. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 172000000 | NPCC-ON |  | NPCC-US
2 | 79780007442 | The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). |  | TOP | [18 empty] | TOP |  |  |  | 2014-08-01 |  | 2015-11-12 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780007445 | Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. |  | GOP | [5 empty] | GOP | [16 empty] | 2014-08-01 |  | 2015-11-12 |  |  |  | 2720000 | NPCC-ON |  | NPCC-US
2 | 79780007447 | To mitigate the magnitude and duration of an IROL exceedance such that the IROL exceedance is relieved within the IROL’s Tv. |  | RC | [11 empty] | RC | [10 empty] | 2015-12-04 | [5 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007455 | Equal to or more negative than its Frequency Response Obligation when Frequency varies from 60 Hz by more than +/- 0.036 Hz. |  | BA | BA | [21 empty] | 2015-11-13 |  | 2020-11-30 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780007469 | Each adjacent Reliability Coordinator within the same Interconnection. |  | RC | [11 empty] | RC | [10 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007471 | Each adjacent Reliability Coordinator within the same Interconnection. |  | RC | [11 empty] | RC | [10 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780007473 | Each Balancing Authority within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780007479 | Electronic Security Perimeters (CIP-005) including Interactive Remote Access; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780007490 | Each Balancing Authority within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780007494 | Each Transmission Operator that operates Facilities within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780007499 | Each Transmission Operator that operates Facilities within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780007502 | Its Transmission Operator. |  | DP |  | DP | [20 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780007504 | Its Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780007513 | The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-25 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780007517 | other locations where, during the seven years immediately prior to the date of the criminal history records check, the subject has resided for six consecutive months or more. If it is not possible to perform a full seven year criminal history records check, conduct as much of the seven year criminal history records check as possible and document the reason the full seven year criminal history records check could not be performed.&lt;br/&gt;&lt;br/&gt;If it is not possible to perform a full seven year criminal history records check, conduct as much of the seven year criminal history records check as possible and document the reason the full seven year criminal history records check could not be performed. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 32200000 | NPCC-ON |  | NPCC-US
2 | 79780007528 | The BES interrupting device owner owns all or part of the Composite Protection System; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-12-04 |  | 2016-06-30 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007532 | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-07-01 |  | 2016-06-30 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780007534 | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-12-04 |  | 2016-06-30 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780007537 | The BES interrupting device owner owns all or part of the Composite Protection System; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-12-04 |  | 2017-04-01 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007542 | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-07-01 |  | 2017-04-01 |  |  |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780007544 | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-12-04 |  | 2017-04-01 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780007551 | The BES interrupting device owner owns all or part of the Composite Protection System; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-11-19 |  | 2021-03-31 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Protection Systems for BES Elements, with the following exclusions:&lt;br/&gt;4.2.1.1 Non-protective functions that are embedded within a Protection System.&lt;br/&gt;4.2.1.2 Protective functions intended to operate as a control function during switching. &lt;br/&gt;4.2.1.3 Special Protection Systems (SPS).&lt;br/&gt;4.2.1.4 Remedial Action Schemes (RAS).&lt;br/&gt;4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.&lt;br/&gt;4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.&lt;br/&gt;4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007556 | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-04-02 |  | 2021-03-31 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Protection Systems for BES Elements, with the following exclusions:&lt;br/&gt;4.2.1.1 Non-protective functions that are embedded within a Protection System.&lt;br/&gt;4.2.1.2 Protective functions intended to operate as a control function during switching. &lt;br/&gt;4.2.1.3 Special Protection Systems (SPS).&lt;br/&gt;4.2.1.4 Remedial Action Schemes (RAS).&lt;br/&gt;4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.&lt;br/&gt;4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.&lt;br/&gt;4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780007557 | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for which that backup protection was provided. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-11-19 |  | 2021-03-31 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Protection Systems for BES Elements, with the following exclusions:&lt;br/&gt;4.2.1.1 Non-protective functions that are embedded within a Protection System.&lt;br/&gt;4.2.1.2 Protective functions intended to operate as a control function during switching. &lt;br/&gt;4.2.1.3 Special Protection Systems (SPS).&lt;br/&gt;4.2.1.4 Remedial Action Schemes (RAS).&lt;br/&gt;4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.&lt;br/&gt;4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.&lt;br/&gt;4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780007565 | A review of the developed Protection System settings. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.1.3. Distribution Provider (that owns Protection Systems identified in the Facilities section 4.2 below)&lt;br/&gt;4.2. Facilities: Protection Systems installed to detect and isolate Faults on BES Elements. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007568 | Respond to any owner(s) that provided its proposed Protection System settings pursuant to Requirement R1, Part 1.3.1 by identifying any coordination issue(s) or affirming that no coordination issue(s) were identified. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.1.3. Distribution Provider (that owns Protection Systems identified in the Facilities section 4.2 below)&lt;br/&gt;4.2. Facilities: Protection Systems installed to detect and isolate Faults on BES Elements. |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780007580 | Include the applicable monitored Component attributes applied to each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-3, and Table 5 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-12-18 |  |  |  | 4.2.1 Protection Systems and Sudden Pressure Relaying that are installed for the purpose of detecting Faults on BES Elements (lines, buses, transformers, etc.)&lt;br/&gt;4.2.2 Protection Systems used for underfrequency load-shedding systems installed per ERO underfrequency load-shedding requirements.&lt;br/&gt;4.2.3 Protection Systems used for undervoltage load-shedding systems installed to prevent system voltage collapse or voltage instability for BES reliability.&lt;br/&gt;4.2.4 Protection Systems installed as a Remedial Action Scheme (RAS) for BES reliability.&lt;br/&gt;4.2.5 Protection Systems and Sudden Pressure Relaying for generator Facilities that are part of the BES, except for generators identified through Inclusion I4 of the BES definition, including:&lt;br/&gt;4.2.5.1 Protection Systems that act to trip the generator either directly or via lockout or auxiliary tripping relays.&lt;br/&gt;4.2.5.2 Protection Systems and Sudden Pressure Relaying for generator step-up transformers for generators that are part of the BES.&lt;br/&gt;4.2.5.3 Protection Systems and Sudden Pressure Relaying for station service or excitation transformers connected to the generator bus of generators which are part of the BES, that act to trip the generator either directly or via lockout or tripping auxiliary relays.&lt;br/&gt;4.2.6 Protection Systems and Sudden Pressure Relaying for the following BES generator Facilities for dispersed power producing resources identified through Inclusion I4 of the BES definition:&lt;br/&gt;4.2.6.1 Protection Systems and Sudden Pressure Relaying for Facilities used in aggregating dispersed BES generation from the point where those resources aggregate to greater than 75 MVA to a common point of connection at 100kV or above.&lt;br/&gt;4.2.7 Automatic Reclosing , including:&lt;br/&gt;4.2.7.1 Automatic Reclosing applied on the terminals of Elements connected to the BES bus located at generating plant substations where the total installed gross generating plant capacity is greater than the gross capacity of the largest BES generating unit within the Balancing Authority Area or, if a member of a Reserve Sharing Group, the largest generating unit within the Reserve Sharing Group. &lt;br/&gt;4.2.7.2 Automatic Reclosing applied on the terminals of all BES Elements at substations one bus away from generating plants specified in Section 4.2.7.1 when the substation is less than 10 circuit-miles from the generating plant substation.&lt;br/&gt;4.2.7.3 Automatic Reclosing applied as an integral part of an RAS specified in Section 4.2.4. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007582 | A timetable for providing the data. (A minimum of 30 calendar days must be allowed for responding to the request). |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-02-18 |  | 2021-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007585 | &lt;p&gt;Monthly and annual integrated peak hour Demands in megawatts for the prior calendar year.&lt;/p&gt; |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | &lt;p&gt;This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.”&lt;/p&gt; |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780007591 | &lt;p&gt;Monthly forecast Net Energy for Load in gigawatthours for the next two calendar years.&lt;/p&gt; |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | &lt;p&gt;This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.”&lt;/p&gt; |  | 14200000 | NPCC-ON |  | NPCC-US
2 | 79780007597 | &lt;p&gt;The Demand and energy effects of controllable and dispatchable Demand Side Management under the control or supervision of the System Operator.&lt;/p&gt; |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | &lt;p&gt;This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.”&lt;/p&gt; |  | 15200000 | NPCC-ON |  | NPCC-US
2 | 79780007609 | document all Reportable Balancing Contingency Events using CR Form 1. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2017-04-03 |  | 2017-12-31 |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007612 | 1.3.2 the Responsible Entity experiences:&lt;br/&gt;• multiple Contingencies where the combined MW loss exceeds its Most Severe Single Contingency and that are defined as a single Balancing Contingency Event, or &lt;br/&gt;• multiple Balancing Contingency Events within the sum of the time periods defined by the Contingency Event Recovery Period and Contingency Reserve Restoration Period whose combined magnitude exceeds the Responsible Entity's Most Severe Single Contingency. |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2017-12-31 |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780007622 | with a minimum accuracy of 0.001 Hz. |  | BA | BA | [21 empty] | 2017-11-27 | [5 empty] | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780007624 | a time synchronized common source to determine hourly megawatt-hour values agreed-upon to aid in the identification and mitigation of errors. |  | BA | BA | [21 empty] | 2017-11-27 | [5 empty] | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780007627 | transmission Facilities; and |  | TO | [22 empty] | 2019-01-01 | [5 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007630 | Procedures for notifying those responsible for the reliability of affected system(s) of new or materially modified existing interconnections. |  | TO | [22 empty] | 2019-01-01 | [5 empty] | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780007633 | Procedures for notifying those responsible for the reliability of affected system(s) of new interconnections. |  | GO | [22 empty] | 2019-01-01 | [5 empty] | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780007640 | An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, (Footnote: Multiple Sustained Outages on an individual line, if caused by the same vegetation, will be reported as one outage regardless of the actual number of outages within a 24-hour period.) |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:&lt;br/&gt;4.1.1. Applicable Transmission Owners&lt;br/&gt;4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.&lt;br/&gt;4.1.2. Applicable Generator Owners&lt;br/&gt;4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. &lt;br/&gt;4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.2.1. Each overhead transmission line operated at 200kV or higher.&lt;br/&gt;4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.&lt;br/&gt;4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.&lt;br/&gt;4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. &lt;br/&gt;4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:&lt;br/&gt;4.3.1.1. Operated at 200kV or higher; or&lt;br/&gt;4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or&lt;br/&gt;4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007644 | An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:&lt;br/&gt;4.1.1. Applicable Transmission Owners&lt;br/&gt;4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.&lt;br/&gt;4.1.2. Applicable Generator Owners&lt;br/&gt;4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. &lt;br/&gt;4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.2.1. Each overhead transmission line operated at 200kV or higher.&lt;br/&gt;4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.&lt;br/&gt;4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.&lt;br/&gt;4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. &lt;br/&gt;4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:&lt;br/&gt;4.3.1.1. Operated at 200kV or higher; or&lt;br/&gt;4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or&lt;br/&gt;4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780007648 | Inter-relationships between vegetation growth rates, vegetation control methods, and inspection frequency. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:&lt;br/&gt;4.1.1. Applicable Transmission Owners&lt;br/&gt;4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.&lt;br/&gt;4.1.2. Applicable Generator Owners&lt;br/&gt;4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. &lt;br/&gt;4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.2.1. Each overhead transmission line operated at 200kV or higher.&lt;br/&gt;4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.&lt;br/&gt;4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.&lt;br/&gt;4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. &lt;br/&gt;4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:&lt;br/&gt;4.3.1.1. Operated at 200kV or higher; or&lt;br/&gt;4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or&lt;br/&gt;4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780007650 | Circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner (Footnote: Circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner include but are not limited to natural disasters such as earthquakes, fires, tornados, hurricanes, landslides, ice storms, floods, or major storms as defined either by the TO or GO or an applicable regulatory body.) |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:&lt;br/&gt;4.1.1. Applicable Transmission Owners&lt;br/&gt;4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.&lt;br/&gt;4.1.2. Applicable Generator Owners&lt;br/&gt;4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. &lt;br/&gt;4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.2.1. Each overhead transmission line operated at 200kV or higher.&lt;br/&gt;4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.&lt;br/&gt;4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.&lt;br/&gt;4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. &lt;br/&gt;4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:&lt;br/&gt;4.3.1.1. Operated at 200kV or higher; or&lt;br/&gt;4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or&lt;br/&gt;4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780007666 | When modeling contingencies the system shall demonstrate transient, dynamic and voltage stability, with no Transmission Element modeled above its Emergency Rating. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780007668 | Where it is impossible to actually simulate a reliability-limited flow in a direction counter to prevailing flows (on an alternating current Transmission line), set the TTC for the non-prevailing direction equal to the TTC in the prevailing direction. If the TTC in the prevailing flow direction is dependent on a Remedial Action Scheme (RAS), set the TTC for the non-prevailing flow direction equal to the greater of the maximum flow that can be simulated in the non-prevailing flow direction or the maximum TTC that can be achieved in the prevailing flow direction without use of a RAS. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780007685 | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System. |  | PCPA | [9 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 220000 | NPCC-ON |  | NPCC-US
2 | 79780007688 | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-2 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 320000 | NPCC-ON |  | NPCC-US
2 | 79780007691 | Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES |  | PCPA | [9 empty] | PA | [12 empty] | 2015-10-01 |  | 2017-09-30 |  |  |  | 332000 | NPCC-ON |  | NPCC-US
2 | 79780007695 | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 420000 | NPCC-ON |  | NPCC-US
2 | 79780007703 | The effectiveness of the UFLS program |  | PCPA | [9 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 2020000 | NPCC-ON |  | NPCC-US
2 | 79780007713 | Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-11-13 |  | 2017-09-25 |  |  |  | 2720000 | NPCC-ON |  | NPCC-US
2 | 79780007726 | Provisions to indicate the quality of Real-time data to the System Operator; and |  | TOP | [18 empty] | TOP |  |  |  | 2016-09-22 |  | 2018-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007730 | Provisions to indicate the quality of Real-time data to the System Operator; and |  | BA | BA | [21 empty] | 2016-09-22 |  | 2018-03-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780007734 | Provisions to indicate the quality of analysis used in its Real-time Assessments; and |  | TOP | [18 empty] | TOP |  |  |  | 2016-09-22 |  | 2018-03-31 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780007740 | Provisions to indicate the quality of Real-time data to the System Operator; and |  | RC | [11 empty] | RC | [10 empty] | 2016-09-22 |  | 2018-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007743 | Provisions to indicate the quality of analysis used in its Real-time Assessments; and |  | RC | [11 empty] | RC | [10 empty] | 2016-09-22 |  | 2018-03-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780007752 | The RAS avoids adverse interactions with other RAS, and protection and control systems. |  | PCPA | [9 empty] | PA | [12 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 41200000 | NPCC-ON |  | NPCC-US
2 | 79780007761 | Provide the results of the RAS evaluation including any identified deficiencies to each reviewing Reliability Coordinator and RAS-entity, and each impacted Transmission Planner and Planning Coordinator. |  | PCPA | [9 empty] | PA | [12 empty] | 2026-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780007765 | The RAS responded as designed. |  | DP, GO, PCPA, RC, TO |  | DP |  |  | GO |  |  |  |  | PA |  | RC | [10 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 51200000 | NPCC-ON |  | NPCC-US
2 | 79780007768 | Provide the results of RAS operational performance analysis that identified any deficiencies to its reviewing Reliability Coordinator(s). |  | DP, GO, PCPA, RC, TO |  | DP |  |  | GO |  |  |  |  | PA |  | RC | [10 empty] | 2017-11-27 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780007772 | Update the CAP if actions or timetables change. |  | DP, GO, PCPA, RC, TO |  | DP |  |  | GO |  |  |  |  | PA |  | RC | [10 empty] | 2017-11-27 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780007777 | Require its operating personnel that issue an oral two-party, person-to-person Operating Instruction to take one of the following actions:&lt;br/&gt;• Confirm the receiver’s response if the repeated information is correct.&lt;br/&gt;• Reissue the Operating Instruction if the repeated information is incorrect or if requested by the receiver.&lt;br/&gt;• Take an alternative action if a response is not received or if the Operating Instruction was not understood by the receiver. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2015-06-22 | [5 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007783 | Assess the effectiveness of its documented communications protocols in Requirement R1 for its operating personnel that issue and receive Operating Instructions and modify its documented communication protocols, as necessary. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2015-06-22 | [5 empty] | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780007787 | Each adjacent Reliability Coordinator within the same Interconnection. |  | RC | [11 empty] | RC | [10 empty] | 2016-10-28 | [5 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007790 | Each adjacent Reliability Coordinator within the same Interconnection. |  | RC | [11 empty] | RC | [10 empty] | 2016-10-28 | [5 empty] | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780007793 | Each Balancing Authority within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2016-10-28 | [5 empty] | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780007800 | Each Balancing Authority within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2016-10-28 | [5 empty] | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780007805 | Each Transmission Operator that operates Facilities within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2016-10-28 | [5 empty] | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780007811 | Each Transmission Operator that operates Facilities within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2016-10-28 | [5 empty] | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780007815 | Its Transmission Operator. |  | DP |  | DP | [20 empty] | 2016-10-28 | [5 empty] | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780007818 | Its Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2016-10-28 | [5 empty] | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780007826 | The UVLS Program is integrated through coordination with generator voltage ride-through capabilities and other protection and control systems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage-based load shedding programs. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-11-19 | [5 empty] | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780007845 | Identify each of the medium impact BES Cyber Systems according to Attachment 1, Section 2, if any, at each asset; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-12-27 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency load shedding (UFLS) or undervoltage load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-002-5.1a: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007849 | Have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 at least once every 15 calendar months, even if it has no identified items in Requirement R1. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-12-27 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency load shedding (UFLS) or undervoltage load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-002-5.1a: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780007853 | Provisions to indicate the quality of Real-time data to the System Operator; and |  | RC | [11 empty] | RC | [10 empty] | 2016-12-14 | [5 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007858 | Provisions to indicate the quality of analysis used in its Real-time Assessments; and |  | RC | [11 empty] | RC | [10 empty] | 2016-12-14 | [5 empty] | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780007862 | Provisions to indicate the quality of Real-time data to the System Operator; and |  | TOP | [18 empty] | TOP |  |  |  | 2016-12-14 | [5 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007866 | Provisions to indicate the quality of Real-time data to the System Operator; and |  | BA | BA | [21 empty] | 2016-12-14 | [5 empty] | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780007871 | &lt;p&gt;Provisions to indicate the quality of analysis used in its Real-time Assessments; and&lt;/p&gt; |  | TOP | [18 empty] | TOP |  |  |  | 2016-12-14 | [5 empty] | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780007888 | A summary description of the elements required to support the backup functionality. These elements shall include: |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007890 | Data exchange capabilities. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2019-04-01 | [5 empty] | 12200000 | NPCC-ON |  | NPCC-US
2 | 79780007899 | Actions to manage the risk to the BES during the transition from primary to backup functionality, as well as during outages of the primary or backup functionality. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2019-04-01 | [5 empty] | 16200000 | NPCC-ON |  | NPCC-US
2 | 79780007909 | The backup functionality for a minimum of two continuous hours. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780007913 | Criteria and conditions for re-establishing interconnections with other Transmission Operators within its Reliability Coordinator Area, with Transmission Operators in other Reliability Coordinator Areas, and with other Reliability Coordinators. |  | RC | [11 empty] | RC | [10 empty] | 2018-03-26 | [5 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007928 | Re-establishing the Interconnection. |  | RC | [11 empty] | RC | [10 empty] | 2018-03-26 | [5 empty] | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780007933 | A description of how all Agreements or mutually-agreed upon procedures or protocols for off-site power requirements of nuclear power plants, including priority of restoration, will be fulfilled during System restoration. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007945 | Prior to implementing a planned permanent BES modification subject to its Reliability Coordinator approval requirements per EOP-006. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780007949 | The location and magnitude of Loads required to control voltages and frequency within acceptable operating limits. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780007953 | A list of required tests including: |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780007955 | The ability to energize a bus. If it is not possible to energize a bus during the test, the testing entity must affirm that the unit has the capability to energize a bus such as verifying that the breaker close coil relay can be energized with the voltage and frequency monitor controls disconnected from the synchronizing circuits. |  | TOP | [18 empty] | TOP |  |  |  | 2019-04-01 | [5 empty] | 72200000 | NPCC-ON |  | NPCC-US
2 | 79780007959 | Restoration priorities. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780007972 | The procedures documented in Requirement R12 |  | GOP | [5 empty] | GOP | [16 empty] | 2018-03-26 | [5 empty] | 152000000 | NPCC-ON |  | NPCC-US
2 | 79780007987 | For its assets identified in CIP-002 containing low impact BES Cyber Systems, if any: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2018-06-25 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780007989 | Electronic Security Perimeters (CIP-005) including Interactive Remote Access; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780007999 | Physical security controls; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12200000 | NPCC-ON |  | NPCC-US
2 | 79780008024 | Monitor the status of Remedial Action Schemes within its Transmission Operator Area; |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-17 |  | 2021-03-31 |  |  |  | 102000000 | NPCC-ON |  | NPCC-US
2 | 79780008044 | document all Reportable Balancing Contingency Events using CR Form 1. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2017-10-02 |  | 2019-03-31 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780008047 | the Responsible Entity experiences:&lt;br/&gt;• multiple Contingencies where the combined MW loss exceeds its Most Severe Single Contingency and that are defined as a single Balancing Contingency Event, or &lt;br/&gt;• multiple Balancing Contingency Events within the sum of the time periods defined by the Contingency Event Recovery Period and Contingency Reserve Restoration Period whose combined magnitude exceeds the Responsible Entity's Most Severe Single Contingency. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2018-01-01 |  | 2019-03-31 |  |  |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780008059 | The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). |  | TOP | [18 empty] | TOP |  |  |  | 2017-09-26 |  | 2018-12-31 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780008069 | Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. |  | GOP | [5 empty] | GOP | [16 empty] | 2017-09-26 |  | 2018-12-31 |  |  |  | 2720000 | NPCC-ON |  | NPCC-US
2 | 79780008073 | When instructed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2017-09-26 | [5 empty] | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780008081 | Available fixed tap ranges. |  | GO | [22 empty] | 2017-09-26 | [5 empty] | 51200000 | NPCC-ON |  | NPCC-US
2 | 79780008087 | One or more process(es) used in procuring BES Cyber Systems that address the following, as applicable: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and&lt;br/&gt;4.1.2.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and&lt;br/&gt;4.2.1.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers&lt;br/&gt;4.2.2.1. All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-013-1:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the identification and categorization process required by CIP-002-5, or any subsequent version of that Reliability Standard. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780008089 | Coordination of responses to vendor-identified incidents related to the products or services provided to the Responsible Entity that pose cyber security risk to the Responsible Entity; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and&lt;br/&gt;4.1.2.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and&lt;br/&gt;4.2.1.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers&lt;br/&gt;4.2.2.1. All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-013-1:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the identification and categorization process required by CIP-002-5, or any subsequent version of that Reliability Standard. |  | 12200000 | NPCC-ON |  | NPCC-US
2 | 79780008098 | All External Routable Connectivity must be through an identified Electronic Access Point (EAP). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, network diagrams showing all external routable communication paths and the identified EAPs. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-005-6:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780008104 | For all Interactive Remote Access sessions, utilize encryption that terminates at an Intermediate System. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, architecture documents detailing where encryption initiates and terminates. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-005-6:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780008111 | Any commercially available or open-source application software (including version) intentionally installed; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780008115 | Authorize and document changes that deviate from the existing baseline configuration. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: &lt;br/&gt;• A change request record and associated electronic authorization (performed by the individual or group with the authority to authorize the change) in a change management system for each change; or&lt;br/&gt;• Documentation that the change was performed in accordance with the requirement. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780008119 | Following the change, verify that required cyber security controls determined in 1.4.1 are not adversely affected; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 14200000 | NPCC-ON |  | NPCC-US
2 | 79780008123 | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 15200000 | NPCC-ON |  | NPCC-US
2 | 79780008126 | Verify the integrity of the software obtained from the software source. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 16200000 | NPCC-ON |  | NPCC-US
2 | 79780008131 | Where technically feasible, at least once every 36 calendar months: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a document listing the date of the assessment (performed at least once every 36 calendar months), the output of the tools used to perform the assessment, and a list of differences between the production and test environments with descriptions of how any differences were accounted for in conducting the assessment. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780008133 | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 32200000 | NPCC-ON |  | NPCC-US
2 | 79780008167 | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780008171 | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-3 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780008175 | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-3 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780008190 | The effectiveness of the UFLS program. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 112000000 | NPCC-ON |  | NPCC-US
2 | 79780008196 | For UFLS design assessments performed under Requirement R12, the Corrective Action Plan shall be developed within the two-year time frame identified in Requirement R12. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 152000000 | NPCC-ON |  | NPCC-US
2 | 79780008332 | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  |  | 41200000 | NPCC-ON |  | NPCC-US
2 | 79780008333 | The study or studies shall be conducted based on the benchmark GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning benchmark GMD event contained in Table 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780008338 | The effective GIC time series, GIC(t), calculated using the benchmark GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 5.1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-01-01 |  | 2019-06-30 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780008341 | Document assumptions used in the analysis; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2019-06-30 |  |  |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780008346 | Be developed within one year of completion of the benchmark GMD Vulnerability Assessment. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780008349 | Specify implementation of hardware mitigation, if any, within four years of development of the CAP. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  |  | 73200000 | NPCC-ON |  | NPCC-US
2 | 79780008352 | Description of the original CAP, and any previous changes to the CAP, with the associated timetable(s) for implementing the selected actions in Part 7.1; and |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  |  | 74200000 | NPCC-ON |  | NPCC-US
2 | 79780008359 | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  |  | 81200000 | NPCC-ON |  | NPCC-US
2 | 79780008360 | The study or studies shall be conducted based on the supplemental GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning supplemental GMD event contained in Table 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  |  | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780008366 | The effective GIC time series, GIC(t), calculated using the supplemental GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 9.1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-01-01 |  | 2019-06-30 |  |  |  | 92000000 | NPCC-ON |  | NPCC-US
2 | 79780008369 | Document assumptions used in the analysis; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2019-06-30 |  |  |  | 102000000 | NPCC-ON |  | NPCC-US
2 | 79780008398 | Transmission operations |  | RC | [11 empty] | RC | [10 empty] | 2019-07-01 | [5 empty] | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780008408 | Emergency preparedness and operations |  | TOP | [18 empty] | TOP |  |  |  | 2019-07-01 | [5 empty] | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780008412 | Certificates&lt;br/&gt;• Reliability Operator&lt;br/&gt;• Balancing, Interchange and Transmission Operator&lt;br/&gt;• Transmission Operator |  | TOP | [18 empty] | TOP |  |  |  | 2018-11-21 | [5 empty] | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780008416 | Emergency preparedness and operations |  | BA | BA | [21 empty] | 2019-07-01 | [5 empty] | 31200000 | NPCC-ON |  | NPCC-US
2 | 79780008419 | Certificates&lt;br/&gt;• Reliability Operator&lt;br/&gt;• Balancing, Interchange and Transmission Operator&lt;br/&gt;• Balancing and Interchange Operator |  | BA | BA | [21 empty] | 2018-11-21 | [5 empty] | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780008424 | document all Reportable Balancing Contingency Events using CR Form 1. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2019-04-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780008427 | the Responsible Entity experiences:&lt;br/&gt;• multiple Contingencies where the combined MW loss exceeds its Most Severe Single Contingency and that are defined as a single Balancing Contingency Event, or &lt;br/&gt;• multiple Balancing Contingency Events within the sum of the time periods defined by the Contingency Event Recovery Period and Contingency Reserve Restoration Period whose combined magnitude exceeds the Responsible Entity's Most Severe Single Contingency. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2019-04-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780008431 | Identification of where the Responsible Entity applied security protection for transmitting Real-time Assessment and Real-time monitoring data between Control Centers; and |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-04-13 |  |  |  | 4.2. Exemptions: The following are exempt from Reliability Standard CIP-012-1:&lt;br/&gt;4.2.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3. A Control Center that transmits to another Control Center Real-time Assessment or Real-time monitoring data pertaining only to the generation resource or Transmission station or substation co-located with the transmitting Control Center. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780008441 | The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). |  | TOP | [18 empty] | TOP |  |  | For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | 2018-10-15 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780008454 | New planned Facilities and changes to existing Facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP | [8 empty] | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780008461 | System Off-Peak Load for one of the five years. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP | [8 empty] | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780008465 | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by the following annual current study, supplemented with qualified past studies as indicated in Requirement R2, Part 2.6: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-04-13 |  | 2020-06-10 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780008470 | System Off-Peak Load for one of the five years. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP | [8 empty] | 24200000 | NPCC-ON |  | NPCC-US
2 | 79780008478 | Include actions to resolve performance deficiencies identified in multiple sensitivity studies or provide a rationale for why actions were not necessary. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP | [8 empty] | 27200000 | NPCC-ON |  | NPCC-US
2 | 79780008483 | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP | [8 empty] | 28200000 | NPCC-ON |  | NPCC-US
2 | 79780008492 | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R3, Part 3.5. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-04-13 |  | 2020-06-10 |  |  |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780008495 | Simulate the expected automatic operation of existing and planned devices designed to provide steady state control of electrical system quantities when such devices impact the study area. These devices may include equipment such as phase-shifting transformers, load tap changing transformers, and switched capacitors and inductors. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP | [8 empty] | 33200000 | NPCC-ON |  | NPCC-US
2 | 79780008508 | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-3 - Attachment 1A, either for 60 seconds or until a steady-state condition between 59.0 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 12000 | NPCC-ON |  | NPCC-US
2 | 79780008512 | Overfrequency trip settings of individual generating units that are part of Quebec BES plants/facilities that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-3 - Attachment 1A, and |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 120000 | NPCC-ON |  | NPCC-US
2 | 79780008520 | &lt;p&gt;One or more processes:&lt;/p&gt; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | &lt;p&gt;Examples of evidence may include, but are not limited to, dated documentation of Cyber Security Incident response plan(s) that provide guidance or thresholds for determining which Cyber Security Incidents are also Reportable Cyber Security Incidents or a Cyber Security Incident that is determined to be an attempt to compromise a system identified in the “Applicable Systems” column including justification for attempt determination criteria and documented processes for notification.&lt;/p&gt; | 2019-06-20 |  |  |  | &lt;p&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes.&lt;/p&gt; |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780008522 | &lt;p&gt;To determine if an identified Cyber Security Incident is:&lt;br/&gt;• A Reportable Cyber Security Incident; or&lt;br/&gt;• An attempt to compromise, as determined by applying the criteria from Part 1.2.1, one or more systems identified in the “Applicable Systems” column for this Part; and&lt;/p&gt; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2021-01-01 |  |  |  | &lt;p&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes.&lt;/p&gt; |  | 12200000 | NPCC-ON |  | NPCC-US
2 | 79780008528 | &lt;p&gt;Use the Cyber Security Incident response plan(s) under Requirement R1 when responding to a Reportable Cyber Security Incident, responding to a Cyber Security Incident that attempted to compromise a system identified in the “Applicable Systems” column for this Part, or performing an exercise of a Reportable Cyber Security Incident. Document deviations from the plan(s) taken during the response to the incident or exercise.&lt;/p&gt; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | &lt;p&gt;Examples of evidence may include, but are not limited to, incident reports, logs, and notes that were kept during the incident response process, and follow-up documentation that describes deviations taken from the plan during the incident response or exercise.&lt;/p&gt; | 2019-06-20 |  |  |  | &lt;p&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes.&lt;/p&gt; |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780008534 | &lt;p&gt;Update the Cyber Security Incident response plan based on any documented lessons learned associated with the plan; and&lt;/p&gt; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2021-01-01 |  |  |  | &lt;p&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes.&lt;/p&gt; |  | 31200000 | NPCC-ON |  | NPCC-US
2 | 79780008536 | &lt;p&gt;No later than 60 calendar days after a change to the roles or responsibilities, Cyber Security Incident response groups or individuals, or technology that the Responsible Entity determines would impact the ability to execute the plan:&lt;/p&gt; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | &lt;p&gt;An example of evidence may include, but is not limited to:&lt;br/&gt;1. Dated and revised Cyber Security Incident response plan with changes to the roles or responsibilities, responders or technology; and&lt;br/&gt;2. Evidence of plan update distribution including, but not limited to:&lt;br/&gt;• Emails;&lt;br/&gt;• USPS or other mail service;&lt;br/&gt;• Electronic distribution system; or &lt;br/&gt;• Training sign-in sheets.&lt;/p&gt; | 2019-06-20 |  |  |  | &lt;p&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes.&lt;/p&gt; |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780008538 | Notify each person or group with a defined role in the Cyber Security Incident response plan of the updates. | [24 empty] | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | 32200000 | NPCC-ON |  | NPCC-US
2 | 79780008541 | &lt;p&gt;The attack vector used; and&lt;/p&gt; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2021-01-01 |  |  |  | &lt;p&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes.&lt;/p&gt; |  | 41200000 | NPCC-ON |  | NPCC-US
2 | 79780008543 | &lt;p&gt;After the Responsible Entity’s determination made pursuant to documented process(es) in Requirement R1, Part 1.2, provide initial notification within the following timelines:&lt;br/&gt;• One hour after the determination of a Reportable Cyber Security Incident.&lt;br/&gt;• By the end of the next calendar day after determination that a Cyber Security Incident was an attempt to compromise a system identified in the “Applicable Systems” column for this Part.&lt;/p&gt; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | &lt;p&gt;Examples of evidence may include, but are not limited to, dated documentation of notices to the E-ISAC and NCCIC.&lt;/p&gt; | 2019-06-20 |  |  |  | &lt;p&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes.&lt;/p&gt; |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780008554 | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 41200000 | NPCC-ON |  | NPCC-US
2 | 79780008555 | The study or studies shall be conducted based on the benchmark GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning benchmark GMD event contained in Table 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2020-10-05 |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780008560 | The effective GIC time series, GIC(t), calculated using the benchmark GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 5.1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-01-01 |  | 2020-10-05 |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780008566 | Document assumptions used in the analysis; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2020-10-05 |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780008571 | Be developed within one year of completion of the benchmark GMD Vulnerability Assessment. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2020-10-05 |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780008576 | Specify implementation of hardware mitigation, if any, within four years of development of the CAP. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 73200000 | NPCC-ON |  | NPCC-US
2 | 79780008578 | Description of the original CAP, and any previous changes to the CAP, with the associated timetable(s) for implementing the selected actions in Part 7.1; and |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 74200000 | NPCC-ON |  | NPCC-US
2 | 79780008583 | The study or studies shall be conducted based on the supplemental GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning supplemental GMD event contained in Table 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2020-10-05 |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780008587 | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 81200000 | NPCC-ON |  | NPCC-US
2 | 79780008591 | The effective GIC time series, GIC(t), calculated using the supplemental GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 9.1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-01-01 |  | 2020-10-05 |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 92000000 | NPCC-ON |  | NPCC-US
2 | 79780008599 | Document assumptions used in the analysis; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2020-10-05 |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 102000000 | NPCC-ON |  | NPCC-US
2 | 79780008682 | Electronic Security Perimeters (CIP-005) including Interactive Remote Access; | [28 empty] | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service &lt;br/&gt;&lt;br/&gt;equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11200000 | NPCC-ON |  | NPCC-US
2 | 79780008690 | For its assets identified in CIP-002 containing low impact BES Cyber Systems, if any: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2019-07-31 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service &lt;br/&gt;&lt;br/&gt;equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780008692 | Physical security controls; | [28 empty] | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service &lt;br/&gt;&lt;br/&gt;equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12200000 | NPCC-ON |  | NPCC-US
2 | 79780008701 | UFLS design assessment |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 142000000 | NPCC-ON |  | NPCC-US
2 | 79780008706 | Each Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if the Scheduling Path (proper connectivity of Adjacent Balancing Authorities) between it and its Adjacent Balancing Authorities is invalid. |  | BA | BA | [21 empty] | 2021-04-01 | [5 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780008713 | Opposite in sign or direction to that of the Adjacent Balancing Authority |  | BA | BA | [21 empty] | 2021-04-01 | [5 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780008724 | The documentation shall be consistent with the principle that the Facility Ratings do not exceed the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | GO | [28 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780008726 | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R2, Part 2.1 including identification of how each of the following were considered: |  | GO | [28 empty] | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780008730 | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. |  | GO | [28 empty] | 22200000 | NPCC-ON |  | NPCC-US
2 | 79780008734 | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | GO | [28 empty] | 24200000 | NPCC-ON |  | NPCC-US
2 | 79780008736 | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R3, Part 3.1 including identification of how each of the following were considered: |  | TO | [28 empty] | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780008741 | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. |  | TO | [28 empty] | 32200000 | NPCC-ON |  | NPCC-US
2 | 79780008745 | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | TO | [28 empty] | 34200000 | NPCC-ON |  | NPCC-US
2 | 79780008748 | The BES interrupting device owner owns all or part of the Composite Protection System; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Protection Systems for BES Elements, with the following exclusions:&lt;br/&gt;4.2.1.1 Non-protective functions that are embedded within a Protection System.&lt;br/&gt;4.2.1.2 Protective functions intended to operate as a control function during switching. &lt;br/&gt;4.2.1.3 Special Protection Systems (SPS).&lt;br/&gt;4.2.1.4 Remedial Action Schemes (RAS).&lt;br/&gt;4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.&lt;br/&gt;4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.&lt;br/&gt;4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780008753 | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Protection Systems for BES Elements, with the following exclusions:&lt;br/&gt;4.2.1.1 Non-protective functions that are embedded within a Protection System.&lt;br/&gt;4.2.1.2 Protective functions intended to operate as a control function during switching. &lt;br/&gt;4.2.1.3 Special Protection Systems (SPS).&lt;br/&gt;4.2.1.4 Remedial Action Schemes (RAS).&lt;br/&gt;4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.&lt;br/&gt;4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.&lt;br/&gt;4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 21200000 | NPCC-ON |  | NPCC-US
2 | 79780008755 | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for which that backup protection was provided. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Protection Systems for BES Elements, with the following exclusions:&lt;br/&gt;4.2.1.1 Non-protective functions that are embedded within a Protection System.&lt;br/&gt;4.2.1.2 Protective functions intended to operate as a control function during switching. &lt;br/&gt;4.2.1.3 Special Protection Systems (SPS).&lt;br/&gt;4.2.1.4 Remedial Action Schemes (RAS).&lt;br/&gt;4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.&lt;br/&gt;4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.&lt;br/&gt;4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780008773 | Monitor the status of Remedial Action Schemes within its Transmission Operator Area; |  | TOP | [18 empty] | TOP |  |  |  | 2021-04-01 | [5 empty] | 102000000 | NPCC-ON |  | NPCC-US
2 | 79780008807 | The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). |  | TOP | [18 empty] | TOP | [5 empty] | 2020-05-14 |  |  |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780008848 | Equal to or more negative than its Frequency Response Obligation when Frequency varies from 60 Hz by more than +/- 0.036 Hz. |  | BA | BA | [21 empty] | 2020-07-15 |  |  |  | Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780008908 | Design auxiliary system(s) or devices used for the control and protection of auxiliary system(s), necessary for the generating unit operation such that they will not trip the generating unit during underfrequency conditions above the appropriate generator underfrequency trip protection setting threshold curve in Figure 2. | [28 empty] | 4.1.3. Distribution Providers that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators&lt;br/&gt;4.1.4. Transmission Owners that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators |  | 122000000 | NPCC-ON |  | NPCC-US
2 | 79780008910 | Each Generator Owner shall transmit the existing underfrequency settings and any changes to the underfrequency settings along with the technical basis for the settings to the Planning Coordinator. |  | GO | [22 empty] | 2020-02-18 |  |  |  | 4.1.3. Distribution Providers that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators&lt;br/&gt;4.1.4. Transmission Owners that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators |  | 132000000 | NPCC-ON |  | NPCC-US
2 | 79780008914 | Set the frequency trip setting upper tolerance to no greater than + 0.1 Hz. |  | GO | [22 empty] | 2020-02-18 |  |  |  | 4.1.3. Distribution Providers that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators&lt;br/&gt;4.1.4. Transmission Owners that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators |  | 162000000 | NPCC-ON |  | NPCC-US
2 | 79780008916 | Each Generator Operator shall provide the blackstart test results within 30 calendar days following a request from its Reliability Coordinator or Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2018-03-26 | [5 empty] | 142000000 | NPCC-ON |  | NPCC-US
2 | 79780008988 | The study or studies shall be conducted based on the benchmark GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning benchmark GMD event contained in Table 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780008993 | The effective GIC time series, GIC(t), calculated using the benchmark GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 5.1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-03-19 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780008996 | Document assumptions used in the analysis; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 62000000 | NPCC-ON |  | NPCC-US
2 | 79780009001 | Be developed within one year of completion of the benchmark GMD Vulnerability Assessment. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 72000000 | NPCC-ON |  | NPCC-US
2 | 79780009004 | Specify implementation of hardware mitigation, if any, within four years of development of the CAP. | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 73200000 | NPCC-ON |  | NPCC-US
2 | 79780009007 | Revisions to the selected actions in Part 7.1, if any, including utilization of Operating Procedures, if applicable; and | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 74200000 | NPCC-ON |  | NPCC-US
2 | 79780009014 | The study or studies shall be conducted based on the supplemental GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning supplemental GMD event contained in Table 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 82000000 | NPCC-ON |  | NPCC-US
2 | 79780009020 | The effective GIC time series, GIC(t), calculated using the supplemental GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 9.1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-03-19 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 92000000 | NPCC-ON |  | NPCC-US
2 | 79780009023 | Document assumptions used in the analysis; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 102000000 | NPCC-ON |  | NPCC-US
2 | 79780009031 | Be developed within one year of completion of the supplemental GMD Vulnerability Assessment. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 112000000 | NPCC-ON |  | NPCC-US
2 | 79780009034 | Specify implementation of hardware mitigation, if any, within four years of development of the CAP. | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 113200000 | NPCC-ON |  | NPCC-US
2 | 79780009037 | Revisions to the selected actions in Part 11.1, if any, including utilization of Operating Procedures, if applicable; and | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 114200000 | NPCC-ON |  | NPCC-US
2 | 79780009059 | Adherence to applicable NERC Reliability Standards; regional and Transmission Owner planning criteria; and Facility interconnection requirements; |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2021-04-01 |  |  |  | Applicable Generator Owner: Generator Owner with a fully executed Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780009068 | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. |  | RC | [11 empty] | RC | [10 empty] | 2021-04-01 | [5 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780009074 | A mutually agreeable process for resolving data conflicts |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2021-04-01 | [5 empty] | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780009078 | A timetable for providing the data. (A minimum of 30 calendar days must be allowed for responding to the request). |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780009081 | Monthly and annual integrated peak hour Demands in megawatts for the prior calendar year. | [24 empty] | 2021-04-01 | [5 empty] | 13200000 | NPCC-ON |  | NPCC-US
2 | 79780009087 | Monthly forecast Net Energy for Load in gigawatthours for the next two calendar years. | [24 empty] | 2021-04-01 | [5 empty] | 14200000 | NPCC-ON |  | NPCC-US
2 | 79780009103 | Comparison of the performance of the Planning Coordinator’s portion of the existing system in a planning dynamic model to actual system response, through simulation of a dynamic local event, at least once every 24 calendar months (use a dynamic local event that occurs within 24 calendar months of the last dynamic local event used in comparison, and complete each comparison within 24 calendar months of the dynamic local event). If no dynamic local event occurs within the 24 calendar months, use the next dynamic local event that occurs; |  | PCPA | [9 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780009112 | Operate the electric system to meet the NPIRs. |  | BA, DP, GO, GOP, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  |  |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780009120 | Technical requirements and analysis: |  | BA, DP, GO, GOP, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  |  |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 92000000 | NPCC-ON |  | NPCC-US
2 | 79780009122 | Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 92200000 | NPCC-ON |  | NPCC-US
2 | 79780009126 | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 93200000 | NPCC-ON |  | NPCC-US
2 | 79780009134 | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 94200000 | NPCC-ON |  | NPCC-US
2 | 79780009172 | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and |  | PCPA | [9 empty] | PA | [16 empty] | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780009176 | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-4 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [16 empty] | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780009180 | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1. |  | PCPA | [9 empty] | PA | [16 empty] | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 42000000 | NPCC-ON |  | NPCC-US
2 | 79780009194 | The effectiveness of the UFLS program. |  | PCPA | [9 empty] | PA | [16 empty] | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 112000000 | NPCC-ON |  | NPCC-US
2 | 79780009199 | UFLS design assessment |  | PCPA | [9 empty] | PA | [16 empty] | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 142000000 | NPCC-ON |  | NPCC-US
2 | 79780009203 | For UFLS design assessments performed under Requirement R12, the Corrective Action Plan shall be developed within the two-year time frame identified in Requirement R12. |  | PCPA | [9 empty] | PA | [16 empty] | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 152000000 | NPCC-ON |  | NPCC-US
2 | 79780009206 | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. |  | TOP | [18 empty] | TOP |  |  |  | 2021-04-01 | [5 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780009211 | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. |  | BA | BA | [21 empty] | 2021-04-01 | [5 empty] | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780009218 | A mutually agreeable process for resolving data conflicts |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  |  | 2021-04-01 | [5 empty] | 52000000 | NPCC-ON |  | NPCC-US
2 | 79780009255 | Identify each of the medium impact BES Cyber System according to Attachment 1, Section 2, if any, at each asset; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [5 empty] | 2021-02-04 |  |  |  | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780009259 | Have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 at least once every 15 calendar months, even if it has no identified items in Requirement R1. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [5 empty] | 2021-02-04 |  |  |  | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780009309 | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by the following annual current study, supplemented with qualified past studies as indicated in Requirement R2, Part 2.6: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780009330 | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R3, Part 3.5. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780009433 | One or more process(es) used in procuring BES Cyber Systems, and their associated EACMS and PACS, that address the following, as applicable: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780009452 | All External Routable Connectivity must be through an identified Electronic Access Point (EAP). |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780009457 | For all Interactive Remote Access sessions, utilize encryption that terminates at an Intermediate System. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 22000000 | NPCC-ON |  | NPCC-US
2 | 79780009462 | Have one or more method(s) to terminate authenticated vendor-initiated remote connections and control the ability to reconnect. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 32000000 | NPCC-ON |  | NPCC-US
2 | 79780009470 | Authorize and document changes that deviate from the existing baseline configuration. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 12000000 | NPCC-ON |  | NPCC-US
2 | 79780009484 | Where technically feasible, at least once every 36 calendar months: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 32000000 | NPCC-ON |  | NPCC-US
2 | RP-2021-04-12-0000002 | The documentation shall be consistent with the principle that the Facility Ratings do not exceed the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | GO | [22 empty] | 2021-10-01 | [5 empty] | 10200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2 | RP-2021-04-12-0000004 | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R2, Part 2.1 including identification of how each of the following were considered: |  | GO | [22 empty] | 2021-10-01 | [5 empty] | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2 | RP-2021-04-12-0000014 | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R3, Part 3.1 including identification of how each of the following were considered: |  | GO | [22 empty] | 2021-10-01 | [5 empty] | 30200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2 | RP-2021-06-14-0000004 |  |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  |  | 71002000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2 | RP-2021-06-14-0000005 | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  |  | 70200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2 | RP-2021-06-15-0000039 | Blackstart unit testing requirements including, but not limited to: |  | RRO | [14 empty] | RRO | [7 empty] | 2011-05-23 |  | 2011-05-23 |  |  |  | 13002000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 101 | The Balancing Authorities that have a fixed schedule (B and C) but do not contain the Jointly Owned Unit shall not include their share of the governor droop response in their Frequency Bias Setting. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2009-06-28 |  |  | BAL-003-0b R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1025 | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  | IRO-005-2 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1052 | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  | IRO-005-3a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1074 | The equivalent Interconnection-wide transmission loading relief procedure for use in the Western Interconnection is the “WSCC Unscheduled Flow Mitigation Plan,” provided at: http://www.wecc.biz/documents/library/UFAS/UFAS_ mitigation_plan _rev_2001-clean_8-8-03.pdf. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-04-22 |  |  | IRO-006-3 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1082 | The Interconnection-wide transmission loading relief procedure for use in the Western Interconnection is WECC-IRO-STD-006-0 provided at: ftp://www.nerc.com/pub/sys/all_updl/standards/rrs/IRO-STD-006-0_17Jan07.pdf. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-23 |  | 2009-12-09 |  |  | IRO-006-4 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1100 | Mutually agreeable format. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2009-08-05 |  |  | IRO-010-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1108 | Energy and capacity shortages. |  | RC | [11 empty] | RC | [9 empty] | M1.1.2 Energy and capacity shortages. | 2007-06-18 |  | 2017-03-31 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1115 | Distributed to all Reliability Coordinators that are required to take the indicated action(s). |  | RC | [11 empty] | RC | [9 empty] | M2.2 Distributed to all Reliability Coordinators that are required to take the indicatedaction(s) | 2007-06-18 |  | 2017-03-31 |  |  | IRO-014-1 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1118 | The agreed-upon actions from the associated Reliability Coordinator-to-Reliability Coordinator Operating Procedure, Process, or Plan. |  | RC | [11 empty] | RC | [9 empty] | M3.2 Include a reference to the associated source document, and Support the agreed-upon actions from the source document. | 2007-06-18 |  | 2017-03-31 |  |  | IRO-014-1 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1121 | Include a distribution list. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  | IRO-014-1 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1130 | If the involved Reliability Coordinators cannot agree on the problem(s) each Reliability Coordinator shall re-evaluate the causes of the disagreement (bad data, status, study results, tools, etc.). |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  | IRO-016-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1132 | If time does not permit, then each Reliability Coordinator shall operate as though the problem(s) exist(s) until the conflicting system status is resolved. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1138 | An accounting for how the reservations and schedules for firm (non-recallable) and non-firm (recallable) transfers, both within and outside the Transmission Service Provider’s system, are included. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-001-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1143 | Daily values for day 8 through the first month at least once per week. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 15200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1153 | Daily values for at least the next 31 calendar days. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-001-1 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1157 | A description of the manner in which the Transmission Service Provider will account for counterflows including: |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-001-1 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1159 | A rationale for that accounting specified in R3.2. |  | TSP | [20 empty] | TSP |  |  |  | 2010-09-16 |  |  |  | 32200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1165 | The criteria used to determine when an outage that is in effect part of a month impacts a monthly calculation. |  | TSP | [20 empty] | TSP |  |  |  | 2010-09-16 |  |  |  | 36200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1169 | Each Reliability Coordinator associated with the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-001-1 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 117 | The Balancing Authority shall offset its Net Interchange Schedule (MW) by an amount equal to the computed bias contribution during a 0.02 Hertz Frequency Deviation (i.e. 20% of the Frequency Bias Setting). |  | BA, RC | BA | [10 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-04-01 |  |  | BAL-004-0 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1179 | Daily values, once per day. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-001-1 R8. | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1184 | If the Transmission Service Provider does not use the data requested in its transfer or Flowgate capability calculations, but maintains that data, it shall make that data available. |  | TSP | [20 empty] | TSP |  |  |  | 2010-09-16 |  |  |  | 91200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1186 | This data shall be made available by the Transmission Provider on the schedule specified by the requestor (but no more frequently than once per hour, unless mutually agreed to by the requester and the provider). |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-001-1 R9. | 92000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1192 | The amount of time it will take for a response. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-003-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1199 | Specify the frequency of calculation of the generation reliability requirement and associated CBM values. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-004-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1210 | The procedure and assumptions for establishing CBM for each Available Transfer Capability (ATC) Path or Flowgate. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1216 | Identifying expected import path(s) or source region(s). |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1224 | The EEA 2 is declared within the Balancing Authority Area of the “energydeficient entity,” and |  | RP | [13 empty] | RP | [8 empty] | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1227 | Be allocated as follows: For ATC Paths, based on the expected import paths or source regions provided by Load-Serving Entities or Resource Planners; For Flowgates, based on the expected import paths or source regions provided by Load-Serving Entities or Resource Planners and the distribution factors associated with those paths or regions, as determined by the Transmission Service Provider |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 123 | The Balancing Authority shall offset its Net Interchange Schedule (MW) by an amount equal to the computed bias contribution during a 0.02 Hertz Frequency Deviation (i.e., 20% of the Frequency Bias Setting). |  | BA, RC | BA | [10 empty] | RC | [12 empty] | 2012-08-16 |  |  | BAL-004-1 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1230 | Be allocated as follows: For ATC Paths, based on the expected import paths or source regions provided by Load-Serving Entities or Resource Planners; For Flowgates, based on the expected import paths or source regions provided by Load-Serving Entities or Resource Planners and the distribution factors associated with those paths or regions, as determined by the Transmission Planner. |  | TP | [19 empty] | TP |  |  | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1235 | To any Transmission Service Provider, Reliability Coordinator, Transmission Planner, Resource Planner, or Planning Coordinator within 30 calendar days of their making a request for the data. |  | TP, TSP | [19 empty] | TP | TSP |  | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. | MOD-004-1 R9. | 92000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1238 | Require review of the process by which CBM values are updated, and their frequency of update, to ensure that the most current CBM values are available to transmission users. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-005-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1245 | Require that CBM shall only be used if the Load-Serving Entity calling for its use is experiencing a generation deficiency and its Transmission Service Provider is also experiencing Transmission Constraints relative to imports of energy on its transmission system. |  | TSP | [20 empty] | TSP |  | 2007-06-18 |  | 2009-05-12 |  |  | MOD-006-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1250 | Require that CBM shall only be used if the Load-Serving Entity calling for its use is experiencing a generation deficiency and its Transmission Service Provider is also experiencing Transmission Constraints relative to imports of energy on its transmission system. |  | TSP | [20 empty] | TSP |  | 2009-05-13 |  | 2011-03-31 |  |  | MOD-006-0.1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1256 | Duration. |  | TSP | [20 empty] | TSP |  | 2007-06-18 |  | 2011-03-31 |  |  | MOD-007-0 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1260 | Specify how TRM values are incorporated into Available Transfer Capability calculations. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-008-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1263 | Load distribution error. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1275 | The description of the method used to allocate TRM across ATC Paths or Flowgates. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  |  |  |  | MOD-008-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1278 | Day-ahead and pre-schedule. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 | [5 empty] | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 128 | Large accumulations of primary inadvertent point to an invalid implementation of ATEC, loose control, metering or accounting errors. A BA in such a situation should identify the source of the error(s) and make the corrections, recalculate the primary inadvertent from the time of the error, adjust the accumulated primary inadvertent caused by the error(s), validate the implementation of ATEC, set Lmax equal to L10 and continue to operate with ATEC reducing the accumulation as system parameters allow. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2014-03-31 |  |  | BAL-004-WECC-01 R1. | 12000000 | WECC-US | [5 empty] | WECC-US
2. | 1286 | Require review of the process by which TRM values are updated, and their frequency of update, to ensure that the most current TRM values are available to transmission users. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-009-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1295 | Generating Units (including synchronous condensers, pumped storage, etc.): location, minimum and maximum Ratings (net Real and Reactive Power), regulated bus and voltage set point, and equipment status. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | MOD-011-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1307 | Unit-specific dynamics data shall be reported for generators and synchronous condensers (including, as appropriate to the model, items such as inertia constant, damping coefficient, saturation parameters, and direct and quadrature axes reactances and time constants), excitation systems, voltage regulators, turbine-governor systems, power system stabilizers, and other associated generation equipment. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | MOD-013-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1309 | The Interconnection-wide requirements shall specify unit size thresholds for permitting: The use of non-detailed vs. detailed models, The netting of small generating units with bus load, and The combining of multiple generating units at one plant. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 133 | All corrections to any previous hour Primary Inadvertent Interchange shall be added to the appropriate On- or Off-Peak accumulated Primary Inadvertent Interchange. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2014-03-31 |  |  | BAL-004-WECC-01 R4. | 42000000 | WECC-US | [5 empty] | WECC-US
2. | 1336 | Monthly and annual peak hour actual demands in MW and Net Energy for Load in gigawatthours (GWh) for the prior year. |  | LSE, PCPA, RP | [7 empty] | LSE |  | PA |  |  |  | RP | [8 empty] | 2007-06-18 |  | 2009-05-12 |  |  | MOD-017-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1341 | Monthly and annual peak hour actual demands in MW and Net Energy for Load in gigawatthours (GWh) for the prior year. |  | LSE, PCPA, RP | [7 empty] | LSE |  | PA |  |  |  | RP | [8 empty] | 2009-05-13 |  | 2016-06-30 |  |  | MOD-017-0.1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1346 | Address assumptions, methods, and the manner in which uncertainties are treated in the forecasts of aggregated peak demands and Net Energy for Load. |  | LSE, PCPA, RP, TP | [7 empty] | LSE |  | PA |  |  |  | RP | [5 empty] | TP |  |  | 2007-06-18 |  | 2016-06-30 |  |  | MOD-018-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1357 | Criteria for reporting generating unit auxiliary loads. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | MOD-024-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1362 | Real power requirements of auxiliary loads. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 15200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1368 | Criteria for reporting generating unit auxiliary loads. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | MOD-025-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1373 | Verified Reactive Power limitations, such as generator terminal voltage limitations, shorted rotor turns, etc. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 15200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 138 | Each Transmission Operator with transmission facilities operating in an Interconnection shall ensure that those transmission facilities are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2008-08-26 |  |  | BAL-005-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1380 | A description of the manner in which the Transmission Operator will account for Interchange Schedules in the calculation of TTC. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2013-09-30 |  |  | MOD-028-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1385 | Define if the sink used for ATC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2013-09-30 |  |  |  | 15200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1392 | Modeling data and topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination areas. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | MOD-028-1 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1397 | Load forecast for the applicable period being calculated. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2013-09-30 |  |  |  | 31200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1399 | For days two through 31 TTCs and for months two through 13 TTCs, use the following (as well as any other values and internal parameters as specified in the ATCID): |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | MOD-028-1 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1401 | Daily load forecast for the days two through 31 TTCs being calculated and monthly forecast for months two through 13 months TTCs being calculated. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2013-09-30 |  |  |  | 32200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1405 | Respect any contractual allocations of TTC. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | MOD-028-1 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1409 | At least once per calendar month for TTCs used in monthly ATC calculations. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | MOD-028-1 R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1413 | If the limit in step R6.1 can not be reached by adjusting any combination of load or generation, then set the incremental Transfer Capability by the results of the case where the maximum adjustments were applied. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | MOD-028-1 R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1418 | Seven calendar days after its determination for TTCs used in monthly ATC calculations. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | MOD-028-1 R7. | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1425 | All Transmission Operator areas contiguous with its own Transmission Operator area. (Equivalent representation is allowed.) |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 11120000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1428 | Models all system Elements as in-service for the assumed initial conditions. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1436 | Uses Facility Ratings as provided by the Transmission Owner and Generator Owner |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-029-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 144 | Balancing Authorities shall ensure the power flow and ACE signals that are utilized for calculating Balancing Authority performance or that are transmitted for Regulation Service are not filtered prior to transmission, except for the Anti-aliasing Filters of Tie Lines. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2008-08-26 |  |  | BAL-005-0 R12. | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1440 | When modeling contingencies the system shall demonstrate transient, dynamic and voltage stability, with no Transmission Element modeled above its Emergency Rating. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1442 | Where it is impossible to actually simulate a reliability-limited flow in a direction counter to prevailing flows (on an alternating current Transmission line), set the TTC for the non-prevailing direction equal to the TTC in the prevailing direction. If the TTC in the prevailing flow direction is dependant on a Special Protection System (SPS), set the TTC for the non-prevailing flow direction equal to the greater of the maximum flow that can be simulated in the non-prevailing flow direction or the maximum TTC that can be achieved in the prevailing flow direction without use of a SPS. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-029-1 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1457 | The following information on how source and sink for transmission service is accounted for in AFC calculations including: |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | MOD-030-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1459 | Define if the sink used for AFC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1464 | For daily AFC, once per day. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | MOD-030-1 R10. | 102000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1471 | Only the most limiting element in a series configuration needs to be included as a Flowgate. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 21120000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1472 | Results of a first Contingency transfer analyses from all adjacent Balancing Authority source and sink (as defined in the ATCID) combinations up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an Outage Transfer Distribution Factor (OTDF) of at least 5% and within the Transmission Operator’s system are included as Flowgates unless the interface between such adjacent Balancing Authorities is accounted for using another ATC methodology. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1474 | Only the most limiting element in a series configuration needs to be included as a Flowgate. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 21220000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1478 | The limiting Element/Contingency combination is included in the requesting Transmission Service Provider’s methodology. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 21420000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1479 | At a minimum, establish the list of Flowgates to create, modify, or delete internal Flowgates definitions at least once per calendar year. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | MOD-030-1 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1487 | Updated at least once per day for AFC calculations for intra-day, next day, and days two through 30. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | MOD-030-1 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1494 | Include in the transmission model expected generation and Transmission outages, additions, and retirements within the scope of the model as specified in the ATCID and in effect during the applicable period of the AFC calculation for the Transmission Service Provider’s area, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | MOD-030-1 R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1499 | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 61200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1500 | The impact of any firm Network Integration Transmission Service, including the impacts of generation to load in the model referenced in R5.2 and has a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed based on:. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | MOD-030-1 R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1502 | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 62200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1510 | The impact of any confirmed non-firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | MOD-030-1 R7. | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1520 | The following information on how source and sink for transmission service is accounted for in AFC calculations including: |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1522 | Define if the sink used for AFC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1527 | For daily AFC, once per day. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R10. | 102000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1534 | Only the most limiting element in a series configuration needs to be included as a Flowgate. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21120000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1536 | Results of a first Contingency transfer analysis from all adjacent Balancing Authority source and sink (as defined in the ATCID) combinations up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an Outage Transfer Distribution Factor (OTDF) of at least 5% and within the Transmission Operator’s system are included as Flowgates unless the interface between such adjacent Balancing Authorities is accounted for using another ATC methodology. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1538 | Only the most limiting element in a series configuration needs to be included as a Flowgate. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21220000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1543 | The limiting Element/Contingency combination is included in the requesting Transmission Service Provider’s methodology. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21420000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1544 | At a minimum, establish a list of Flowgates by creating, modifying, or deleting Flowgate definitions at least once per calendar year. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1552 | Updated at least once per day for AFC calculations for intra-day, next day, and days two through 30. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1559 | Include in the transmission model expected generation and Transmission outages, additions, and retirements within the scope of the model as specified in the ATCID and in effect during the applicable period of the AFC calculation for the Transmission Service Provider’s area, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1564 | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 61200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1565 | The impact of any firm Network Integration Transmission Service, including the impacts of generation to load in the model referenced in R5.2 and has a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed based on:. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1567 | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 62200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1575 | The impact of any confirmed non-firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R7. | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1588 | Operate the electric system to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2008-11-26 |  | 2010-03-31 |  |  | NUC-001-1 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1597 | Names of the responsible entities, organizational relationships, andresponsibilities related to the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 91200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1600 | Technical requirements and analysis: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2008-11-26 |  | 2010-03-31 |  |  | NUC-001-1 R9. | 92000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1602 | Identification of facilities, components, and configuration restrictionsthat are essential for meeting the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 92200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1606 | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 93200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1614 | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 94200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1622 | Positions directly responsible for complying with NERC standards. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-03-31 |  |  | PER-002-0 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1625 | The training program must include a plan for the initial and continuing training of Transmission Operator and Balancing Authority operating personnel. That plan shall address knowledge and competencies required for reliable system operations. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-03-31 |  |  | PER-002-0 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 163 | Each Transmission Operator with transmission facilities operating in an Interconnection shall ensure that those transmission facilities are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2009-05-13 |  | 2012-09-12 |  |  | BAL-005-0.1b R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1631 | Positions directly responsible for complying with NERC standards. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2012-09-30 |  |  | PER-003-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1642 | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall design and develop learning objectives and training materials based on the task list created in R1.1. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | M1.2 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection its learning objectives and training materials, as specified in R1.2. | 2013-04-01 |  | 2016-06-30 |  |  | PER-005-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1652 | If a protective relay or equipment failure reduces system reliability, the Transmission Operator shall notify its Reliability Coordinator and affected Transmission Operators and Balancing Authorities. The Transmission Operator shall take corrective action as soon as possible. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-03-31 |  |  | PRC-001-1 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1655 | Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-03-31 |  |  | PRC-001-1 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1659 | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ protection systems. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-03-31 |  |  | PRC-001-1 R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1664 | Devices to be monitored. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1668 | Elements to be monitored at each location. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1671 | Three phase currents and neutral currents. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 21320000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1675 | Technical requirements, including the following: |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | PRC-002-1 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1677 | Minimum sampling rate of 16 samples per cycle. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 22200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1682 | Elements and number of phases to be monitored at each location. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 31200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1685 | Megawatts and megavars. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 31320000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1686 | Technical requirements, including the following: |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | PRC-002-1 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1688 | Each device shall sample data at a rate of at least 960 samples per second and shall record the RMS value of electrical quantities at a rate of at least 6 records per second. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 32200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 169 | Balancing Authorities shall ensure the power flow and ACE signals that are utilized for calculating Balancing Authority performance or that are transmitted for Regulation Service are not filtered prior to transmission, except for the Anti-aliasing Filters of Tie Lines. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2009-05-13 |  | 2012-09-12 |  |  | BAL-005-0.1b R12. | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1691 | List of entities that must be provided with recorded Disturbance data. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | PRC-002-1 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1700 | Data reporting requirements (periodicity and format) for Misoperations. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | PRC-003-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1710 | System Protection personnel shall analyze all operations of Protection Systems and RAS within 20 business days for correctness to characterize whether a Misoperation has occurred that may not have been identified by System Operators. |  | GO, TO |  |  |  |  | GO | [16 empty] | M1.2 Transmission Owners and Generation Owners shall have evidence that System Protection personnel analyzed all operations of Protection System and RAS for correctness within 20 business days. | 2011-06-27 |  | 2017-03-31 |  |  | PRC-004-WECC-1 R1. | 12000000 | WECC-US | [5 empty] | WECC-US
2. | 1713 | If the Protection System or RAS has a Security-Based Misoperation and only one FEPS or FERAS remains in service to ensure BES reliability, the Transmission Owner or Generator Owner shall perform the following. [Time Horizon: Same-day Operations] |  | GO, TO |  |  |  |  | GO | [16 empty] | M2.2 Transmission Owners and Generation Owners shall have evidence that they removed from service and repaired the Protection System or RAS that misoperated per measurements M2.2.1 through M2.2.2. | 2011-06-27 |  | 2017-03-31 |  |  | PRC-004-WECC-1 R2. | 22000000 | WECC-US | [5 empty] | WECC-US
2. | 1715 | The Transmission Owner or Generator Owner shall repair or replace any Protection System or RAS that misoperated with a FEPS or FERAS within 20 business days of the date of removal. The Transmission Owner or Generator Owner shall remove the Element from service or disable the RAS if repair or replacement is not completed within 20 business days. |  | GO, TO |  |  |  |  | GO | [16 empty] | M2.2.2 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days or either removed the Element from service or disabled the RAS. | 2011-10-01 |  | 2017-03-31 |  |  |  | 22200000 | WECC-US | [5 empty] | WECC-US
2. | 1718 | When FERAS is not available, then |  | GO, TOP |  |  |  |  | GO | [13 empty] | TOP |  |  | M2.3.2 The Generator Owners and Transmission Operators shall have documentation describing all actions taken that adjusted generation or SOLs and operated facilities within established limits. | 2011-10-01 |  | 2017-03-31 |  |  |  | 23200000 | WECC-US | [5 empty] | WECC-US
2. | 1720 | Transmission Operators shall adjust the SOL and operate the facilities within established limits. |  | TOP | [18 empty] | TOP |  |  |  | 2011-10-01 |  | 2017-03-31 |  |  |  | 23220000 | WECC-US | [5 empty] | WECC-US
2. | 1723 | Transmission Owners or Generator Owners shall remove from service the associated Element or RAS. [Time Horizon: Operations Assessment] |  | GO, TO |  |  |  |  | GO | [16 empty] | M2.4.2 Transmission Owners and Generation Owners shall have evidence that they removed the associated Element or RAS from service. | 2011-10-01 |  | 2017-03-31 |  |  |  | 24200000 | WECC-US | [5 empty] | WECC-US
2. | 1726 | Completion of repairs or the replacement of Protection System and/or RAS that misoperated. |  | GO, TO |  |  |  |  | GO | [16 empty] | M3.2 Completion of repair or replacement of Protection System and/or RAS that misoperated. | 2011-06-27 |  | 2017-03-31 |  |  | PRC-004-WECC-1 R3. | 32000000 | WECC-US | [5 empty] | WECC-US
2. | 1729 | Summary of maintenance and testing procedures. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2007-06-18 |  | 2011-09-25 |  |  | PRC-005-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1732 | Date each Protection System device was last tested/maintained. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2007-06-18 |  | 2011-09-25 |  |  | PRC-005-1 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1735 | Design details shall include, but are not limited to: |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  | PRC-006-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1737 | Size of corresponding load shedding blocks (% of connected loads.) |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1747 | Dynamic simulation of possible Disturbance that cause the Region or portions of the Region to experience the largest imbalance between Demand (Load) and generation. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  |  | 14200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1757 | A review of the UFLS set points and tripping times. |  | DP, LSE, TO, TOP |  | DP | [5 empty] | LSE | [9 empty] | TO | TOP |  |  |  | 2007-06-18 |  | 2013-09-30 |  |  | PRC-009-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1764 | Simulations that demonstrate that the UVLS programs performance is consistent with Reliability Standards TPL-001-0, TPL-002-0, TPL-003-0 and TPL-004-0. |  | DP, LSE, TO, TOP |  | DP | [5 empty] | LSE | [9 empty] | TO | TOP |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1770 | Instrument transformers. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2027-03-31 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1773 | Documentation of maintenance and testing intervals and their basis. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2027-03-31 |  |  | PRC-011-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1781 | Requirements to provide data that describes design, operation, and modeling of an SPS. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  | PRC-012-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1792 | Operation — The actions taken by the SPS in response to Disturbance conditions, and |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  | PRC-013-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1799 | Study years, system conditions, and contingencies analyzed in the technical studies on which the assessment is based and when those technical studies were performed. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  | PRC-014-0 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1815 | Instrument transformers. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1818 | Documentation of maintenance and testing intervals and their basis. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2007-06-18 |  | 2017-03-31 |  |  | PRC-017-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1826 | Recorded data from each Disturbance shall be retrievable for ten calendar days.. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2022-06-30 |  |  | PRC-018-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1830 | Make and model of equipment. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2022-06-30 |  |  | PRC-018-1 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1841 | Summary of maintenance and testing procedures. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2022-06-30 |  |  | PRC-018-1 R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1844 | Size and location of customer load, or percent of connected load, to be interrupted. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  | PRC-020-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1852 | Corresponding voltage set points and overall scheme clearing times. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2017-03-31 |  |  | PRC-021-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1859 | A review of the UVLS set points and tripping times. |  | DP, LSE, TOP |  | DP | [5 empty] | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | PRC-022-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1870 | Evaluate the relay loadability in amperes at the relay trip point at 0.85 per unit voltage and a power factor angle of 30 degrees. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  |  | 20400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1873 | Set transmission line relays so they do not operate at or below 115% of the highest seasonal 15-minute Facility Rating2 of a circuit (expressed in amperes). |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  | PRC-023-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1876 | An impedance at each end of the line, which reflects the actual system source impedance with a 1.05 per unit voltage behind each source impedance. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 188 | Each Transmission Operator with transmission facilities operating in an Interconnection shall ensure that those transmission facilities are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2008-08-27 |  | 2009-05-12 |  |  | BAL-005-0b R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1887 | The Planning Coordinator shall maintain a current list of facilities determined according to the process described in R3.1. |  | PCPA | [9 empty] | PA | [12 empty] | 2011-11-17 |  | 2012-06-30 |  |  | PRC-023-1 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1900 | For a transmission facility, the Transmission Operator shall notify and coordinate with its Reliability Coordinator. The Transmission Operator shall notify other affected Transmission Operators, and coordinate the impact of removing the Bulk Electric System facility. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-11-20 |  |  | TOP-001-1 R7. | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1910 | Automatic Voltage Regulator status and mode setting. (Retired August 1, 2007) |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2009-12-01 |  |  | TOP-002-2 R14. | 142000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1914 | Changes in transmission facility rating. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-12-01 |  |  | TOP-002-2 R16. | 162000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1933 | Automatic Voltage Regulator status and mode setting. (Retired August 1, 2007) |  | GOP | [5 empty] | GOP | [16 empty] | 2009-12-02 |  | 2011-10-19 |  |  | TOP-002-2a R14. | 142000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1937 | Changes in transmission facility rating. |  | TOP | [18 empty] | TOP |  |  |  | 2009-12-02 |  | 2011-10-19 |  |  | TOP-002-2a R16. | 162000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 194 | Balancing Authorities shall ensure the power flow and ACE signals that are utilized for calculating Balancing Authority performance or that are transmitted for Regulation Service are not filtered prior to transmission, except for the Anti-aliasing Filters of Tie Lines. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2008-08-27 |  | 2009-05-12 |  |  | BAL-005-0b R12. | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1951 | Each Transmission Operator shall provide outage information daily to its Reliability Coordinator, and to affected Balancing Authorities and Transmission Operators for scheduled generator and bulk transmission outages planned for the next day (any foreseen outage of a transmission line or transformer greater than 100 kV or generator greater than 50 MW) that may collectively cause or contribute to an SOL or IROL violation or a regional operating area limitation. The Reliability Coordinator shall establish the outage reporting requirements. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-09-30 |  |  | TOP-003-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1958 | Each Transmission Operator shall provide outage information daily to affected Balancing Authorities and Transmission Operators for scheduled generator and bulk transmission outages planned for the next day (any foreseen outage of a transmission line or transformer greater than 100 kV or generator greater than 50 MW) that may collectively cause or contribute to an SOL or IROL violation or a regional operating area limitation. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2017-03-31 |  |  | TOP-003-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1970 | Monitoring and controlling voltage levels and real and reactive power flows. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-01-21 |  |  | TOP-004-1 R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 1982 | Switching transmission elements. |  | TOP | [18 empty] | TOP |  |  |  | 2009-01-22 |  | 2017-03-31 |  |  | TOP-004-2 R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2005 | Each Transmission Operator and Balancing Authority shall inform the Reliability Coordinator and other affected Balancing Authorities and Transmission Operators of all generation and transmission resources available for use. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-09-30 |  | VSL SevereThe responsible entity failed to inform the Reliability Coordinator and other affected Balancing Authorities and Transmission Operators of all generation and transmission resources available for use. | TOP-006-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2014 | Each Transmission Operator and Balancing Authority shall inform the Reliability Coordinator and other affected Balancing Authorities and Transmission Operators of all generation and transmission resources available for use. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2017-03-31 |  |  | TOP-006-2 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2035 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  | TPL-001-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2038 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2050 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2052 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  | TPL-001-0 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2056 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  | TPL-001-0.1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2059 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2071 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2073 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  | TPL-001-0.1 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2077 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | TPL-002-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2083 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2096 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2098 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | TPL-002-0 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 21 | Its allocation among members. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  | BAL-002-0 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2102 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | TPL-002-0a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2108 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2121 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2123 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | TPL-002-0a R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2127 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | TPL-003-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2133 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2146 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2148 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | TPL-003-0 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2152 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | TPL-003-0a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2158 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 217 | The hourly integrated megawatt-hour values of Net Actual Interchange. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | 41200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2171 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2173 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | TPL-003-0a R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2177 | Be conducted for near-term (years one through five). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  | TPL-004-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 218 | Each Balancing Authority shall use the agreed-to daily and monthly accounting data to compile its monthly accumulated Inadvertent Interchange for the On-Peak and Off-Peak hours of the month. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  | BAL-006-1 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2180 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2193 | Summer. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2195 | Near-term planning horizons (years one through five). Detailed assessments shall be conducted. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | TPL-005-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2201 | Operational assessments. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | TPL-005-0 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2208 | Resource Adequacy and supporting information (Regional assessment reports, existing and planned resource data, resource availability and characteristics, and fuel types and requirements.) |  | RRO | [14 empty] | RRO | [9 empty] | 2009-04-15 |  |  | TPL-006-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2221 | For each generator that is on this exemption list, the Transmission Operator shall notify the associated Generator Owner. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-09-30 |  |  | VAR-001-1 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2237 | For each generator that is on this exemption list, the Transmission Operator shall notify the associated Generator Owner. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-05-21 |  |  | VAR-001-1a R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2249 | When directed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2008-08-26 |  |  | VAR-002-1 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2252 | A status or capability change on any other Reactive Power resources under the Generator Operator’s control and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-06-18 |  | 2008-08-26 |  |  | VAR-002-1 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2256 | Available fixed tap ranges. |  | GO | [22 empty] | 2007-08-02 |  | 2008-08-26 |  |  |  | 41200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2264 | When directed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2009-05-13 |  | 2010-09-15 |  |  | VAR-002-1.1a R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2267 | A status or capability change on any other Reactive Power resources under the Generator Operator’s control and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2009-05-13 |  | 2010-09-15 |  |  | VAR-002-1.1a R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 227 | The hourly integrated megawatt-hour values of Net Actual Interchange. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-03-31 |  |  |  | 41200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2271 | Available fixed tap ranges. |  | GO | [22 empty] | 2009-05-13 |  | 2010-09-15 |  |  |  | 41200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2279 | When directed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2010-09-16 |  | 2013-06-30 |  |  | VAR-002-1.1b R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 228 | Each Balancing Authority shall use the agreed-to daily and monthly accounting data to compile its monthly accumulated Inadvertent Interchange for the On-Peak and Off-Peak hours of the month. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-03-31 |  |  | BAL-006-1.1 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2282 | A status or capability change on any other Reactive Power resources under the Generator Operator’s control and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2010-09-16 |  | 2013-06-30 |  |  | VAR-002-1.1b R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2286 | Available fixed tap ranges. |  | GO | [22 empty] | 2010-09-16 |  | 2013-06-30 |  |  |  | 41200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2294 | When directed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2008-08-27 |  | 2009-05-12 |  |  | VAR-002-1a R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2297 | A status or capability change on any other Reactive Power resources under the Generator Operator’s control and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2008-08-27 |  | 2009-05-12 |  |  | VAR-002-1a R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2301 | Available fixed tap ranges. |  | GO | [22 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 41200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2309 | Performing maintenance and testing up to a maximum of seven calendar days per calendar quarter. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-06-27 |  | 2015-03-31 |  |  | VAR-002-WECC-1 R1. | 12000000 | WECC-US | [5 empty] | WECC-US
2. | 2323 | Performing maintenance and testing up to a maximum of seven calendar days per calendar quarter. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-06-27 |  | 2015-03-31 |  |  | VAR-501-WECC-1 R1. | 12000000 | WECC-US | [5 empty] | WECC-US
2. | 2336 | The Interconnection-wide transmission loading relief procedure for use in the Western Interconnection is the WECC Unscheduled Flow Reduction Procedure provided at: http://www.wecc.biz/documents/library/UFAS/UFAS_mitigation_plan_rev_2001-clean_8-8-03.pdf. |  | RC | [11 empty] | RC | [10 empty] | 2009-12-10 |  | 2011-06-30 |  |  | IRO-006-4.1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2348 | Resource Adequacy and supporting information (Regional assessment reports, existing and planned resource data, resource availability and characteristics, and fuel types and requirements.) |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | TPL-006-0.1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2356 | The risk-based assessment shall consider the following assets: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-002-2 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2358 | Transmission substations that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2367 | The Cyber Asset uses a routable protocol within a control center; or, |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-002-2 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2372 | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-003-2 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2376 | Changes to the senior manager must be documented within thirty calendar days of the effective date. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-003-2 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2381 | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-003-2 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2385 | The Responsible Entity shall classify information to be protected under this program based on the sensitivity of the Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-003-2 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2390 | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 51200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2391 | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-003-2 R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2397 | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-2, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-004-2 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2399 | Physical and electronic access controls to Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 22200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2405 | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-004-2 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2409 | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-004-2 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2412 | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-005-2 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2419 | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-005-2 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2424 | The authentication methods. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 25200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2430 | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-005-2 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2433 | A review to verify that only ports and services required for operations at these access points are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-005-2 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2439 | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-005-2 R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2443 | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  | CIP-006-2 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2452 | Be afforded the protective measures specified in Standard CIP-003-2; Standard CIP-004-2 Requirement R3; Standard CIP-005-2 Requirements R2 and R3; Standard CIP-006-2 Requirements R4 and R5; Standard CIP-007-2; Standard CIP-008-2; and Standard CIP-009-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  | CIP-006-2 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 246 | The risk-based assessment shall consider the following assets: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-04-07 |  | 2010-03-31 |  |  | CIP-002-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2460 | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  | CIP-006-2 R8. | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2464 | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | CIP-007-2 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2468 | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | CIP-007-2 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2472 | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | CIP-007-2 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2475 | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | CIP-007-2 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2479 | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 51200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 248 | Transmission substations that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2481 | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | CIP-007-2 R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2483 | The Responsible Entity shall identify those individuals with access to shared accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 52200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2487 | Each password shall consist of a combination of alpha, numeric, and “special” characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 53200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2491 | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | CIP-007-2 R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2497 | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | CIP-007-2 R7. | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2501 | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | CIP-007-2 R8. | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2507 | Response actions, including roles and responsibilities of Cyber Security Incident response teams, Cyber Security Incident handling procedures, and communication plans. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-008-2 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2515 | Define the roles and responsibilities of responders. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-009-2 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2525 | Operate the electric system to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  | NUC-001-2 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2534 | Names of the responsible entities, organizational relationships, and responsibilities related to the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2014-01-21 |  |  |  | 91200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2537 | Technical requirements and analysis: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  | NUC-001-2 R9. | 92000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2539 | Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 92200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2543 | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 93200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2551 | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 94200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2558 | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  | EOP-001-2 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2562 | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  | EOP-001-2 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2569 | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  | EOP-001-2 R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 257 | The Cyber Asset uses a routable protocol within a control center; or, |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-002-1 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2574 | A description of how all Agreements or mutually agreed upon procedures or protocols for off-site power requirements of nuclear power plants, including priority of restoration, will be fulfilled during System restoration. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | EOP-005-2 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2584 | Restoration priorities. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | EOP-005-2 R10. | 102000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2594 | Each Generator Operator shall provide the blackstart test results within 30 calendar days following a request from its Reliability Coordinator or Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-05-23 |  | 2019-03-31 |  |  | EOP-005-2 R16. | 162000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2597 | The procedures documented in Requirement R14. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-05-23 |  | 2019-03-31 |  |  | EOP-005-2 R17. | 172000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2607 | The location and magnitude of Loads required to control voltages and frequency within acceptable operating limits. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | EOP-005-2 R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2613 | A list of required tests including: |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | EOP-005-2 R9. | 92000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2615 | The ability to energize a bus. If it is not possible to energize a bus during the test, the testing entity must affirm that the unit has the capability to energize a bus such as verifying that the breaker close coil relay can be energized with the voltage and frequency monitor controls disconnected from the synchronizing circuits. |  | TOP | [18 empty] | TOP |  |  |  | 2013-07-01 |  | 2019-03-31 |  |  |  | 92200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2619 | Operating Processes for restoring the Interconnection. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  | EOP-006-2 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 262 | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-003-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2640 | Reestablishing the Interconnection. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  | EOP-006-2 R9. | 92000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2652 | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | CIP-007-2a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2653 | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | CIP-007-2a R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2657 | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | CIP-007-2a R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2658 | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | CIP-007-2a R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 266 | Changes to the senior manager must be documented within thirty calendar days of the effective date. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-003-1 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2660 | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | CIP-007-2a R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2663 | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 51200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2668 | The Responsible Entity shall identify those individuals with access to shared accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 52200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2671 | Each password shall consist of a combination of alpha, numeric, and “special” characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 53200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2674 | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | CIP-007-2a R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2677 | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | CIP-007-2a R7. | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2680 | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | CIP-007-2a R8. | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2691 | State that SOLs shall not exceed associated Facility Ratings. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | FAC-010-2.1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2693 | Following the single Contingencies identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | FAC-010-2.1 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2699 | Loss of any generator, line, transformer, or shunt device without a Fault. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 22200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 270 | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures, or a statement accepting risk. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-003-1 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2701 | System reconfiguration through manual or automatic control or protection actions. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 23200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2709 | Selection of applicable Contingencies. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | FAC-010-2.1 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2710 | Each Reliability Coordinator and Transmission Operator that operates any portion of the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | FAC-010-2.1 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2715 | The risk-based assessment shall consider the following assets: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. | CIP-002-3 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2717 | Transmission substations that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2726 | The Cyber Asset uses a routable protocol within a control center; or, |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. | CIP-002-3 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2731 | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | CIP-003-3 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2735 | Changes to the senior manager must be documented within thirty calendar days of the effective date. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | CIP-003-3 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 274 | The Responsible Entity shall classify information to be protected under this program based on the sensitivity of the Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-003-1 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2740 | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | CIP-003-3 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2744 | The Responsible Entity shall classify information to be protected under this program based on the sensitivity of the Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | CIP-003-3 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2749 | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  |  |  | 51200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2750 | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | CIP-003-3 R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2756 | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-3, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2012-12-11 |  |  | CIP-004-3 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2758 | Physical and electronic access controls to Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2012-12-11 |  |  |  | 22200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2764 | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2012-12-11 |  |  | CIP-004-3 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2768 | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2012-12-11 |  |  | CIP-004-3 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2771 | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | CIP-005-3 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2778 | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | CIP-005-3 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2783 | The authentication methods. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2011-02-01 |  |  |  | 25200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2789 | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | CIP-005-3 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 279 | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 51200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2792 | A review to verify that only ports and services required for operations at these access points are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | CIP-005-3 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2798 | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | CIP-005-3 R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 280 | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-003-1 R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2802 | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  | CIP-006-3 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2808 | Continuous escorted access of visitors within the Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-09-30 |  |  |  | 16200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2813 | Be afforded the protective measures specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirements R4 and R5; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  | CIP-006-3 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2821 | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  | CIP-006-3 R8. | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2825 | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-007-3a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2829 | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-007-3a R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2833 | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-007-3a R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2836 | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-007-3a R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2840 | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 51200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2842 | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-007-3a R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2844 | The Responsible Entity shall identify those individuals with access to shared accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 52200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2848 | Each password shall consist of a combination of alpha, numeric, and “special” characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 53200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2852 | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-007-3a R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2858 | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-007-3a R7. | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 286 | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-04-07 |  | 2010-03-31 |  |  | CIP-004-1 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2862 | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-007-3a R8. | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2868 | Response actions, including roles and responsibilities of Cyber Security Incident response teams, Cyber Security Incident handling procedures, and communication plans. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | CIP-008-3 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2876 | Define the roles and responsibilities of responders. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | CIP-009-3 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 288 | Physical and electronic access controls to Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 22200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2894 | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  | CIP-006-2b R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2897 | Be afforded the protective measures specified in Standard CIP-003-2; Standard CIP-004-2 Requirement R3; Standard CIP-005-2 Requirements R2 and R3; Standard CIP-006-2 Requirements R4 and R5; Standard CIP-007-2; Standard CIP-008-2; and Standard CIP-009-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  | CIP-006-2b R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2900 | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  | CIP-006-2b R8. | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2915 | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | CIP-006-2c R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2918 | Be afforded the protective measures specified in Standard CIP-003-2; Standard CIP-004-2 Requirement R3; Standard CIP-005-2 Requirements R2 and R3; Standard CIP-006-2 Requirements R4 and R5; Standard CIP-007-2; Standard CIP-008-2; and Standard CIP-009-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | CIP-006-2c R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2921 | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | CIP-006-2c R8. | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2935 | Processes to identify all access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1b R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2938 | Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1b R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 294 | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-004-1 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2943 | Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R2.3. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1b R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2944 | Video Recording: Electronic capture of video images of sufficient quality to determine identity. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1b R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2948 | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R6.1. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1b R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2956 | Video Recording: Electronic capture of video images of sufficient quality to determine identity. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | CIP-006-1c R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2961 | Processes to identify all access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | CIP-006-1c R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2970 | Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | CIP-006-1c R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2972 | Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R2.3. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | CIP-006-1c R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2975 | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R6.1. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | CIP-006-1c R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 298 | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-04-07 |  | 2010-03-31 |  |  | CIP-004-1 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2990 | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  | CIP-006-3c R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2994 | Continuous escorted access of visitors within the Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  |  | 16200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2996 | Be afforded the protective measures specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirements R4 and R5; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  | CIP-006-3c R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 2998 | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  | CIP-006-3c R8. | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 30 | The default Disturbance Recovery Period is 15 minutes after the start of a Reportable Disturbance. This period may be adjusted to better suit the needs of an Interconnection based on analysis approved by the NERC Operating Committee. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  | BAL-002-0 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3009 | Daily values for at least the next 31 calendar days. |  | TSP | [20 empty] | TSP | M2.2 -- There has been at least 31 consecutive calendar days of daily values calculated at all times. | 2010-09-16 |  |  |  |  | MOD-001-1a R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 301 | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | CIP-005-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3017 | A description of the manner in which the Transmission Service Provider will account for counterflows including: |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  |  |  |  | MOD-001-1a R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3018 | A rationale for that accounting specified in R3.2. |  | TSP | [20 empty] | TSP |  | 2011-04-01 | [5 empty] | 32200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3021 | The criteria used to determine when an outage that is in effect part of a month impacts a monthly calculation. |  | TSP | [20 empty] | TSP |  | 2011-04-01 | [5 empty] | 36200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3027 | Each Reliability Coordinator associated with the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  |  |  |  | MOD-001-1a R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3029 | Daily values, once per day. |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  |  |  |  | MOD-001-1a R8. | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3033 | This data shall be made available by the Transmission Provider on the schedule specified by the requestor (but no more frequently than once per hour, unless mutually agreed to by the requester and the provider). |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  |  |  |  | MOD-001-1a R9. | 92000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3035 | This data shall be made available by the Transmission Provider on theschedule specified by the requestor (but no more frequently than once perhour, unless mutually agreed to by the requester and the provider). |  | TSP | [20 empty] | TSP |  | 2011-04-01 | [5 empty] | 91300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3046 | Uses Facility Ratings as provided by the Transmission Owner and Generator Owner |  | TOP | [18 empty] | TOP |  |  | M1.2. The Transmission model produced must include the areas listed in R1.1.1 (or an equivalent representation, as described in the requirement) | 2010-09-16 |  | 2017-03-31 |  |  | MOD-029-1a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3052 | Models all system Elements as in-service for the assumed initial conditions. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3058 | All Transmission Operator areas contiguous with its own Transmission Operator area. (Equivalent representation is allowed.) |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 11120000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3066 | Where it is impossible to actually simulate a reliability-limited flow in a direction counter to prevailing flows (on an alternating current Transmission line), set the TTC for the non-prevailing direction equal to the TTC in the prevailing direction. If the TTC in the prevailing flow direction is dependant on a Special Protection System (SPS), set the TTC for the non-prevailing flow direction equal to the greater of the maximum flow that can be simulated in the non-prevailing flow direction or the maximum TTC that can be achieved in the prevailing flow direction without use of a SPS. |  | TOP | [18 empty] | TOP |  |  |  | 2010-09-16 |  | 2017-03-31 |  |  | MOD-029-1a R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3069 | When modeling contingencies the system shall demonstrate transient, dynamic and voltage stability, with no Transmission Element modeled above its Emergency Rating. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3074 | Mutually agreeable format. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2017-03-31 |  |  | IRO-010-1a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 308 | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-005-1 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 313 | The authentication methods. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 25200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3162 | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. | CIP-005-3a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3168 | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. | CIP-005-3a R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3172 | The authentication methods. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. |  | 25200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3173 | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. | CIP-005-3a R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3175 | A review to verify that only ports and services required for operations at these access points are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. | CIP-005-3a R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3181 | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. | CIP-005-3a R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3187 | Its allocation among members. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  | BAL-002-1 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 319 | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | CIP-005-1 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3196 | The default Disturbance Recovery Period is 15 minutes after the start of a Reportable Disturbance. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  | BAL-002-1 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3199 | The Reserve Sharing Group reviews each member’s ACE in response to the activation of reserves. To be in compliance, a member’s ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  | BAL-002-1 R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3202 | The default Contingency Reserve Restoration Period is 90 minutes. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  | BAL-002-1 R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3209 | The hourly integrated megawatt-hour values of Net Actual Interchange. |  | BA | BA | [21 empty] | 2011-04-01 |  | 2018-12-31 |  |  |  | 41200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3210 | Each Balancing Authority shall use the agreed-to daily and monthly accounting data to compile its monthly accumulated Inadvertent Interchange for the On-Peak and Off-Peak hours of the month. |  | BA | BA | [21 empty] | 2011-04-01 |  | 2018-12-31 |  |  | BAL-006-2 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 322 | A review to verify that only ports and services required for operations at these access points are enabled; |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | CIP-005-1 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3220 | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-003-4 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3224 | Changes to the senior manager must be documented within thirty calendar days of the effective date. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-003-4 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3229 | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-003-4 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3233 | The Responsible Entity shall classify information to be protected under this program based on the sensitivity of the Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-003-4 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3238 | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 51200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3239 | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-003-4 R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3245 | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-4, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2012-12-11 |  |  | CIP-004-4 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3247 | Physical and electronic access controls to Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2012-12-11 |  |  |  | 22200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3253 | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2012-12-11 |  |  | CIP-004-4 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3257 | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2012-12-11 |  |  | CIP-004-4 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3260 | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-005-4a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3267 | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-005-4a R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3272 | The authentication methods. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 25200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3278 | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-005-4a R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 328 | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-005-1 R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3281 | A review to verify that only ports and services required for operations at these access points are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-005-4a R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3287 | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-005-4a R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3291 | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-006-4c R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3297 | Continuous escorted access of visitors within the Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 16200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 33 | The Reserve Sharing Group reviews each member’s ACE in response to the activation of reserves. To be in compliance, a member’s ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  | BAL-002-0 R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3302 | Be afforded the protective measures specified in Standard CIP-003-4; Standard CIP-004-4 Requirement R3; Standard CIP-005-4 Requirements R2 and R3; Standard CIP-006-4 Requirements R4 and R5; Standard CIP-007-4; Standard CIP-008-4; and Standard CIP-009-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-006-4c R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3310 | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-006-4c R8. | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3314 | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-007-4a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3318 | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-007-4a R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 332 | Processes to identify all access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-006-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3322 | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-007-4a R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3325 | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-007-4a R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3329 | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 51200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3331 | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-007-4a R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3333 | The Responsible Entity shall identify those individuals with access to shared accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 52200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3337 | Each password shall consist of a combination of alpha, numeric, and “special” characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 53200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3341 | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-007-4a R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3347 | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-007-4a R7. | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3351 | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-007-4a R8. | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3357 | Response actions, including roles and responsibilities of Cyber Security Incident response teams, Cyber Security Incident handling procedures, and communication plans. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-008-4 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3365 | Define the roles and responsibilities of responders. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-009-4 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3377 | Deploying all available operating reserve. |  | BA | BA | [21 empty] | 2011-01-10 |  | 2012-09-12 |  |  | EOP-002-3 R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3384 | Request the Reliability Coordinator to declare an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0 “Energy Emergency Alert Levels.” |  | BA | BA | [21 empty] | 2011-01-10 |  | 2012-09-12 |  |  | EOP-002-3 R7. | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3388 | The Reliability Coordinator shall submit the report to NERC for posting on the NERC Website, noting the expected total MW that may have its transmission service priority changed. |  | RC | [11 empty] | RC | [10 empty] | 2011-01-10 |  | 2012-09-12 |  |  | EOP-002-3 R9. | 92000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3409 | Ensurance of compliance with NERC Reliability Standards and applicable Regional, subregional, Power Pool, and individual system planning criteria and facility connection requirements. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [14 empty] | 2011-01-10 |  | 2015-12-31 |  |  | FAC-002-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 342 | Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-006-1 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3423 | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  | IRO-005-2a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3454 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | TPL-001-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3457 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  | M2. The Planning Authority and Transmission Planner shall have evidence it reported documentation of results of its reliability assessments and corrective plans per Reliability Standard TPL-002-0(i)b_R3. |  |  | 2012-07-06 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3469 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 347 | Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R2.3. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-006-1 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3471 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | TPL-001-1 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3475 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | TPL-002-0b R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3481 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3494 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3496 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | TPL-002-0b R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 350 | Video Recording: Electronic capture of video images of sufficient quality to determine identity. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-006-1 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3500 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | TPL-002-1b R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3506 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3519 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3521 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | TPL-002-1b R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3525 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | TPL-003-1a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3531 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3544 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3546 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | TPL-003-1a R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 355 | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R6.1. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-006-1 R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3550 | Be conducted for near-term (years one through five). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | TPL-004-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3553 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3569 | Energy profile. |  | BA | BA | [21 empty] | 2011-04-01 |  | 2014-09-30 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3570 | If a high voltage direct current (HVDC) tie is on the Scheduling Path, then the Sending Balancing Authorities and Receiving Balancing Authorities shall coordinate the Interchange Schedule with the Transmission Operator of the HVDC tie. |  | BA | BA | [21 empty] | 2011-04-01 |  | 2014-09-30 |  |  | INT-003-3 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 359 | Processes to identify all access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 36 | The default Contingency Reserve Restoration Period is 90 minutes. This period may be adjusted to better suit the reliability targets of the Interconnection based on analysis approved by the NERC Operating Committee. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  | BAL-002-0 R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3603 | For each generator that is on this exemption list, the Transmission Operator shall notify the associated Generator Owner. |  | TOP | [18 empty] | TOP |  |  |  | 2011-01-10 |  | 2013-12-31 |  |  | VAR-001-2 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3626 | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | CIP-005-1a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3632 | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | CIP-005-1a R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3636 | The authentication methods. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 25200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3637 | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | CIP-005-1a R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3639 | A review to verify that only ports and services required for operations at these access points are enabled; |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | CIP-005-1a R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3645 | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | CIP-005-1a R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3657 | For a dial-up accessible Critical Cyber Asset that uses a non-routable protocol, the Responsible Entity shall define an Electronic Security Perimeter for that single access point at the dial-up device. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | CIP-005-2a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3663 | At all access points to the Electronic Security Perimeter(s), the Responsible Entity shall enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter, and shall document, individually or by specified grouping, the configuration of those ports and services. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | CIP-005-2a R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3667 | The authentication methods. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 25200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3668 | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | CIP-005-2a R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3670 | A review to verify that only ports and services required for operations at these access points are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | CIP-005-2a R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3676 | The Responsible Entity shall update the documentation to reflect the modification of the network or controls within ninety calendar days of the change. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | CIP-005-2a R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 369 | Special Locks: These include, but are not limited to, locks with “restricted key” systems, magnetic locks that can be operated remotely, and “man-trap” systems. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1a R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3695 | Each Transmission Operator with transmission facilities operating in an Interconnection shall ensure that those transmission facilities are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP | [5 empty] | 2008-04-15 |  |  | BAL-005-0a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3699 | Balancing Authorities shall ensure the power flow and ACE signals that are utilized for calculating Balancing Authority performance or that are transmitted for Regulation Service are not filtered prior to transmission, except for the Anti-aliasing Filters of Tie Lines. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP | [5 empty] | 2008-04-15 |  |  | BAL-005-0a R12. | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3706 | Summary of maintenance and testing procedures. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2011-09-26 |  | 2012-03-13 |  |  | PRC-005-1a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3708 | Date each Protection System device was last tested/maintained. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2011-09-26 |  | 2012-03-13 |  |  | PRC-005-1a R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3719 | Each Balancing Authority shall report its Frequency Bias Setting, and method for determining that setting, to the NERC Operating Committee. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2009-06-28 |  |  | BAL-003-0.1a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3720 | The Balancing Authority may use a variable (linear or non-linear) bias value, which is based on a variable function of Tie Line deviation to Frequency Deviation. The Balancing Authority shall determine the variable frequency bias value by analyzing Frequency Response as it varies with factors such as load, generation, governor characteristics, and frequency. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2009-06-28 |  |  | BAL-003-0.1a R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3722 | The Balancing Authorities that have a fixed schedule (B and C) but do not contain the Jointly Owned Unit shall not include their share of the governor droop response in their Frequency Bias Setting. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2009-06-28 |  |  | BAL-003-0.1a R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 374 | Human Observation of Access Points: Monitoring of physical access points by authorized personnel as specified in Requirement R2.3. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1a R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 377 | Video Recording: Electronic capture of video images of sufficient quality to determine identity. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1a R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3786 | Automatic Voltage Regulator status and mode setting. (Retired August 1, 2007) |  | GOP | [5 empty] | GOP | [16 empty] | 2011-10-20 |  | 2012-09-12 |  |  | TOP-002-2b R14. | 142000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3788 | Changes in transmission facility rating. |  | TOP | [18 empty] | TOP |  |  |  | 2011-10-20 |  | 2012-09-12 |  |  | TOP-002-2b R16. | 162000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3808 | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  | IRO-005-3 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 382 | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R6.1. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1a R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3820 | For a transmission facility, the Transmission Operator shall notify and coordinate with its Reliability Coordinator. The Transmission Operator shall notify other affected Transmission Operators, and coordinate the impact of removing the Bulk Electric System facility. |  | TOP | [18 empty] | TOP |  |  |  | 2011-11-21 |  | 2017-03-31 |  |  | TOP-001-1a R7. | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3834 | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | EOP-001-0b R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3837 | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | EOP-001-0b R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3842 | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | EOP-001-0b R7. | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3851 | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | EOP-001-2b R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3854 | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | EOP-001-2b R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3859 | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | EOP-001-2b R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 386 | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-007-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 390 | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-007-1 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3903 | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | CIP-006-2a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3906 | Be afforded the protective measures specified in Standard CIP-003-2; Standard CIP-004-2 Requirement R3; Standard CIP-005-2 Requirements R2 and R3; Standard CIP-006-2 Requirements R4 and R5; Standard CIP-007-2; Standard CIP-008-2; and Standard CIP-009-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | CIP-006-2a R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3909 | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | CIP-006-2a R8. | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3924 | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  | CIP-006-3a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3928 | Continuous escorted access of visitors within the Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2011-05-18 |  |  |  | 16200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3930 | Be afforded the protective measures specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirements R4 and R5; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  | CIP-006-3a R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3932 | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  | CIP-006-3a R8. | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 394 | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure or an acceptance of risk. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-007-1 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3962 | A description of the manner in which the Transmission Operator will account for Interchange Schedules in the calculation of TTC. |  | TSP | [20 empty] | TSP |  | 2013-09-27 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | MOD-028-2 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3967 | Define if the sink used for ATC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation |  | TSP | [20 empty] | TSP |  | 2013-10-01 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 15200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 397 | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | CIP-007-1 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3974 | Modeling data and topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination areas. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | MOD-028-2 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3979 | A daily or hourly load forecast for TTCs used in current-day and next-day ATC calculations. |  | TOP | [18 empty] | TOP |  |  |  | 2013-10-01 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 31200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3985 | Respect any contractual allocations of TTC. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | MOD-028-2 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3989 | At least once per calendar month for TTCs used in monthly ATC calculations. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | MOD-028-2 R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3993 | If the limit in step R6.1 can not be reached by adjusting any combination of load or generation, then set the incremental Transfer Capability by the results of the case where the maximum adjustments were applied. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | MOD-028-2 R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 3998 | Seven calendar days after its determination for TTCs used in monthly ATC calculations. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | MOD-028-2 R7. | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 40 | An amount of reserve equal to the sum of three percent of the load (generation minus station service minus Net Actual Interchange) and three percent of net generation (generation minus station service). |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2010-11-26 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 401 | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 51200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 403 | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-007-1 R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4035 | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-006-3d R8. | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4044 | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-006-3d R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4046 | Be afforded the protective measures specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirements R4 and R5; Standard CIP-007-3; Standard CIP-008-3; and Standard CIP-009-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-006-3d R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4048 | Continuous escorted access of visitors within the Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 16200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 405 | The Responsible Entity shall identify those individuals with access to shared accounts. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 52200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4063 | Identification of all physical access points through each Physical Security Perimeter and measures to control entry at those access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-006-4d R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4067 | Continuous escorted access of visitors within the Physical Security Perimeter. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 16200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4069 | Be afforded the protective measures specified in Standard CIP-003-4; Standard CIP-004-4 Requirement R3; Standard CIP-005-4 Requirements R2 and R3; Standard CIP-006-4 Requirements R4 and R5; Standard CIP-007-4; Standard CIP-008-4; and Standard CIP-009-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-006-4d R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4071 | Retention of testing and maintenance records for the cycle determined by the Responsible Entity in Requirement R8.1. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-006-4d R8. | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4079 | Summary of maintenance and testing procedures. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2012-03-14 |  | 2013-11-24 |  |  | PRC-005-1b R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4081 | Date each Protection System device was last tested/maintained. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2012-03-14 |  | 2013-11-24 |  |  | PRC-005-1b R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4088 | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  | EOP-001-2.1b R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 409 | Each password shall consist of a combination of alpha, numeric, and “special” characters. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 53200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4094 | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  | EOP-001-2.1b R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4095 | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  | EOP-001-2.1b R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 41 | If the Source Balancing Authority designates an Interchange Transaction(s) as part of its Non-Spinning Contingency Reserve, the Sink Balancing Authority shall carry an amount of additional Non-Spinning Contingency Reserve equal to the Interchange Transaction(s). This type of transaction cannot be designated as Spinning Reserves by the source BA. If the Source Balancing Authority does not designate the Interchange Transaction as part of its Contingency Reserve, the Sink Balancing Authority is not required to carry any additional Contingency Reserves under this Requirement. |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2010-11-26 |  |  | BAL-002-WECC-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4116 | Each Transmission Operator with transmission facilities operating in an Interconnection shall ensure that those transmission facilities are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2012-09-13 |  | 2018-12-31 |  |  | BAL-005-0.2b R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4120 | Balancing Authorities shall ensure the power flow and ACE signals that are utilized for calculating Balancing Authority performance or that are transmitted for Regulation Service are not filtered prior to transmission, except for the Anti-aliasing Filters of Tie Lines. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2012-09-13 |  | 2018-12-31 |  |  | BAL-005-0.2b R12. | 122000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 413 | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | CIP-007-1 R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4135 | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  | EOP-001-0.1b R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4139 | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  | EOP-001-0.1b R7. | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4143 | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  | EOP-001-0.1b R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4164 | Changes in transmission facility rating. |  | TOP | [18 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  | TOP-002-2.1b R16. | 162000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4184 | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  | IRO-005-3.1a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 419 | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-007-1 R7. | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4202 | Deploying all available operating reserve. |  | BA | BA | [21 empty] | 2012-09-13 |  | 2017-03-31 |  |  | EOP-002-3.1 R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4203 | Request the Reliability Coordinator to declare an Energy Emergency Alert in accordance with Attachment 1-EOP-002 “Energy Emergency Alerts.” |  | BA | BA | [21 empty] | 2012-09-13 |  | 2017-03-31 |  |  | EOP-002-3.1 R7. | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4206 | The Reliability Coordinator shall submit the report to NERC for posting on the NERC Website, noting the expected total MW that may have its transmission service priority changed. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  | EOP-002-3.1 R9. | 92000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4220 | Operate the electric system to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP | M4.2 The electric system was operated to meet the NPIRs. (Requirement 4.2) | 2013-04-01 |  | 2015-12-31 |  |  |  | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4223 | Technical requirements and analysis: |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 92000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4228 | Names of the responsible entities, organizational relationships, and responsibilities related to the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2014-01-21 |  |  |  | 91200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4229 | Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 92200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 423 | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | CIP-007-1 R8. | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4235 | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 93200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4240 | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 94200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4255 | Operate the electric system to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  | NUC-001-2.1 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4258 | Technical requirements and analysis: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  | NUC-001-2.1 R9. | 92000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4286 | If a protective relay or equipment failure reduces system reliability, the Transmission Operator shall notify its Reliability Coordinator and affected Transmission Operators and Balancing Authorities. The Transmission Operator shall take corrective action as soon as possible. |  | TOP | [18 empty] | TOP |  |  |  | 2013-04-01 |  | 2015-05-28 |  |  | PRC-001-1.1 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4287 | Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities. |  | TOP | [18 empty] | TOP |  |  |  | 2013-04-01 |  | 2015-05-28 |  |  | PRC-001-1.1 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4289 | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ Protection Systems. |  | TOP | [18 empty] | TOP |  |  |  | 2013-04-01 |  | 2015-05-28 |  |  | PRC-001-1.1 R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 429 | Response actions, including roles and responsibilities of incident response teams, incident handling procedures, and communication plans. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-008-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4294 | Summary of maintenance and testing procedures. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2013-11-25 |  | 2027-03-31 |  |  | PRC-005-1.1b R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4296 | Date each Protection System device was last tested/maintained. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2013-11-25 |  | 2027-03-31 |  |  | PRC-005-1.1b R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4320 | For each generator that is on this exemption list, the Transmission Operator shall notify the associated Generator Owner. |  | TOP | [18 empty] | TOP |  |  |  | 2013-06-20 |  | 2014-09-30 |  |  | VAR-001-3 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4336 | The risk-based assessment shall consider the following assets: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-002-3a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4341 | Transmission substations that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4347 | The Cyber Asset uses a routable protocol within a control center; or, |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-002-3a R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4361 | Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities. |  | TOP | [18 empty] | TOP | [5 empty] | 2016-01-26 |  |  | PRC-001-2 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4367 | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-3, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-004-3 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 437 | Define the roles and responsibilities of responders. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-009-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4370 | Physical and electronic access controls to Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 22200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4374 | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-004-3 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4378 | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-004-3 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4383 | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-4, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2014-02-03 |  |  | CIP-004-4 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4386 | Physical and electronic access controls to Critical Cyber Assets; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 22200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4390 | The Responsible Entity shall update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2014-02-03 |  |  | CIP-004-4 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4394 | The Responsible Entity shall revoke such access to Critical Cyber Assets within 24 hours for personnel terminated for cause and within seven calendar days for personnel who no longer require such access to Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2014-02-03 |  |  | CIP-004-4 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4401 | When directed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2013-07-01 |  | 2014-09-30 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4404 | A status or capability change on any other Reactive Power resources under the Generator Operator’s control and the expected duration of the change in status or capability. |  | GOP | [5 empty] | GOP | [16 empty] | 2013-07-01 |  | 2014-09-30 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4408 | Available fixed tap ranges. |  | GO | [22 empty] | 2013-07-01 |  | 2014-09-30 |  |  |  | 41200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 444 | Between the Reliability Coordinator and its Transmission Operators and Balancing Authorities. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-05-12 |  |  | COM-001-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4448 | Its allocation among members. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  | BAL-002-1a R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4451 | The default Disturbance Recovery Period is 15 minutes after the start of a Reportable Disturbance. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  | BAL-002-1a R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4454 | The Reserve Sharing Group reviews each member’s ACE in response to the activation of reserves. To be in compliance, a member’s ACE (or its equivalent) must meet the Disturbance Recovery Criterion after the schedule change(s) related to reserve sharing have been fully implemented, and within the Disturbance Recovery Period. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  | BAL-002-1a R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4456 | The default Contingency Reserve Restoration Period is 90 minutes. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  | BAL-002-1a R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4464 | Each Transmission Operator shall inform the Reliability Coordinator and other affected Transmission Operators of all transmission resources available for use. |  | TOP | [18 empty] | TOP | [5 empty] | 2015-03-18 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 45 | Capable of fully responding within ten minutes. |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2010-11-26 |  |  | BAL-002-WECC-1 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 454 | Between the Reliability Coordinator and its Transmission Operators and Balancing Authorities. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2009-05-13 |  | 2015-09-30 |  |  | COM-001-1.1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4558 | The Cyber Asset uses a routable protocol within a control center; or, |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-002-3a R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4561 | The risk-based assessment shall consider the following assets: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-002-3a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4568 | Transmission substations that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4583 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | TPL-001-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4591 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4597 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | TPL-001-1 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4599 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4626 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | TPL-002-0b R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4631 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4643 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | TPL-002-0b R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4645 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4651 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | TPL-003-0a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4656 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4668 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | TPL-003-0a R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4670 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4675 | Be conducted for near-term (years one through five). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | TPL-004-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4682 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 469 | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  | EOP-001-0 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4691 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | TPL-003-0a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4696 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4708 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | TPL-003-0a R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4710 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4716 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | TPL-003-0a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4721 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | TPL-003-0a R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4729 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4734 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 474 | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  | EOP-001-0 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4740 | Be conducted for near-term (years one through five). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | TPL-004-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4747 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4757 | Be conducted for near-term (years one through five). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | TPL-004-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4762 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 48 | Interruptible Load; |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2010-11-26 |  |  | BAL-002-WECC-1 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4800 | The hourly integrated megawatt-hour values of Net Actual Interchange. |  | BA | BA | [23 empty] | 2006-05-01 |  |  |  | 41200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4801 | Each Balancing Authority shall use the agreed-to daily and monthly accounting data tocompile its monthly accumulated Inadvertent Interchange for the On-Peak and OffPeak hours of the month. |  | BA | BA | [23 empty] | 2006-05-01 |  |  |  | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 481 | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  | EOP-001-0 R7. | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4810 | Between the Reliability Coordinator and its Transmission Operators and BalancingAuthorities. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4821 | The Transmission Operator recognizes that potential or actual line loadings, andvoltage or reactive levels are such that a single Contingency could threaten thereliability of the Interconnection. (Once a single Contingency occurs, theTransmission Operator must prepare for the next Contingency.) |  | TOP | [18 empty] | TOP | [5 empty] | 2006-11-01 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4830 | The Reliability Coordinator shall submit the report to NERC for posting on the NERCWebsite, noting the expected total MW that may have its transmission service prioritychanged. |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 102000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4839 | Deploying all available operating reserve. |  | BA | BA | [23 empty] | 2006-11-01 |  |  |  | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4846 | Request the Reliability Coordinator to declare an Energy Emergency Alert inaccordance with Attachment 1-EOP-002-0 “Energy Emergency Alert Levels.” |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4856 | Deploying all available operating reserve. |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4863 | Request the Reliability Coordinator to declare an Energy Emergency Alert inaccordance with Attachment 1-EOP-002-0 “Energy Emergency Alert Levels.” |  | BA, RC | BA | [10 empty] | RC | [12 empty] | 2007-01-01 |  |  |  | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4867 | The Reliability Coordinator shall submit the report to NERC for posting on the NERCWebsite, noting the expected total MW that may have its transmission service prioritychanged. |  | RC | [11 empty] | RC | [12 empty] | 2007-01-01 |  |  |  | 92000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 487 | Develop, maintain, and implement a set of plans to mitigate operating emergencies on the transmission system. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  | EOP-001-1 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4888 | The affected Transmission Operators and Balancing Authorities shall take the necessary actions to restore Bulk Electric System frequency to normal, including adjusting generation, placing additional generators online, or load shedding. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2007-05-02 |  |  |  | 92000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4893 | The size of the area being reconnected and the capacity of the transmission lines effecting the reconnection and the number of synchronizing points across the system are considered. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-05-02 |  |  |  | 95200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4904 | Trimming clearances. |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-04-07 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4910 | Transformers. |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-08-01 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4916 | The Rating of a facility shall not exceed the Rating(s) of the most Limiting Element(s)in the circuit, including terminal connections and associated equipment. |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-08-01 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 492 | A list of controlling actions to resolve the emergency. Load reduction, in sufficient quantity to resolve the emergency within NERC-established timelines, shall be one of the controlling actions. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  | EOP-001-1 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4926 | All transfers that are entirely within a Balancing Authority Area using Point-to-Point Transmission Service (including all grandfathered and “non-Order 888” Point-to-Point Transmission Service). |  | BA, PSE | BA | [9 empty] | PSE | [13 empty] | 2007-01-01 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4930 | To replace unexpected generation loss, such as through prearranged reserve sharing agreements or other arrangements. If the duration of the Emergency Transaction to replace the generation loss is less than 60 minutes, then the Transaction shall be exempt from Tagging. |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4939 | For each bilateral Inadvertent Interchange payback. |  | BA | BA | [23 empty] | 2006-11-01 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4942 | Intermediate Balancing Authorities on the Schedule Path. |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4948 | Transmission priority matches reservation |  | TSP | [20 empty] | TSP |  |  |  | 2007-01-01 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4955 | Energy profile (ability to support the magnitude of the transaction). |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4963 | Energy profile. |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4965 | If a high voltage direct current (HVDC) tie is on the Scheduling Path, then the Sending Balancing Authorities and Receiving Balancing Authorities shall coordinate the Interchange Schedule with the Transmission Operator of the HVDC tie. |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4973 | The established network Total Transfer Capability between Balancing Authorities, which considers other transmission facilities available to them under specific arrangements, and the overall physical constraints of the transmission network. |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4977 | Energy profile. |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4978 | If a high voltage direct current (HVDC) tie is on the Scheduling Path, then the Sending Balancing Authorities and Receiving Balancing Authorities shall coordinate the Interchange Schedule with the Transmission Operator of the HVDC tie. |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4981 | Interconnection, regional, or local overload relief or congestion management procedures. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4987 | When a loss of Load necessitates curtailing Interchange Transactions, the Sink Balancing Authority shall coordinate the modifications to the appropriate tags. |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 499 | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  | EOP-001-1 R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 4992 | The average energy profile in an hour is less than or equal to 250 MW and in that hour the actual hourly integrated energy deviates from the hourly average energy profile indicated on the tag by more than +25 megawatt-hours. |  | PSE | [10 empty] | PSE | [13 empty] | 2007-01-01 |  |  |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5028 | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5055 | The equivalent Interconnection-wide transmission loading relief procedure for use inthe Western Interconnection is the “WSCC Unscheduled Flow Mitigation Plan,”provided at:http://www.wecc.biz/documents/library/UFAS/UFAS_mitigation_plan_rev_2001-clean_8-8-03.pdf. |  | RC | [11 empty] | RC | [12 empty] | 2005-08-08 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5064 | The equivalent Interconnection-wide transmission loading relief procedure for use inthe Western Interconnection is the “WSCC Unscheduled Flow Mitigation Plan,”provided at:http://www.wecc.biz/documents/library/UFAS/UFAS_mitigation_plan_rev_2001-clean_8-8-03.pdf. |  | RC | [11 empty] | RC | [12 empty] | 2006-09-29 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5073 | The equivalent Interconnection-wide transmission loading relief procedure foruse in the Western Interconnection is the “WSCC Unscheduled Flow MitigationPlan,” provided at:http://www.wecc.biz/documents/library/UFAS/UFAS_mitigation_plan_rev_2001-clean_8-8-03.pdf. |  | RC | [11 empty] | RC | [12 empty] | 2006-09-29 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5082 | The Interconnection-wide requirements shall specify unit size thresholds for permitting: − The use of non-detailed vs. detailed models, − The netting of small generating units with bus load, and − The combining of multiple generating units at one plant. |  | RRO | [14 empty] | RRO | [9 empty] | 2006-11-02 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5083 | Device specific dynamics data shall be reported for dynamic devices, including, among others, static VAR controllers, high voltage direct current systems, flexible AC transmission systems, and static compensators. |  | RRO | [14 empty] | RRO | [9 empty] | 2006-11-02 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 509 | Deploying all available operating reserve. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  | EOP-002-2 R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5098 | If a protective relay or equipment failure reduces system reliability, the Transmission Operator shall notify its Reliability Coordinator and affected Transmission Operators and Balancing Authorities. The Transmission Operator shall take corrective action as soon as possible. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5101 | Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5105 | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ protection systems. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5109 | Equipment characteristics including but not limited to: |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5111 | Time synchronization requirements. |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5116 | Current. |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5123 | Transmission lines. |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 16200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5130 | Description of the data reporting requirements (periodicity and format) for those misoperations that adversely affects the reliability of the Bulk Electric Systems as specified by the Regional Reliability Organization. |  | RRO | [14 empty] | RRO | [9 empty] | 2006-05-01 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5140 | Instrument transformers. |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2006-05-01 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5143 | Documentation of maintenance and testing intervals and their basis. |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2006-05-01 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 516 | Request the Reliability Coordinator to declare an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0 “Energy Emergency Alert Levels.” |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  | EOP-002-2 R7. | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5162 | Automatic Voltage Regulator status and mode setting. |  | GOP | [5 empty] | GOP | [18 empty] | 2007-08-07 |  |  |  | 142000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5166 | Changes in transmission facility rating. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-08-07 |  |  |  | 162000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5188 | Changes in transmission facility rating. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 162000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 520 | The Reliability Coordinator shall submit the report to NERC for posting on the NERC Website, noting the expected total MW that may have its transmission service priority changed. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-05-12 |  |  | EOP-002-2 R9. | 92000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5207 | Monitoring and controlling voltage levels and real and reactive power flows. |  | TOP | [18 empty] | TOP | [5 empty] | 2005-04-01 |  |  |  | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5220 | Each Transmission Operator and Balancing Authority shall inform the Reliability Coordinator and other affected Balancing Authorities and Transmission Operators of all generation and transmission resources available for use. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5271 | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | CIP-003-3 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5276 | Changes to the senior manager must be documented within thirty calendar days of the effective date. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | CIP-003-3 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5279 | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | CIP-003-3 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5281 | The Responsible Entity shall classify information to be protected under this program based on the sensitivity of the Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | CIP-003-3 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5285 | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | CIP-003-3 R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5287 | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | 51200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5295 | The cyber security policy is readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-003-4 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 530 | Deploying all available operating reserve. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-09-30 |  |  | EOP-002-2.1 R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5300 | Changes to the senior manager must be documented within thirty calendar days of the effective date. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-003-4 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5303 | Documented exceptions to the cyber security policy must include an explanation as to why the exception is necessary and any compensating measures. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-003-4 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5305 | The Responsible Entity shall classify information to be protected under this program based on the sensitivity of the Critical Cyber Asset information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-003-4 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5309 | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-003-4 R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5311 | The list of personnel responsible for authorizing access to protected information shall be verified at least annually. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 51200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5323 | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-007-3a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5324 | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-007-3a R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5328 | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-007-3a R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5329 | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-007-3a R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5331 | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-007-3a R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5334 | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 51200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5339 | The Responsible Entity shall identify those individuals with access to shared accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 52200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5342 | Each password shall consist of a combination of alpha, numeric, and “special” characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 53200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5345 | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-007-3a R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5348 | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-007-3a R7. | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5351 | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-007-3a R8. | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5366 | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-007-4a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5367 | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-007-4a R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 537 | Request the Reliability Coordinator to declare an Energy Emergency Alert in accordance with Attachment 1-EOP-002-0 “Energy Emergency Alert Levels.” |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-09-30 |  |  | EOP-002-2.1 R7. | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5371 | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-007-4a R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5372 | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-007-4a R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5374 | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-007-4a R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5377 | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 51200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5382 | The Responsible Entity shall identify those individuals with access to shared accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 52200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5385 | Each password shall consist of a combination of alpha, numeric, and “special” characters. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 53200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5388 | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-007-4a R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5391 | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-007-4a R7. | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5394 | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-007-4a R8. | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 541 | The Reliability Coordinator shall submit the report to NERC for posting on the NERC Website, noting the expected total MW that may have its transmission service priority changed. |  | RC | [11 empty] | RC | [10 empty] | 2009-05-13 |  | 2011-09-30 |  |  | EOP-002-2.1 R9. | 92000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 55 | Each Balancing Authority shall report its Frequency Bias Setting, and method for determining that setting, to the NERC Operating Committee. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  | BAL-003-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 556 | Applicable reporting forms are provided in Attachments 1-EOP-004 and 2-EOP-004. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-12-31 |  |  | EOP-004-1 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5600 | State that SOLs shall not exceed associated Facility Ratings. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5603 | Following the single Contingencies1 identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5619 | Selection of applicable Contingencies |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5626 | Each Reliability Coordinator and Transmission Operator that operates any portion of the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5631 | State that SOLs shall not exceed associated Facility Ratings. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5634 | Following the single Contingencies1 identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5647 | Selection of applicable Contingencies |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5657 | Each Planning Authority and Transmission Planner that models any portion of the Reliability Coordinator’s Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 566 | The affected Transmission Operators and Balancing Authorities shall take the necessary actions to restore Bulk Electric System frequency to normal, including adjusting generation, placing additional generators on line, or load shedding. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | EOP-005-1 R11. | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5662 | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5684 | The following information on how source and sink for transmission service is accounted for in AFC calculations including: |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5686 | Define if the sink used for AFC calculations is obtained from the sink field or the Point of Delivery (POD) field of the transmission reservation. |  | TSP | [20 empty] | TSP |  | 2017-04-01 | [5 empty] | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5693 | Only the most limiting element in a series configuration needs to be included as a Flowgate. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 21120000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5695 | Results of a first Contingency transfer analysis from all adjacent Balancing Authority source and sink (as defined in the ATCID) combinations up to the path capability such that at a minimum the first three limiting Elements and their worst associated Contingency combinations with an Outage Transfer Distribution Factor (OTDF) of at least 5% and within the Transmission Operator’s system are included as Flowgates unless the interface between such adjacent Balancing Authorities is accounted for using another ATC methodology. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5697 | Only the most limiting element in a series configuration needs to be included as a Flowgate. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 21220000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5703 | The limiting Element/Contingency combination is included in the requesting Transmission Service Provider’s methodology. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 21420000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5704 | At a minimum, establish a list of Flowgates by creating, modifying, or deleting Flowgate definitions at least once per calendar year. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 571 | The size of the area being reconnected and the capacity of the transmission lines effecting the reconnection and the number of synchronizing points across the system are considered. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  |  | 115200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5712 | Updated at least once per day for AFC calculations for intra-day, next day, and days two through 30. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5719 | Include in the transmission model expected generation and Transmission outages, additions, and retirements within the scope of the model as specified in the ATCID and in effect during the applicable period of the AFC calculation for the Transmission Service Provider’s area, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5724 | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. |  | TSP | [20 empty] | TSP |  | 2017-04-01 | [5 empty] | 61200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5725 | The impact of any firm Network Integration Transmission Service, including the impacts of generation to load in the model referenced in R5.2 and has a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed based on: (Footnote:A percentage less than that used in the Interconnection-wide congestion management procedure may be utilized.) |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5727 | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. |  | TSP | [20 empty] | TSP |  | 2017-04-01 | [5 empty] | 62200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5735 | The impact of any confirmed non-firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5745 | For daily AFC, once per day. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 102000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5752 | The risk-based assessment shall consider the following assets: |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5754 | Transmission substations that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5761 | The Cyber Asset uses a routable protocol within a control center; or, |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5764 | The risk-based assessment shall consider the following assets: |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5766 | Transmission substations that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5773 | The Cyber Asset uses a routable protocol within a control center; or, |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5781 | Operate the electric system to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  |  | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5790 | Names of the responsible entities, organizational relationships, and responsibilities related to the NPIRs. (Retirement approved by FERC effective January 21, 2014.) | [26 empty] | 2014-11-13 |  |  |  | 91200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5793 | Technical requirements and analysis: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  |  | 92000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5795 | Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 92200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5799 | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 93200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 58 | The Balancing Authority may use a variable (linear or non-linear) bias value, which is based on a variable function of Tie Line deviation to Frequency Deviation. The Balancing Authority shall determine the variable frequency bias value by analyzing Frequency Response as it varies with factors such as load, generation, governor characteristics, and frequency. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  | BAL-003-0 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5807 | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 94200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5813 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5816 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5828 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5830 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5834 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5837 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5853 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5855 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5859 | Be conducted for near-term (years one through five) and longer-term (years six through ten) planning horizons. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5862 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5878 | Including a discussion of expected required in-service dates of facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5880 | Review, in subsequent annual assessments, (where sufficient lead time exists), the continuing need for identified system facilities. Detailed implementation plans are not needed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5884 | Be conducted for near-term (years one through five). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5887 | Cover critical system conditions and study years as deemed appropriate by the responsible entity. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5899 | Requirements to provide data that describes design, operation, and modeling of a RAS. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 590 | A requirement to demonstrate that blackstart units perform their intended functions as required in the Regional SRP. This requirement can be met through either simulation or testing. The BCP must consider the availability of designated BCP units and initial transmission switching requirements. |  | RRO | [14 empty] | RRO | [7 empty] | 2011-05-23 |  | 2011-05-23 |  |  | EOP-007-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5918 | Study years, system conditions, and contingencies analyzed in the technical studies on which the assessment is based and when those technical studies were performed. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5924 | Operation — The actions taken by the RAS in response to Disturbance conditions, and |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 593 | Type of test required, including the requirement to start when isolated from the system. |  | RRO | [14 empty] | RRO | [9 empty] | 2011-05-23 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5936 | Instrument transformers. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-04-01 |  | 2027-03-31 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5939 | Documentation of maintenance and testing intervals and their basis. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-01-25 |  | 2027-03-31 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5948 | Size and location of customer load, or percent of connected load, to be interrupted. | [26 empty] | 2014-11-13 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5956 | Corresponding voltage set points and overall scheme clearing times. | [26 empty] | 2014-11-13 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5964 | If a protective relay or equipment failure reduces system reliability, the Generator Operator shall notify its Transmission Operator and Host Balancing Authority. The Generator Operator shall take corrective action as soon as possible. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 |  | 2015-05-28 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5967 | Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 |  | 2015-05-28 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5971 | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ Protection Systems. |  | TO | [22 empty] | 2017-04-01 |  | 2015-05-28 |  |  |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5976 | If the Protection System or RAS has a Security-Based Misoperation and only one FEPS or FERAS remains in service to ensure BES reliability, the Transmission Owner or Generator Owner shall perform the following.R2.2.1. Following identification of the Protection System or RAS Misoperation, Transmission Owners and Generator Owners shall remove from service within 22 hours for repair or modification the Protection System or RAS that misoperated.R2.2.2. The Transmission Owner or Generator Owner shall repair or replace any Protection System or RAS that misoperated with a FEPS or FERAS within 20 business days of the date of removal. The Transmission Owner or Generator Owner shall remove the Element from service or disable the RAS if repair or replacement is not completed within 20 business days. |  | GO, TO |  |  |  |  | GO | [16 empty] | M2.2 Transmission Owners and Generation Owners shall have evidence that they removed from service and repaired the Protection System or RAS that misoperated per measurements M2.2.1 through M2.2.2.M2.2.1 Transmission Owners and Generation Owners shall have evidence that they removed the Protection System or RAS that misoperated from service within 22 hours following identification of the Protection System or RAS Misoperation.M2.2.2 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated within 20 business days or either removed the Element from service or disabled the RAS. | 2017-04-01 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf..4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. |  | 22000000 | WECC-US | [5 empty] | WECC-US
2. | 5985 | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ Protection Systems. |  | TO | [22 empty] | 2016-01-25 |  | 2015-05-28 |  |  |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5987 | System Protection personnel shall analyze all operations of Protection Systems and RAS within 20 business days for correctness to characterize whether a Misoperation has occurred that may not have been identified by System Operators. |  | GO, TO |  |  |  |  | GO | [16 empty] | M1.2 Transmission Owners and Generation Owners shall have evidence that System Protection personnel analyzed all operations of Protection System and RAS for correctness within 20 business days. | 2016-01-25 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf..4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. |  | 12000000 | WECC-US | [5 empty] | WECC-US
2. | 5988 | If the Protection System or RAS has a Security-Based Misoperation and only one FEPS or FERAS remains in service to ensure BES reliability, the Transmission Owner or Generator Owner shall perform the following. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-01-25 |  | 2021-01-01 |  |  |  | 22000000 | WECC-US | [5 empty] | WECC-US
2. | 599 | The plan shall include procedures and responsibilities for providing basic tie line control and procedures and for maintaining the status of all inter-area schedules, such that there is an hourly accounting of all schedules. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | EOP-008-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 5993 | When FERAS is not available, then | [23 empty] | M2.3.2 The Generator Owners and Transmission Operators shall have documentation describing all actions taken that adjusted generation or SOLs and operated facilities within established limits. | 2017-04-01 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf..4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. |  | 23200000 | WECC-US | [5 empty] | WECC-US
2. | 5996 | Transmission Owners or Generator Owners shall remove from service the associated Element or RAS. |  | GO, TO |  |  |  |  | GO | [16 empty] | M2.4.2 Transmission Owners and Generation Owners shall have evidence that they removed the associated Element or RAS from service. | 2017-04-01 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf..4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. |  | 24200000 | WECC-US | [5 empty] | WECC-US
2. | 5999 | Completion of repairs or the replacement of Protection System and/or RAS that misoperated. | [23 empty] | M3.2 Completion of repair or replacement of Protection System and/or RAS that misoperated. | 2017-04-01 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf..4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. |  | 32000000 | WECC-US | [5 empty] | WECC-US
2. | 6026 | All Transmission Operator areas contiguous with its own Transmission Operator area. (Equivalent representation is allowed.) |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 11120000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6028 | Models all system Elements as in-service for the assumed initial conditions. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6041 | Uses Facility Ratings as provided by the Transmission Owner and Generator Owner |  | TOP | [18 empty] | TOP |  |  | M1.2. The Transmission model produced must include the areas listed in R1.1.1 (or an equivalent representation, as described in the requirement) (R1.1)M1.3. The Transmission model produced must show the use of the modeling parameters stated in R1.1.2 through R1.1.10; except that, no evidence shall be required to prove: 1) utilization of a Remedial Action Scheme where none was included in the model or 2) that no additions or retirements to the generation or Transmission system occurred. (R1.1.2 through R1.1.10)M1.4. The Transmission Operator must provide evidence that the models used to determine TTC included Facility Ratings as provided by the Transmission Owner and Generator Owner. (R1.2) | 2016-01-25 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 610 | Transmission facilities, and |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  | FAC-001-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6116 | If a protective relay or equipment failure reduces system reliability, the Transmission Operator shall notify its Reliability Coordinator and affected Transmission Operators and Balancing Authorities. The Transmission Operator shall take corrective action as soon as possible. |  | TOP | [18 empty] | TOP |  |  |  | 2015-05-29 |  | 2020-09-30 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6119 | Each Transmission Operator shall coordinate all new protective systems and all protective system changes with neighboring Transmission Operators and Balancing Authorities. |  | TOP | [18 empty] | TOP |  |  |  | 2015-05-29 |  | 2020-09-30 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6123 | Each Transmission Operator shall notify neighboring Transmission Operators in advance of changes in generation, transmission, load, or operating conditions that could require changes in the other Transmission Operators’ Protection Systems. |  | TOP | [18 empty] | TOP |  |  |  | 2015-05-29 |  | 2020-09-30 |  |  |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6161 | Electronic Security Perimeters (CIP-005) including Interactive Remote Access; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6170 | Physical security controls; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2016-06-30 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6174 | One or more processes to determine if an identified Cyber Security Incident is a Reportable Cyber Security Incident and notify the Electricity Sector Information Sharing and Analysis Center (ES-ISAC), unless prohibited by law. Initial notification to the ES-ISAC, which may be only a preliminary notice, shall not exceed one hour from the determination of a Reportable Cyber Security Incident. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.2. Examples of evidence may include, but are not limited to, dated documentation of Cyber Security Incident response plan(s) that provide guidance or thresholds for determining which Cyber Security Incidents are also Reportable Cyber Security Incidents and documentation of initial notices to the Electricity Sector Information Sharing and Analysis Center (ES-ISAC). | 2014-02-03 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6178 | Use the Cyber Security Incident response plan(s) under Requirement R1 when responding to a Reportable Cyber Security Incident or performing an exercise of a Reportable Cyber Security Incident. Document deviations from the plan(s) taken during the response to the incident or exercise. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.2. Examples of evidence may include, but are not limited to, incident reports, logs, and notes that were kept during the incident response process, and follow-up documentation that describes deviations taken from the plan during the incident or exercise. | 2014-02-03 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6182 | Update the Cyber Security Incident response plan based on any documented lessons learned associated with the plan; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | 31200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6184 | No later than 60 calendar days after a change to the roles or responsibilities, Cyber Security Incident response groups or individuals, or technology that the Responsible Entity determines would impact the ability to execute the plan: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.2. An example of evidence may include, but is not limited to:1. Dated and revised Cyber Security Incident response plan with changes to the roles or responsibilities, responders or technology; and2. Evidence of plan update distribution including, but not limited to:• Emails;• USPS or other mail service;• Electronic distribution system; or • Training sign-in sheets. | 2014-02-03 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6186 | Notify each person or group with a defined role in the Cyber Security Incident response plan of the updates. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | 32200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6188 | Protect against the use of unnecessary physical input/output ports used for network connectivity, console commands, or removable media. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6190 | At least once every 35 calendar days, evaluate security patches for applicability that have been released since the last evaluation from the source or sources identified in Part 2.1. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6194 | Mitigate the threat of detected malicious code. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6197 | Generate alerts for security events that the Responsible Entity determines necessitates an alert, that includes, as a minimum, each of the following types of events (per Cyber Asset or BES Cyber System capability): |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 62 | The Balancing Authorities that have a fixed schedule (B and C) but do not contain the Jointly Owned Unit shall not include their share of the governor droop response in their Frequency Bias Setting. See Standard for Graphic. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  | BAL-003-0 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6201 | Identify and inventory all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6208 | Detected failed access attempts and failed login attempts; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 41200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6211 | Detected failure of Part 4.1 event logging. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 42200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6213 | Minimum password complexity that is the lesser of three or more different types of characters (e.g., uppercase alphabetic, lowercase alphabetic, numeric, non-alphanumeric) or the maximum complexity supported by the Cyber Asset. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 55200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6215 | Procedure(s) for protecting and securely handling BES Cyber System Information, including storage, transit, and use. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6217 | Prior to the disposal of applicable Cyber Assets that contain BES Cyber System Information, the Responsible Entity shall take action to prevent the unauthorized retrieval of BES Cyber System Information from the Cyber Asset or destroy the data storage media. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 622 | Procedures for notification of new or modified facilities to others (those responsible for the reliability of the interconnected transmission systems) as soon as feasible. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6220 | Any commercially available or open-source application software (including version) intentionally installed; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6224 | Authorize and document changes that deviate from the existing baseline configuration. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6228 | Following the change, verify that required cyber security controls determined in 1.4.1 are not adversely affected; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 14200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6232 | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 15200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6235 | Where technically feasible, at least once every 36 calendar months: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6237 | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 32200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6241 | All External Routable Connectivity must be through an identified Electronic Access Point (EAP). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.2. An example of evidence may include, but is not limited to, network diagrams showing all external routable communication paths and the identified EAPs. | 2014-02-03 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6246 | For all Interactive Remote Access sessions, utilize encryption that terminates at an Intermediate System. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.2. An example of evidence may include, but is not limited to, architecture documents detailing where encryption initiates and terminates. | 2014-02-03 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6249 | Utilize at least one physical access control to allow unescorted physical access into each applicable Physical Security Perimeter to only those individuals who have authorized unescorted physical access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 1.2 An example of evidence may include, but is not limited to, language in the physical security plan that describes each Physical Security Perimeter and how unescorted physical access is controlled by one or more different methods and proof that unescorted physical access is restricted to only authorized individuals, such as a list of authorized individuals accompanied by access logs. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6258 | Require manual or automated logging of visitor entry into and exit from the Physical Security Perimeter that includes date and time of the initial entry and last exit, the visitor’s name, and the name of an individual point of contact responsible for the visitor, except during CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 2.2 An example of evidence may include, but is not limited to, language in a visitor control program that requires continuous escorted access of visitors within Physical Security Perimeters and additional evidence to demonstrate that the process was implemented, such as dated visitor logs that include the required information. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6262 | Roles and responsibilities of responders. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6267 | Test a representative sample of information used to recover BES Cyber System functionality at least once every 15 calendar months to ensure that the information is useable and is compatible with current configurations.An actual recovery that incorporates the information used to recover BES Cyber System functionality substitutes for this test. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6271 | Update the recovery plan based on any documented lessons learned associated with the plan; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 31200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6273 | No later than 60 calendar days after a change to the roles or responsibilities, responders, or technology that the Responsible Entity determines would impact the ability to execute the recovery plan: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6275 | Notify each person or group with a defined role in the recovery plan of the updates. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 32200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6286 | Require completion of the training specified in Part 2.1 prior to granting authorized electronic access and authorized unescorted physical access to applicable Cyber Assets, except during CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, training records and documentation of when CIP Exceptional Circumstances were invoked. | 2014-02-03 |  | 2016-06-30 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6299 | Process to perform a seven year criminal history records check as part of each personnel risk assessment that includes: | [23 empty] | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to perform a seven year criminal history records check. |  |  | 2016-06-30 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6301 | other locations where, during the seven years immediately prior to the date of the criminal history records check, the subject has resided for six consecutive months or more. If it is not possible to perform a full seven year criminal history records check, conduct as much of the seven year criminal history records check as possible and document the reason the full seven year criminal history records check could not be performed. | [23 empty] | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to perform a seven year criminal history records check. |  |  | 2016-06-30 |  |  |  | 32200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6307 | Unescorted physical access into a Physical Security Perimeter; and | [23 empty] | An example of evidence may include, but is not limited to, dated documentation of the process to authorize electronic access, unescorted physical access in a Physical Security Perimeter, and access to designated storage locations, whether physical or electronic, for BES Cyber System Information. |  |  | 2016-06-30 |  |  |  | 41200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6309 | Verify at least once each calendar quarter that individuals with active electronic access or unescorted physical access have authorization records. | [23 empty] | Examples of evidence may include, but are not limited to:• Dated documentation of the verification between the system generated list of individuals who have been authorized for access (i.e., workflow database) and a system generated list of personnel who have access (i.e., user account listing), or• Dated documentation of the verification between a list of individuals who have been authorized for access (i.e., authorization forms) and a list of individuals provisioned for access (i.e., provisioning forms or shared account listing). |  |  | 2016-06-30 |  |  |  | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6313 | For reassignments or transfers, revoke the individual’s authorized electronic access to individual accounts and authorized unescorted physical access that the Responsible Entity determines are not necessary by the end of the next calendar day following the date that the Responsible Entity determines that the individual no longer requires retention of that access. | [23 empty] | An example of evidence may include, but is not limited to, documentation of all of the following:1. Dated workflow or sign-off form showing a review of logical and physical access; and 2. Logs or other demonstration showing such persons no longer have access that the Responsible Entity determines is not necessary. |  |  | 2016-06-30 |  |  |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6318 | Identify each of the medium impact BES Cyber Systems according to Attachment 1, Section 2, if any, at each asset; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-12-26 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6321 | Have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 at least once every 15 calendar months, even if it has no identified items in Requirement R1. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-12-26 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6323 | The documentation shall be consistent with the principle that the Facility Ratings do not exceed the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | GO | [22 empty] | 2011-11-17 |  | 2021-09-30 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6324 | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R2, Part 2.1 including identification of how each of the following were considered: |  | GO | [22 empty] | 2011-11-17 |  | 2021-09-30 |  |  |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6325 | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R2, Part 2.1 including identification of how each of the following were considered: |  | GO | [22 empty] | 2011-11-17 |  | 2021-09-30 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6327 | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. |  | GO | [22 empty] | 2013-01-01 |  | 2021-09-30 |  |  |  | 22200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 633 | Ensurance of compliance with NERC Reliability Standards and applicable Regional, subregional, Power Pool, and individual system planning criteria and facility connection requirements. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [14 empty] | 2007-06-18 |  | 2011-09-30 |  |  | FAC-002-0 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6333 | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | GO | [22 empty] | 2013-01-01 |  | 2021-09-30 |  |  |  | 24200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6334 | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R3, Part 3.1 including identification of how each of the following were considered: |  | TO | [22 empty] | 2011-11-17 |  | 2021-09-30 |  |  |  | 31000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6335 | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R3, Part 3.1 including identification of how each of the following were considered: |  | TO | [22 empty] | 2011-11-17 |  | 2021-09-30 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6337 | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. |  | TO | [22 empty] | 2013-01-01 |  | 2021-09-30 |  |  |  | 32200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6343 | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | TO | [22 empty] | 2013-01-01 |  | 2021-09-30 |  |  |  | 34200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6346 | Within 30 calendar days (or a later date if specified by the requester), for any requested Facility with a Thermal Rating that limits the use of Facilities under the requester’s authority by causing any of the following: 1) An Interconnection Reliability Operating Limit, 2) A limitation of Total Transfer Capability, 3) An impediment to generator deliverability, or 4) An impediment to service to a major load center: |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-01-01 |  | 2021-09-30 |  |  |  | 81200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6347 | Within 30 calendar days (or a later date if specified by the requester), for any requested Facility with a Thermal Rating that limits the use of Facilities under the requester’s authority by causing any of the following: 1) An Interconnection Reliability Operating Limit, 2) A limitation of Total Transfer Capability, 3) An impediment to generator deliverability, or 4) An impediment to service to a major load center: |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-11-17 |  | 2021-09-30 |  |  |  | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6349 | The Thermal Rating for the next most limiting equipment identified in Requirement R8, Part 8.2.1. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-01-01 |  | 2021-09-30 |  |  |  | 82200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6351 | Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. |  | PCPA | [9 empty] | PA | [12 empty] | 2014-01-01 |  | 2014-09-30 |  |  |  | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6355 | The BES interrupting device owner owns all or part of the Composite Protection System; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-11-19 |  | 2017-04-01 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6361 | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-04-02 |  | 2017-04-01 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6363 | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-11-19 |  | 2017-04-01 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6369 | The calculation results shall be submitted to the Compliance Enforcement Authority and made available to the GO by the end of the month in which they were completed. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [16 empty] | 2014-01-16 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01.4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. |  | 22000000 | TXRE-US |  |  |  |  | TXRE-US
2. | 6373 | Include the applicable monitored Component attributes applied to each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-2, and Table 5 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [19 empty] | 2015-12-31 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6380 | The Transmission Owner shall identify the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment. |  | TO | [22 empty] | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.Voltage Value of a Line Weight Value per Lineless than 200 kV (not applicable) (not applicable)200 kV to 299 kV 700300 kV to 499 kV 1300500 kV and above 04.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6381 | The Transmission Owner shall identify the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment. |  | TO | [22 empty] | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.Voltage Value of a Line Weight Value per Lineless than 200 kV (not applicable) (not applicable)200 kV to 299 kV 700300 kV to 499 kV 1300500 kV and above 04.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6383 | The unaffiliated third party verification shall verify the Transmission Owner’s risk assessment performed under Requirement R1, which may include recommendations for the addition or deletion of a Transmission station(s) or Transmission substation(s). The Transmission Owner shall ensure the verification is completed within 90 calendar days following the completion of the Requirement R1 risk assessment. |  | TO | [22 empty] | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.Voltage Value of a Line Weight Value per Lineless than 200 kV (not applicable) (not applicable)200 kV to 299 kV 700300 kV to 499 kV 1300500 kV and above 04.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 21000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6384 | The unaffiliated third party verification shall verify the Transmission Owner’s risk assessment performed under Requirement R1, which may include recommendations for the addition or deletion of a Transmission station(s) or Transmission substation(s). The Transmission Owner shall ensure the verification is completed within 90 calendar days following the completion of the Requirement R1 risk assessment. |  | TO | [22 empty] | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.Voltage Value of a Line Weight Value per Lineless than 200 kV (not applicable) (not applicable)200 kV to 299 kV 700300 kV to 499 kV 1300500 kV and above 04.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6391 | Prior history of attack on similar facilities taking into account the frequency, geographic proximity, and severity of past physical security related events; and |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.Voltage Value of a Line Weight Value per Lineless than 200 kV (not applicable) (not applicable)200 kV to 299 kV 700300 kV to 499 kV 1300500 kV and above 04.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6395 | Law enforcement contact and coordination information. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.Voltage Value of a Line Weight Value per Lineless than 200 kV (not applicable) (not applicable)200 kV to 299 kV 700300 kV to 499 kV 1300500 kV and above 04.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 640 | The Transmission Owner, in the TVMP, shall identify and document clearances between vegetation and any overhead, ungrounded supply conductors, taking into consideration transmission line voltage, the effects of ambient temperature on conductor sag under maximum design loading, and the effects of wind velocities on conductor sway. Specifically, the Transmission Owner shall establish clearances to be achieved at the time of vegetation management work identified herein as Clearance 1, and shall also establish and maintain a set of clearances identified herein as Clearance 2 to prevent flashover between vegetation and overhead ungrounded supply conductors. |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  | FAC-003-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6400 | The Transmission Owner or Transmission Operator, respectively, shall ensure that the unaffiliated third party review is completed within 90 calendar days of completing the security plan(s) developed in Requirement R5. The unaffiliated third party review may, but is not required to, include recommended changes to the evaluation performed under Requirement R4 or the security plan(s) developed under Requirement R5. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.Voltage Value of a Line Weight Value per Lineless than 200 kV (not applicable) (not applicable)200 kV to 299 kV 700300 kV to 499 kV 1300500 kV and above 04.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 61000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6402 | The Transmission Owner or Transmission Operator, respectively, shall ensure that the unaffiliated third party review is completed within 90 calendar days of completing the security plan(s) developed in Requirement R5. The unaffiliated third party review may, but is not required to, include recommended changes to the evaluation performed under Requirement R4 or the security plan(s) developed under Requirement R5. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.Voltage Value of a Line Weight Value per Lineless than 200 kV (not applicable) (not applicable)200 kV to 299 kV 700300 kV to 499 kV 1300500 kV and above 04.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6407 | The UVLS Program is integrated through coordination with generator voltage ride-through capabilities and other protection and control systems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage-based load shedding programs. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-11-19 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6412 | The performance (i.e., operation and non-operation) of the UVLS Program equipment. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-11-19 | [5 empty] | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6419 | One of the following TLR levels: TLR-1, TLR-2, TLR-3A, TLR-3B, TLR-4, TLR-5A, TLR-5B, TLR-6, TLR-0 |  | RC | [11 empty] | RC | [10 empty] | 2011-04-21 |  | 2016-03-31 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US | MRO-US | NPCC-US | RF-US | SERC-US
2. | 642 | Clearance 2 — The Transmission Owner shall determine and document specific radial clearances to be maintained between vegetation and conductors under all rated electrical operating conditions. These minimum clearance distances are necessary to prevent flashover between vegetation and conductors and will vary due to such factors as altitude and operating voltage. These Transmission Owner-specific minimum clearance distances shall be no less than those set forth in the Institute of Electrical and Electronics Engineers (IEEE) Standard 516-2003 (Guide for Maintenance Methods on Energized Power Lines) and as specified in its Section 4.2.2.3, Minimum Air Insulation Distances without Tools in the Air Gap. |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6421 | Communicate the list of congestion management actions to be implemented to 1.) all Reliability Coordinators in the Eastern Interconnection, and 2.) those Reliability Coordinators in other Interconnections responsible for curtailing Interchange Transactions crossing Interconnection boundaries identified in the list of congestion management actions. |  | RC | [11 empty] | RC | [10 empty] | 2011-04-21 |  | 2016-03-31 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US | MRO-US | NPCC-US | RF-US | SERC-US
2. | 6425 | Manufacturer, model number (if available), and type of the excitation control system including, but not limited to static, AC brushless, DC rotating, and/or the plant volt/var control function (if installed), |  | GO | [22 empty] | 2018-07-01 |  |  |  | 4.2. Facilities:For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following:4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).4.2.2 Generation in the Western Interconnection with the following characteristics:4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.3 Generation in the ERCOT Interconnection with the following characteristics:4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.4 For all Interconnections:• A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6431 | A no-disturbance simulation results in negligible transients, and |  | TP | [19 empty] | TP |  |  | 2014-05-26 |  |  |  | 4.2. Facilities:For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following:4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).4.2.2 Generation in the Western Interconnection with the following characteristics:4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.3 Generation in the ERCOT Interconnection with the following characteristics:4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.4 For all Interconnections:• A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. |  | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6435 | Type of governor and load control or active power control/frequency control equipment,Footnote: Turbine/governor and load control or active power/frequency control: |  | GO | [22 empty] | 2014-07-01 |  |  |  | 4.2. FacilitiesFor the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred to as an “applicable unit” that meet the following:4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics:4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).4.2.2 Generation in the Western Interconnection with the following characteristics:4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.3 Generation in the ERCOT Interconnection with the following characteristics:4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 644 | Where transmission system transient overvoltage factors are known, clearances shall be derived from Table 7, IEEE 516-2003, phase-to-phase voltages, with appropriate altitude correction factors applied. |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  |  | 12220000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6440 | A no-disturbance simulation results in negligible transients, and |  | TP | [19 empty] | TP |  |  | 2014-05-26 |  |  |  | 4.2. FacilitiesFor the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred to as an “applicable unit” that meet the following:4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics:4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).4.2.2 Generation in the Western Interconnection with the following characteristics:4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.3 Generation in the ERCOT Interconnection with the following characteristics:4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6444 | Transmission operations |  | RC | [11 empty] | RC | [10 empty] | 2012-10-01 |  | 2019-06-30 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6453 | Emergency preparedness and operations |  | TOP | [18 empty] | TOP |  |  |  | 2012-10-01 |  | 2019-06-30 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6457 | Certificates:• Reliability Operator• Balancing, Interchange and Transmission Operator• Transmission Operator |  | TOP | [18 empty] | TOP |  |  |  | 2011-09-15 |  | 2019-06-30 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6460 | Emergency preparedness and operations |  | BA | BA | [21 empty] | 2012-10-01 |  | 2019-06-30 |  |  |  | 31200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6463 | Certificates• Reliability Operator• Balancing, Interchange and Transmission Operator• Balancing and Interchange Operator |  | BA | BA | [21 empty] | 2012-10-01 |  | 2019-06-30 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6464 | Certificates• Reliability Operator• Balancing, Interchange and Transmission Operator• Balancing and Interchange Operator |  | BA | BA | [21 empty] | 2011-09-15 |  | 2019-06-30 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6466 | Limit Governor droop settings such that they do not exceed those listed in Table 6.2, unless directed otherwise by the BA. (see standard for table) | See Standard for table | BA, GO, GOP | BA |  |  |  | GO | GOP | [16 empty] | 2014-01-16 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01.4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. |  | 62000000 | TXRE-US |  |  |  |  | TXRE-US
2. | 6469 | If a generating unit/generating facility has not participated in a minimum of eight FMEs in a 12-month period, performance shall be based on a rolling eight-FME average. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [16 empty] | 2014-01-16 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01.4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. |  | 92000000 | TXRE-US |  |  |  |  | TXRE-US
2. | 6473 | If a generating unit/generating facility has not participated in a minimum of eight FMEs in a 12-month period, performance shall be based on a rolling eight- FME average. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [16 empty] | 2014-01-16 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01.4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. |  | 102000000 | TXRE-US |  |  |  |  | TXRE-US
2. | 6476 | Comprised of any combination of the reserve types specified below:• Operating Reserve – Spinning• Operating Reserve - Supplemental • Interchange Transactions designated by the Source Balancing Authority as Operating Reserve – Supplemental • Reserve held by other entities by agreement that is deliverable on Firm Transmission Service• A resource, other than generation or load, that can provide energy or reduce energy consumption • Load, including demand response resources, Demand-Side Management resources, Direct Control Load Management, Interruptible Load or Interruptible Demand, or any other Load made available for curtailment by the Balancing Authority or the Reserve Sharing Group via contract or agreement.• All other load, not identified above, once the Reliability Coordinator has declared an energy emergency alert signifying that firm load interruption is imminent or in progress. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | 1.2 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates compliance with Requirement R1, Part 1.2. Evidence may include, but is not limited to, documentation that reserves were comprised of the types listed in Requirement R1, Part 1.2 for purposes of meeting the Contingency Reserve obligation of Requirement R1. Additionally, for purposes of the last bullet of Requirement R1, Part 1.2, evidence of compliance may include, but is not limited to, documentation that the reliability coordinator had issued an energy emergency alert, indicating that firm Load interruption was imminent or was in progress. | 2014-01-28 |  | 2017-01-23 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity.4.2.1. The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group.4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | 12000000 | WECC-US | [5 empty] | WECC-US
2. | 6480 | Reserve that is capable of fully responding within ten minutes. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2014-01-28 |  | 2017-01-23 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity.4.2.1. The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group.4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | 22000000 | WECC-US | [5 empty] | WECC-US
2. | 6482 | Equal to or more negative than its Frequency Response Obligation when Frequency varies from 60 Hz by more than +/- 0.036 Hz. |  | BA, FRSG | BA |  |  | FRSG | [12 empty] | RSG | [5 empty] | 2014-03-24 |  | 2015-11-12 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6484 | For generation-only Balancing Authorities, 150% of the previous calendar year’s integrated hourly peak generation. |  | BA | BA | [21 empty] | 2013-10-16 |  | 2018-09-30 |  |  |  | 12000000 | WECC-US | [5 empty] | WECC-US
2. | 6486 | PIIaccum, |  | BA | BA | [21 empty] | 2013-10-16 |  | 2018-09-30 |  |  |  | 42000000 | WECC-US | [5 empty] | WECC-US
2. | 6489 | A summary description of the elements required to support the backup functionality. These elements shall include, at a minimum: |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6491 | Data communications. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2013-07-01 |  | 2019-03-31 |  |  |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6500 | Actions to manage the risk to the BES during the transition from primary to backup functionality as well as during outages of the primary or backup functionality. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2013-07-01 |  | 2019-03-31 |  |  |  | 16200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6504 | The backup functionality for a minimum of two continuous hours. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  |  | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6506 | A process for the Reliability Coordinator to review the GMD Operating Procedures or Operating Processes of Transmission Operators within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2015-04-01 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6508 | System Operator actions to be initiated based on predetermined conditions. |  | TOP | [18 empty] | TOP |  |  |  | 2015-04-01 | [5 empty] | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 651 | The Transmission Owner is not required to report to the RRO, or the RRO’s designee, certain sustained transmission line outages caused by vegetation: (1) Vegetation-related outages that result from vegetation falling into lines from outside the ROW that result from natural disasters shall not be considered reportable (examples of disasters that could create non-reportable outages include, but are not limited to, earthquakes, fires, tornados, hurricanes, landslides, wind shear, major storms as defined either by the Transmission Owner or an applicable regulatory body, ice storms, and floods), and (2) Vegetation-related outages due to human or animal activity shall not be considered reportable (examples of human or animal activity that could cause a non-reportable outage include, but are not limited to, logging, animal severing tree, vehicle contact with tree, arboricultural activities or horticultural or agricultural activities, or removal or digging of vegetation). |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  | FAC-003-1 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6514 | Outside its Transmission Operator Area, obtain and utilize status, voltages, and flow data for Facilities and the status of Special Protection Systems. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-26 |  | 2018-06-30 |  |  |  | 102000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6526 | Provide its Planning Coordinator with a technical study that demonstrates that the Distribution Providers or Transmission Owners specific deviations from the requirements of UFLS Attachment C, Table 1 will not have a significant adverse impact on the bulk power system. |  | DP, DP-UFLS, TO |  | DP | [20 empty] | 2016-01-01 |  | 2020-03-31 |  |  |  | 52000000 | NPCC-US |  | NPCC-US
2. | 6532 | Transmit the existing underfrequency settings and any changes to the underfrequency settings along with the technical basis for the settings to the Planning Coordinator. |  | DP-UFLS, GO |  | DP | [20 empty] | 2013-04-29 |  | 2020-03-31 |  |  |  | 162000000 | NPCC-US |  | NPCC-US
2. | 6533 | Design auxiliary system(s) or devices used for the control and protection of auxiliary system(s), necessary for the generating unit operation such that they will not trip the generating unit during underfrequency conditions above the appropriate generator underfrequency trip protection settings threshold curve in Figure 1. |  | DP-UFLS, GO |  | DP | [20 empty] | 2013-04-29 |  | 2020-03-31 |  |  |  | 152000000 | NPCC-US |  | NPCC-US
2. | 6535 | Set the frequency trip setting upper tolerance to no greater than + 0.1 Hz. |  | DP-UFLS, GO |  | DP | [20 empty] | 2013-04-29 |  | 2020-03-31 |  |  |  | 192000000 | NPCC-US |  | NPCC-US
2. | 6538 | The buses at which the Load is modeled in the NPCC library power flow case. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2013-04-29 |  | 2020-03-31 |  |  |  | 202000000 | NPCC-US |  | NPCC-US
2. | 6542 | Québec Interconnection – 200 ms |  | DP, DP-UFLS, TO |  | DP | [20 empty] | 2016-01-01 |  | 2020-03-31 |  |  |  | 72000000 | NPCC-US |  | NPCC-US
2. | 6545 | Include the applicable monitored Component attributes applied to each Protection System Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, and Table 3 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System Components. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2014-02-24 |  | 2015-05-28 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6547 | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 655 | Category 2 — Fall-ins: Outages caused by vegetation falling into lines from inside the ROW; |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  |  | 34200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6550 | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-1 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6553 | Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES |  | PCPA | [9 empty] | PA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  |  | 33200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6556 | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6563 | UFLS design assessment |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 142000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6566 | Inter-relationships between vegetation growth rates, vegetation control methods, and inspection frequency. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-11-25 |  | 2016-09-30 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6568 | A statement that the assessment shall respect known System Operating Limits (SOLs). |  | PCPA | [9 empty] | PA | [12 empty] | 2012-01-23 |  | 2020-12-14 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6573 | Distribute to each functional entity that has a reliability-related need for the Transfer Capability methodology and submits a request for that methodology within 30 calendar days of receiving that written request. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-01-23 |  | 2020-12-14 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6578 | Generating plants/facilities greater than 50 MVA (gross aggregate nameplate rating) directly connected to the BES |  | PCPA | [9 empty] | PA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  |  | 332000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6584 | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 220000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6586 | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-1 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 320000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6589 | Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES |  | PCPA | [9 empty] | PA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  |  | 332000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6592 | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 420000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6599 | The effectiveness of the UFLS program |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 2020000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6602 | Shed load with a minimum of three frequency set points. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2013-02-25 |  | 2017-12-31 |  |  |  | 22000000 | SERC-US |  |  |  | SERC-US
2. | 6610 | The amount of load in each load shedding step shall be within -1.0 and +3.0 of the percentage specified by the Planning Coordinator (for example, if the specified percentage step load shed is 12%, the allowable range is 11 to 15%). |  | DP, DP-UFLS, TO |  | DP | [20 empty] | 2015-10-01 |  | 2017-12-31 |  |  |  | 42000000 | SERC-US |  |  |  | SERC-US
2. | 6613 | The amount of total UFLS load shall be within ± 5.0 of the percentage specified by the Planning Coordinator for the total UFLS load in the UFLS scheme. |  | DP, DP-UFLS, TO |  | DP | [20 empty] | 2015-10-01 |  | 2017-12-31 |  |  |  | 52000000 | SERC-US |  |  |  | SERC-US
2. | 6615 | Total clearing time associated with each set point (sec). This includes the time from when frequency reaches the set point and ends when the breaker opens. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2013-02-25 |  | 2017-12-31 |  |  |  | 72000000 | SERC-US |  |  |  | SERC-US
2. | 6618 | Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. |  | PCPA | [9 empty] | PA | [12 empty] | 2014-09-22 |  | 2017-03-31 |  |  |  | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6620 | Total clearing time associated with each set point (sec). This is defined as the time that begins when frequency reaches the set point and ends when the breaker opens. If inverse time underfrequency relays are used, provide the total clearing time at 59.0, 58.5, 58.0, and 57.0 Hz. |  | DP-UFLS, GO |  | DP | [20 empty] | 2013-02-25 |  | 2017-12-31 |  |  |  | 82000000 | SERC-US |  |  |  | SERC-US
2. | 6624 | Known outage(s) of generation or Transmission Facility(ies) with a duration of at least six months. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-01-01 | [5 empty] | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6631 | System Off-Peak Load for one of the five years. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6635 | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by the following annual current study, supplemented with qualified past studies as indicated in Requirement R2, Part 2.6: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6640 | When instructed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2014-08-01 |  | 2015-05-28 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6644 | Available fixed tap ranges. |  | GO | [22 empty] | 2014-10-01 |  | 2015-05-28 |  |  |  | 51200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6649 | System Off-Peak Load for one of the five years. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 24200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6654 | For steady state, short circuit, or Stability analysis: no material changes have occurred to the System represented in the study. Documentation to support the technical rationale for determining material changes shall be included. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 26200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6657 | Include actions to resolve performance deficiencies identified in multiple sensitivity studies or provide a rationale for why actions were not necessary. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 27200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6662 | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 28200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6664 | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R3, Part 3.5. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6667 | Simulate the expected automatic operation of existing and planned devices designed to provide steady state control of electrical system quantities when such devices impact the study area. These devices may include equipment such as phase-shifting transformers, load tap changing transformers, and switched capacitors and inductors. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 33200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6669 | Tripping of Transmission elements where relay loadability limits are exceeded. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 33120000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6675 | For planning events P2 through P7: When a generator pulls out of synchronism in the simulations, the resulting apparent impedance swings shall not result in the tripping of any Transmission system elements other than the generating unit and its directly connected Facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 41200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6677 | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R4, Part 4.5. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6681 | Tripping of generators where simulations show generator bus voltages or high side of the GSU voltages are less than known or assumed generator low voltage ride through capability. Include in the assessment any assumptions made. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 43120000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6683 | Simulate the expected automatic operation of existing and planned devices designed to provide dynamic control of electrical system quantities when such devices impact the study area. These devices may include equipment such as generation exciter control and power system stabilizers, static var compensators, power flow controllers, and DC Transmission controllers. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 43200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6692 | Transmission system topology, including but not limited to long term planned Transmission outages, additions, and retirements. |  | PCPA | [9 empty] | PA | [12 empty] | 2013-04-01 |  | 2020-12-14 |  |  |  | 14200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6699 | Each Transmission Planner within the Planning Coordinator’s Planning Coordinator area. |  | PCPA | [9 empty] | PA | [12 empty] | 2013-04-01 |  | 2020-12-14 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6701 | For Confirmed Interchange less than or equal to 250 MW for the last hour, the actual hourly integrated energy deviates from the Confirmed Interchange by more than 25 MW for that hour and that deviation is expected to persist. |  | PSE | [10 empty] | PSE | [11 empty] | 2014-11-26 |  | 2020-12-14 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6704 | Each Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if the Scheduling Path (proper connectivity of Adjacent Balancing Authorities) between it and its Adjacent Balancing Authorities is invalid. |  | BA | BA | [21 empty] | 2014-06-30 |  | 2021-03-31 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6708 | Each Intermediate Balancing Authority, |  | BA | BA | [21 empty] | 2014-06-30 |  | 2021-03-31 |  |  |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6713 | Opposite in sign or direction to that of the Adjacent Balancing Authority. |  | BA | BA | [21 empty] | 2014-11-26 |  | 2021-03-31 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6715 | Each adjacent Reliability Coordinator within the same Interconnection. |  | RC | [11 empty] | RC | [10 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6717 | Each adjacent Reliability Coordinator within the same Interconnection. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6719 | Each Balancing Authority within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6725 | Each Balancing Authority within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  |  | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6729 | Each Transmission Operator that operates Facilities within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6734 | Each Transmission Operator that operates Facilities within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6737 | Its Transmission Operator. |  | DP |  | DP | [20 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6739 | Its Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6741 | The Transmission Owner shall identify the primary control center that operationally controls each Transmission station or Transmission substation identified in the Requirement R1 risk assessment. |  | TO | [22 empty] | 2015-10-01 |  | 2015-10-01 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6743 | The unaffiliated third party verification shall verify the Transmission Owner’s risk assessment performed under Requirement R1, which may include recommendations for the addition or deletion of a Transmission station(s) or Transmission substation(s). The Transmission Owner shall ensure the verification is completed within 90 calendar days following the completion of the Requirement R1 risk assessment. |  | TO | [22 empty] | 2015-10-01 |  | 2015-10-01 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6748 | Prior history of attack on similar facilities taking into account the frequency, geographic proximity, and severity of past physical security related events; and |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  |  | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6751 | Law enforcement contact and coordination information. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6755 | The Transmission Owner or Transmission Operator, respectively, shall ensure that the unaffiliated third party review is completed within 90 calendar days of completing the security plan(s) developed in Requirement R5. The unaffiliated third party review may, but is not required to, include recommended changes to the evaluation performed under Requirement R4 or the security plan(s) developed under Requirement R5. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  |  | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6759 | transmission Facilities; and |  | TO | [22 empty] | 2014-11-06 |  | 2018-12-31 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6762 | Procedures for notifying those responsible for the reliability of affected system(s) of new or materially modified existing interconnections. |  | TO | [22 empty] | 2014-11-06 |  | 2018-12-31 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6764 | Procedures for notifying those responsible for the reliability of affected system(s) of new interconnections. |  | GO | [22 empty] | 2014-11-06 |  | 2018-12-31 |  |  |  | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6766 | Adherence to applicable NERC Reliability Standards; regional and Transmission Owner planning criteria; and Facility interconnection requirements; |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2014-11-06 |  | 2021-03-31 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6770 | Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. |  | GO | [22 empty] | 2014-05-27 |  |  |  | For the purpose of this standard, the term, “applicable Facility” shall mean any one of the following:4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.4.2.2 Synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.4.2.3 Generating plant/Facility greater than 75 MVA (gross aggregate nameplate rating) directly connected to the Bulk Electric System. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6772 | Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. |  | GO | [22 empty] | 2014-05-27 |  |  |  | For the purpose of this standard, the term, “applicable Facility” shall mean any one of the following:4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.4.2.2 Synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.4.2.3 Generating plant/Facility greater than 75 MVA (gross aggregate nameplate rating) directly connected to the Bulk Electric System. |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6774 | Submit a completed Attachment 2 (or a form containing the same information as identified in Attachment 2) to its Transmission Planner within 90 calendar days of either (i) the date the data is recorded for a staged test; or (ii) the date the data is selected for verification using historical operational data. |  | TO | [22 empty] | 2014-05-27 |  |  |  | For the purpose of this standard, the term, “applicable Facility” shall mean any one of the following:4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.4.2.2 Synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.4.2.3 Generating plant/Facility greater than 75 MVA (gross aggregate nameplate rating) directly connected to the Bulk Electric System. |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6776 | A timetable for providing the data. (A minimum of 30 calendar days must be allowed for responding to the request). |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2015-04-27 |  | 2016-09-30 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6779 | Monthly and annual integrated peak hour Demands in megawatts for the prior calendar year. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6785 | Monthly forecast Net Energy for Load in gigawatthours for the next two calendar years. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 14200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6791 | The Demand and energy effects of controllable and dispatchable Demand Side Management under the control or supervision of the System Operator. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 15200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6797 | Specifications of the following items consistent with procedures for building the Interconnection-wide case(s): |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-07-01 |  |  |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6799 | Level of detail to which equipment shall be modeled; |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-07-01 |  |  |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 68 | Each Balancing Authority shall report its Frequency Bias Setting, and method for determining that setting, to the NERC Operating Committee. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2015-03-31 |  |  | BAL-003-0.1b R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6804 | Provide the response within 90 calendar days of receipt, unless a longer time period is agreed upon by the notifying Planning Coordinator or Transmission Planner. |  | BA, GO, LSE, RP, TO, TSP | BA |  |  |  | GO |  |  | LSE | [5 empty] | RP |  |  |  | TO |  |  | TSP |  | 2015-07-01 |  |  |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6806 | Comparison of the performance of the Planning Coordinator’s portion of the existing system in a planning dynamic model to actual system response, through simulation of a dynamic local event, at least once every 24 calendar months (use a dynamic local event that occurs within 24 calendar months of the last dynamic local event used in comparison, and complete each comparison within 24 calendar months of the dynamic local event). If no dynamic local event occurs within the 24 calendar months, use the next dynamic local event that occurs; |  | PCPA | [9 empty] | PA | [12 empty] | 2014-05-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6810 | Energy and capacity shortages. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-26 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6815 | Obtain written agreement from all of the Reliability Coordinators required to take the indicated action(s) for each update. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-26 | [5 empty] | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6819 | Assignment of coordination responsibilities for outage schedules between Transmission Operator(s) and Balancing Authority(s). |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6820 | Specify outage submission timing requirements. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-26 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6824 | A mutually-agreeable format. |  | TOP | [18 empty] | TOP | [5 empty] | 2016-01-26 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6828 | A mutually-agreeable format. |  | BA | BA | [23 empty] | 2016-01-26 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6832 | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-26 |  | 2021-03-31 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6836 | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. |  | BA | BA | [21 empty] | 2016-01-26 |  | 2021-03-31 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6840 | A mutually agreeable process for resolving data conflicts |  | BA, DP, GO, GOP, LSE, TO, TOP | BA | DP |  |  | GO | GOP |  | LSE | [9 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2021-03-31 |  |  |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6843 | When instructed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-05-29 |  | 2017-09-25 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6847 | Available fixed tap ranges. |  | GO | [22 empty] | 2015-05-29 |  | 2017-09-25 |  |  |  | 51200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6851 | Processes to prepare for and mitigate Emergencies including: |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6859 | Processes to prepare for and mitigate Emergencies including: |  | BA | BA | [21 empty] | 2016-01-25 | [5 empty] | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6861 | Requesting an Energy Emergency Alert, per Attachment 1; |  | BA | BA | [21 empty] | 2017-04-01 | [5 empty] | 22200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6864 | fuel supply and inventory concerns; |  | BA | BA | [21 empty] | 2017-04-01 | [5 empty] | 22320000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 687 | The method by which the Rating (of major BES equipment that comprises a Facility) is determined. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2012-12-31 |  |  | FAC-008-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6875 | Review each submitted Operating Plan(s) for coordination to avoid risk to Wide Area reliability; and |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 31200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6878 | Include the applicable monitored Component attributes applied to each Protection System and Automatic Reclosing Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System and Automatic Reclosing Components. |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2015-12-31 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6880 | Include the applicable monitored Component attributes applied to each Protection System and Automatic Reclosing Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System and Automatic Reclosing Components. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-01-25 |  | 2015-12-31 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6882 | Include the applicable monitored Component attributes applied to each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-2, and Table 5 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [19 empty] | 2015-12-31 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6884 | The UVLS Program is integrated through coordination with generator voltage ride-through capabilities and other protection and control systems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage-based load shedding programs. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2017-04-01 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6886 | The UVLS Program is integrated through coordination with generator voltage ride-through capabilities and other protection and control systems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage-based load shedding programs. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2017-04-01 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6888 | Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 |  |  |  | 4.2. Circuits:4.2.1 Circuits Subject to Requirements R1 – R5:4.2.1.1 Transmission lines operated at 200 kV and above, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads.4.2.1.2 Transmission lines operated at 100 kV to 200 kV selected by the Planning Coordinator in accordance with Requirement R6.4.2.1.3 Transmission lines operated below 100 kV that are part of the BES and selected by the Planning Coordinator in accordance with Requirement R6.4.2.1.4 Transformers with low voltage terminals connected at 200 kV and above.4.2.1.5 Transformers with low voltage terminals connected at 100 kV to 200 kV selected by the Planning Coordinator in accordance with Requirement R6.4.2.1.6 Transformers with low voltage terminals connected below 100 kV that are part of the BES and selected by the Planning Coordinator in accordance with Requirement R6.4.2.2 Circuits Subject to Requirement R6:4.2.2.1 Transmission lines operated at 100 kV to 200 kV and transformers with low voltage terminals connected at 100 kV to 200 kV, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads.4.2.2.2 Transmission lines operated below 100 kV and transformers with low voltage terminals connected below 100 kV that are part of the BES, except Elements that connect the GSU transformer(s) to the Transmission system that are used exclusively to export energy directly from a BES generating unit or generating plant. Elements may also supply generating plant loads. |  | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 689 | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2012-12-31 |  |  |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6890 | Within 12 full calendar months of becoming aware of a generator, transformer, or transmission line BES Element that tripped in response to a stable or unstable power swing due to the operation of its protective relay(s), determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-1 – Attachment B. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2020-01-01 | [5 empty] | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6892 | Operate the electric system to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2014-11-04 |  | 2021-03-31 |  |  |  | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6899 | Technical requirements and analysis: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2014-11-04 |  | 2021-03-31 |  |  |  | 92000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6901 | Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 92200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6905 | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 93200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6914 | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 94200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6918 | Roles and responsibilities of responders. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.2. An example of evidence may include, but is not limited to, one or more recovery plans that include language identifying the roles and responsibilities of responders. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 692 | Design criteria (e.g., including applicable references to industry Rating practices such as manufacturer’s warranty, IEEE, ANSI or other standards). |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2012-12-31 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6923 | Test a representative sample of information used to recover BES Cyber System functionality at least once every 15 calendar months to ensure that the information is useable and is compatible with current configurations.An actual recovery that incorporates the information used to recover BES Cyber System functionality substitutes for this test. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.2. An example of evidence may include, but is not limited to, operational logs or test results with criteria for testing the usability (e.g. sample tape load, browsing tape contents) and compatibility with current system configurations (e.g. manual or automated comparison checkpoints between backup media contents and current configuration). | 2017-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6926 | No later than 60 calendar days after a change to the roles or responsibilities, responders, or technology that the Responsible Entity determines would impact the ability to execute the recovery plan: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.2. An example of evidence may include, but is not limited to, all of the following:1. Dated and revised recovery plan with changes to the roles or responsibilities, responders, or technology; and2. Evidence of plan update distribution including, but not limited to:• Emails;• USPS or other mail service; • Electronic distribution system; or• Training sign-in sheets. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6928 | Update the recovery plan based on any documented lessons learned associated with the plan; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 31200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6931 | Notify each person or group with a defined role in the recovery plan of the updates. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 32200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6933 | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6936 | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-2 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6939 | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6946 | The effectiveness of the UFLS program. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6950 | UFLS design assessment |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 142000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6954 | For UFLS design assessments performed under Requirement R12, the Corrective Action Plan shall be developed within the two-year time frame identified in Requirement R12. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 152000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6957 | The applicable in-service Protection System devices are set to operate to isolate or de-energize equipment in order to limit the extent of damage when operating conditions exceed equipment capabilities or stability limits. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-07-01 |  | 2016-06-30 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6961 | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall design and develop training materials according to its training program, based on the BES company-specific Real-time reliability-related task list created in part 1.1. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | M1.2 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection training materials, as specified in Requirement R1 part 1.2. | 2014-06-19 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6966 | Each Transmission Owner shall design and develop training materials according to its training program, based on the BES company-specific Real-time reliabilityrelated task list created in part 2.1. |  | TO | [21 empty] | M2.2 Each Transmission Owner shall have available for inspection training materials, as specified in Requirement R2 part 2.2. | 2014-06-19 | [5 empty] | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 6974 | Include the applicable monitored Component attributes applied to each Protection System and Automatic Reclosing Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, and Table 4-1 through 4-2 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System and Automatic Reclosing Components. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [19 empty] | 2015-12-31 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 702 | State that SOLs shall not exceed associated Facility Ratings. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-010-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7042 | For its assets identified in CIP-002 containing low impact BES Cyber Systems, if any: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7044 | Physical security controls; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7048 | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. |  | RC | [11 empty] | RC | [10 empty] | 2017-01-01 |  | 2021-03-31 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7052 | A mutually agreeable process for resolving data conflicts |  | BA, DP, GO, GOP, LSE, RC, TO, TOP | BA | DP |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2021-03-31 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7055 | Energy and capacity shortages. |  | RC | [11 empty] | RC | [12 empty] | 2016-01-26 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 706 | Following the single Contingencies (see footnote in standard) identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading Outages or uncontrolled separation shall not occur. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-05-29 |  | 2009-04-28 |  |  | FAC-010-1 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7062 | Obtain written agreement from all of the Reliability Coordinators required to take the indicated action(s) for each update. |  | RC | [11 empty] | RC | [9 empty] | 2.2 Agreed to, in writing, by all the Reliability Coordinators required to take the indicated action(s). |  |  | 2016-01-26 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7066 | System voltage limits; |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7070 | Each methodology shall describe the method used to account for each of the following elements, provided such elements impact the determination of TFC or TTC: |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7072 | Transmission topology, including, but not limited to, additions and retirements; |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 708 | Loss of any generator, line, transformer, or shunt device without a Fault. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-07-01 |  | 2009-04-28 |  |  |  | 22200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7080 | Each Transmission Operator that uses the Area Interchange or Rated System Path Methodology shall describe in its methodology the process it uses to account for requested constraints that have a five percent or greater distribution factor for a transfer between areas in the TTC determination; otherwise the requested constraint is not required to be included. When testing transfers involving the requesting Transmission Operator’s area, the requested constraint may be excluded. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7084 | Transmission topology, including, but not limited to, additions and retirements; |  | TSP | [20 empty] | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7090 | Each Transmission Service Provider that uses the Flowgate Methodology shall, for reliability-related constraints identified in part 1.3, use the AFC determined by the Transmission Service Provider for that constraint. |  | TSP | [20 empty] | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7092 | If not publicly posted on OASIS or its company website, the Transmission Operator’s effective: |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7094 | TFC or TTC methodology. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 52200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7097 | CBMID. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 53200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7099 | In responding to all other data requests, each Transmission Operator or Transmission Service Provider shall make available the requested data within 45 calendar days of receipt of the written request. Unless otherwise agreed upon, the Transmission Operator or Transmission Service Provider is not required to alter the format in which it maintains or uses the data. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 71 | The Balancing Authority may use a variable (linear or non-linear) bias value, which is based on a variable function of Tie Line deviation to Frequency Deviation. The Balancing Authority shall determine the variable frequency bias value by analyzing Frequency Response as it varies with factors such as load, generation, governor characteristics, and frequency. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2015-03-31 |  |  | BAL-003-0.1b R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7102 | Make available the requested data on a more frequent basis than it produces the data and in no event shall it be required to provide the data more frequently than once an hour. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 61200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7105 | Interchange scheduling |  | BA | BA | [21 empty] | 2016-01-26 | [5 empty] | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7113 | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities:4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 41200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7114 | The study or studies shall be conducted based on the benchmark GMD event described in Attachment 1 to determine whether the System meets the performance requirements in Table 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities:4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7118 | The effective GIC time series, GIC(t), calculated using the benchmark GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 5.1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2019-01-01 |  | 2019-06-30 |  | 4.2. Facilities:4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 712 | System reconfiguration through manual or automatic control or protection actions. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-07-01 |  | 2009-04-28 |  |  |  | 23200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7130 | Document assumptions used in the analysis; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2021-01-01 |  | 2019-06-30 |  | 4.2. Facilities:4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7134 | Be reviewed in subsequent GMD Vulnerability Assessments until it is determined that the System meets the performance requirements contained in Table 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities:4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7139 | The applicable in-service Protection System devices are set to operate to isolate or de-energize equipment in order to limit the extent of damage when operating conditions exceed equipment capabilities or stability limits. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-07-01 |  |  |  | 4.2. FacilitiesFor the purpose of this standard, the term, “applicable Facility” shall mean any one of the following:4.2.1 Individual generating unit greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.4.2.2 Individual synchronous condenser greater than 20 MVA (gross nameplate rating) directly connected to the Bulk Electric System.4.2.3 Generating plant/ Facility consisting of one or more units that are connected to the Bulk Electric System at a common bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.3.1 This includes individual generating units of the dispersed power producing resources identified through Inclusion I4 of the Bulk Electric System definition where voltage regulating control for the facility is performed solely at the individual generating unit of the dispersed power producing resources. 4.2.4 Any generator, regardless of size, that is a blackstart unit material to and designated as part of a Transmission Operator’s restoration plan. |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7142 | The BES interrupting device owner owns all or part of the Composite Protection System; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-05-13 |  | 2016-06-30 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7146 | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-07-01 |  | 2016-06-30 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7148 | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-05-13 |  | 2016-06-30 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7150 | The BES interrupting device owner owns all or part of the Composite Protection System; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-05-29 |  | 2016-06-30 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7154 | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2016-06-30 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7156 | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-05-29 |  | 2016-06-30 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7158 | Include the applicable monitored Component attributes applied to each Protection System Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, and Table 3 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System Components. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-05-29 |  | 2016-12-31 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7161 | Include the applicable monitored Component attributes applied to each Protection System Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, and Table 3 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System Components. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-01-25 |  | 2015-12-31 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7164 | Notify other owners of BES Elements connected to those BES buses, if any, within 90-calendar days of completion of Part 1.1, that those BES Elements require SER data and/or FR data. |  | TO | [22 empty] | 2015-11-24 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7167 | Each phase current and the residual or neutral current for the following BES Elements: |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7169 | Transmission Lines. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 32200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7171 | A minimum recording rate of 16 samples per cycle. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7174 | Phase undervoltage or overcurrent. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 43200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7178 | Gross individual nameplate rating greater than or equal to 300 MVA where the gross plant/facility aggregate nameplate rating is greater than or equal to 1,000 MVA. |  | PCPA, RC | [9 empty] | PA |  | RC | [10 empty] | 2016-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 51120000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7179 | Any one BES Element that is part of a stability (angular or voltage) related System Operating Limit (SOL). |  | PCPA, RC | [9 empty] | PA |  | RC | [10 empty] | 2016-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 51200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7183 | Identify a minimum DDR coverage, inclusive of those BES Elements identified in Part 5.1, of at least: |  | PCPA, RC | [9 empty] | PA |  | RC | [10 empty] | 2015-11-24 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7185 | One BES Element per 3,000 MW of the Responsible Entity’s historical simultaneous peak System Demand. |  | PCPA, RC | [9 empty] | PA |  | RC | [10 empty] | 2016-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 52200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7189 | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R6, Part 6.1, or the positive sequence current. |  | TO | [22 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 719 | Selection of applicable Contingencies. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-010-1 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7193 | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R7, Part 7.1, phase current(s) for any phase-to-phase voltages, or positive sequence current. |  | GO | [22 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7197 | At least one of the following three triggers: • Off nominal frequency trigger set at: Low Higho Eastern Interconnection <59.75 Hz >61.0 Hzo Western Interconnection <59.55 Hz >61.0 Hzo ERCOT Interconnection <59.35 Hz >61.0 Hzo Hydro-Quebec Interconnection <58.55 Hz >61.5 Hz• Rate of change of frequency trigger set at:o Eastern Interconnection < -0.03125 Hz/sec > 0.125 Hz/seco Western Interconnection < -0.05625 Hz/sec > 0.125 Hz/seco ERCOT Interconnection < -0.08125 Hz/sec > 0.125 Hz/seco Hydro-Quebec Interconnection < -0.18125 Hz/sec > 0.1875 Hz/sec• Undervoltage trigger set no lower than 85 percent of normal operating voltage for a duration of 5 seconds. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7199 | Output recording rate of electrical quantities of at least 30 times per second. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 92000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7201 | Synchronized device clock accuracy within ± 2 milliseconds of UTC. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 102000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7203 | Data subject to Part 11.1 will be provided within 30-calendar days of a request unless an extension is granted by the requestor. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7210 | Physical access controls; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7218 | Require completion of the training specified in Part 2.1 prior to granting authorized electronic access and authorized unescorted physical access to applicable Cyber Assets, except during CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.2. Examples of evidence may include, but are not limited to, training records and documentation of when CIP Exceptional Circumstances were invoked. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7221 | Any commercially available or open-source application software (including version) intentionally installed; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7225 | Authorize and document changes that deviate from the existing baseline configuration. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.2. Examples of evidence may include, but are not limited to: • A change request record and associated electronic authorization (performed by the individual or group with the authority to authorize the change) in a change management system for each change; or• Documentation that the change was performed in accordance with the requirement. | 2016-03-31 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7229 | Following the change, verify that required cyber security controls determined in 1.4.1 are not adversely affected; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 14200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7233 | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 15200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7236 | Where technically feasible, at least once every 36 calendar months: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.2. An example of evidence may include, but is not limited to, a document listing the date of the assessment (performed at least once every 36 calendar months), the output of the tools used to perform the assessment, and a list of differences between the production and test environments with descriptions of how any differences were accounted for in conducting the assessment. | 2018-07-01 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7238 | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2018-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 32200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7242 | Procedure(s) for protecting and securely handling BES Cyber System Information, including storage, transit, and use. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.2. Examples of acceptable evidence include, but are not limited to: • Procedures for protecting and securely handling, which include topics such as storage, security during transit, and use of BES Cyber System Information; or • Records indicating that BES Cyber System Information is handled in a manner consistent with the entity’s documented procedure(s). | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-011-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7244 | Prior to the disposal of applicable Cyber Assets that contain BES Cyber System Information, the Responsible Entity shall take action to prevent the unauthorized retrieval of BES Cyber System Information from the Cyber Asset or destroy the data storage media. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.2. Examples of acceptable evidence include, but are not limited to: • Records that indicate that data storage media was destroyed prior to the disposal of an applicable Cyber Asset; or• Records of actions taken to prevent unauthorized retrieval of BES Cyber System Information prior to the disposal of an applicable Cyber Asset. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting. 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-011-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7247 | Process to perform a seven year criminal history records check as part of each personnel risk assessment that includes: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.2. An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to perform a seven year criminal history records check. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 726 | Each Reliability Coordinator and Transmission Operator that operates any portion of the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-010-1 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7260 | Unescorted physical access into a Physical Security Perimeter; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 41200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7262 | Verify at least once each calendar quarter that individuals with active electronic access or unescorted physical access have authorization records. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.2. Examples of evidence may include, but are not limited to:• Dated documentation of the verification between the system generated list of individuals who have been authorized for access (i.e., workflow database) and a system generated list of personnel who have access (i.e., user account listing), or• Dated documentation of the verification between a list of individuals who have been authorized for access (i.e., authorization forms) and a list of individuals provisioned for access (i.e., provisioning forms or shared account listing). | 2016-10-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7266 | For reassignments or transfers, revoke the individual’s authorized electronic access to individual accounts and authorized unescorted physical access that the Responsible Entity determines are not necessary by the end of the next calendar day following the date that the Responsible Entity determines that the individual no longer requires retention of that access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.2. An example of evidence may include, but is not limited to, documentation of all of the following:1. Dated workflow or sign-off form showing a review of logical and physical access; and 2. Logs or other demonstration showing such persons no longer have access that the Responsible Entity determines is not necessary. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7287 | Protect against the use of unnecessary physical input/output ports used for network connectivity, console commands, or Removable Media. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.2. An example of evidence may include, but is not limited to, documentation showing types of protection of physical input/output ports, either logically through system configuration or physically using a port lock or signage. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7289 | At least once every 35 calendar days, evaluate security patches for applicability that have been released since the last evaluation from the source or sources identified in Part 2.1. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.2. An example of evidence may include, but is not limited to, an evaluation conducted by, referenced by, or on behalf of a Responsible Entity of security-related patches released by the documented sources at least once every 35 calendar days. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7293 | Mitigate the threat of detected malicious code. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.2. Examples of evidence may include, but are not limited to:• Records of response processes for malicious code detection• Records of the performance of these processes when malicious code is detected. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7303 | Detected failed access attempts and failed login attempts; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.1. Examples of evidence may include, but are not limited to, a paper or system generated listing of event types for which the BES Cyber System is capable of detecting and, for generated events, is configured to log. This listing must include the required types of events. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 41200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7305 | Generate alerts for security events that the Responsible Entity determines necessitates an alert, that includes, as a minimum, each of the following types of events (per Cyber Asset or BES Cyber System capability): |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.2. Examples of evidence may include, but are not limited to, paper or system-generated listing of security events that the Responsible Entity determined necessitate alerts, including paper or system generated list showing how alerts are configured. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7307 | Detected failure of Part 4.1 event logging. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.2. Examples of evidence may include, but are not limited to, paper or system-generated listing of security events that the Responsible Entity determined necessitate alerts, including paper or system generated list showing how alerts are configured. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 42200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 731 | State that SOLs shall not exceed associated Facility Ratings. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | FAC-010-2 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7311 | Identify and inventory all known enabled default or other generic account types, either by system, by groups of systems, by location, or by system type(s). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.2. An example of evidence may include, but is not limited to, a listing of accounts by account types showing the enabled or generic account types in use for the BES Cyber System. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7317 | Minimum password complexity that is the lesser of three or more different types of characters (e.g., uppercase alphabetic, lowercase alphabetic, numeric, non-alphanumeric) or the maximum complexity supported by the Cyber Asset. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 55200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7340 | Utilize at least one physical access control to allow unescorted physical access into each applicable Physical Security Perimeter to only those individuals who have authorized unescorted physical access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.2. An example of evidence may include, but is not limited to, language in the physical security plan that describes each Physical Security Perimeter and how unescorted physical access is controlled by one or more different methods and proof that unescorted physical access is restricted to only authorized individuals, such as a list of authorized individuals accompanied by access logs. | 2016-07-01 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 735 | Following the single Contingencies identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | FAC-010-2 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7350 | Require manual or automated logging of visitor entry into and exit from the Physical Security Perimeter that includes date and time of the initial entry and last exit, the visitor’s name, and the name of an individual point of contact responsible for the visitor, except during CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.2. An example of evidence may include, but is not limited to, language in a visitor control program that requires continuous escorted access of visitors within Physical Security Perimeters and additional evidence to demonstrate that the process was implemented, such as dated visitor logs that include the required information. | 2016-07-01 | [5 empty] | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7354 | Three phase currents and neutral currents. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 52000000 | NPCC-US |  | NPCC-US
2. | 7359 | Each Fault recorder shall have a minimum recording rate of 16 samples per cycle. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 62000000 | NPCC-US |  | NPCC-US
2. | 7362 | Neutral (residual) overcurrent set at 0.2 pu or less of rated CT secondary current. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 63200000 | NPCC-US |  | NPCC-US
2. | 7366 | Records dynamic disturbance information with consideration of the following facilities/locations: |  | RC | [11 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 72000000 | NPCC-US |  | NPCC-US
2. | 737 | Loss of any generator, line, transformer, or shunt device without a Fault. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 22200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7387 | The effectiveness of the UFLS program. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7389 | Monitor the following at each location listed in 1.1: |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 12000000 | NPCC-US |  | NPCC-US
2. | 7391 | Protective Relay tripping for all Protection Groups that operate to trip circuit breakers identified in 1.2.1. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 12200000 | NPCC-US |  | NPCC-US
2. | 7402 | Major Generation clusters. |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 72200000 | NPCC-US |  | NPCC-US
2. | 7409 | A minimum data sample rate of 960 samples per second, and a minimum data storage rate for RMS quantities of six (6) data points per second. |  | RC | [11 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 92000000 | NPCC-US |  | NPCC-US
2. | 741 | System reconfiguration through manual or automatic control or protection actions. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 23200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7412 | Rate of change of Power. |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 93200000 | NPCC-US |  | NPCC-US
2. | 7416 | Bus voltages such that normal bus maintenance activities do not interfere with DDR functionality. |  | RC | [11 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 102000000 | NPCC-US |  | NPCC-US
2. | 7421 | Summary of maintenance and testing procedures. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 142000000 | NPCC-US |  | NPCC-US
2. | 7428 | Request from other Transmission Owners, Generator Owners within NPCC. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 152000000 | NPCC-US |  | NPCC-US
2. | 7430 | Disturbance Data files shall be named in conformance with the latest revision of IEEE Standard C37.232. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 162000000 | NPCC-US |  | NPCC-US
2. | 7433 | Make and model of equipment. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 172000000 | NPCC-US |  | NPCC-US
2. | 7442 | The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). |  | TOP | [18 empty] | TOP |  |  |  | 2014-08-01 |  | 2015-11-12 |  |  |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7445 | Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. |  | GOP | [5 empty] | GOP | [16 empty] | 2014-08-01 |  | 2015-11-12 |  |  |  | 2720000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7447 | To mitigate the magnitude and duration of an IROL exceedance such that the IROL exceedance is relieved within the IROL’s Tv. |  | RC | [11 empty] | RC | [10 empty] | 2015-12-04 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7455 | Equal to or more negative than its Frequency Response Obligation when Frequency varies from 60 Hz by more than +/- 0.036 Hz. |  | BA, FRSG | BA |  |  | FRSG | [12 empty] | RSG | [5 empty] | 2015-11-13 |  | 2020-11-30 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7469 | Each adjacent Reliability Coordinator within the same Interconnection. |  | RC | [11 empty] | RC | [10 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7471 | Each adjacent Reliability Coordinator within the same Interconnection. |  | RC | [11 empty] | RC | [10 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7473 | Each Balancing Authority within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7479 | Electronic Security Perimeters (CIP-005) including Interactive Remote Access; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 748 | Selection of applicable Contingencies. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | FAC-010-2 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7490 | Each Balancing Authority within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  |  | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7494 | Each Transmission Operator that operates Facilities within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7499 | Each Transmission Operator that operates Facilities within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 75 | The Balancing Authorities that have a fixed schedule (B and C) but do not contain the Jointly Owned Unit shall not include their share of the governor droop response in their Frequency Bias Setting. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2015-03-31 |  |  | BAL-003-0.1b R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7502 | Its Transmission Operator. |  | DP |  | DP | [20 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7504 | Its Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7513 | The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-25 |  |  |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7517 | other locations where, during the seven years immediately prior to the date of the criminal history records check, the subject has resided for six consecutive months or more. If it is not possible to perform a full seven year criminal history records check, conduct as much of the seven year criminal history records check as possible and document the reason the full seven year criminal history records check could not be performed.If it is not possible to perform a full seven year criminal history records check, conduct as much of the seven year criminal history records check as possible and document the reason the full seven year criminal history records check could not be performed. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 32200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7528 | The BES interrupting device owner owns all or part of the Composite Protection System; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-12-04 |  | 2016-06-30 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7532 | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-07-01 |  | 2016-06-30 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7534 | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-12-04 |  | 2016-06-30 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7537 | The BES interrupting device owner owns all or part of the Composite Protection System; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-12-04 |  | 2017-04-01 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7542 | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-07-01 |  | 2017-04-01 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7544 | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-12-04 |  | 2017-04-01 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 755 | Each Reliability Coordinator and Transmission Operator that operates any portion of the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | FAC-010-2 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7551 | The BES interrupting device owner owns all or part of the Composite Protection System; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-11-19 |  | 2021-03-31 |  | 4.2. Facilities:4.2.1 Protection Systems for BES Elements, with the following exclusions:4.2.1.1 Non-protective functions that are embedded within a Protection System.4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS).4.2.1.4 Remedial Action Schemes (RAS).4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7556 | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-04-02 |  | 2021-03-31 |  | 4.2. Facilities:4.2.1 Protection Systems for BES Elements, with the following exclusions:4.2.1.1 Non-protective functions that are embedded within a Protection System.4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS).4.2.1.4 Remedial Action Schemes (RAS).4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7557 | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for which that backup protection was provided. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-11-19 |  | 2021-03-31 |  | 4.2. Facilities:4.2.1 Protection Systems for BES Elements, with the following exclusions:4.2.1.1 Non-protective functions that are embedded within a Protection System.4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS).4.2.1.4 Remedial Action Schemes (RAS).4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7565 | A review of the developed Protection System settings. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.1.3. Distribution Provider (that owns Protection Systems identified in the Facilities section 4.2 below)4.2. Facilities: Protection Systems installed to detect and isolate Faults on BES Elements. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7568 | Respond to any owner(s) that provided its proposed Protection System settings pursuant to Requirement R1, Part 1.3.1 by identifying any coordination issue(s) or affirming that no coordination issue(s) were identified. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.1.3. Distribution Provider (that owns Protection Systems identified in the Facilities section 4.2 below)4.2. Facilities: Protection Systems installed to detect and isolate Faults on BES Elements. |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7580 | Include the applicable monitored Component attributes applied to each Protection System, Automatic Reclosing, and Sudden Pressure Relaying Component Type consistent with the maintenance intervals specified in Tables 1-1 through 1-5, Table 2, Table 3, Table 4-1 through 4-3, and Table 5 where monitoring is used to extend the maintenance intervals beyond those specified for unmonitored Protection System, Automatic Reclosing, and Sudden Pressure Relaying Components. |  | DP, DP-UFLS, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-12-18 |  |  |  | 4.2.1 Protection Systems and Sudden Pressure Relaying that are installed for the purpose of detecting Faults on BES Elements (lines, buses, transformers, etc.)4.2.2 Protection Systems used for underfrequency load-shedding systems installed per ERO underfrequency load-shedding requirements.4.2.3 Protection Systems used for undervoltage load-shedding systems installed to prevent system voltage collapse or voltage instability for BES reliability.4.2.4 Protection Systems installed as a Remedial Action Scheme (RAS) for BES reliability.4.2.5 Protection Systems and Sudden Pressure Relaying for generator Facilities that are part of the BES, except for generators identified through Inclusion I4 of the BES definition, including:4.2.5.1 Protection Systems that act to trip the generator either directly or via lockout or auxiliary tripping relays.4.2.5.2 Protection Systems and Sudden Pressure Relaying for generator step-up transformers for generators that are part of the BES.4.2.5.3 Protection Systems and Sudden Pressure Relaying for station service or excitation transformers connected to the generator bus of generators which are part of the BES, that act to trip the generator either directly or via lockout or tripping auxiliary relays.4.2.6 Protection Systems and Sudden Pressure Relaying for the following BES generator Facilities for dispersed power producing resources identified through Inclusion I4 of the BES definition:4.2.6.1 Protection Systems and Sudden Pressure Relaying for Facilities used in aggregating dispersed BES generation from the point where those resources aggregate to greater than 75 MVA to a common point of connection at 100kV or above.4.2.7 Automatic Reclosing , including:4.2.7.1 Automatic Reclosing applied on the terminals of Elements connected to the BES bus located at generating plant substations where the total installed gross generating plant capacity is greater than the gross capacity of the largest BES generating unit within the Balancing Authority Area or, if a member of a Reserve Sharing Group, the largest generating unit within the Reserve Sharing Group. 4.2.7.2 Automatic Reclosing applied on the terminals of all BES Elements at substations one bus away from generating plants specified in Section 4.2.7.1 when the substation is less than 10 circuit-miles from the generating plant substation.4.2.7.3 Automatic Reclosing applied as an integral part of an RAS specified in Section 4.2.4. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7582 | A timetable for providing the data. (A minimum of 30 calendar days must be allowed for responding to the request). |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-02-18 |  | 2021-03-31 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7585 | Monthly and annual integrated peak hour Demands in megawatts for the prior calendar year. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7591 | Monthly forecast Net Energy for Load in gigawatthours for the next two calendar years. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” |  | 14200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7597 | The Demand and energy effects of controllable and dispatchable Demand Side Management under the control or supervision of the System Operator. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” |  | 15200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 760 | State that SOLs shall not exceed associated Facility Ratings. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-011-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7609 | document all Reportable Balancing Contingency Events using CR Form 1. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2017-04-03 |  | 2017-12-31 |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7612 | 1.3.2 the Responsible Entity experiences:• multiple Contingencies where the combined MW loss exceeds its Most Severe Single Contingency and that are defined as a single Balancing Contingency Event, or • multiple Balancing Contingency Events within the sum of the time periods defined by the Contingency Event Recovery Period and Contingency Reserve Restoration Period whose combined magnitude exceeds the Responsible Entity's Most Severe Single Contingency. |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2017-12-31 |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7622 | with a minimum accuracy of 0.001 Hz. |  | BA | BA | [21 empty] | 2017-11-27 | [5 empty] | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7624 | a time synchronized common source to determine hourly megawatt-hour values agreed-upon to aid in the identification and mitigation of errors. |  | BA | BA | [21 empty] | 2017-11-27 | [5 empty] | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7626 | transmission Facilities; and |  | TO | [22 empty] | 2019-01-01 | [5 empty] | 11000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7627 | transmission Facilities; and |  | TO | [22 empty] | 2019-01-01 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7630 | Procedures for notifying those responsible for the reliability of affected system(s) of new or materially modified existing interconnections. |  | TO | [22 empty] | 2019-01-01 | [5 empty] | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7633 | Procedures for notifying those responsible for the reliability of affected system(s) of new interconnections. |  | GO | [22 empty] | 2019-01-01 | [5 empty] | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 764 | Following the single Contingencies identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading Outages or uncontrolled separation shall not occur. |  | RC | [11 empty] | RC | [10 empty] | 2008-05-29 |  | 2009-04-28 |  |  | FAC-011-1 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7640 | An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, (Footnote: Multiple Sustained Outages on an individual line, if caused by the same vegetation, will be reported as one outage regardless of the actual number of outages within a 24-hour period.) |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:4.1.1. Applicable Transmission Owners4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.4.1.2. Applicable Generator Owners4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.2.1. Each overhead transmission line operated at 200kV or higher.4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:4.3.1.1. Operated at 200kV or higher; or4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7644 | An encroachment due to a fall-in from inside the ROW that caused a vegetation-related Sustained Outage, |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:4.1.1. Applicable Transmission Owners4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.4.1.2. Applicable Generator Owners4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.2.1. Each overhead transmission line operated at 200kV or higher.4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:4.3.1.1. Operated at 200kV or higher; or4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7648 | Inter-relationships between vegetation growth rates, vegetation control methods, and inspection frequency. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:4.1.1. Applicable Transmission Owners4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.4.1.2. Applicable Generator Owners4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.2.1. Each overhead transmission line operated at 200kV or higher.4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:4.3.1.1. Operated at 200kV or higher; or4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7649 | Circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator OwnerFootnote: Circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner include but are not limited to natural disasters such as earthquakes, fires, tornados, hurricanes, landslides, ice storms, floods, or major storms as defined either by the TO or GO or an applicable regulatory body. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:4.1.1. Applicable Transmission Owners4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.4.1.2. Applicable Generator Owners4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.2.1. Each overhead transmission line operated at 200kV or higher.4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:4.3.1.1. Operated at 200kV or higher; or4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 71000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 766 | Loss of any generator, line, transformer, or shunt device without a Fault. |  | RC | [11 empty] | RC | [10 empty] | 2008-10-01 |  | 2009-04-28 |  |  |  | 22200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7666 | When modeling contingencies the system shall demonstrate transient, dynamic and voltage stability, with no Transmission Element modeled above its Emergency Rating. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7668 | Where it is impossible to actually simulate a reliability-limited flow in a direction counter to prevailing flows (on an alternating current Transmission line), set the TTC for the non-prevailing direction equal to the TTC in the prevailing direction. If the TTC in the prevailing flow direction is dependent on a Remedial Action Scheme (RAS), set the TTC for the non-prevailing flow direction equal to the greater of the maximum flow that can be simulated in the non-prevailing flow direction or the maximum TTC that can be achieved in the prevailing flow direction without use of a RAS. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7685 | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System. |  | PCPA | [9 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 220000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7688 | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-2 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 320000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7691 | Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES |  | PCPA | [9 empty] | PA | [12 empty] | 2015-10-01 |  | 2017-09-30 |  |  |  | 332000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7695 | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 420000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 770 | Interruption of other network customers, only if the system has already been adjusted, or is being adjusted, following at least one prior outage, or, if the real-time operating conditions are more adverse than anticipated in the corresponding studies, e.g., load greater than studied. |  | RC | [11 empty] | RC | [10 empty] | 2008-10-01 |  | 2009-04-28 |  |  |  | 23200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7703 | The effectiveness of the UFLS program |  | PCPA | [9 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 2020000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7713 | Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-11-13 |  | 2017-09-25 |  |  |  | 2720000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7715 | Performing maintenance and testing up to a maximum of seven calendar days per calendar quarter. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2015-03-03 |  | 2018-09-05 |  |  |  | 12000000 | WECC-US | [5 empty] | WECC-US
2. | 7726 | Provisions to indicate the quality of Real-time data to the System Operator; and |  | TOP | [18 empty] | TOP |  |  |  | 2016-09-22 |  | 2018-03-31 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7730 | Provisions to indicate the quality of Real-time data to the System Operator; and |  | BA | BA | [21 empty] | 2016-09-22 |  | 2018-03-31 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7734 | Provisions to indicate the quality of analysis used in its Real-time Assessments; and |  | TOP | [18 empty] | TOP |  |  |  | 2016-09-22 |  | 2018-03-31 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7740 | Provisions to indicate the quality of Real-time data to the System Operator; and |  | RC | [11 empty] | RC | [10 empty] | 2016-09-22 |  | 2018-03-31 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7743 | Provisions to indicate the quality of analysis used in its Real-time Assessments; and |  | RC | [11 empty] | RC | [10 empty] | 2016-09-22 |  | 2018-03-31 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 775 | Selection of applicable Contingencies. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-011-1 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7752 | The RAS avoids adverse interactions with other RAS, and protection and control systems. |  | PCPA | [9 empty] | PA | [12 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 41200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7756 | Cascading shall not occur. |  | PCPA | [9 empty] | PA | [12 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 41420000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7761 | Provide the results of the RAS evaluation including any identified deficiencies to each reviewing Reliability Coordinator and RAS-entity, and each impacted Transmission Planner and Planning Coordinator. |  | PCPA | [9 empty] | PA | [12 empty] | 2026-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7765 | The RAS responded as designed. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 51200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7768 | Provide the results of RAS operational performance analysis that identified any deficiencies to its reviewing Reliability Coordinator(s). |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-11-27 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7772 | Update the CAP if actions or timetables change. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-11-27 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7777 | Require its operating personnel that issue an oral two-party, person-to-person Operating Instruction to take one of the following actions:• Confirm the receiver’s response if the repeated information is correct.• Reissue the Operating Instruction if the repeated information is incorrect or if requested by the receiver.• Take an alternative action if a response is not received or if the Operating Instruction was not understood by the receiver. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2015-06-22 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7783 | Assess the effectiveness of its documented communications protocols in Requirement R1 for its operating personnel that issue and receive Operating Instructions and modify its documented communication protocols, as necessary. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2015-06-22 | [5 empty] | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7787 | Each adjacent Reliability Coordinator within the same Interconnection. |  | RC | [11 empty] | RC | [10 empty] | 2016-10-28 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7790 | Each adjacent Reliability Coordinator within the same Interconnection. |  | RC | [11 empty] | RC | [10 empty] | 2016-10-28 | [5 empty] | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7793 | Each Balancing Authority within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2016-10-28 | [5 empty] | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7800 | Each Balancing Authority within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2016-10-28 | [5 empty] | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7805 | Each Transmission Operator that operates Facilities within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2016-10-28 | [5 empty] | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7811 | Each Transmission Operator that operates Facilities within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2016-10-28 | [5 empty] | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7815 | Its Transmission Operator. |  | DP |  | DP | [20 empty] | 2016-10-28 | [5 empty] | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7818 | Its Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2016-10-28 | [5 empty] | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7826 | The UVLS Program is integrated through coordination with generator voltage ride-through capabilities and other protection and control systems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage-based load shedding programs. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-11-19 | [5 empty] | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7829 | Performing maintenance and testing up to a maximum of seven calendar days per calendar quarter. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-04-01 |  | 2017-06-30 |  |  |  | 12000000 | WECC-US | [5 empty] | WECC-US
2. | 784 | Each Planning Authority and Transmission Planner that models any portion of the Reliability Coordinator’s Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-011-1 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7842 | Transmission Operators shall adjust the SOL and operate the facilities within established limits. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf..4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. |  | 23220000 | WECC-US | [5 empty] | WECC-US
2. | 7845 | Identify each of the medium impact BES Cyber Systems according to Attachment 1, Section 2, if any, at each asset; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-12-27 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency load shedding (UFLS) or undervoltage load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-002-5.1a: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7849 | Have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 at least once every 15 calendar months, even if it has no identified items in Requirement R1. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-12-27 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency load shedding (UFLS) or undervoltage load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-002-5.1a: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7853 | Provisions to indicate the quality of Real-time data to the System Operator; and |  | RC | [11 empty] | RC | [10 empty] | 2016-12-14 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7858 | Provisions to indicate the quality of analysis used in its Real-time Assessments; and |  | RC | [11 empty] | RC | [10 empty] | 2016-12-14 | [5 empty] | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7862 | Provisions to indicate the quality of Real-time data to the System Operator; and |  | TOP | [18 empty] | TOP |  |  |  | 2016-12-14 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7866 | Provisions to indicate the quality of Real-time data to the System Operator; and |  | BA | BA | [21 empty] | 2016-12-14 | [5 empty] | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7871 | Provisions to indicate the quality of analysis used in its Real-time Assessments; and |  | TOP | [18 empty] | TOP |  |  |  | 2016-12-14 | [5 empty] | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7876 | Comprised of any combination of the reserve types specified below:• Operating Reserve – Spinning• Operating Reserve - Supplemental • Interchange Transactions designated by the Source Balancing Authority as Operating Reserve – Supplemental • Reserve held by other entities by agreement that is deliverable on Firm Transmission Service• A resource, other than generation or load, that can provide energy or reduce energy consumption • Load, including demand response resources, Demand-Side Management resources, Direct Control Load Management, Interruptible Load or Interruptible Demand, or any other Load made available for curtailment by the Balancing Authority or the Reserve Sharing Group via contract or agreement.• All other load, not identified above, once the Reliability Coordinator has declared an energy emergency alert signifying that firm load interruption is imminent or in progress. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Part 1.2. Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates compliance with Requirement R1, Part 1.2. Evidence may include, but is not limited to, documentation that reserves were comprised of the types listed in Requirement R1, Part 1.2 for purposes of meeting the Contingency Reserve obligation of Requirement R1. Additionally, for purposes of the last bullet of Requirement R1, Part 1.2, evidence of compliance may include, but is not limited to, documentation that the reliability coordinator had issued an energy emergency alert, indicating that firm Load interruption was imminent or was in progress. | 2017-01-24 |  | 2021-06-27 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity.4.2.1.The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group.4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | 12000000 | WECC-US | [5 empty] | WECC-US
2. | 7881 | Reserve that is capable of fully responding within ten minutes. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2017-01-24 |  | 2021-06-27 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity.4.2.1.The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group.4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | 22000000 | WECC-US | [5 empty] | WECC-US
2. | 7888 | A summary description of the elements required to support the backup functionality. These elements shall include: |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 789 | State that SOLs shall not exceed associated Facility Ratings. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | FAC-011-2 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7890 | Data exchange capabilities. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2019-04-01 | [5 empty] | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7899 | Actions to manage the risk to the BES during the transition from primary to backup functionality, as well as during outages of the primary or backup functionality. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2019-04-01 | [5 empty] | 16200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7909 | The backup functionality for a minimum of two continuous hours. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7913 | Criteria and conditions for re-establishing interconnections with other Transmission Operators within its Reliability Coordinator Area, with Transmission Operators in other Reliability Coordinator Areas, and with other Reliability Coordinators. |  | RC | [11 empty] | RC | [10 empty] | 2018-03-26 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7928 | Re-establishing the Interconnection. |  | RC | [11 empty] | RC | [10 empty] | 2018-03-26 | [5 empty] | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 793 | Following the single Contingencies identified in Requirement 2.2.1 through Requirement 2.2.3, the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | FAC-011-2 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7933 | A description of how all Agreements or mutually-agreed upon procedures or protocols for off-site power requirements of nuclear power plants, including priority of restoration, will be fulfilled during System restoration. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7945 | Prior to implementing a planned permanent BES modification subject to its Reliability Coordinator approval requirements per EOP-006. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7949 | The location and magnitude of Loads required to control voltages and frequency within acceptable operating limits. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 795 | Loss of any generator, line, transformer, or shunt device without a Fault. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 22200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7953 | A list of required tests including: |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7955 | The ability to energize a bus. If it is not possible to energize a bus during the test, the testing entity must affirm that the unit has the capability to energize a bus such as verifying that the breaker close coil relay can be energized with the voltage and frequency monitor controls disconnected from the synchronizing circuits. |  | TOP | [18 empty] | TOP |  |  |  | 2019-04-01 | [5 empty] | 72200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7959 | Restoration priorities. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7972 | The procedures documented in Requirement R12 |  | GOP | [5 empty] | GOP | [16 empty] | 2018-03-26 | [5 empty] | 152000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7978 | PSS output limits shall be set to provide at least ±5% of the synchronous machine’s nominal terminal voltage. |  | GO | [22 empty] | 2017-04-28 |  | 2017-09-25 |  |  |  | 32000000 | WECC-US | [5 empty] | WECC-US
2. | 7987 | For its assets identified in CIP-002 containing low impact BES Cyber Systems, if any: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2018-06-25 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7989 | Electronic Security Perimeters (CIP-005) including Interactive Remote Access; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 799 | Interruption of other network customers, (a) only if the system has already been adjusted, or is being adjusted, following at least one prior outage, or (b) if the real-time operating conditions are more adverse than anticipated in the corresponding studies |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 23200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 7999 | Physical security controls; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8024 | Monitor the status of Remedial Action Schemes within its Transmission Operator Area; |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-17 |  | 2021-03-31 |  |  |  | 102000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 804 | Selection of applicable Contingencies |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | FAC-011-2 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8044 | document all Reportable Balancing Contingency Events using CR Form 1. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2017-10-02 |  | 2019-03-31 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8047 | the Responsible Entity experiences:• multiple Contingencies where the combined MW loss exceeds its Most Severe Single Contingency and that are defined as a single Balancing Contingency Event, or • multiple Balancing Contingency Events within the sum of the time periods defined by the Contingency Event Recovery Period and Contingency Reserve Restoration Period whose combined magnitude exceeds the Responsible Entity's Most Severe Single Contingency. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2018-01-01 |  | 2019-03-31 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8059 | The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). |  | TOP | [18 empty] | TOP |  |  |  | 2017-09-26 |  | 2018-12-31 |  |  |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8069 | Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. |  | GOP | [5 empty] | GOP | [16 empty] | 2017-09-26 |  | 2018-12-31 |  |  |  | 2720000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8073 | When instructed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2017-09-26 | [5 empty] | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8081 | Available fixed tap ranges. |  | GO | [22 empty] | 2017-09-26 | [5 empty] | 51200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8087 | One or more process(es) used in procuring BES Cyber Systems that address the following, as applicable: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and4.1.2.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and4.2.1.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers4.2.2.1. All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-013-1:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the identification and categorization process required by CIP-002-5, or any subsequent version of that Reliability Standard. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8089 | Coordination of responses to vendor-identified incidents related to the products or services provided to the Responsible Entity that pose cyber security risk to the Responsible Entity; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and4.1.2.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and4.2.1.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers4.2.2.1. All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-013-1:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the identification and categorization process required by CIP-002-5, or any subsequent version of that Reliability Standard. |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8098 | All External Routable Connectivity must be through an identified Electronic Access Point (EAP). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, network diagrams showing all external routable communication paths and the identified EAPs. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-005-6:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 81 | Each Balancing Authority shall report its Frequency Bias Setting, and method for determining that setting, to the NERC Operating Committee. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2009-05-12 |  |  | BAL-003-0a R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8104 | For all Interactive Remote Access sessions, utilize encryption that terminates at an Intermediate System. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, architecture documents detailing where encryption initiates and terminates. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-005-6:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8111 | Any commercially available or open-source application software (including version) intentionally installed; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8115 | Authorize and document changes that deviate from the existing baseline configuration. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to: • A change request record and associated electronic authorization (performed by the individual or group with the authority to authorize the change) in a change management system for each change; or• Documentation that the change was performed in accordance with the requirement. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8119 | Following the change, verify that required cyber security controls determined in 1.4.1 are not adversely affected; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 14200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8123 | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 15200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8126 | Verify the integrity of the software obtained from the software source. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 16200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 813 | Each Planning Authority and Transmission Planner that models any portion of the Reliability Coordinator’s Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | FAC-011-2 R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8131 | Where technically feasible, at least once every 36 calendar months: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a document listing the date of the assessment (performed at least once every 36 calendar months), the output of the tools used to perform the assessment, and a list of differences between the production and test environments with descriptions of how any differences were accounted for in conducting the assessment. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8133 | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 32200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8141 | Shed load with a minimum of three frequency set points. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2017-10-16 | [5 empty] | 22000000 | SERC-US |  |  |  | SERC-US
2. | 8150 | The amount of load in each load shedding step shall be within -1.0 and +3.0 of the percentage specified by the Planning Coordinator (for example, if the specified percentage step load shed is 12%, the allowable range is 11 to 15%). |  | DP, DP-UFLS, TO |  | DP | [20 empty] | 2017-10-16 | [5 empty] | 42000000 | SERC-US |  |  |  | SERC-US
2. | 8154 | The amount of total UFLS load shall be within ± 5.0 of the percentage specified by the Planning Coordinator for the total UFLS load in the UFLS scheme. |  | DP, DP-UFLS, TO |  | DP | [20 empty] | 2017-10-16 | [5 empty] | 52000000 | SERC-US |  |  |  | SERC-US
2. | 8158 | Total clearing time associated with each set point (sec). This includes the time from when frequency reaches the set point and ends when the breaker opens. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-16 | [5 empty] | 72000000 | SERC-US |  |  |  | SERC-US
2. | 8162 | Total clearing time associated with each set point (sec). This is defined as the time that begins when frequency reaches the set point and ends when the breaker opens. If inverse time underfrequency relays are used, provide the total clearing time at 59.0, 58.5, 58.0, and 57.0 Hz. |  | DP-UFLS, GO |  | DP | [20 empty] | 2017-10-16 | [5 empty] | 82000000 | SERC-US |  |  |  | SERC-US
2. | 8167 | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8171 | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-3 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8175 | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-3 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 818 | A definition stating whether the methodology is applicable to the planning horizon or the operating horizon. |  | PCPA, RC | [9 empty] | PA |  | RC | [12 empty] | 2013-03-31 |  |  | FAC-012-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8190 | The effectiveness of the UFLS program. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8196 | For UFLS design assessments performed under Requirement R12, the Corrective Action Plan shall be developed within the two-year time frame identified in Requirement R12. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 152000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8200 | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 220000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8203 | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-3 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 320000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8206 | Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 332000 | WECC-US | [5 empty] | WECC-US
2. | 821 | System demand |  | PCPA, RC | [9 empty] | PA |  | RC | [12 empty] | 2013-03-31 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8210 | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-3 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 420000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8218 | The effectiveness of the UFLS program |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 2020000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8223 | The planning reserve margin developed from R1.1 shall be expressed as a percentage of the median forecast peak Net Internal Demand (planning reserve margin).The median forecast is expected to have a 50% probability of being too high and 50% probability of being too low (50:50). |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 11200000 | RF-US |  |  | RF-US
2. | 8224 | Be performed or verified separately for each of the following planning years: |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-16 | [5 empty] | 12000000 | RF-US |  |  | RF-US
2. | 8226 | Perform an analysis or verification at a minimum for one year in the 2 through 5 year period and at a minimum one year in the 6 though 10 year period. |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 12200000 | RF-US |  |  | RF-US
2. | 8232 | Load forecast uncertainty (reflects variability in the Load forecast due to weather and regional economic forecasts). |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 13120000 | RF-US |  |  | RF-US
2. | 8237 | Resource characteristics: |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 13200000 | RF-US |  |  | RF-US
2. | 8239 | Seasonal resource ratings |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 13220000 | RF-US |  |  | RF-US
2. | 8249 | Common mode outages that affect resource availability |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 14200000 | RF-US |  |  | RF-US
2. | 826 | Each Planning Authority and Transmission Planner that models any portion of the Reliability Coordinator’s Reliability Coordinator Area. |  | RC | [11 empty] | RC | [12 empty] | 2013-03-31 |  |  | FAC-012-1 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8261 | This documentation shall include the Planning Reserve margin calculated per requirement R1.1 for each of the three years in the analysis. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-16 | [5 empty] | 22000000 | RF-US |  |  | RF-US
2. | 8268 | PSS output limits shall be set to provide at least ±5% of the synchronous machine’s nominal terminal voltage. |  | GO | [22 empty] | 2017-09-26 |  |  |  | 5. Facilities: This standard applies to synchronous generators, connected to the Bulk Electric System, that meet the definition of Commercial Operation. |  | 32000000 | WECC-US | [5 empty] | WECC-US
2. | 830 | Each Adjacent Planning Authority and each Planning Authority that indicated a reliability-related need for the methodology. |  | PCPA | [9 empty] | PA | [14 empty] | 2013-03-31 |  |  | FAC-012-1 R3. | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8332 | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  |  | 41200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8333 | The study or studies shall be conducted based on the benchmark GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning benchmark GMD event contained in Table 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  |  | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8338 | The effective GIC time series, GIC(t), calculated using the benchmark GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 5.1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-01-01 |  | 2019-06-30 |  |  |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8341 | Document assumptions used in the analysis; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2019-06-30 |  |  |  | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8346 | Be developed within one year of completion of the benchmark GMD Vulnerability Assessment. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  |  | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8349 | Specify implementation of hardware mitigation, if any, within four years of development of the CAP. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  |  | 73200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8352 | Description of the original CAP, and any previous changes to the CAP, with the associated timetable(s) for implementing the selected actions in Part 7.1; and |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  |  | 74200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8359 | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  |  | 81200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 836 | The Planning Authority shall provide its Transfer Capabilities to its associated Reliability Coordinator(s) and Regional Reliability Organization(s), and to the Transmission Planners and Transmission Service Provider(s) that work in its Planning Authority Area. |  | PCPA | [9 empty] | PA | [12 empty] | 2007-06-18 |  | 2013-03-31 |  |  | FAC-013-1 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8360 | The study or studies shall be conducted based on the supplemental GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning supplemental GMD event contained in Table 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  |  | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8366 | The effective GIC time series, GIC(t), calculated using the supplemental GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 9.1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-01-01 |  | 2019-06-30 |  |  |  | 92000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8369 | Document assumptions used in the analysis; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2019-06-30 |  |  |  | 102000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8377 | For generation-only Balancing Authorities, 150% of the previous calendar year’s integrated hourly peak generation. |  | BA | BA | [21 empty] | 2018-05-30 | [5 empty] | 12000000 | WECC-US | [5 empty] | WECC-US
2. | 8382 | PIIaccum, |  | BA | BA | [21 empty] | 2018-05-30 | [5 empty] | 42000000 | WECC-US | [5 empty] | WECC-US
2. | 8398 | Transmission operations |  | RC | [11 empty] | RC | [10 empty] | 2019-07-01 | [5 empty] | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 84 | The Balancing Authority may use a variable (linear or non-linear) bias value, which is based on a variable function of Tie Line deviation to Frequency Deviation. The Balancing Authority shall determine the variable frequency bias value by analyzing Frequency Response as it varies with factors such as load, generation, governor characteristics, and frequency. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2009-05-12 |  |  | BAL-003-0a R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8408 | Emergency preparedness and operations |  | TOP | [18 empty] | TOP |  |  |  | 2019-07-01 | [5 empty] | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8412 | Certificates• Reliability Operator• Balancing, Interchange and Transmission Operator• Transmission Operator |  | TOP | [18 empty] | TOP |  |  |  | 2018-11-21 | [5 empty] | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8416 | Emergency preparedness and operations |  | BA | BA | [21 empty] | 2019-07-01 | [5 empty] | 31200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8419 | Certificates• Reliability Operator• Balancing, Interchange and Transmission Operator• Balancing and Interchange Operator |  | BA | BA | [21 empty] | 2018-11-21 | [5 empty] | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8424 | document all Reportable Balancing Contingency Events using CR Form 1. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2019-04-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8427 | the Responsible Entity experiences:• multiple Contingencies where the combined MW loss exceeds its Most Severe Single Contingency and that are defined as a single Balancing Contingency Event, or • multiple Balancing Contingency Events within the sum of the time periods defined by the Contingency Event Recovery Period and Contingency Reserve Restoration Period whose combined magnitude exceeds the Responsible Entity's Most Severe Single Contingency. |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2019-04-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8431 | Identification of where the Responsible Entity applied security protection for transmitting Real-time Assessment and Real-time monitoring data between Control Centers; and |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-04-13 |  |  |  | 4.2. Exemptions: The following are exempt from Reliability Standard CIP-012-1:4.2.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.2. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3. A Control Center that transmits to another Control Center Real-time Assessment or Real-time monitoring data pertaining only to the generation resource or Transmission station or substation co-located with the transmitting Control Center. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 844 | The value of the IROL and its associated Tv. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-01 |  | 2009-04-28 |  |  |  | 51200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8441 | The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). |  | TOP | [18 empty] | TOP |  |  | For part 5.2, the Transmission Operator shall have evidence it provided notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). | 2018-10-15 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8449 | Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. |  | GOP | [5 empty] | GOP | [16 empty] | 2018-10-15 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | 2620000 | WECC-US | [5 empty] | WECC-US
2. | 8454 | New planned Facilities and changes to existing Facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8461 | System Off-Peak Load for one of the five years. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8465 | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by the following annual current study, supplemented with qualified past studies as indicated in Requirement R2, Part 2.6: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-04-13 |  | 2020-06-10 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 847 | The Transmission Operator shall provide any SOLs it developed to its Reliability Coordinator and to the Transmission Service Providers that share its portion of the Reliability Coordinator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2008-02-08 |  | 2009-04-28 |  |  | FAC-014-1 R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8470 | System Off-Peak Load for one of the five years. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  |  | 24200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8478 | Include actions to resolve performance deficiencies identified in multiple sensitivity studies or provide a rationale for why actions were not necessary. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  |  | 27200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8483 | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  |  | 28200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8492 | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R3, Part 3.5. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-04-13 |  | 2020-06-10 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8495 | Simulate the expected automatic operation of existing and planned devices designed to provide steady state control of electrical system quantities when such devices impact the study area. These devices may include equipment such as phase-shifting transformers, load tap changing transformers, and switched capacitors and inductors. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  |  | 33200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8497 | Tripping of Transmission elements where relay loadability limits are exceeded. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  |  | 33120000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8508 | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-3 - Attachment 1A, either for 60 seconds or until a steady-state condition between 59.0 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 12000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8512 | Overfrequency trip settings of individual generating units that are part of Quebec BES plants/facilities that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-3 - Attachment 1A, and |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 120000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 852 | If the Planning Authority does not identify any stability-related multiple contingencies, the Planning Authority shall so notify the Reliability Coordinator. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-014-1 R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8520 | One or more processes: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of Cyber Security Incident response plan(s) that provide guidance or thresholds for determining which Cyber Security Incidents are also Reportable Cyber Security Incidents or a Cyber Security Incident that is determined to be an attempt to compromise a system identified in the “Applicable Systems” column including justification for attempt determination criteria and documented processes for notification. | 2019-06-20 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8522 | To determine if an identified Cyber Security Incident is:• A Reportable Cyber Security Incident; or• An attempt to compromise, as determined by applying the criteria from Part 1.2.1, one or more systems identified in the “Applicable Systems” column for this Part; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8528 | Use the Cyber Security Incident response plan(s) under Requirement R1 when responding to a Reportable Cyber Security Incident, responding to a Cyber Security Incident that attempted to compromise a system identified in the “Applicable Systems” column for this Part, or performing an exercise of a Reportable Cyber Security Incident. Document deviations from the plan(s) taken during the response to the incident or exercise. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, incident reports, logs, and notes that were kept during the incident response process, and follow-up documentation that describes deviations taken from the plan during the incident response or exercise. | 2019-06-20 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8534 | Update the Cyber Security Incident response plan based on any documented lessons learned associated with the plan; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | 31200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8536 | No later than 60 calendar days after a change to the roles or responsibilities, Cyber Security Incident response groups or individuals, or technology that the Responsible Entity determines would impact the ability to execute the plan: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to:1. Dated and revised Cyber Security Incident response plan with changes to the roles or responsibilities, responders or technology; and2. Evidence of plan update distribution including, but not limited to:• Emails;• USPS or other mail service;• Electronic distribution system; or • Training sign-in sheets. | 2019-06-20 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8538 | Notify each person or group with a defined role in the Cyber Security Incident response plan of the updates. | [24 empty] | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | 32200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8541 | The attack vector used; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | 41200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8543 | After the Responsible Entity’s determination made pursuant to documented process(es) in Requirement R1, Part 1.2, provide initial notification within the following timelines:• One hour after the determination of a Reportable Cyber Security Incident.• By the end of the next calendar day after determination that a Cyber Security Incident was an attempt to compromise a system identified in the “Applicable Systems” column for this Part. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of notices to the E-ISAC and NCCIC. | 2019-06-20 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8554 | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 41200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8555 | The study or studies shall be conducted based on the benchmark GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning benchmark GMD event contained in Table 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2020-10-05 |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8560 | The effective GIC time series, GIC(t), calculated using the benchmark GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 5.1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-01-01 |  | 2020-10-05 |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8566 | Document assumptions used in the analysis; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2020-10-05 |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8571 | Be developed within one year of completion of the benchmark GMD Vulnerability Assessment. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2020-10-05 |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8576 | Specify implementation of hardware mitigation, if any, within four years of development of the CAP. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 73200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8578 | Description of the original CAP, and any previous changes to the CAP, with the associated timetable(s) for implementing the selected actions in Part 7.1; and |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 74200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8583 | The study or studies shall be conducted based on the supplemental GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning supplemental GMD event contained in Table 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2020-10-05 |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8587 | System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 81200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8591 | The effective GIC time series, GIC(t), calculated using the supplemental GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 9.1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-01-01 |  | 2020-10-05 |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 92000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8599 | Document assumptions used in the analysis; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2020-10-05 |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 102000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 860 | The value of the IROL and its associated Tv. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 | [5 empty] | 51200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8607 | The Responsible Entity shall document that testing is performed in a manner that reflects the production environment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 12000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC | MRO-US | NPCC-US |  |  |  | WECC-US
2. | 861 | The Transmission Operator shall provide any SOLs it developed to its Reliability Coordinator and to the Transmission Service Providers that share its portion of the Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 | [5 empty] | 51300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8611 | The Responsible Entity shall disable other ports and services, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 22000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC | MRO-US | NPCC-US |  |  |  | WECC-US
2. | 8615 | The Responsible Entity shall document the implementation of security patches. In any case where the patch is not installed, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 32000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC | MRO-US | NPCC-US |  |  |  | WECC-US
2. | 8618 | The Responsible Entity shall document and implement a process for the update of anti-virus and malware prevention “signatures.” The process must address testing and installing the signatures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 42000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC | MRO-US | NPCC-US |  |  |  | WECC-US
2. | 8622 | The Responsible Entity shall establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 51200000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC | MRO-US | NPCC-US |  |  |  | WECC-US
2. | 8624 | The Responsible Entity shall implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 52000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC | MRO-US | NPCC-US |  |  |  | WECC-US
2. | 8626 | The Responsible Entity shall identify those individuals with access to shared accounts. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 52200000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC | MRO-US | NPCC-US |  |  |  | WECC-US
2. | 863 | The Transmission Operator shall provide any SOLs it developed to its Reliability Coordinator and to the Transmission Service Providers that share its portion of the Reliability Coordinator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2009-04-29 |  |  |  |  | FAC-014-2 R5. | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8630 | Each password shall consist of a combination of alpha, numeric, and “special” characters. | [30 empty] | 53200000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC | MRO-US | NPCC-US |  |  |  | WECC-US
2. | 8634 | The security monitoring controls shall issue automated or manual alerts for detected Cyber Security Incidents. | [30 empty] | 62000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC | MRO-US | NPCC-US |  |  |  | WECC-US
2. | 8640 | Prior to redeployment of such assets, the Responsible Entity shall, at a minimum, erase the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 72000000 | MRO-MB | MRO-US
2. | 8644 | A review to verify that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter are enabled; | [30 empty] | 82000000 | MRO-MB | MRO-US
2. | 8650 | Specify implementation of hardware mitigation, if any, within four years of the later of the development of the CAP or receipt of regulatory approvals, if required. | [24 empty] | 2019-07-01 |  |  |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 732000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC | MRO-US | NPCC-US |  |  |  | WECC-US
2. | 8659 | The impacts of Inter-area oscillations; | [24 empty] | 2020-01-01 |  | 2021-03-31 |  | ApplicabilityAs used in this WECC Regional Variance, Reliability Coordinator is specific to those Reliability Coordinators providing Reliability Coordinator service(s) to entities operating within the Western Interconnection, regardless of where the Reliability Coordinator may be located. |  | 720000 | WECC-US | [5 empty] | WECC-US
2. | 8673 | The impacts of Inter-area oscillations; |  | RC | [11 empty] | RC | [10 empty] | 2021-04-01 | [5 empty] | 720000 | WECC-US | [5 empty] | WECC-US
2. | 868 | If the Planning Authority does not identify any stability-related multiple contingencies, the Planning Authority shall so notify the Reliability Coordinator. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  |  |  |  | FAC-014-2 R6. | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8682 | Electronic Security Perimeters (CIP-005) including Interactive Remote Access; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8690 | For its assets identified in CIP-002 containing low impact BES Cyber Systems, if any: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8692 | Physical security controls; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8701 | UFLS design assessment |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 142000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8706 | Each Balancing Authority shall deny the Arranged Interchange or curtail Confirmed Interchange if the Scheduling Path (proper connectivity of Adjacent Balancing Authorities) between it and its Adjacent Balancing Authorities is invalid. |  | BA | BA | [21 empty] | 2021-04-01 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8713 | Opposite in sign or direction to that of the Adjacent Balancing Authority |  | BA | BA | [21 empty] | 2021-04-01 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8724 | The documentation shall be consistent with the principle that the Facility Ratings do not exceed the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | GO | [24 empty] | 2021-02-04 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8726 | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R2, Part 2.1 including identification of how each of the following were considered: |  | GO | [24 empty] | 2021-02-04 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8730 | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. |  | GO | [24 empty] | 2021-02-04 |  |  |  | 22200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8734 | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | GO | [24 empty] | 2021-02-04 |  |  |  | 24200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8736 | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R3, Part 3.1 including identification of how each of the following were considered: |  | TO | [24 empty] | 2021-02-04 |  |  |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8741 | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. |  | TO | [24 empty] | 2021-02-04 |  |  |  | 32200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8745 | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | TO | [24 empty] | 2021-02-04 |  |  |  | 34200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8748 | The BES interrupting device owner owns all or part of the Composite Protection System; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.2. Facilities:4.2.1 Protection Systems for BES Elements, with the following exclusions:4.2.1.1 Non-protective functions that are embedded within a Protection System.4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS).4.2.1.4 Remedial Action Schemes (RAS).4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8753 | The BES interrupting device owner has determined that a Misoperation occurred or cannot rule out a Misoperation; and |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.2. Facilities:4.2.1 Protection Systems for BES Elements, with the following exclusions:4.2.1.1 Non-protective functions that are embedded within a Protection System.4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS).4.2.1.4 Remedial Action Schemes (RAS).4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 21200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8755 | For a BES interrupting device operation by a Protection System component intended to operate as backup protection for a condition on another entity’s BES Element, notification of the operation shall be provided to the other Protection System owner(s) for which that backup protection was provided. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.2. Facilities:4.2.1 Protection Systems for BES Elements, with the following exclusions:4.2.1.1 Non-protective functions that are embedded within a Protection System.4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS).4.2.1.4 Remedial Action Schemes (RAS).4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 877 | For each bilateral Inadvertent Interchange payback. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  | INT-001-2 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8773 | Monitor the status of Remedial Action Schemes within its Transmission Operator Area; |  | TOP | [18 empty] | TOP |  |  |  | 2021-04-01 | [5 empty] | 102000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8798 | Each control loop is only used by mutual agreement between the Generator Operator and the Transmission Operator affected by the control loop. |  | GOP | [5 empty] | GOP | [18 empty] | 2020-05-14 |  |  |  | 2620000 | WECC-US | [5 empty] | WECC-US
2. | 88 | The Balancing Authorities that have a fixed schedule (B and C) but do not contain the Jointly Owned Unit shall not include their share of the governor droop response in their Frequency Bias Setting. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2009-05-12 |  |  | BAL-003-0a R4. | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8807 | The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). |  | TOP | [18 empty] | TOP | [5 empty] | 2020-05-14 |  |  |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 882 | For each bilateral Inadvertent Interchange payback. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2014-09-30 |  |  | INT-001-3 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8840 | Composed of any combination of the reserve types specified below:• Operating Reserve—Spinning• Operating Reserve—Supplemental • Interchange Transactions designated by the Source Balancing Authority as Operating Reserve—Supplemental • Reserve held by other entities by agreement that is deliverable on Firm Transmission Service• A resource, other than generation or load, that can provide energy or reduce energy consumption • Load, including demand response resources, Demand-Side Management resources, Direct Control Load Management, Interruptible Load or Interruptible Demand, or any other Load made available for curtailment by the Balancing Authority or the Reserve Sharing Group via contract or agreement.• All other load, not identified above, once the Reliability Coordinator has declared an energy emergency alert signifying that firm load interruption is imminent or in progress. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Part 1.2 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates compliance with Requirement R1, Part 1.2. Evidence may include, but is not limited to, documentation that reserves were comprised of the types listed in Requirement R1, Part 1.2 for purposes of meeting the Contingency Reserve obligation of Requirement R1. Additionally, for purposes of the last bullet of Requirement R1, Part 1.2, evidence of compliance may include, but is not limited to, documentation that the reliability coordinator had issued an energy emergency alert, indicating that firm Load interruption was imminent or was in progress. | 2021-06-28 |  |  |  | 4.1.2.1 The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group.4.1.2.2 The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | 12000000 | WECC-US | [5 empty] | WECC-US
2. | 8848 | Equal to or more negative than its Frequency Response Obligation when Frequency varies from 60 Hz by more than +/- 0.036 Hz. |  | BA, FRSG | BA |  |  | FRSG | [12 empty] | RSG | [5 empty] | 2020-07-15 |  |  |  | Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Frequency Response Sharing Group, in which case, the Frequency Response Sharing Group becomes the responsible entity. |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 886 | Energy profile. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2011-03-31 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 887 | If a high voltage direct current (HVDC) tie is on the Scheduling Path, then the Sending Balancing Authorities and Receiving Balancing Authorities shall coordinate the Interchange Schedule with the Transmission Operator of the HVDC tie. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2011-03-31 |  |  | INT-003-2 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8908 | Design auxiliary system(s) or devices used for the control and protection of auxiliary system(s), necessary for the generating unit operation such that they will not trip the generating unit during underfrequency conditions above the appropriate generator underfrequency trip protection setting threshold curve in Figure 2. | [28 empty] | 4.1.3. Distribution Providers that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators4.1.4. Transmission Owners that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators |  | 122000000 | NPCC-US |  | NPCC-US
2. | 8910 | Each Generator Owner shall transmit the existing underfrequency settings and any changes to the underfrequency settings along with the technical basis for the settings to the Planning Coordinator. |  | GO | [22 empty] | 2020-02-18 |  |  |  | 4.1.3. Distribution Providers that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators4.1.4. Transmission Owners that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators |  | 132000000 | NPCC-US |  | NPCC-US
2. | 8914 | Set the frequency trip setting upper tolerance to no greater than + 0.1 Hz. |  | GO | [22 empty] | 2020-02-18 |  |  |  | 4.1.3. Distribution Providers that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators4.1.4. Transmission Owners that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators |  | 162000000 | NPCC-US |  | NPCC-US
2. | 8916 | Each Generator Operator shall provide the blackstart test results within 30 calendar days following a request from its Reliability Coordinator or Transmission Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2018-03-26 | [5 empty] | 142000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 894 | The average energy profile in an hour is less than or equal to 250 MW and in that hour the actual hourly integrated energy deviates from the hourly average energy profile indicated on the tag by more than +25 megawatt-hours. |  | PSE | [10 empty] | PSE | [11 empty] | 2007-06-18 |  | 2008-08-26 |  |  | INT-004-1 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8980 | Specify implementation of hardware mitigation, if any, within four years of the later of the development of the CAP or receipt of regulatory approvals, if required. | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 732000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8988 | The study or studies shall be conducted based on the benchmark GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning benchmark GMD event contained in Table 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 899 | The average energy profile in an hour is less than or equal to 250 MW and in that hour the actual hourly integrated energy deviates from the hourly average energy profile indicated on the tag by more than +25 megawatt-hours. |  | PSE | [10 empty] | PSE | [11 empty] | 2008-08-27 |  | 2014-09-30 |  |  | INT-004-2 R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8993 | The effective GIC time series, GIC(t), calculated using the benchmark GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 5.1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-03-19 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 8996 | Document assumptions used in the analysis; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 62000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9001 | Be developed within one year of completion of the benchmark GMD Vulnerability Assessment. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9004 | Specify implementation of hardware mitigation, if any, within four years of development of the CAP. | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 73200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9007 | Revisions to the selected actions in Part 7.1, if any, including utilization of Operating Procedures, if applicable; and | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 74200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9014 | The study or studies shall be conducted based on the supplemental GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning supplemental GMD event contained in Table 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 82000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9020 | The effective GIC time series, GIC(t), calculated using the supplemental GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 9.1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-03-19 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 92000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9023 | Document assumptions used in the analysis; |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 102000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9031 | Be developed within one year of completion of the supplemental GMD Vulnerability Assessment. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9034 | Specify implementation of hardware mitigation, if any, within four years of development of the CAP. | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 113200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9037 | Revisions to the selected actions in Part 11.1, if any, including utilization of Operating Procedures, if applicable; and | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 114200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9044 | Revisions to the selected actions in Part 7.1, if any, including utilization of Operating Procedures if applicable; and | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 742000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9050 | Specify implementation of hardware mitigation, if any, within four years of the later of the development of the CAP or receipt of regulatory approvals, if required. | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 2032000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9053 | Revisions to the selected actions in Part 11.1, if any, including utilization of Operating Procedures if applicable; and | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 2042000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9059 | Adherence to applicable NERC Reliability Standards; regional and Transmission Owner planning criteria; and Facility interconnection requirements; |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2021-04-01 |  |  |  | Applicable Generator Owner: Generator Owner with a fully executed Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9068 | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. |  | RC | [11 empty] | RC | [10 empty] | 2021-04-01 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9074 | A mutually agreeable process for resolving data conflicts |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2021-04-01 | [5 empty] | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9078 | A timetable for providing the data. (A minimum of 30 calendar days must be allowed for responding to the request). |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9081 | Monthly and annual integrated peak hour Demands in megawatts for the prior calendar year. | [24 empty] | 2021-04-01 | [5 empty] | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9087 | Monthly forecast Net Energy for Load in gigawatthours for the next two calendar years. | [24 empty] | 2021-04-01 | [5 empty] | 14200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 910 | Ramp (ability of generation maneuverability to accommodate). |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9103 | Comparison of the performance of the Planning Coordinator’s portion of the existing system in a planning dynamic model to actual system response, through simulation of a dynamic local event, at least once every 24 calendar months (use a dynamic local event that occurs within 24 calendar months of the last dynamic local event used in comparison, and complete each comparison within 24 calendar months of the dynamic local event). If no dynamic local event occurs within the 24 calendar months, use the next dynamic local event that occurs; |  | PCPA | [9 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9112 | Operate the electric system to meet the NPIRs. |  | BA, DP, GO, GOP, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  |  |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 912 | Each involved Transmission Service Provider shall confirm that the transmission service arrangements associated with the Arranged Interchange have adjacent Transmission Service Provider connectivity, are valid and prevailing transmission system limits will not be violated. |  | TSP | [20 empty] | TSP |  | 2007-06-18 |  | 2008-08-26 |  |  | INT-006-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9120 | Technical requirements and analysis: |  | BA, DP, GO, GOP, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  |  |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 92000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9122 | Identification of facilities, components, and configuration restrictions that are essential for meeting the NPIRs. | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 92200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9126 | Identification of any maintenance requirements for equipment not owned or controlled by the Nuclear Plant Generator Operator that are necessary to meet the NPIRs. | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 93200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9134 | Provisions for coordination during an off-normal or emergency event affecting the NPIRs, including the need to provide timely information explaining the event, an estimate of when the system will be returned to a normal state, and the actual time the system is returned to normal. | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 94200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9140 | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-4 - Attachment 1A, either for 60 seconds or until a steady-state condition between 59.0 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 320000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9144 | Overfrequency trip settings of individual generating units that are part of Quebec BES plants/facilities that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-4 - Attachment 1A, and |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 420000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9149 | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System. |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 220000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9152 | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-4 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 320000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9155 | Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES | [26 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 332000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9159 | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1. |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 420000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 916 | Ramp (ability of generation maneuverability to accommodate). |  | BA | BA | [21 empty] | 2008-08-27 |  | 2010-06-30 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9167 | The effectiveness of the UFLS program |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 2020000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9172 | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9176 | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-4 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 918 | Each involved Transmission Service Provider shall confirm that the transmission service arrangements associated with the Arranged Interchange have adjacent Transmission Service Provider connectivity, are valid and prevailing transmission system limits will not be violated. |  | TSP | [20 empty] | TSP |  | 2008-08-27 |  | 2010-06-30 |  |  | INT-006-2 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9180 | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1. |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 42000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9194 | The effectiveness of the UFLS program. |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 112000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9199 | UFLS design assessment |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 142000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9203 | For UFLS design assessments performed under Requirement R12, the Corrective Action Plan shall be developed within the two-year time frame identified in Requirement R12. |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 152000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9206 | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. |  | TOP | [18 empty] | TOP |  |  |  | 2021-04-01 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9211 | Provisions for notification of current Protection System and Special Protection System status or degradation that impacts System reliability. |  | BA | BA | [21 empty] | 2021-04-01 | [5 empty] | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9218 | A mutually agreeable process for resolving data conflicts |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  |  | 2021-04-01 | [5 empty] | 52000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 922 | Ramp (ability of generation maneuverability to accommodate). |  | BA | BA | [21 empty] | 2010-07-01 |  | 2014-09-30 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9230 | The calculation results shall be submitted to the Compliance Enforcement Authority and made available to the Generator Owner by the end of the month in which they were completed. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [16 empty] | 2020-05-19 |  |  |  | 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL001-TRE-2. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-2. 4.2.3 Any generators that are not required by the Balancing Authority to provide primary frequency response are exempt from this standard. |  | 22000000 | TXRE-US |  |  |  |  | TXRE-US
2. | 9237 | 6.2. Limit Governor droop settings such that they do not exceed those listed in Table 6.2, unless directed otherwise by the Balancing Authority. (see standard for table) |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [16 empty] | 2020-05-19 |  |  |  | 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL001-TRE-2. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-2. 4.2.3 Any generators that are not required by the Balancing Authority to provide primary frequency response are exempt from this standard. |  | 62000000 | TXRE-US |  |  |  |  | TXRE-US
2. | 924 | Each involved Transmission Service Provider shall confirm that the transmission service arrangements associated with the Arranged Interchange have adjacent Transmission Service Provider connectivity, are valid and prevailing transmission system limits will not be violated. |  | TSP | [20 empty] | TSP |  | 2010-01-25 |  | 2014-09-30 |  |  | INT-006-3 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9243 | If a generating unit/generating facility has not participated in a minimum of eight FMEs in a 12-month period, performance shall be based on a rolling eight-FME average. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [16 empty] | 2020-05-19 |  |  |  | 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL001-TRE-2. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-2. 4.2.3 Any generators that are not required by the Balancing Authority to provide primary frequency response are exempt from this standard. |  | 92000000 | TXRE-US |  |  |  |  | TXRE-US
2. | 9247 | If a generating unit/generating facility has not participated in a minimum of eight FMEs in a 12-month period, performance shall be based on a rolling eight- FME average. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [16 empty] | 2020-05-19 |  |  |  | 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL001-TRE-2. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-2. 4.2.3 Any generators that are not required by the Balancing Authority to provide primary frequency response are exempt from this standard. |  | 102000000 | TXRE-US |  |  |  |  | TXRE-US
2. | 9255 | Identify each of the medium impact BES Cyber System according to Attachment 1, Section 2, if any, at each asset; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [5 empty] | 2021-02-04 |  |  |  | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9259 | Have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 at least once every 15 calendar months, even if it has no identified items in Requirement R1. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [5 empty] | 2021-02-04 |  |  |  | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 927 | All reliability entities involved in the Arranged Interchange are currently in the NERC registry. |  | IA | [6 empty] | IA | [15 empty] | 2007-06-18 |  | 2014-09-30 |  |  | INT-007-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 930 | Megawatt profile. |  | IA | [6 empty] | IA | [15 empty] | 2007-06-18 |  | 2014-09-30 |  |  |  | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9309 | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the steady state analysis shall be assessed annually and be supported by the following annual current study, supplemented with qualified past studies as indicated in Requirement R2, Part 2.6: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9330 | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R3, Part 3.5. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9351 | Any portions of the BES designed to detach from the Western Interconnection (planned islands) as a result of the operation of a relay scheme or Remedial Action Scheme. |  | PCPA | [9 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 220000 | WECC-US | [5 empty] | WECC-US
2. | 9357 | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-5 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | PCPA | [9 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 320000 | WECC-US | [5 empty] | WECC-US
2. | 9368 | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-5 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 420000 | WECC-US | [5 empty] | WECC-US
2. | 937 | Necessary Interchange information to NERC-identified reliability analysis services. |  | IA | [6 empty] | IA | [15 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9377 | The effectiveness of the UFLS program |  | PCPA | [9 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 2020000 | WECC-US | [5 empty] | WECC-US
2. | 94 | Each Balancing Authority shall report its Frequency Bias Setting, and method for determining that setting, to the NERC Operating Committee. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2009-06-28 |  |  | BAL-003-0b R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 941 | Necessary Interchange information to NERC-identified reliability analysis services. |  | IA | [6 empty] | IA | [15 empty] | 2008-08-27 |  | 2010-06-30 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9433 | One or more process(es) used in procuring BES Cyber Systems, and their associated EACMS and PACS, that address the following, as applicable: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 945 | Necessary Interchange information to NERC-identified reliability analysis services. |  | IA | [6 empty] | IA | [15 empty] | 2010-07-01 |  | 2014-09-30 |  |  |  | 11200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9452 | All External Routable Connectivity must be through an identified Electronic Access Point (EAP). |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9457 | For all Interactive Remote Access sessions, utilize encryption that terminates at an Intermediate System. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9462 | Have one or more method(s) to terminate authenticated vendor-initiated remote connections and control the ability to reconnect. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9470 | Authorize and document changes that deviate from the existing baseline configuration. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 9484 | Where technically feasible, at least once every 36 calendar months: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 32000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 97 | The Balancing Authority may use a variable (linear or non-linear) bias value, which is based on a variable function of Tie Line deviation to Frequency Deviation. The Balancing Authority shall determine the variable frequency bias value by analyzing Frequency Response as it varies with factors such as load, generation, governor characteristics, and frequency. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2009-06-28 |  |  | BAL-003-0b R2. | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | 998 | Current pre-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  | IRO-005-1 R1. | 12000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-04-12-0000025 | Within 30 calendar days (or a later date if specified by the requester), for any requested Facility with a Thermal Rating that limits the use of Facilities under the requester’s authority by causing any of the following: 1) An Interconnection Reliability Operating Limit, 2) A limitation of Total Transfer Capability, 3) An impediment to generator deliverability, or 4) An impediment to service to a major load center: |  | GO | [22 empty] | 2021-10-01 | [5 empty] | 81200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-05-26-0000002 | Actions to manage the risk to the BES during the transition from primary to backup functionality as well as during outages of the primary or backup functionality. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  |  | 16002000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-03-0000006 | When directed to modify voltage, the Generator Operator shall comply or provide anexplanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2007-08-02 |  | 2008-08-26 |  |  |  | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-03-0000008 | When directed to modify voltage, the Generator Operator shall comply or provide anexplanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2009-05-13 |  | 2010-09-15 |  |  |  | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-03-0000010 | When directed to modify voltage, the Generator Operator shall comply or provide anexplanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2010-09-16 |  | 2013-06-30 |  |  |  | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-03-0000012 | When directed to modify voltage, the Generator Operator shall comply or provide anexplanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-03-0000014 | When directed to modify voltage, the Generator Operator shall comply or provide anexplanation of why the schedule cannot be met |  | GOP | [5 empty] | GOP | [16 empty] | 2013-07-01 |  | 2014-09-30 |  |  |  | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-07-0000001 | This data shall be made available by the Transmission Provider on theschedule specified by the requestor (but no more frequently than once perhour, unless mutually agreed to by the requester and the provider). |  | TSP | [20 empty] | TSP |  |  |  | 2010-09-16 |  |  |  | 90200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-08-0000002 | The intentional relay time delay for UFLS shall be less than or equal to 30 cycles. |  | DP, TO |  | DP | [22 empty] | 2013-11-07 |  |  |  | 10200000 | SPPRE-US
2. | RP-2021-06-08-0000005 | The minimum accumulated Load relief shall be at least 30% of the forecasted peak Load. |  | DP, TO |  | DP | [22 empty] | 2013-11-07 |  |  |  | 20200000 | SPPRE-US
2. | RP-2021-06-08-0000009 | Trip frequency(s) for each location |  | DP, TO |  | DP | [22 empty] | 2013-11-07 |  |  |  | 50200000 | SPPRE-US
2. | RP-2021-06-08-0000017 | Trip frequency(s) for each location |  | GO | [24 empty] | 2013-11-07 |  |  |  | 60200000 | SPPRE-US
2. | RP-2021-06-09-0000003 | Provide the list of circuits to all Regional Entities, Reliability Coordinators,Transmission Owners, Generator Owners, and Distribution Providers within itsPlanning Coordinator area within 30 calendar days of the establishment of the initiallist and within 30 calendar days of any changes to that list. |  | PCPA | [9 empty] | PA | [12 empty] | 2014-01-01 |  | 2014-09-30 |  |  |  | 60200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-09-0000005 | For a transmission facility, the Transmission Operator shall notify and coordinate withits Reliability Coordinator. The Transmission Operator shall notify other affectedTransmission Operators, and coordinate the impact of removing the Bulk ElectricSystem facility. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 70200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-14-0000013 | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-14-0000014 | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-2, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-14-0000016 | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-3, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2012-12-11 |  |  |  | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-14-0000017 | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-4, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2012-12-11 |  |  |  | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-14-0000019 | Training shall cover the policies, access controls, and procedures as developed for the Critical Cyber Assets covered by CIP-004-4, and include, at a minimum, the following required items appropriate to personnel roles and responsibilities: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-14-0000022 | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 30200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-14-0000025 | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 30200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-14-0000028 | Where technically feasible, the security monitoring process(es) shall detect and alert for attempts at or actual unauthorized accesses. These alerts shall provide for appropriate notification to designated response personnel. Where alerting is not technically feasible, the Responsible Entity shall review or otherwise assess access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 30200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-15-0000002 | Where technically feasible, the security monitoring process(es) shall detect and alert forattempts at or actual unauthorized accesses. These alerts shall provide for appropriatenotification to designated response personnel. Where alerting is not technicallyfeasible, the Responsible Entity shall review or otherwise assess access logs forattempts at or actual unauthorized accesses at least every ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 30200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-15-0000004 | Where technically feasible, the security monitoring process(es) shall detect and alert forattempts at or actual unauthorized accesses. These alerts shall provide for appropriatenotification to designated response personnel. Where alerting is not technicallyfeasible, the Responsible Entity shall review or otherwise assess access logs forattempts at or actual unauthorized accesses at least every ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2011-02-01 |  |  |  | 30200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-15-0000007 | Where technically feasible, the security monitoring process(es) shall detect and alert forattempts at or actual unauthorized accesses. These alerts shall provide for appropriatenotification to designated response personnel. Where alerting is not technicallyfeasible, the Responsible Entity shall review or otherwise assess access logs forattempts at or actual unauthorized accesses at least every ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 30200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-15-0000008 | Video Recording: Electronic capture of video images of sufficient quality todetermine identity. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 40200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-15-0000009 | Video Recording: Electronic capture of video images of sufficient quality todetermine identity. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 40200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-15-0000010 | Video Recording: Electronic capture of video images of sufficient quality todetermine identity. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 40200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-15-0000011 | Video Recording: Electronic capture of video images of sufficient quality todetermine identity. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  |  | 40200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-15-0000029 | Transmission facilities, and |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 10200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-15-0000030 | Transmission facilities, and |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 10200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-15-0000035 | The Transmission Owner, in the TVMP, shall identify and document clearancesbetween vegetation and any overhead, ungrounded supply conductors, taking intoconsideration transmission line voltage, the effects of ambient temperature onconductor sag under maximum design loading, and the effects of wind velocities onconductor sway. Specifically, the Transmission Owner shall establish clearances to beachieved at the time of vegetation management work identified herein as Clearance 1,and shall also establish and maintain a set of clearances identified herein as Clearance2 to prevent flashover between vegetation and overhead ungrounded supplyconductors. |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  |  | 10200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-15-0000036 | The Transmission Owner is not required to report to the RRO, or the RRO’s designee,certain sustained transmission line outages caused by vegetation: (1) Vegetationrelated outages that result from vegetation falling into lines from outside the ROW thatresult from natural disasters shall not be considered reportable (examples of disastersthat could create non-reportable outages include, but are not limited to, earthquakes,fires, tornados, hurricanes, landslides, wind shear, major storms as defined either bythe Transmission Owner or an applicable regulatory body, ice storms, and floods), and(2) Vegetation-related outages due to human or animal activity shall not be consideredreportable (examples of human or animal activity that could cause a non-reportableoutage include, but are not limited to, logging, animal severing tree, vehicle contactwith tree, arboricultural activities or horticultural or agricultural activities, or removalor digging of vegetation). |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  |  | 30200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-15-0000038 | Inter-relationships between vegetation growth rates,vegetation control methods, and inspection frequency. |  | TO | [22 empty] | 2014-07-01 |  | 2013-11-25 |  |  |  | 30200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-16-0000002 | The documentation shall be consistent with the principle that the Facility Ratings do not exceed the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | GO | [24 empty] | 2011-05-24 |  |  |  | 10200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-16-0000004 | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R2, Part 2.1 including identification of how each of the following were considered: |  | GO | [24 empty] | 2011-05-24 |  |  |  | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-16-0000014 | The underlying assumptions, design criteria, and methods used to determine the Equipment Ratings identified in Requirement R3, Part 3.1 including identification of how each of the following were considered: |  | TO | [24 empty] | 2011-05-24 |  |  |  | 30200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-16-0000030 | Be performed or verified separately for each of the following planning years: |  | PCPA | [9 empty] | PA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  |  | 10200000 | RF-US |  |  | RF-US
2. | RP-2021-06-16-0000045 | This documentation shall include the planning reserve margin calculated per requirement R1.1 for each of the three years in the analysis. |  | PCPA | [9 empty] | PA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  |  | 20200000 | RF-US |  |  | RF-US
2. | RP-2021-06-17-0000002 | Training shall cover the policies, access controls, and procedures as developed for theCritical Cyber Assets covered by CIP-004-3, and include, at a minimum, the followingrequired items appropriate to personnel roles and responsibilities: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-17-0000006 | Verify at least once each calendar quarter that individuals with active electronic access or unescorted physical access have authorization records. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 40200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-17-0000010 | Where technically feasible, the security monitoring process(es) shall detect and alert forattempts at or actual unauthorized accesses. These alerts shall provide for appropriatenotification to designated response personnel. Where alerting is not technicallyfeasible, the Responsible Entity shall review or otherwise assess access logs forattempts at or actual unauthorized accesses at least every ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. |  | 30200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-17-0000014 | Utilize at least one physical accesscontrol to allow unescorted physicalaccess into each applicable PhysicalSecurity Perimeter to only thoseindividuals who have authorizedunescorted physical access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 10200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-18-0000003 | Use the Cyber Security Incident response plan(s) under Requirement R1 when responding to a Reportable Cyber Security Incident or performing an exercise of a Reportable Cyber Security Incident. Document deviations from the plan(s) taken during the response to the incident or exercise. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-12-31 |  | 1.2 High Impact BES Cyber Systems and their associated:• EACMSMedium Impact BES Cyber Systems and their associated:• EACMS |  | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-18-0000012 | Where technically feasible, at leastonce every 36 calendar months: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 30200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-18-0000013 | The Transmission Owner shall identify the primary control center thatoperationally controls each Transmission station or Transmission substationidentified in the Requirement R1 risk assessment. |  | TO | [22 empty] | 2015-10-01 |  | 2015-10-01 |  |  |  | 10200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-18-0000014 | The unaffiliated third party verification shall verify the Transmission Owner’s riskassessment performed under Requirement R1, which may includerecommendations for the addition or deletion of a Transmission station(s) orTransmission substation(s). The Transmission Owner shall ensure theverification is completed within 90 calendar days following the completion of theRequirement R1 risk assessment. |  | TO | [22 empty] | 2015-10-01 |  | 2015-10-01 |  |  |  | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-18-0000016 | The Transmission Owner or Transmission Operator, respectively, shall ensurethat the unaffiliated third party review is completed within 90 calendar days ofcompleting the security plan(s) developed in Requirement R5. The unaffiliatedthird party review may, but is not required to, include recommended changes tothe evaluation performed under Requirement R4 or the security plan(s)developed under Requirement R5. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  |  | 60200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-21-0000001 | The Transmission Operator and Balancing Authority shall arrange new interchange agreements to provide for emergency capacity or energy transfers if existing agreements cannot be used. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2013-07-01 |  | 2017-03-31 |  |  |  | 60200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-21-0000005 | Transmission Facilities, and |  | TO | [22 empty] | 2013-11-25 |  | 2015-12-31 |  |  |  | 10200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-21-0000024 | transmission Facilities; and |  | TO | [22 empty] | 2016-01-01 |  | 2018-12-31 |  |  |  | 10200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-22-0000014 | Unit-specific dynamics data shall be reported for generators and synchronouscondensers (including, as appropriate to the model, items such as inertia constant,damping coefficient, saturation parameters, and direct and quadrature axes reactancesand time constants), excitation systems, voltage regulators, turbine-governor systems,power system stabilizers, and other associated generation equipment. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 10200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-22-0000023 | Uses Facility Ratings as provided by the Transmission Owner and GeneratorOwner |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 10200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-22-0000024 | Where it is impossible to actually simulate a reliability-limited flow in adirection counter to prevailing flows (on an alternating current Transmissionline), set the TTC for the non-prevailing direction equal to the TTC in theprevailing direction. If the TTC in the prevailing flow direction is dependanton a Special Protection System (SPS), set the TTC for the non-prevailing flowdirection equal to the greater of the maximum flow that can be simulated inthe non-prevailing flow direction or the maximum TTC that can be achievedin the prevailing flow direction without use of a SPS. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-22-0000031 | Updated at least once per day for AFC calculations for intra-day, next day, and daystwo through 30. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 30200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-23-0000011 | Autotransformers or phase-shifters connected to busses. |  | TO | [22 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 20200000 | NPCC-US |  | NPCC-US
2. | RP-2021-06-23-0000017 | Three phase currents and neutral currents. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 50200000 | NPCC-US |  | NPCC-US
2. | RP-2021-06-23-0000033 | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and |  | PCPA | [9 empty] | PA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  |  | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-23-0000036 | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  |  | 40200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-23-0000039 | UFLS design assessment |  | PCPA | [9 empty] | PA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  |  | 140200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-23-0000042 | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-10-01 |  | 2017-09-30 |  |  |  | 40200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-23-0000045 | UFLS design assessment |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2015-10-01 |  | 2017-09-30 |  |  |  | 140200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-24-0000004 | Underfrequency trip settings of generating plants/facilities greater than 75 MVA(gross aggregate nameplate rating) directly connected to the BES that trip abovethe Generator Underfrequency Trip Modeling curve in PRC-006-3 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 40200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-24-0000007 | UFLS design assessment |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 140200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-24-0000011 | Underfrequency trip settings of generating plants/facilities greater than 75 MVA(gross aggregate nameplate rating) directly connected to the BES that trip abovethe Generator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1. |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 40200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-24-0000014 | UFLS design assessment |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 140200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-24-0000016 | Transmit the existing underfrequency settings and any changes to theunderfrequency settings along with the technical basis for the settings to thePlanning Coordinator. |  | DP-UFLS, GO |  | DP | [20 empty] | 2015-07-01 |  | 2020-03-31 |  |  |  | 160200000 | NPCC-US |  | NPCC-US
2. | RP-2021-06-24-0000021 | Total clearing time associated with each set point (sec). This includes the timefrom when frequency reaches the set point and ends when the breaker opens. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2014-04-01 |  | 2017-12-31 |  |  |  | 70200000 | SERC-US |  |  |  | SERC-US
2. | RP-2021-06-24-0000022 | Total clearing time associated with each set point (sec). This is defined as thetime that begins when frequency reaches the set point and ends when thebreaker opens. If inverse time underfrequency relays are used, provide the totalclearing time at 59.0, 58.5, 58.0, and 57.0 Hz. |  | DP-UFLS, GO |  | DP | [20 empty] | 2014-04-01 |  | 2017-12-31 |  |  |  | 80200000 | SERC-US |  |  |  | SERC-US
2. | RP-2021-06-24-0000023 | The UVLS Program isintegrated through coordination with generator voltageride‐through capabilities and other protection and controlsystems, including,but not limited to, transmission line protection, autoreclosing, Remedial ActionSchemes, and other undervoltage‐based load shedding programs. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2017-04-01 |  | 2017-04-01 |  |  |  | 10200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-24-0000025 | The UVLS Program isintegrated through coordination with generator voltageride‐through capabilities and other protection and controlsystems, including,but not limited to, transmission line protection, autoreclosing, RemedialAction Schemes, and other undervoltage‐based load shedding programs. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2017-04-01 |  | 2017-04-01 |  |  |  | 30200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-24-0000044 | Studies shall be performed to assess the impact of the extreme events whichare identified by the list created in Requirement R4, Part 4.5. If the analysisconcludes there is Cascading caused by the occurrence of extreme events, anevaluation of possible actions designed to reduce the likelihood or mitigatethe consequences of the event (s) shall be conducted. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-07-01 |  | 2020-06-10 |  |  |  | 40200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-24-0000058 | The study or studies shall be conducted based on the benchmark GMD eventdescribed in Attachment 1 to determine whether the System meets theperformance requirements for the steady state planning benchmark GMD eventcontained in Table 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  |  | 40200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-24-0000061 | The Transmission Operator shall provide the Generator Operator with the notificationrequirements for deviations from the voltage or Reactive Power schedule (which is either arange or a target value with an associated tolerance band). |  | TOP | [18 empty] | TOP |  |  |  | 2014-10-01 |  | 2015-11-12 |  |  |  | 50200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-24-0000064 | The Transmission Operator shall provide the Generator Operator with the notificationrequirements for deviations from the voltage or Reactive Power schedule (which is either arange or a target value with an associated tolerance band). |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-25 |  |  |  | 50200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-24-0000067 | The Transmission Operator shall provide the Generator Operator with the notificationrequirements for deviations from the voltage or Reactive Power schedule (which is either arange or a target value with an associated tolerance band). |  | TOP | [18 empty] | TOP |  |  |  | 2017-09-26 |  | 2018-12-31 |  |  |  | 50200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-24-0000070 | The Transmission Operator shall provide the Generator Operator with thenotification requirements for deviationsfrom the voltage or Reactive Powerschedule (which is either a range or a target value with an associated toleranceband). |  | TOP | [18 empty] | TOP | [5 empty] | 2020-05-14 |  |  |  | 50200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-24-0000073 | When instructed to modify voltage, the Generator Operator shall comply or provide anexplanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2014-10-01 |  | 2015-05-28 |  |  |  | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-24-0000075 | When instructed to modify voltage, the Generator Operator shall comply orprovide an explanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-05-29 |  | 2017-09-25 |  |  |  | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-24-0000079 | Processes to prepare for and mitigate Emergencies including: |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 10200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-24-0000089 | Processes to prepare for and mitigate Emergencies including: |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-24-0000110 | Annual inspection and maintenance of generating unit(s) freeze protection measures; |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 70200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-24-0000122 | Provisions for notification of current Protection System and Remedial Action Scheme (RAS) status or degradation that impacts System reliability. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 10200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-24-0000136 | A mutually agreeable process for resolving data conflicts |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 30200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-24-0000139 | Provisions for notification of current Protection System and Remedial Action Scheme (RAS) status or degradation that impacts System reliability. |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 10200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-24-0000153 | Provisions for notification of current Protection System and Remedial Action Scheme status or degradation that impacts System reliability. |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-24-0000168 | A mutually agreeable process for resolving data conflicts |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 50200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-29-0000004 | with a minimum accuracy of 0.001 Hz. |  | BA | BA | [21 empty] | 2019-01-01 | [5 empty] | 30200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-29-0000008 | This documentation shall include the Planning Reserve margin calculated perrequirement R1.1 for each of the three years in the analysis. |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 20200000 | RF-US |  |  | RF-US
2. | RP-2021-06-30-0000004 | Verify at least once each calendar quarter that individuals with active electronic access or unescorted physical access have authorization records. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 40200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-30-0000008 | Utilize at least one physical access control to allow unescorted physical access into each applicable Physical Security Perimeter to only those individuals who have authorized unescorted physical access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 | [5 empty] | 10200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-30-0000020 | Where technically feasible, at least once every 36 calendar months: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 30200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-06-30-0000033 | Where technically feasible, at least once every 36 calendar months: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 30200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-05-0000001 | To mitigate the magnitude and duration of an IROL exceedance such that the IROL exceedance is relieved within the IROL’s Tv . |  | RC | [11 empty] | RC | [10 empty] | 2016-01-01 | [5 empty] | 10200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-06-0000003 | Identifying expected import path(s) or source region(s). |  | LSE | [7 empty] | LSE | [14 empty] | 2011-04-01 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 30100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-06-0000005 | To any Transmission Service Provider, Reliability Coordinator, TransmissionPlanner, Resource Planner, or Planning Coordinator within 30 calendar days oftheir making a request for the data. |  | TP, TSP | [19 empty] | TP | TSP |  | 2011-04-01 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 90200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-07-0000011 | Uses Facility Ratings as provided by the Transmission Owner and Generator Owner |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 10200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-07-0000012 | Where it is impossible to actually simulate a reliability-limited flow in a direction counter to prevailing flows (on an alternating current Transmission line), set the TTC for the non-prevailing direction equal to the TTC in the prevailing direction. If the TTC in the prevailing flow direction is dependent on a Remedial Action Scheme (RAS), set the TTC for the non-prevailing flow direction equal to the greater of the maximum flow that can be simulated in the non-prevailing flow direction or the maximum TTC that can be achieved in the prevailing flow direction without use of a RAS. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-07-0000022 | Updated at least once per day for AFC calculations for intra-day, next day, and days two through 30. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 30200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-09-0000002 | Any portions of the BES designed to detach from the Interconnection (planned islands) as a result of the operation of a relay scheme or Special Protection System, and |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2021-04-01 |  |  |  | UFLS entities shall mean all entities that are responsible for the ownership,operation, or control of UFLS equipment as required by the UFLS programestablished by the Planning Coordinators. Such entities may include one ormore of the following: 4.2.1 Transmission Owners4.2.2 Distribution Providers4.2.3 UFLS-Only Distribution Providers4.3. Transmission Owners that own Elements identified in the UFLS programestablished by the Planning Coordinators. |  | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-09-0000005 | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006-5 - Attachment 1, either for 60 seconds or until a steady-state condition between 59.3 Hz and 60.7 Hz is reached, and |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2021-04-01 |  |  |  | UFLS entities shall mean all entities that are responsible for the ownership,operation, or control of UFLS equipment as required by the UFLS programestablished by the Planning Coordinators. Such entities may include one ormore of the following: 4.2.1 Transmission Owners4.2.2 Distribution Providers4.2.3 UFLS-Only Distribution Providers4.3. Transmission Owners that own Elements identified in the UFLS programestablished by the Planning Coordinators. |  | 30200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-09-0000008 | Underfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-5 - Attachment 1. |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2021-04-01 |  |  |  | UFLS entities shall mean all entities that are responsible for the ownership,operation, or control of UFLS equipment as required by the UFLS programestablished by the Planning Coordinators. Such entities may include one ormore of the following: 4.2.1 Transmission Owners4.2.2 Distribution Providers4.2.3 UFLS-Only Distribution Providers4.3. Transmission Owners that own Elements identified in the UFLS programestablished by the Planning Coordinators. |  | 40200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-09-0000015 | The effectiveness of the UFLS program. |  | DP, DP-UFLS, TO |  | DP | [20 empty] | 2021-04-01 | [5 empty] | 80200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-09-0000017 | UFLS design assessment |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2021-04-01 |  |  |  | UFLS entities shall mean all entities that are responsible for the ownership,operation, or control of UFLS equipment as required by the UFLS programestablished by the Planning Coordinators. Such entities may include one ormore of the following: 4.2.1 Transmission Owners4.2.2 Distribution Providers4.2.3 UFLS-Only Distribution Providers4.3. Transmission Owners that own Elements identified in the UFLS programestablished by the Planning Coordinators. |  | 140200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-09-0000020 | For UFLS design assessments performed under Requirement R12, the Corrective Action Plan shall be developed within the two-year time frame identified in Requirement R12. |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2021-04-01 |  |  |  | UFLS entities shall mean all entities that are responsible for the ownership,operation, or control of UFLS equipment as required by the UFLS programestablished by the Planning Coordinators. Such entities may include one ormore of the following: 4.2.1 Transmission Owners4.2.2 Distribution Providers4.2.3 UFLS-Only Distribution Providers4.3. Transmission Owners that own Elements identified in the UFLS programestablished by the Planning Coordinators. |  | 150200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-09-0000022 | Frequency shall remain below the Overfrequency Performance Characteristic curve in PRC-006 - Attachment 1A, either for 60 seconds or until a steady-state condition between 59.0 Hz and 60.7 Hz is reached, and |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2021-04-01 |  |  |  | UFLS entities shall mean all entities that are responsible for the ownership,operation, or control of UFLS equipment as required by the UFLS programestablished by the Planning Coordinators. Such entities may include one ormore of the following: 4.2.1 Transmission Owners4.2.2 Distribution Providers4.2.3 UFLS-Only Distribution Providers4.3. Transmission Owners that own Elements identified in the UFLS programestablished by the Planning Coordinators. |  | 68030200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-09-0000034 | Total clearing time associated with each set point (sec). This includes the time from when frequency reachesthe set point and ends when the breaker opens. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 70200000 | SERC-US |  |  |  | SERC-US
2. | RP-2021-07-09-0000035 | Total clearing time associated with each set point (sec). This is defined as the time that begins when frequency reaches the set point and ends when the breaker opens. If inverse time underfrequency relays are used, provide the total clearing time at 59.0, 58.5, 58.0, and 57.0 Hz. |  | DP-UFLS, GO |  | DP | [20 empty] | 2018-01-01 | [5 empty] | 80200000 | SERC-US |  |  |  | SERC-US
2. | RP-2021-07-09-0000036 | The UVLS Program is integrated through coordination with generator voltage ride-through capabilities and other protection and control systems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage-based load shedding programs. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2017-04-02 | [5 empty] | 10200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-09-0000038 | The UVLS Program is integrated through coordination with generator voltage ride-through capabilities and other protection and control systems, including, but not limited to, transmission line protection, autoreclosing, Remedial Action Schemes, and other undervoltage-based load shedding programs. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2017-04-02 | [5 empty] | 30200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-09-0000042 | Update the CAP if actions or timetables change. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 70200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-09-0000046 | Within 12 full calendar months of becoming aware3 of a generator, transformer, or transmission line BES Element that tripped in response to a stable or unstable4 power swing due to the operation of its protective relay(s), determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-1 – Attachment B. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2020-01-01 | [5 empty] | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-12-0000036 | Studies shall be performed to assess the impact of the extreme events which are identified by the list created in Requirement R4, Part 4.5. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences of the event (s) shall be conducted. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 40200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-12-0000051 | Specify implementation of hardware mitigation, if any, within four years of the later of the development of the CAP or receipt of regulatory approvals, if required. |  | GO, PCPA, TO, TP |  |  |  |  | GO |  |  |  |  | PA | [7 empty] | TO |  | TP |  |  | 2020-10-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 68730200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-12-0000053 | The study or studies shall be conducted based on the benchmark GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning benchmark GMD event contained in Table 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 40200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-12-0000056 | The study or studies shall be conducted based on the supplemental GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning supplemental GMD event contained in Table 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 80200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-12-0000058 | The Transmission Operator shall provide the Generator Operator with the notification requirements for deviations from the voltage or Reactive Power schedule (which is either a range or a target value with an associated tolerance band). |  | TOP | [18 empty] | TOP |  |  |  | 2019-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | 50200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-12-0000061 | When instructed to modify voltage, the Generator Operator shall comply or provide an explanation of why the schedule cannot be met. |  | GOP | [5 empty] | GOP | [16 empty] | 2017-09-26 | [5 empty] | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-13-0000002 | Monitor the status of Remedial Action Schemes within its Transmission Operator Area; |  | BA, DP, GOP, TOP | BA | DP |  |  |  | GOP | [12 empty] | TOP | [9 empty] | 100200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-13-0000008 | Require that System Voltage Limits respect voltage-based Facility Ratings; |  | RC | [11 empty] | RC | [16 empty] | 30200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-13-0000017 | Require that stability limits are established to meet the criteria specified in Part 4.1 for the Contingencies identified in Requirement R5 applicable to the establishment of stability limits that are expected to produce more severe System impacts on its portion of the BES. |  | RC | [11 empty] | RC | [16 empty] | 40200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-13-0000025 | Specify additional single or multiple Contingency events or types of Contingency events, if any. |  | RC | [11 empty] | RC | [16 empty] | 50200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-13-0000032 | System performance for the single Contingencies listed in Part 5.1 demonstrates the following: |  | RC | [11 empty] | RC | [16 empty] | 60200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-13-0000045 | A requirement that the following SOL exceedances must be communicated, if not resolved within 30 minutes, within a timeframe identified by the Reliability Coordinator. |  | RC | [11 empty] | RC | [16 empty] | 70200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-13-0000049 | Criteria for determining when exceeding a SOL qualifies as exceeding an IROL and criteria for developing any associated IROL Tv. |  | RC | [11 empty] | RC | [16 empty] | 80200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-13-0000051 | Each of the following entities prior to the effective date of the SOL methodology: |  | RC | [11 empty] | RC | [16 empty] | 90200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-13-0000057 | Each impacted Planning Coordinator and each impacted Transmission Planner within its Reliability Coordinator Area, the following information for each established stability limit and each established IROL at least once every twelve calendar months: |  | RC, TOP, TP | [11 empty] | RC | [6 empty] | TOP | TP | [8 empty] | 50200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-13-0000069 | The type of instability addressed by the Corrective Action Plan (e.g. steady-state and/or transient voltage instability, angular instability including generating unit loss of synchronism and/or unacceptable damping); |  | RC, TOP, TP | [11 empty] | RC | [6 empty] | TOP | TP | [8 empty] | 70200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-13-0000074 | An encroachment due to a fall‐in from inside the ROW that caused a vegetation‐ related Sustained Outage,Footnote: Multiple Sustained Outages on an individual line, if caused by the same vegetation, will be reported as one outage regardless of the actual number of outages within a 24‐hour period. |  | GO, TO |  |  |  |  | GO | [23 empty] | 10200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-13-0000078 | Inter‐relationships between vegetation growth rates, vegetation control methods, and inspection frequency. |  | GO, TO |  |  |  |  | GO | [23 empty] | 30200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-13-0000080 | Circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator OwnerFootnote: Circumstances that are beyond the control of an applicable Transmission Owner or applicable Generator Owner include but are not limited to natural disasters such as earthquakes, fires, tornados, hurricanes, landslides, ice storms, floods, or major storms as defined either by the TO or GO or an applicable regulatory body. |  | GO, TO |  |  |  |  | GO | [23 empty] | 70200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-15-0000002 | Notify other owners of BES Elements connected to those BES buses, if any, within 90-calendar days of completion of Part 1.1, that those BES Elements require SER data and/or FR data. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 10200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-15-0000005 | Each phase current and the residual or neutral current for the following BES Elements: |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 30200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-15-0000009 | A minimum recording rate of 16 samples per cycle. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 40200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-15-0000021 | Identify a minimum DDR coverage, inclusive of those BES Elements identified in Part 5.1, of at least: |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 50200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-15-0000027 | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R6, Part 6.1, or the positive sequence current. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 60200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-15-0000031 | The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R7, Part 7.1, phase current(s) for any phase-to-phase voltages, or positive sequence current. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 70200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-15-0000035 | At least one of the following three triggers: · Off nominal frequency trigger set at: Low Higho Eastern Interconnection <59.75 Hz >61.0 Hzo Western Interconnection <59.55 Hz >61.0 Hzo ERCOT Interconnection <59.35 Hz >61.0 Hzo Hydro-Quebec Interconnection <58.55 Hz >61.5 Hz · Rate of change of frequency trigger set at:o Eastern Interconnection < -0.03125 Hz/sec > 0.125 Hz/seco Western Interconnection < -0.05625 Hz/sec > 0.125 Hz/seco ERCOT Interconnection < -0.08125 Hz/sec > 0.125 Hz/seco Hydro-Quebec Interconnection < -0.18125 Hz/sec > 0.1875 Hz/sec · Undervoltage trigger set no lower than 85 percent of normal operating voltage for a duration of 5 seconds. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 80200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-15-0000037 | Output recording rate of electrical quantities of at least 30 times per second. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 90200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-15-0000039 | Synchronized device clock accuracy within ± 2 milliseconds of UTC. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 100200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-15-0000041 | Data subject to Part 11.1 will be provided within 30-calendar days of a request unless an extension is granted by the requestor. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 110200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-15-0000046 | Provide the list of circuits to all Regional Entities, Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within its Planning Coordinator area within 30 calendar days of the establishment of the initial list and within 30 calendar days of any changes to that list. |  | DP, GO, PCPA, TO |  | DP |  |  | GO |  |  |  |  | PA | [18 empty] | 60200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-07-15-0000048 | Within 12 full calendar months of becoming aware2 of a generator, transformer, or transmission line BES Element that tripped in response to a stable or unstable3 power swing due to the operation of its protective relay(s), determine whether its load-responsive protective relay(s) applied to that BES Element meets the criteria in PRC-026-2 – Attachment B. |  | GO, PCPA, TO |  |  |  |  | GO |  |  |  |  | PA | [18 empty] | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-08-12-0000002 | Identify each of the medium impact BES Cyber Systems according to Attachment 1, Section 2, if any, at each asset; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2014-02-03 |  |  |  | 10200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-08-12-0000005 | Have its CIP Senior Manager or delegate approve the identifications required by Requirement R1 at least once every 15 calendar months, even if it has no identified items in Requirement R1. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2014-02-03 |  |  |  | 20200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-08-13-0000005 | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 50200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-08-13-0000010 | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 50200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-08-13-0000014 | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  |  |  | 50200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-08-13-0000018 | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | 50200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-08-13-0000022 | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 50200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2. | RP-2021-08-13-0000026 | The Responsible Entity shall review at least annually the access privileges to protected information to confirm that access privileges are correct and that they correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 50200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.1 | RP-2021-04-12-0000027 | Identity of the existing next most limiting equipment of the Facility |  | GO | [22 empty] | 2021-10-01 | [5 empty] | 82100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.1. | 5604 | Single line to ground or three-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.1. | 5635 | Single line to ground or 3-phase Fault (whichever is more severe), with Normal Clearing, on any Faulted generator, line, transformer, or shunt device. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 22000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.1. | RP-2021-04-12-0000009 | Equipment Rating standard(s) used in development of this methodology. |  | GO | [22 empty] | 2021-10-01 | [5 empty] | 20300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.1. | RP-2021-04-12-0000019 | Equipment Rating standard(s) used in development of this methodology. |  | GO | [22 empty] | 2021-10-01 | [5 empty] | 30300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.1. | RP-2021-06-16-0000005 | Equipment Rating standard(s) used in development of this methodology. |  | GO | [24 empty] | 2011-05-24 |  |  |  | 22100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.1. | RP-2021-06-16-0000015 | Equipment Rating standard(s) used in development of this methodology. |  | TO | [24 empty] | 2011-05-24 |  |  |  | 32100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.1. | RP-2021-06-16-0000031 | Perform an analysis for Year One. |  | PCPA | [9 empty] | PA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  |  | 12100000 | RF-US |  |  | RF-US
2.1. | RP-2021-06-18-0000005 | Update the Cyber Security Incident response plan(s); and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-12-31 |  | 1.3 High Impact BES Cyber Systems and their associated:• EACMSMedium Impact BES Cyber Systems and their associated:• EACMS |  | 32100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.1. | RP-2021-06-18-0000007 | Update the recovery plan; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 32100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.1. | RP-2021-06-22-0000012 | TRMID; and |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 52100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.1. | RP-2021-06-23-0000020 | Transmission and Generator circuit breaker positions |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 12100000 | NPCC-US |  | NPCC-US
2.1. | RP-2021-06-24-0000080 | Notification to its Reliability Coordinator, to include current and projected conditions, when experiencing an operating Emergency; |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.1. | RP-2021-06-24-0000090 | Notification to its Reliability Coordinator, to include current and projected conditions when experiencing a Capacity Emergency or Energy Emergency; |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 22100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.1. | RP-2021-06-30-0000014 | Update the Cyber Security Incident response plan(s); and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | 32100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.1. | RP-2021-06-30-0000016 | Update the recovery plan; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 32100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.1. | RP-2021-06-30-0000034 | Perform an active vulnerability assessment in a test environment, or perform an active vulnerability assessment in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration of the BES Cyber System in a production environment; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 32100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.1. | RP-2021-06-30-0000037 | Notification by the vendor of vendor-identified incidents related to the products or services provided to the Responsible Entity that pose cyber security risk to the Responsible Entity; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.1. | RP-2021-07-01-0000003 | Tools and applications to ensure that System Operators have situational awareness of the BES. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2019-04-01 | [5 empty] | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.1. | RP-2021-07-08-0000002 | Transformers that have a low-side operating voltage of 100kV or above. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date.Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date.Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 32100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.1. | RP-2021-07-12-0000011 | A current study assessing expected System peak Load conditions for one of the years in the Long-Term Transmission Planning Horizon and the rationale for why that year was selected. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 22100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US