2.1. | RP-2021-07-13-0000033 | Steady state post-Contingency flow through Facilities within applicable Emergency Ratings. Steady state post-Contingency flow through a Facility must not be above the Facility’s highest Emergency Rating. |  | RC | [11 empty] | RC | [16 empty] | 62100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.1. | RP-2021-07-13-0000046 | Post-Contingency SOL exceedances of Facility Ratings and emergency System Voltage Limits, and |  | RC | [11 empty] | RC | [16 empty] | 72100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.1. | RP-2021-07-13-0000052 | Each adjacent Reliability Coordinator within the same; Interconnection; |  | RC | [11 empty] | RC | [16 empty] | 92100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.1. | RP-2021-07-13-0000058 | The value of the stability limit or IROL; |  | RC, TOP, TP | [11 empty] | RC | [6 empty] | TOP | TP | [8 empty] | 52100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.1. | RP-2021-07-15-0000006 | Transformers that have a low-side operating voltage of 100kV or above. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 32100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.1. | RP-2021-07-15-0000022 | One BES Element; and |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 52100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2 | RP-2021-04-12-0000028 | The Thermal Rating for the next most limiting equipment identified in Requirement R8, Part 8.2.1. |  | GO | [22 empty] | 2021-10-01 | [5 empty] | 82200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | 5636 | Loss of any generator, line, transformer, or shunt device without a Fault. |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 22100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | RP-2021-04-12-0000010 | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. |  | GO | [22 empty] | 2021-10-01 | [5 empty] | 20400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | RP-2021-04-12-0000020 | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. |  | GO | [22 empty] | 2021-10-01 | [5 empty] | 30400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | RP-2021-06-14-0000002 | Transmission substations that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | RP-2021-06-14-0000003 | Transmission substations that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | RP-2021-06-14-0000006 | Transmission substations that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | RP-2021-06-14-0000007 | Transmission substations that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | RP-2021-06-14-0000008 | Transmission substations that support the reliable operation of the Bulk Electric System |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | RP-2021-06-16-0000006 | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. |  | GO | [24 empty] | 2011-05-24 |  |  |  | 22200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | RP-2021-06-16-0000016 | Ratings provided by equipment manufacturers or obtained from equipment manufacturer specifications. |  | TO | [24 empty] | 2011-05-24 |  |  |  | 32200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | RP-2021-06-16-0000032 | Perform an analysis or verification at a minimum for one year in the 2 through 5 year period and at a minimum one year in the 6 though 10 year period. |  | PCPA | [9 empty] | PA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  |  | 12200000 | RF-US |  |  | RF-US
2.2. | RP-2021-06-16-0000047 | Transmission substations that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | RP-2021-06-16-0000048 | Transmission substations that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | RP-2021-06-22-0000010 | Transmission topology, including, but not limited to, additions and retirements; |  | TOP | [18 empty] | TOP |  |  |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | RP-2021-06-22-0000035 | Unit commitment and Dispatch Order, to include all designated networkresources and other resources that are committed or have the legalobligation to run as specified in the Transmission Service Provider'sATCID. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 62200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | RP-2021-06-23-0000022 | The Transmission Owner or Generator Owner shall repair or replace any Protection System or RAS that misoperated with a FEPS or FERAS within 20 business days of the date of removal. The Transmission Owner or Generator Owner shall remove the Element from service or disable the RAS if repair or replacement is not completed within 20 business days. |  | GO, TO, TOP |  |  |  |  | GO | [12 empty] | TO | TOP |  |  |  | 2011-10-01 |  | 2017-03-31 |  |  |  | 22200000 | WECC-US | [5 empty] | WECC-US
2.2. | RP-2021-06-24-0000081 | Cancellation or recall of Transmission and generation outages; |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | RP-2021-06-24-0000091 | Requesting an Energy Emergency Alert, per Attachment 1; |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 22200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | RP-2021-06-30-0000035 | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 32200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | RP-2021-06-30-0000038 | Coordination of responses to vendor-identified incidents related to the products or services provided to the Responsible Entity that pose cyber security risk to the Responsible Entity; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | RP-2021-07-01-0000005 | Cancellation or recall of Transmission and generation outages; |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 12100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | RP-2021-07-01-0000011 | Loss of any generator, line, transformer, or shunt device without a Fault. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 22100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | RP-2021-07-01-0000024 | The Thermal Rating for the next most limiting equipment identified inRequirement R8, Part 8.2.1. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-01-01 |  | 2021-09-30 |  |  |  | 82200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | RP-2021-07-07-0000026 | Unit commitment and Dispatch Order, to include all designated network resources and other resources that are committed or have the legal obligation to run as specified in the Transmission Service Provider's ATCID. |  | TSP | [20 empty] | TSP |  | 2017-04-01 | [5 empty] | 62200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | RP-2021-07-08-0000003 | Transmission Lines. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date.Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date.Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 32200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | RP-2021-07-13-0000034 | Steady state post-Contingency voltages are within emergency System Voltage Limits. |  | RC | [11 empty] | RC | [16 empty] | 62200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | RP-2021-07-13-0000047 | Pre-Contingency SOL exceedances of normal maximum System Voltage Limits. |  | RC | [11 empty] | RC | [16 empty] | 72200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | RP-2021-07-13-0000053 | Each Planning Coordinator and Transmission Planner that is responsible for planning any portion of the Reliability Coordinator Area; |  | RC | [11 empty] | RC | [16 empty] | 92200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | RP-2021-07-13-0000059 | Identification of the Facilities that are critical to the derivation of the stability limit or the IROL; |  | RC, TOP, TP | [11 empty] | RC | [6 empty] | TOP | TP | [8 empty] | 52200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | RP-2021-07-15-0000007 | Transmission Lines. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 32200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2. | RP-2021-07-15-0000023 | One BES Element per 3,000 MW of the Reliability Coordinator’s historical simultaneous peak System Demand. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 52200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2.1 | RP-2021-06-15-0000033 | Where transmission system transient overvoltage factors are notknown, clearances shall be derived from Table 5, IEEE 516-2003,phase-to-ground distances, with appropriate altitude correctionfactors applied. |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  |  | 32100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.2.1. | RP-2021-06-16-0000033 | If the analysis is verified, the verification must be supported by current or past studies for the same planning year. |  | PCPA | [9 empty] | PA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  |  | 32100000 | RF-US |  |  | RF-US
2.2.2. | RP-2021-06-15-0000034 | Where transmission system transient overvoltage factors areknown, clearances shall be derived from Table 7, IEEE 516-2003,phase-to-phase voltages, with appropriate altitude correctionfactors applied. |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  |  | 32200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.3. | 5637 | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 22200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.3. | RP-2021-04-12-0000005 | Ambient conditions (for particular or average conditions or as they vary in real-time). |  | GO | [22 empty] | 2021-10-01 | [5 empty] | 22100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.3. | RP-2021-04-12-0000015 | Ambient conditions (for particular or average conditions or as they vary in real-time). |  | GO | [22 empty] | 2021-10-01 | [5 empty] | 32100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.3. | RP-2021-06-15-0000021 | Where such accounts must be shared, the Responsible Entity shall have apolicy for managing the use of such accounts that limits access to only thosewith authorization, an audit trail of the account use (automated or manual),and steps for securing the account in the event of personnel changes (forexample, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 52300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.3. | RP-2021-06-15-0000022 | Where such accounts must be shared, the Responsible Entity shall have apolicy for managing the use of such accounts that limits access to only thosewith authorization, an audit trail of the account use (automated or manual),and steps for securing the account in the event of personnel changes (forexample, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 52300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.3. | RP-2021-06-15-0000023 | Where such accounts must be shared, the Responsible Entity shall have apolicy for managing the use of such accounts that limits access to only thosewith authorization, an audit trail of the account use (automated or manual),and steps for securing the account in the event of personnel changes (forexample, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 52300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.3. | RP-2021-06-15-0000024 | Where such accounts must be shared, the Responsible Entity shall have apolicy for managing the use of such accounts that limits access to only thosewith authorization, an audit trail of the account use (automated or manual),and steps for securing the account in the event of personnel changes (forexample, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 52300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.3. | RP-2021-06-15-0000025 | Where such accounts must be shared, the Responsible Entity shall have apolicy for managing the use of such accounts that limits access to only thosewith authorization, an audit trail of the account use (automated or manual),and steps for securing the account in the event of personnel changes (forexample, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 52300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.3. | RP-2021-06-16-0000007 | Ambient conditions (for particular or average conditions or as they vary in real-time). |  | GO | [24 empty] | 2011-05-24 |  |  |  | 22300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.3. | RP-2021-06-16-0000017 | Ambient conditions (for particular or average conditions or as they vary in real-time). |  | TO | [24 empty] | 2011-05-24 |  |  |  | 32300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.3. | RP-2021-06-17-0000016 | Where such accounts must be shared, the Responsible Entity shall have apolicy for managing the use of such accounts that limits access to only thosewith authorization, an audit trail of the account use (automated or manual),and steps for securing the account in the event of personnel changes (forexample, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 52300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.3. | RP-2021-06-17-0000017 | Where such accounts must be shared, the Responsible Entity shall have apolicy for managing the use of such accounts that limits access to only thosewith authorization, an audit trail of the account use (automated or manual),and steps for securing the account in the event of personnel changes (forexample, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 52300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.3. | RP-2021-06-22-0000037 | Types of planning and operational analyses performed specifically tosupport the NPIRs, including the frequency of studies and types ofContingencies and scenarios required. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 92300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.3. | RP-2021-06-22-0000038 | Types of planning and operational analyses performed specifically tosupport the NPIRs, including the frequency of studies and types ofContingencies and scenarios required. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 92300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.3. | RP-2021-06-24-0000082 | Transmission system reconfiguration; |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 12300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.3. | RP-2021-06-24-0000092 | Managing generating resources in its Balancing Authority Area to address: |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 22300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.3. | RP-2021-06-30-0000039 | Notification by vendors when remote or onsite access should no longer be granted to vendor representatives; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 12300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.3. | RP-2021-07-01-0000012 | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 22200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.3. | RP-2021-07-07-0000018 | The source/sink or POR/POD identification and mapping to the model. |  | TSP | [20 empty] | TSP |  | 2017-04-01 | [5 empty] | 12300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.3. | RP-2021-07-07-0000028 | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. |  | BA, DP, GO, GOP, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  |  |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 92300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.3. | RP-2021-07-13-0000035 | The stability performance criteria defined in the Reliability Coordinator’s SOL methodology are met.Footnote: Stability evaluations and assessments of instability, Cascading, and uncontrolled separation can be performed using real-time stability assessments, predetermined stability limits or other offline analysis techniques. |  | RC | [11 empty] | RC | [16 empty] | 62300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.3. | RP-2021-07-13-0000054 | Each Transmission Operator within its Reliability Coordinator Area; and |  | RC | [11 empty] | RC | [16 empty] | 92300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.3. | RP-2021-07-13-0000060 | The associated IROL Tv for any IROL; |  | RC, TOP, TP | [11 empty] | RC | [6 empty] | TOP | TP | [8 empty] | 52300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.3.1. | RP-2021-06-24-0000093 | capability and availability; |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 43100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.3.2. | RP-2021-06-24-0000094 | fuel supply and inventory concerns; |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 43200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.3.3. | RP-2021-06-24-0000095 | fuel switching capabilities; and |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 43300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.3.4. | RP-2021-06-24-0000096 | environmental constraints. |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 43400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.4. | RP-2021-04-12-0000006 | Operating limitations.Footnote: Such as temporary de-ratings of impaired equipment in accordance with good utility practice. |  | GO | [22 empty] | 2021-10-01 | [5 empty] | 22200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.4. | RP-2021-04-12-0000016 | Operating limitations.Footnote: Such as temporary de-ratings of impaired equipment in accordance with good utility practice. |  | GO | [22 empty] | 2021-10-01 | [5 empty] | 32200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.4. | RP-2021-06-16-0000008 | Operating limitations.Note: Such as temporary de-ratings of impaired equipment in accordance with good utility practice. |  | GO | [24 empty] | 2011-05-24 |  |  |  | 22400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.4. | RP-2021-06-16-0000018 | Operating limitations.Note: Such as temporary de-ratings of impaired equipment in accordance with good utility practice. |  | TO | [24 empty] | 2011-05-24 |  |  |  | 32400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.4. | RP-2021-06-24-0000083 | Redispatch of generation request; |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 12400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.4. | RP-2021-06-24-0000097 | Public appeals for voluntary Load reductions; |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 22400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.4. | RP-2021-06-30-0000040 | Disclosure by vendors of known vulnerabilities related to the products or services provided to the Responsible Entity; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 12400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.4. | RP-2021-07-13-0000036 | Instability, Cascading or uncontrolled separation that adversely impact the reliability of the Bulk Electric System does not occur.Footnote: Stability evaluations and assessments of instability, Cascading, and uncontrolled separation can be performed using real-time stability assessments, predetermined stability limits or other offline analysis techniques. |  | RC | [11 empty] | RC | [16 empty] | 62400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.4. | RP-2021-07-13-0000055 | Each Reliability Coordinator that has requested to receive updates and indicated it had a reliability-related need. |  | RC | [11 empty] | RC | [16 empty] | 92400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.4. | RP-2021-07-13-0000061 | The associated critical Contingency(ies); |  | RC, TOP, TP | [11 empty] | RC | [6 empty] | TOP | TP | [8 empty] | 52400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.5. | RP-2021-06-10-0000001 | Tie tripping schemes. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  |  | 12500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.5. | RP-2021-06-17-0000001 | Transient Cyber Assets and Removable Media malicious code riskmitigation; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.5. | RP-2021-06-24-0000084 | Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 12500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.5. | RP-2021-06-24-0000098 | Requests to government agencies to implement their programs to achieve necessary energy reductions; |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 22500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.5. | RP-2021-06-29-0000009 | Transient Cyber Assets and Removable Media malicious code riskmitigation; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.5. | RP-2021-06-30-0000036 | Verification of software integrity and authenticity of all software and patches provided by the vendor for use in the BES Cyber System; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and4.1.2.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and4.2.1.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers4.2.2.1. All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-013-1:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the identification and categorization process required by CIP-002-5, or any subsequent version of that Reliability Standard. |  | 12500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.5. | RP-2021-06-30-0000041 | Verification of software integrity and authenticity of all software and patches provided by the vendor for use in the BES Cyber System and their associated EACMS and PACS; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 12500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.5. | RP-2021-07-13-0000062 | A description of system conditions associated with the stability limit or IROL; and |  | RC, TOP, TP | [11 empty] | RC | [6 empty] | TOP | TP | [8 empty] | 52500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.6. | RP-2021-06-24-0000085 | Provisions to determine reliability impacts of: |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 12600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.6. | RP-2021-06-24-0000099 | Reduction of internal utility energy use; |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 22600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.6. | RP-2021-06-30-0000042 | Coordination of controls for vendor-initiated remote access. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 12600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.6. | RP-2021-07-13-0000063 | The type of limitation represented by the stability limit or IROL (e.g., voltage collapse, angular stability). |  | RC, TOP, TP | [11 empty] | RC | [6 empty] | TOP | TP | [8 empty] | 52600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.6.1. | RP-2021-06-24-0000086 | cold weather conditions; and |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 36100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.6.2. | RP-2021-06-24-0000087 | extreme weather conditions. |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 36200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.7. | RP-2021-06-24-0000100 | Use of Interruptible Load, curtailable Load and demand response; |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 22700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.7. | RP-2021-07-01-0000007 | Use of Interruptible Load, curtailable Load and demand response; |  | BA | BA | [21 empty] | 2017-04-01 | [5 empty] | 22700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.8. | RP-2021-06-24-0000101 | Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 22800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.9. | RP-2021-06-24-0000102 | Provisions to determine reliability impacts of: |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 22900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.9.1. | RP-2021-06-24-0000103 | cold weather conditions; and |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 49100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
2.9.2. | RP-2021-06-24-0000104 | extreme weather conditions. |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 49200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3 | 79780000022 | The permissible mix of Operating Reserve - Spinning and Operating Reserve - Supplemental that may be included in Contingency Reserve. |  | RRO, RSG | [14 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780000139 | Each Load-Serving Entity with load operating in an Interconnection shall ensure that those loads are included within the metered boundaries of a Balancing Authority Area. |  | LSE | [7 empty] | LSE | [14 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780000145 | Balancing Authorities shall install common metering equipment where Dynamic Schedules or Pseudo-Ties are implemented between two or more Balancing Authorities to deliver the output of Jointly Owned Units or to serve remote load. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 123000000 | NPCC-ON |  | NPCC-US
3 | 79780000164 | Each Load-Serving Entity with load operating in an Interconnection shall ensure that those loads are included within the metered boundaries of a Balancing Authority Area. |  | LSE | [7 empty] | LSE | [14 empty] | 2009-05-13 |  | 2012-09-12 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780000170 | Balancing Authorities shall install common metering equipment where Dynamic Schedules or Pseudo-Ties are implemented between two or more Balancing Authorities to deliver the output of Jointly Owned Units or to serve remote load. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2012-09-12 |  |  |  | 123000000 | NPCC-ON |  | NPCC-US
3 | 79780000189 | Each Load-Serving Entity with load operating in an Interconnection shall ensure that those loads are included within the metered boundaries of a Balancing Authority Area. |  | LSE | [7 empty] | LSE | [14 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780000195 | Balancing Authorities shall install common metering equipment where Dynamic Schedules or Pseudo-Ties are implemented between two or more Balancing Authorities to deliver the output of Jointly Owned Units or to serve remote load. |  | BA | BA | [21 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 123000000 | NPCC-ON |  | NPCC-US
3 | 79780000219 | A Balancing Authority shall make after-the-fact corrections to the agreed-to daily and monthly accounting data only as needed to reflect actual operating conditions (e.g. a meter being used for control was sending bad data). Changes or corrections based on non-reliability considerations shall not be reflected in the Balancing Authority’s Inadvertent Interchange. After-the-fact corrections to scheduled or actual values will not be accepted without agreement of the Adjacent Balancing Authority(ies). |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780000229 | A Balancing Authority shall make after-the-fact corrections to the agreed-to daily and monthly accounting data only as needed to reflect actual operating conditions (e.g. a meter being used for control was sending bad data). Changes or corrections based on non-reliability considerations shall not be reflected in the Balancing Authority’s Inadvertent Interchange. After-the-fact corrections to scheduled or actual values will not be accepted without agreement of the Adjacent Balancing Authority(ies). |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-03-31 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780000249 | Generation resources that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 12300000 | NPCC-ON |  | NPCC-US
3 | 79780000258 | The Cyber Asset is dial-up accessible. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780000263 | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780000267 | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780000271 | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780000275 | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780000281 | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780000289 | The proper handling of Critical Cyber Asset information; and, |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 22300000 | NPCC-ON |  | NPCC-US
3 | 79780000291 | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780000295 | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780000302 | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780000309 | The Responsible Entity shall maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780000314 | The review process for authorization rights, in accordance with Standard CIP-004 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 25300000 | NPCC-ON |  | NPCC-US
3 | 79780000323 | The discovery of all access points to the Electronic Security Perimeter; |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780000329 | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780000333 | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780000343 | Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780000351 | Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R2.3. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780000356 | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780000360 | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780000370 | Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780000378 | Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R2.3. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780000383 | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780000387 | The Responsible Entity shall document test results. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780000391 | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure or an acceptance of risk. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780000402 | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003 Requirement R5 and Standard CIP-004 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 51300000 | NPCC-ON |  | NPCC-US
3 | 79780000406 | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 52300000 | NPCC-ON |  | NPCC-US
3 | 79780000407 | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780000410 | Each password shall be changed at least annually, or more frequently based on risk. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 53300000 | NPCC-ON |  | NPCC-US
3 | 79780000414 | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780000420 | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 73000000 | NPCC-ON |  | NPCC-US
3 | 79780000424 | A review of controls for default accounts; and, |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  |  | 83000000 | NPCC-ON |  | NPCC-US
3 | 79780000430 | Process for reporting Cyber Security Incidents to the Electricity Sector Information Sharing and Analysis Center (ES ISAC). The Responsible Entity must ensure that all reportable Cyber Security Incidents are reported to the ES ISAC either directly or through an intermediary. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780000445 | With other Reliability Coordinators, Transmission Operators, and Balancing Authorities as necessary to maintain reliability. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780000455 | With other Reliability Coordinators, Transmission Operators, and Balancing Authorities as necessary to maintain reliability. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2009-05-13 |  | 2015-09-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780000470 | Develop, maintain, and implement a set of plans for load shedding. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780000475 | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780000482 | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  |  | 73000000 | NPCC-ON |  | NPCC-US
3 | 79780000488 | Develop, maintain, and implement a set of plans for load shedding. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780000493 | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780000500 | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780000510 | Interrupting interruptible load and exports. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780000521 | The Reliability Coordinator shall use EEA 1 to forecast the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | 93000000 | NPCC-ON |  | NPCC-US
3 | 79780000531 | Interrupting interruptible load and exports. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-09-30 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780000542 | The Reliability Coordinator shall use EEA 1 to forecast the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  | RC | [11 empty] | RC | [10 empty] | 2009-05-13 |  | 2011-09-30 |  |  |  | 93000000 | NPCC-ON |  | NPCC-US
3 | 79780000557 | Under certain adverse conditions, e.g., severe weather, it may not be possible to assess the damage caused by a disturbance and issue a written Interconnection Reliability Operating Limit and Preliminary Disturbance Report within 24 hours. In such cases, the affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load-Serving Entity shall promptly notify its Regional Reliability Organization(s) and NERC, and verbally provide as much information as is available at that time. The affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load-Serving Entity shall then provide timely, periodic verbal updates until adequate information is available to issue a written Preliminary Disturbance Report. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-12-31 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780000567 | The affected Balancing Authorities, working with their Reliability Coordinator(s), shall immediately review the Interchange Schedules between those Balancing Authority Areas or fragments of those Balancing Authority Areas within the separated area and make adjustments as needed to facilitate the restoration. The affected Balancing Authorities shall make all attempts to maintain the adjusted Interchange Schedules, whether generation control is manual or automatic. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2013-06-30 |  |  |  | 113000000 | NPCC-ON |  | NPCC-US
3 | 79780000572 | Reliability Coordinator(s) and adjacent areas are notified and Reliability Coordinator approval is given. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  |  | 115300000 | NPCC-ON |  | NPCC-US
3 | 79780000591 | Blackstart unit testing requirements including, but not limited to: |  | RRO | [14 empty] | RRO | [7 empty] | 2011-05-23 |  | 2011-05-23 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780000594 | Minimum duration of tests. |  | RRO | [14 empty] | RRO | [9 empty] | 2011-05-23 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780000600 | The contingency plan must address monitoring and control of critical transmission facilities, generation control, voltage control, time and frequency control, control of critical substation devices, and logging of significant power system events. The plan shall list the critical facilities. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780000611 | End-user facilities. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780000623 | Voltage level and MW and MVAR capacity or demand at point of connection. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780000634 | Evidence that the parties involved in the assessment have coordinated and cooperated on the assessment of the reliability impacts of new facilities on the interconnected transmission systems. While these studies may be performed independently, the results shall be jointly evaluated and coordinated by the entities involved. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [14 empty] | 2007-06-18 |  | 2011-09-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780000645 | All personnel directly involved in the design and implementation of the TVMP shall hold appropriate qualifications and training, as defined by the Transmission Owner, to perform their duties. |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780000652 | The outage information provided by the Transmission Owner to the RRO, or the RRO’s designee, shall include at a minimum: the name of the circuit(s) outaged, the date, time and duration of the outage; a description of the cause of the outage; other pertinent comments; and any countermeasures taken by the Transmission Owner. |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780000656 | Category 3 — Fall-ins: Outages caused by vegetation falling into lines from outside the ROW. |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  |  | 34300000 | NPCC-ON |  | NPCC-US
3 | 79780000690 | Consideration of the following: |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2012-12-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780000693 | Ambient conditions. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2012-12-31 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780000703 | Include a description of how to identify the subset of SOLs that qualify as IROLs. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780000709 | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-07-01 |  | 2009-04-28 |  |  |  | 22300000 | NPCC-ON |  | NPCC-US
3 | 79780000710 | Starting with all Facilities in service, the system’s response to a single Contingency, may include any of the following: |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780000713 | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-07-01 |  | 2009-04-28 |  |  |  | 23300000 | NPCC-ON |  | NPCC-US
3 | 79780000720 | Level of detail of system models used to determine SOLs. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780000727 | Each Transmission Planner that works in the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780000732 | Include a description of how to identify the subset of SOLs that qualify as IROLs. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780000738 | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 22300000 | NPCC-ON |  | NPCC-US
3 | 79780000739 | Starting with all Facilities in service, the system’s response to a single Contingency, may include any of the following: |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780000749 | Level of detail of system models used to determine SOLs. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780000756 | Each Transmission Planner that works in the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780000761 | Include a description of how to identify the subset of SOLs that qualify as IROLs. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780000767 | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. |  | RC | [11 empty] | RC | [10 empty] | 2008-10-01 |  | 2009-04-28 |  |  |  | 22300000 | NPCC-ON |  | NPCC-US
3 | 79780000768 | In determining the system’s response to a single Contingency, the following shall be acceptable: |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780000771 | System reconfiguration through manual or automatic control or protection actions. |  | RC | [11 empty] | RC | [10 empty] | 2008-10-01 |  | 2009-04-28 |  |  |  | 23300000 | NPCC-ON |  | NPCC-US
3 | 79780000776 | A process for determining which of the stability limits associated with the list of multiple contingencies (provided by the Planning Authority in accordance with FAC-014 Requirement 6) are applicable for use in the operating horizon given the actual or expected system conditions. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780000785 | Each Transmission Operator that operates in the Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780000790 | Include a description of how to identify the subset of SOLs that qualify as IROLs. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780000796 | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 22300000 | NPCC-ON |  | NPCC-US
3 | 79780000797 | In determining the system’s response to a single Contingency, the following shall be acceptable: |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780000800 | System reconfiguration through manual or automatic control or protection actions. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 23300000 | NPCC-ON |  | NPCC-US
3 | 79780000805 | A process for determining which of the stability limits associated with the list of multiple contingencies (provided by the Planning Authority in accordance with FAC-014 Requirement 6) are applicable for use in the operating horizon given the actual or expected system conditions. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780000814 | Each Transmission Operator that operates in the Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780000819 | A description of how each of the following is addressed, including any reliability margins applied to reflect uncertainty with projected BES conditions: |  | PCPA, RC | [9 empty] | PA |  | RC | [12 empty] | 2013-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780000822 | Generation dispatch |  | PCPA, RC | [9 empty] | PA |  | RC | [12 empty] | 2013-03-31 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780000827 | Each Transmission Operator that operates in the Reliability Coordinator Area. |  | RC | [11 empty] | RC | [12 empty] | 2013-03-31 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780000831 | Each Reliability Coordinator and Transmission Operator that operates any portion of the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PA | [14 empty] | 2013-03-31 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780000845 | The associated Contingency(ies). |  | RC | [11 empty] | RC | [10 empty] | 2009-01-01 |  | 2009-04-28 |  |  |  | 51300000 | NPCC-ON |  | NPCC-US
3 | 79780000848 | The Planning Authority shall provide its SOLs (including the subset of SOLs that are IROLs) to adjacent Planning Authorities, and to Transmission Planners, Transmission Service Providers, Transmission Operators and Reliability Coordinators that work within its Planning Authority Area. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780000861 | The associated Contingency(ies). |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 | [5 empty] | 51300000 | NPCC-ON |  | NPCC-US
3 | 79780000864 | The Planning Authority shall provide its SOLs (including the subset of SOLs that are IROLs) to adjacent Planning Authorities, and to Transmission Planners, Transmission Service Providers, Transmission Operators and Reliability Coordinators that work within its Planning Authority Area. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 | [5 empty] | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780000895 | A Reliability Coordinator or Transmission Operator determines the deviation, regardless of magnitude, to be a reliability concern and notifies the Purchasing-Selling Entity of that determination and the reasons. |  | RC, TOP | [11 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2008-08-26 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780000900 | A Reliability Coordinator or Transmission Operator determines the deviation, regardless of magnitude, to be a reliability concern and notifies the Purchasing-Selling Entity of that determination and the reasons. |  | PSE | [10 empty] | PSE | [11 empty] | 2008-08-27 |  | 2014-09-30 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780000911 | Scheduling path (proper connectivity of Adjacent Balancing Authorities). |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 11300000 | NPCC-ON |  | NPCC-US
3 | 79780000917 | Scheduling path (proper connectivity of Adjacent Balancing Authorities). |  | BA | BA | [21 empty] | 2008-08-27 |  | 2010-06-30 |  |  |  | 11300000 | NPCC-ON |  | NPCC-US
3 | 79780000923 | Scheduling path (proper connectivity of Adjacent Balancing Authorities). |  | BA | BA | [21 empty] | 2010-07-01 |  | 2014-09-30 |  |  |  | 11300000 | NPCC-ON |  | NPCC-US
3 | 79780000928 | The following are defined: |  | IA | [6 empty] | IA | [15 empty] | 2007-06-18 |  | 2014-09-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780000931 | Ramp start and stop times. |  | IA | [6 empty] | IA | [15 empty] | 2007-06-18 |  | 2014-09-30 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780000999 | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001026 | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001053 | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001075 | The Interconnection-wide transmission loading relief procedure for use in ERCOT is provided as Section 7 of the ERCOT Protocols, posted at: &lt;a href=&quot;http://www.ercot.com/tac/retailisoadhoccommittee/protocols/keydocs/draftercotprotocols.htm.&quot;&gt;http://www.ercot.com/tac/retailisoadhoccommittee/protocols/keydocs/draftercotprotocols.htm.&lt;/a&gt; |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-04-22 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780001083 | The Interconnection-wide transmission loading relief procedure for use in ERCOT is provided as Section 7 of the ERCOT Protocols, posted at: &lt;a href=&quot;http://www.ercot.com/mktrules/protocols/current.html&quot;&gt;http://www.ercot.com/mktrules/protocols/current.html&lt;/a&gt; |  | RC | [11 empty] | RC | [10 empty] | 2009-04-23 |  | 2009-12-09 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001101 | Timeframe and periodicity for providing data and information (based on its hardware and software requirements, and the time needed to do its Operational Planning Analyses). |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2009-08-05 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001109 | Planned or unplanned outage information. |  | RC | [11 empty] | RC | [9 empty] | M1.1.3 Planned or unplanned outage information. | 2007-06-18 |  | 2017-03-31 |  |  |  | 11300000 | NPCC-ON |  | NPCC-US
3 | 79780001122 | Be reviewed, at least once every three years, and updated if needed. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780001133 | If the involved Reliability Coordinators cannot agree on the solution, the more conservative solution shall be implemented. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001139 | An accounting for the ultimate points of power injection (sources) and power extraction (sinks) in TTC and ATC calculations. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001144 | Monthly values for months 2 through 13 at least once per month. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 15300000 | NPCC-ON |  | NPCC-US
3 | 79780001154 | Monthly values for at least the next 12 months (months 2-13). |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780001160 | The identity of the Transmission Operators and Transmission Service Providers from which the Transmission Service Provider receives data for use in calculating ATC or AFC. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780001166 | How outages from other Transmission Service Providers that can not be mapped to the Transmission model used to calculate transfer or Flowgate capability are addressed. |  | TSP | [20 empty] | TSP |  |  |  | 2010-09-16 |  |  |  | 36300000 | NPCC-ON |  | NPCC-US
3 | 79780001170 | Each Transmission Operator associated with the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780001180 | Monthly values, once per week. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 83000000 | NPCC-ON |  | NPCC-US
3 | 79780001185 | If the Transmission Service Provider does not use the data requested in its transfer or Flowgate capability calculations, and does not maintain that data, it shall not be required to make that data available. |  | TSP | [20 empty] | TSP |  |  |  | 2010-09-16 |  |  |  | 91300000 | NPCC-ON |  | NPCC-US
3 | 79780001193 | The manner in which the response will be communicated (e.g., email, letter, telephone, etc). |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001200 | Require that generation unit outages considered in a Transmission Service Provider’s CBM calculation be restricted to those units within the Transmission Service Provider’s system. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001211 | The procedure for a Load-Serving Entity or Balancing Authority to use Transmission capacity set aside as CBM, including the manner in which the Transmission Service Provider will manage situations where the requested use of CBM exceeds the amount of CBM available. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001217 | The Load of the “energy deficient entity” is located within the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 123000000 | NPCC-ON |  | NPCC-US
3 | 79780001239 | Require review of the consistency of the Transmission Service Provider’s CBM components with its published planning criteria. A CBM value is considered consistent with published planning criteria if the components that comprise CBM are addressed in the planning criteria. The methodology used to determine and apply CBM does not have to involve the same mechanics as the planning process, but the same uncertainties must be considered and any simplifying assumptions explained. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001246 | Describe the conditions under which CBM may be available as Non-Firm Transmission Service. |  | TSP | [20 empty] | TSP |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001251 | Describe the conditions under which CBM may be available as Non-Firm Transmission Service. |  | TSP | [20 empty] | TSP |  | 2009-05-13 |  | 2011-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001257 | Amount of CBM used. |  | TSP | [20 empty] | TSP |  | 2007-06-18 |  | 2011-03-31 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780001261 | Specify the uncertainties accounted for in TRM and the methods used to determine their impacts on the TRM values. Any component of uncertainty, other than those identified in MOD-008-0_R1.3.1 through MOD-008-0_R1.3.7, shall benefit the interconnected transmission systems as a whole before they shall be permitted to be included in TRM calculations. The components of uncertainty identified in MOD-008-0_R1.3.1 through MOD-008-0_R1.3.7, if applied, shall be accounted for solely in TRM and not CBM. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001264 | Variations in facility Loadings due to balancing of generation within a Balancing Authority Area. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780001276 | The identification of the TRM calculation used for the following time periods: |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 | [5 empty] | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001279 | Beyond day-ahead and pre-schedule, up to thirteen months ahead. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 | [5 empty] | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780001287 | Require review of the consistency of the Transmission Service Provider’s TRM components with its published planning criteria. A TRM value is considered consistent with published planning criteria if the same components that comprise TRM are also addressed in the planning criteria. The methodology used to determine and apply TRM does not have to involve the same mechanics as the planning process, but the same uncertainties must be considered and any simplifying assumption explained. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001296 | AC Transmission Line or Circuit (overhead and underground): nominal voltage, impedance, line charging, Normal and Emergency Ratings (consistent with methodologies defined and Ratings supplied per Reliability Standard FAC-004-0 and FAC-005-0 ) equipment status, and metering locations. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001310 | Device specific dynamics data shall be reported for dynamic devices, including, among others, static VAR controllers, high voltage direct current systems, flexible AC transmission systems, and static compensators. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001337 | Monthly peak hour forecast demands in MW and Net Energy for Load in GWh for the next two years. |  | LSE, PCPA, RP | [7 empty] | LSE |  | PA |  |  |  | RP | [8 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001342 | Monthly peak hour forecast demands in MW and Net Energy for Load in GWh for the next two years. |  | LSE, PCPA, RP | [7 empty] | LSE |  | PA |  |  |  | RP | [8 empty] | 2009-05-13 |  | 2016-06-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001347 | Items (MOD-018-0_R 1.1) and (MOD-018-0_R 1.2) shall be addressed as described in the reporting procedures developed for Standard MOD-016-1_R 1. |  | LSE, PCPA, RP, TP | [7 empty] | LSE |  | PA |  |  |  | RP | [5 empty] | TP |  |  | 2007-06-18 |  | 2016-06-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001358 | Acceptable methods for model and data verification, including any applicable conditions under which the data should be verified. Such methods can include use of manufacturer data, commissioning data, performance tracking, and testing, etc. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001363 | Method of verification, including date and conditions. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 15300000 | NPCC-ON |  | NPCC-US
3 | 79780001369 | Acceptable methods for model and data verification, including any applicable conditions under which the data should be verified. Such methods can include use of commissioning data, performance tracking, engineering analysis, testing, etc. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001374 | Verified Reactive Power of auxiliary loads. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 15300000 | NPCC-ON |  | NPCC-US
3 | 79780001381 | Any contractual obligations for allocation of TTC. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2013-09-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001386 | The source/sink or POR/POD identification and mapping to the model. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2013-09-30 |  |  |  | 15300000 | NPCC-ON |  | NPCC-US
3 | 79780001393 | Facility Ratings specified by the Generator Owners and Transmission Owners. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780001398 | Unit commitment and dispatch order, to include all designated network resources and other resources that are committed or have the legal obligation to run, (within or out of economic dispatch) as they are expected to run. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2013-09-30 |  |  |  | 31300000 | NPCC-ON |  | NPCC-US
3 | 79780001402 | Unit commitment and dispatch order, to include all designated network resources and other resources that are committed or have the legal obligation to run, (within or out of economic dispatch) as they are expected to run. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2013-09-30 |  |  |  | 32300000 | NPCC-ON |  | NPCC-US
3 | 79780001406 | Include, for each time period, the Firm Transmission Service expected to be scheduled as specified in the ATCID (filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers) for the Transmission Service Provider, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed modeling the source and sink as follows: - If the source, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the source, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the sink, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point shall as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can not be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is to be delivered as the sink. - If the sink, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is being delivered as the sink. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780001410 | Within 24 hours of the unexpected outage of a 500 kV or higher transmission Facility or a transformer with a low-side voltage of 200 kV or higher for TTCs in effect during the anticipated duration of the outage, provided such outage is expected to last 24 hours or longer. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780001414 | Use (as the TTC) the lesser of: The sum of the incremental Transfer Capability and the impacts of Firm Transmission Services, as specified in the Transmission Service Provider’s ATCID, that were included in the study model, or The sum of Facility Ratings of all ties comprising the ATC Path. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780001426 | Any other Transmission Operator area linked to the Transmission Operator’s area by joint operating agreement. (Equivalent representation is allowed.) |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 11130000 | NPCC-ON |  | NPCC-US
3 | 79780001429 | Models all generation (may be either a single generator or multiple generators) that is greater than 20 MVA at the point of interconnection in the studied area. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 11300000 | NPCC-ON |  | NPCC-US
3 | 79780001441 | Uncontrolled separation shall not occur. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780001443 | For an ATC Path whose capacity is limited by contract, set TTC on the ATC Path at the lesser of the maximum allowable contract capacity or the reliability limit as determined by R2.1. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780001460 | The source/sink or POR/POD identification and mapping to the model. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 12300000 | NPCC-ON |  | NPCC-US
3 | 79780001465 | For monthly AFC, once per week. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 103000000 | NPCC-ON |  | NPCC-US
3 | 79780001475 | Any limiting Element/Contingency combination at least within the Transmission model identified in R3.4 and R3.5 that has been subjected to an Interconnection-wide congestion management procedure within the last 12 months, unless the limiting Element/Contingency combination is accounted for using another ATC methodology. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780001480 | At a minimum, establish the list of Flowgates to create, modify, or delete external Flowgates that have been requested as part of R2.1.4 within thirty calendar days from the request. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780001488 | Updated at least once per month for AFC calculations for months two through 13. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780001495 | For external Flowgates, identified in R2.1.4, use the AFC provided by the Transmission Service Provider that calculates AFC for that Flowgate. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780001503 | The impact of all confirmed firm Point-to-Point Transmission Service expected to be scheduled, including roll-over rights for Firm Transmission Service contracts, for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780001511 | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 73000000 | NPCC-ON |  | NPCC-US
3 | 79780001523 | The source/sink or POR/POD identification and mapping to the model. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 12300000 | NPCC-ON |  | NPCC-US
3 | 79780001528 | For monthly AFC, once per week. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 103000000 | NPCC-ON |  | NPCC-US
3 | 79780001539 | If any limiting element is kept within its limit for its associated worst Contingency by operating within the limits of another Flowgate, then no new Flowgate needs to be established for such limiting elements or Contingencies. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21230000 | NPCC-ON |  | NPCC-US
3 | 79780001540 | Any limiting Element/Contingency combination at least within its Reliability Coordinator’s Area that has been subjected to an Interconnection-wide congestion management procedure within the last 12 months, unless the limiting Element/Contingency combination is accounted for using another ATC methodology or was created to address temporary operating conditions. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780001545 | At a minimum, establish a list of Flowgates by creating, modifying, or deleting Flowgates that have been requested as part of R2.1.4 within thirty calendar days from the request. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780001553 | Updated at least once per month for AFC calculations for months two through 13. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780001560 | For external Flowgates, identified in R2.1.4, use the AFC provided by the Transmission Service Provider that calculates AFC for that Flowgate. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780001568 | The impact of all confirmed firm Point-to-Point Transmission Service expected to be scheduled, including roll-over rights for Firm Transmission Service contracts, for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780001576 | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 73000000 | NPCC-ON |  | NPCC-US
3 | 79780001589 | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2008-11-26 |  | 2010-03-31 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780001598 | A requirement to review the agreement(s) at least every three years. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 91300000 | NPCC-ON |  | NPCC-US
3 | 79780001603 | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 92300000 | NPCC-ON |  | NPCC-US
3 | 79780001604 | Operations and maintenance coordination: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2008-11-26 |  | 2010-03-31 |  |  |  | 93000000 | NPCC-ON |  | NPCC-US
3 | 79780001607 | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 93300000 | NPCC-ON |  | NPCC-US
3 | 79780001615 | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 94300000 | NPCC-ON |  | NPCC-US
3 | 79780001626 | The training program must include training time for all Transmission Operator and Balancing Authority operating personnel to ensure their operating proficiency. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-03-31 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780001643 | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall deliver the training established in R1.2. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | M1.3 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection System Operator training records showing the names of the people trained, the title of the training delivered and the dates of delivery to show that it delivered the training, as specified in R1.3. | 2013-04-01 |  | 2016-06-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001669 | Electrical quantities to be recorded for each monitored element shall be sufficient to determine the following: |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780001672 | Polarizing currents and voltages, if used. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 21330000 | NPCC-ON |  | NPCC-US
3 | 79780001678 | Event triggering requirements. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 22300000 | NPCC-ON |  | NPCC-US
3 | 79780001683 | Electrical quantities to be recorded for each monitored element shall be sufficient to determine the following: |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 31300000 | NPCC-ON |  | NPCC-US
3 | 79780001692 | Timetable for response to data request. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780001701 | Process for review, analysis follow up, and documentation of Corrective Action Plans for Misoperations. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001738 | Intentional and total tripping time delays. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  |  | 12300000 | NPCC-ON |  | NPCC-US
3 | 79780001744 | A Regional Reliability Organization UFLS program database. This database shall be updated as specified in the Regional Reliability Organization program (but at least every five years) and shall include sufficient information to model the UFLS program in dynamic simulations of the interconnected transmission systems. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001758 | A simulation of the event. |  | DP, LSE, TO, TOP |  | DP | [5 empty] | LSE | [9 empty] | TO | TOP |  |  |  | 2007-06-18 |  | 2013-09-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001765 | A review of the voltage set points and timing. |  | DP, LSE, TO, TOP |  | DP | [5 empty] | LSE | [9 empty] | TO | TOP |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  |  | 11300000 | NPCC-ON |  | NPCC-US
3 | 79780001771 | Communications systems, where appropriate. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2021-03-31 |  |  |  | 11300000 | NPCC-ON |  | NPCC-US
3 | 79780001774 | Summary of testing procedure. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2021-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001782 | Requirements to demonstrate that the SPS shall be designed so that a single SPS component failure, when the SPS was intended to operate, does not prevent the interconnected transmission system from meeting the performance requirements defined in Reliability Standards TPL-001-0, TPL-002-0, and TPL-003-0. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001793 | Modeling — Information on detection logic or relay settings that control operation of the SPS. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001800 | Identification of SPSs that were found not to comply with NERC standards and Regional Reliability Organization criteria. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780001816 | Communications systems, where appropriate. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 11300000 | NPCC-ON |  | NPCC-US
3 | 79780001819 | Summary of testing procedure. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001831 | Installation location. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2022-06-30 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780001845 | Corresponding voltage set points and overall scheme clearing times. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001853 | Time delay from initiation to trip signal. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001860 | A simulation of the event, if deemed appropriate by the Regional Reliability Organization. For most events, analysis of sequence of events may be sufficient and dynamic simulations may not be needed. |  | DP, LSE, TOP |  | DP | [5 empty] | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001871 | Include a relay setting component of 87% of the current calculated in R1.12.2 in the Facility Rating determination for the circuit. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  |  | 20500000 | NPCC-ON |  | NPCC-US
3 | 79780001874 | Set transmission line relays so they do not operate at or below 115% of the maximum theoretical power transfer capability (using a 90-degree angle between the sending-end and receiving-end voltages and either reactance or complex impedance) of the circuit (expressed in amperes) using one of the following to perform the power transfer calculation: |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001888 | The Planning Coordinator shall provide a list of facilities to its Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within 30 days of the establishment of the initial list and within 30 days of any changes to the list. |  | PCPA | [9 empty] | PA | [12 empty] | 2011-11-17 |  | 2012-06-30 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780001901 | When time does not permit such notifications and coordination, or when immediate action is required to prevent a hazard to the public, lengthy customer service interruption, or damage to facilities, the Generator Operator shall notify the Transmission Operator, and the Transmission Operator shall notify its Reliability Coordinator and adjacent Transmission Operators, at the earliest possible time. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-11-20 |  |  |  | 73000000 | NPCC-ON |  | NPCC-US
3 | 79780001952 | Such information shall be available by 1200 Central Standard Time for the Eastern Interconnection and 1200 Pacific Standard Time for the Western Interconnection. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-09-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001959 | Such information shall be available by 1200 Central Standard Time for the Eastern Interconnection and 1200 Pacific Standard Time for the Western Interconnection. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-05-23 |  | 2017-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780001971 | Switching transmission elements. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-01-21 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780001983 | Planned outages of transmission elements. |  | TOP | [18 empty] | TOP |  |  |  | 2009-01-22 |  | 2017-03-31 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780002036 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category A of Table 1 (no contingencies). The specific elements selected (from each of the following categories) shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002039 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780002051 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780002057 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category A of Table 1 (no contingencies). The specific elements selected (from each of the following categories) shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002060 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780002072 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780002078 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category B of Table 1 (single contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002084 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780002097 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780002103 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories,, showing system performance following Category B of Table 1 (single contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002109 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780002122 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780002128 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002134 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780002147 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780002153 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002159 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780002172 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780002178 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002181 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780002194 | Other system conditions as deemed appropriate by the Regional Reliability Organization. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  |  | 11300000 | NPCC-ON |  | NPCC-US
3 | 79780002196 | Longer-term planning horizons (years six through ten). Assessment shall focus on the analysis of trends in resources and transmission Adequacy, other industry trends and developments, and reliability concerns. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002202 | Evaluations of emergency response preparedness. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780002209 | Demand-Side resources and their characteristics (program ratings, effects on annual system loads and load shapes, contractual arrangements, and program durations.) |  | RRO | [14 empty] | RRO | [9 empty] | 2009-04-15 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002257 | Impedance data. |  | GO | [22 empty] | 2007-08-02 |  | 2008-08-26 |  |  |  | 41300000 | NPCC-ON |  | NPCC-US
3 | 79780002272 | Impedance data. |  | GO | [22 empty] | 2009-05-13 |  | 2010-09-15 |  |  |  | 41300000 | NPCC-ON |  | NPCC-US
3 | 79780002287 | Impedance data. |  | GO | [22 empty] | 2010-09-16 |  | 2013-06-30 |  |  |  | 41300000 | NPCC-ON |  | NPCC-US
3 | 79780002302 | Impedance data. |  | GO | [22 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 41300000 | NPCC-ON |  | NPCC-US
3 | 79780002337 | The Interconnection-wide transmission loading relief procedure for use in ERCOT is provided as Section 7 of the ERCOT Protocols, posted at: &lt;a href=&quot;http://www.ercot.com/mktrules/protocols/current.html&quot;&gt;http://www.ercot.com/mktrules/protocols/current.html&lt;/a&gt; |  | RC | [11 empty] | RC | [10 empty] | 2009-12-10 |  | 2011-06-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002349 | Demand-Side resources and their characteristics (program ratings, effects on annual system loads and load shapes, contractual arrangements, and program durations.) |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002359 | Generation resources that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 12300000 | NPCC-ON |  | NPCC-US
3 | 79780002368 | The Cyber Asset is dial-up accessible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780002373 | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002377 | Where allowed by Standards CIP-002-2 through CIP-009-2, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780002382 | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780002386 | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780002392 | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780002400 | The proper handling of Critical Cyber Asset information; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 22300000 | NPCC-ON |  | NPCC-US
3 | 79780002402 | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780002406 | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780002413 | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002420 | The Responsible Entity shall implement and maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780002425 | The review process for authorization rights, in accordance with Standard CIP-004-2 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 25300000 | NPCC-ON |  | NPCC-US
3 | 79780002434 | The discovery of all access points to the Electronic Security Perimeter; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780002440 | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780002444 | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002461 | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  |  | 83000000 | NPCC-ON |  | NPCC-US
3 | 79780002465 | The Responsible Entity shall document test results. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002469 | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780002480 | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-2 Requirement R5 and Standard CIP-004-2 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 51300000 | NPCC-ON |  | NPCC-US
3 | 79780002484 | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 52300000 | NPCC-ON |  | NPCC-US
3 | 79780002485 | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780002488 | Each password shall be changed at least annually, or more frequently based on risk. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 53300000 | NPCC-ON |  | NPCC-US
3 | 79780002492 | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780002498 | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  |  | 73000000 | NPCC-ON |  | NPCC-US
3 | 79780002502 | A review of controls for default accounts; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  |  | 83000000 | NPCC-ON |  | NPCC-US
3 | 79780002508 | Process for reporting Cyber Security Incidents to the Electricity Sector Information Sharing and Analysis Center (ES-ISAC). The Responsible Entity must ensure that all reportable Cyber Security Incidents are reported to the ES-ISAC either directly or through an intermediary. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002526 | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780002535 | A requirement to review the agreement(s) at least every three years. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2014-01-21 |  |  |  | 91300000 | NPCC-ON |  | NPCC-US
3 | 79780002540 | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 92300000 | NPCC-ON |  | NPCC-US
3 | 79780002541 | Operations and maintenance coordination: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 93000000 | NPCC-ON |  | NPCC-US
3 | 79780002544 | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 93300000 | NPCC-ON |  | NPCC-US
3 | 79780002552 | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 94300000 | NPCC-ON |  | NPCC-US
3 | 79780002559 | Develop, maintain, and implement a set of plans for load shedding. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780002563 | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780002570 | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780002575 | Procedures for restoring interconnections with other Transmission Operators under the direction of the Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002585 | Building of cranking paths. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  |  | 103000000 | NPCC-ON |  | NPCC-US
3 | 79780002608 | The capability of generating resources required to control voltages and frequency within acceptable operating limits. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780002616 | The minimum duration of each of the required tests. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  |  | 93000000 | NPCC-ON |  | NPCC-US
3 | 79780002620 | Descriptions of the elements of coordination between individual Transmission Operator restoration plans. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002650 | The Responsible Entity shall document test results. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002655 | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780002662 | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780002665 | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-2 Requirement R5 and Standard CIP-004-2 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 51300000 | NPCC-ON |  | NPCC-US
3 | 79780002666 | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 52300000 | NPCC-ON |  | NPCC-US
3 | 79780002669 | Each password shall be changed at least annually, or more frequently based on risk. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 53300000 | NPCC-ON |  | NPCC-US
3 | 79780002675 | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780002679 | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  |  | 73000000 | NPCC-ON |  | NPCC-US
3 | 79780002681 | A review of controls for default accounts; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  |  | 83000000 | NPCC-ON |  | NPCC-US
3 | 79780002689 | Include a description of how to identify the subset of SOLs that qualify as IROLs. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002692 | Starting with all Facilities in service, the system’s response to a single Contingency, may include any of the following: |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780002698 | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 22300000 | NPCC-ON |  | NPCC-US
3 | 79780002704 | Level of detail of system models used to determine SOLs. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780002711 | Each Transmission Planner that works in the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780002718 | Generation resources that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | 12300000 | NPCC-ON |  | NPCC-US
3 | 79780002727 | The Cyber Asset is dial-up accessible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780002732 | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002736 | Where allowed by Standards CIP-002-3 through CIP-009-3, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780002741 | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780002745 | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780002751 | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780002759 | The proper handling of Critical Cyber Asset information; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2012-12-11 |  |  |  | 22300000 | NPCC-ON |  | NPCC-US
3 | 79780002761 | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2012-12-11 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780002765 | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2012-12-11 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780002772 | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002779 | The Responsible Entity shall implement and maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780002784 | The review process for authorization rights, in accordance with Standard CIP-004-3 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2011-02-01 |  |  |  | 25300000 | NPCC-ON |  | NPCC-US
3 | 79780002793 | The discovery of all access points to the Electronic Security Perimeter; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780002799 | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780002803 | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002822 | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  |  | 83000000 | NPCC-ON |  | NPCC-US
3 | 79780002826 | The Responsible Entity shall document test results. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002830 | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780002841 | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-3 Requirement R5 and Standard CIP-004-3 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 51300000 | NPCC-ON |  | NPCC-US
3 | 79780002845 | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 52300000 | NPCC-ON |  | NPCC-US
3 | 79780002846 | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780002849 | Each password shall be changed at least annually, or more frequently based on risk. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 53300000 | NPCC-ON |  | NPCC-US
3 | 79780002853 | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780002859 | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 73000000 | NPCC-ON |  | NPCC-US
3 | 79780002863 | A review of controls for default accounts; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 83000000 | NPCC-ON |  | NPCC-US
3 | 79780002869 | Process for reporting Cyber Security Incidents to the Electricity Sector Information Sharing and Analysis Center (ES-ISAC). The Responsible Entity must ensure that all reportable Cyber Security Incidents are reported to the ES-ISAC either directly or through an intermediary. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002895 | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002901 | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  |  | 83000000 | NPCC-ON |  | NPCC-US
3 | 79780002916 | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002922 | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  |  | 83000000 | NPCC-ON |  | NPCC-US
3 | 79780002934 | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002940 | Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780002946 | Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R2.3. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780002949 | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780002957 | Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R2.3. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780002965 | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002969 | Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780002974 | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780002991 | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780002999 | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  |  | 83000000 | NPCC-ON |  | NPCC-US
3 | 79780003011 | Monthly values for at least the next 12 months (months 2-13). |  | TSP | [20 empty] | TSP | M2.3 - - There has been at least the next 12 months of monthly values calculated at all times (Months 2-13). | 2010-09-16 | [5 empty] | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780003012 | The identity of the Transmission Operators and Transmission Service Providers from which the Transmission Service Provider receives data for use in calculating ATC or AFC. |  | TSP | [20 empty] | TSP |  | 2010-09-16 | [5 empty] | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780003020 | How outages from other Transmission Service Providers that can not be mapped to the Transmission model used to calculate transfer or Flowgate capability are addressed. |  | TSP | [20 empty] | TSP |  | 2011-04-01 | [5 empty] | 36300000 | NPCC-ON |  | NPCC-US
3 | 79780003023 | Each Transmission Operator associated with the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-09-16 | [5 empty] | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780003031 | Monthly values, once per week. |  | TSP | [20 empty] | TSP |  | 2010-09-16 | [5 empty] | 83000000 | NPCC-ON |  | NPCC-US
3 | 79780003035 | If the Transmission Service Provider does not use the data requested in its transfer or Flowgate capability calculations, and does not maintain that data, it shall not be required to make that data available. |  | TSP | [20 empty] | TSP |  | 2011-04-01 | [5 empty] | 91300000 | NPCC-ON |  | NPCC-US
3 | 79780003056 | Models all generation (may be either a single generator or multiple generators) that is greater than 20 MVA at the point of interconnection in the studied area. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 11300000 | NPCC-ON |  | NPCC-US
3 | 79780003060 | For an ATC Path whose capacity is limited by contract, set TTC on the ATC Path at the lesser of the maximum allowable contract capacity or the reliability limit as determined by R2.1. |  | TOP | [18 empty] | TOP |  |  |  | 2010-09-16 |  | 2017-03-31 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780003070 | Uncontrolled separation shall not occur. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780003076 | Timeframe and periodicity for providing data and information (based on its hardware and software requirements, and the time needed to do its Operational Planning Analyses). |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2017-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780003157 | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780003165 | The Responsible Entity shall implement and maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780003170 | The review process for authorization rights, in accordance with Standard CIP-004-3 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | 25300000 | NPCC-ON |  | NPCC-US
3 | 79780003176 | The discovery of all access points to the Electronic Security Perimeter; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780003182 | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780003188 | The permissible mix of Operating Reserve – Spinning and Operating Reserve – Supplemental that may be included in Contingency Reserve. |  | RRO, RSG | [14 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780003211 | A Balancing Authority shall make after-the-fact corrections to the agreed-to daily and monthly accounting data only as needed to reflect actual operating conditions (e.g. a meter being used for control was sending bad data). Changes or corrections based on non-reliability considerations shall not be reflected in the Balancing Authority’s Inadvertent Interchange. After-the-fact corrections to scheduled or actual values will not be accepted without agreement of the Adjacent Balancing Authority(ies). |  | BA | BA | [21 empty] | 2011-04-01 |  | 2018-12-31 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780003221 | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780003225 | Where allowed by Standards CIP-002-4 through CIP-009-4, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780003230 | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780003234 | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780003240 | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780003248 | The proper handling of Critical Cyber Asset information; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2012-12-11 |  |  |  | 22300000 | NPCC-ON |  | NPCC-US
3 | 79780003250 | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2012-12-11 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780003254 | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2012-12-11 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780003261 | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780003268 | The Responsible Entity shall implement and maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780003273 | The review process for authorization rights, in accordance with Standard CIP-004-4 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 25300000 | NPCC-ON |  | NPCC-US
3 | 79780003282 | The discovery of all access points to the Electronic Security Perimeter; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780003288 | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780003292 | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780003311 | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 83000000 | NPCC-ON |  | NPCC-US
3 | 79780003315 | The Responsible Entity shall document test results. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780003319 | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780003330 | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-4 Requirement R5 and Standard CIP-004-4 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 51300000 | NPCC-ON |  | NPCC-US
3 | 79780003334 | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 52300000 | NPCC-ON |  | NPCC-US
3 | 79780003335 | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780003338 | Each password shall be changed at least annually, or more frequently based on risk. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 53300000 | NPCC-ON |  | NPCC-US
3 | 79780003342 | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780003348 | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 73000000 | NPCC-ON |  | NPCC-US
3 | 79780003352 | A review of controls for default accounts; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 83000000 | NPCC-ON |  | NPCC-US
3 | 79780003358 | Process for reporting Cyber Security Incidents to the Electricity Sector Information Sharing and Analysis Center (ES-ISAC). The Responsible Entity must ensure that all reportable Cyber Security Incidents are reported to the ES-ISAC either directly or through an intermediary. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780003378 | Interrupting interruptible load and exports. |  | BA | BA | [21 empty] | 2011-01-10 |  | 2012-09-12 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780003389 | The Reliability Coordinator shall use EEA 1 to forecast the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  | RC | [11 empty] | RC | [10 empty] | 2011-01-10 |  | 2012-09-12 |  |  |  | 93000000 | NPCC-ON |  | NPCC-US
3 | 79780003410 | Evidence that the parties involved in the assessment have coordinated and cooperated on the assessment of the reliability impacts of new facilities on the interconnected transmission systems. While these studies may be performed independently, the results shall be jointly evaluated and coordinated by the entities involved. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [14 empty] | 2011-01-10 |  | 2015-12-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780003424 | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780003455 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category A of Table 1 (no contingencies). The specific elements selected (from each of the following categories) shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780003458 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780003470 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780003476 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories,, showing system performance following Category B of Table 1 (single contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780003482 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780003495 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780003501 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category B of Table 1 (single contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780003507 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780003520 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780003526 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780003532 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780003545 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780003551 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780003554 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780003621 | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780003629 | The Responsible Entity shall maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780003634 | The review process for authorization rights, in accordance with Standard CIP-004 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 25300000 | NPCC-ON |  | NPCC-US
3 | 79780003640 | The discovery of all access points to the Electronic Security Perimeter; |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780003646 | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780003652 | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780003660 | The Responsible Entity shall implement and maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780003665 | The review process for authorization rights, in accordance with Standard CIP-004-2 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 25300000 | NPCC-ON |  | NPCC-US
3 | 79780003671 | The discovery of all access points to the Electronic Security Perimeter; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780003677 | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780003696 | Each Load-Serving Entity with load operating in an Interconnection shall ensure that those loads are included within the metered boundaries of a Balancing Authority Area. |  | LSE | [7 empty] | LSE | [16 empty] | 2008-04-15 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780003700 | Balancing Authorities shall install common metering equipment where Dynamic Schedules or Pseudo-Ties are implemented between two or more Balancing Authorities to deliver the output of Jointly Owned Units or to serve remote load. |  | BA | BA | [23 empty] | 2008-04-15 |  |  |  | 123000000 | NPCC-ON |  | NPCC-US
3 | 79780003807 | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780003821 | When time does not permit such notifications and coordination, or when immediate action is required to prevent a hazard to the public, lengthy customer service interruption, or damage to facilities, the Generator Operator shall notify the Transmission Operator, and the Transmission Operator shall notify its Reliability Coordinator and adjacent Transmission Operators, at the earliest possible time. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-11-21 |  | 2017-03-31 |  |  |  | 73000000 | NPCC-ON |  | NPCC-US
3 | 79780003835 | Develop, maintain, and implement a set of plans for load shedding. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780003838 | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780003843 | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  |  | 73000000 | NPCC-ON |  | NPCC-US
3 | 79780003853 | Develop, maintain, and implement a set of plans for load shedding. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780003855 | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780003860 | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780003904 | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780003910 | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  |  | 83000000 | NPCC-ON |  | NPCC-US
3 | 79780003925 | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780003933 | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  |  | 83000000 | NPCC-ON |  | NPCC-US
3 | 79780003963 | Any contractual obligations for allocation of TTC. |  | TSP | [20 empty] | TSP |  | 2013-09-27 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780003968 | The source/sink or POR/POD identification and mapping to the model. |  | TSP | [20 empty] | TSP |  | 2013-10-01 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 15300000 | NPCC-ON |  | NPCC-US
3 | 79780003975 | Facility Ratings specified by the Generator Owners and Transmission Owners. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780003980 | A daily load forecast for TTCs used in ATC calculations for days two through 31. |  | TOP | [18 empty] | TOP |  |  |  | 2013-10-01 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 31300000 | NPCC-ON |  | NPCC-US
3 | 79780003986 | Include, for each time period, the Firm Transmission Service expected to be scheduled as specified in the ATCID (filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers) for the Transmission Service Provider, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed modeling the source and sink as follows:&lt;br/&gt;- If the source, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the source.&lt;br/&gt;- If the source, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the source.&lt;br/&gt;- If the source, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source.&lt;br/&gt;- If the source, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source.&lt;br/&gt;- If the sink, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point shall as the sink.&lt;br/&gt;- If the sink, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the sink.&lt;br/&gt;- If the sink, as specified in the ATCID, has been identified in the reservation and the point can not be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is to be delivered as the sink.&lt;br/&gt;- If the sink, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is being delivered as the sink. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780003990 | Within 24 hours of the unexpected outage of a 500 kV or higher transmission Facility or a transformer with a low-side voltage of 200 kV or higher for TTCs in effect during the anticipated duration of the outage, provided such outage is expected to last 24 hours or longer. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780003994 | Use (as the TTC) the lesser of:&lt;br/&gt;- The sum of the incremental Transfer Capability and the impacts of Firm Transmission Services, as specified in the Transmission Service Provider’s ATCID, that were included in the study model, or&lt;br/&gt;- The sum of Facility Ratings of all ties comprising the ATC Path. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780004037 | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 83000000 | NPCC-ON |  | NPCC-US
3 | 79780004043 | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780004064 | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780004072 | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 83000000 | NPCC-ON |  | NPCC-US
3 | 79780004091 | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780004093 | Develop, maintain, and implement a set of plans for load shedding. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780004097 | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780004117 | Each Load-Serving Entity with load operating in an Interconnection shall ensure that those loads are included within the metered boundaries of a Balancing Authority Area. |  | LSE | [7 empty] | LSE | [14 empty] | 2012-09-13 |  | 2018-12-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780004121 | Balancing Authorities shall install common metering equipment where Dynamic Schedules or Pseudo-Ties are implemented between two or more Balancing Authorities to deliver the output of Jointly Owned Units or to serve remote load. |  | BA | BA | [21 empty] | 2012-09-13 |  | 2018-12-31 |  |  |  | 123000000 | NPCC-ON |  | NPCC-US
3 | 79780004132 | Develop, maintain, and implement a set of plans for load shedding. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780004138 | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  |  | 73000000 | NPCC-ON |  | NPCC-US
3 | 79780004140 | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780004183 | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780004198 | Interrupting interruptible load and exports. |  | BA | BA | [21 empty] | 2012-09-13 |  | 2017-03-31 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780004207 | The Reliability Coordinator shall use EEA 1 to forecast the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  |  | 93000000 | NPCC-ON |  | NPCC-US
3 | 79780004219 | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP | M4.3 The Transmission Entity informed the Nuclear Plant Generator Operator when it became aware it lost the capability to assess the operation of the electric system affecting the NPIRs. (Requirement 4.3) | 2013-04-01 |  | 2015-12-31 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780004224 | Operations and maintenance coordination: |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 93000000 | NPCC-ON |  | NPCC-US
3 | 79780004225 | A requirement to review the agreement(s) at least every three years. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2014-01-21 |  |  |  | 91300000 | NPCC-ON |  | NPCC-US
3 | 79780004231 | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 92300000 | NPCC-ON |  | NPCC-US
3 | 79780004234 | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 93300000 | NPCC-ON |  | NPCC-US
3 | 79780004241 | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 94300000 | NPCC-ON |  | NPCC-US
3 | 79780004254 | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780004259 | Operations and maintenance coordination: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 93000000 | NPCC-ON |  | NPCC-US
3 | 79780004344 | Generation resources that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 12300000 | NPCC-ON |  | NPCC-US
3 | 79780004346 | The Cyber Asset is dial-up accessible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780004369 | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:&lt;br/&gt;&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780004371 | The proper handling of Critical Cyber Asset information; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:&lt;br/&gt;&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 22300000 | NPCC-ON |  | NPCC-US
3 | 79780004376 | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:&lt;br/&gt;&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780004385 | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2014-02-03 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780004387 | The proper handling of Critical Cyber Asset information; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 22300000 | NPCC-ON |  | NPCC-US
3 | 79780004392 | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2014-02-03 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780004409 | Impedance data. |  | GO | [22 empty] | 2013-07-01 |  | 2014-09-30 |  |  |  | 41300000 | NPCC-ON |  | NPCC-US
3 | 79780004444 | The permissible mix of Operating Reserve – Spinning and Operating Reserve – Supplemental that may be included in Contingency Reserve. |  | RRO, RSG | [14 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780004465 | Each Balancing Authority shall inform its Reliability Coordinator of all generation resources available for use. |  | BA | BA | [23 empty] | 2015-03-18 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780004557 | The Cyber Asset is dial-up accessible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780004567 | Generation resources that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 12300000 | NPCC-ON |  | NPCC-US
3 | 79780004584 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category A of Table 1 (no contingencies). The specific elements selected (from each of the following categories) shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780004594 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780004598 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780004625 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories,, showing system performance following Category B of Table 1 (single contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780004640 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780004644 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780004650 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780004665 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780004669 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780004674 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780004678 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780004690 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780004705 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780004709 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780004719 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780004726 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780004736 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780004739 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780004743 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780004756 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780004764 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780004802 |  |  | BA | BA | [23 empty] | 2006-05-01 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780004811 |  |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780004822 |  |  | TOP | [18 empty] | TOP | [5 empty] | 2006-11-01 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780004831 |  |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 103000000 | NPCC-ON |  | NPCC-US
3 | 79780004840 |  |  | BA | BA | [23 empty] | 2006-11-01 |  |  |  | 73000000 | NPCC-ON |  | NPCC-US
3 | 79780004857 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780004868 |  |  | RC | [11 empty] | RC | [12 empty] | 2007-01-01 |  |  |  | 93000000 | NPCC-ON |  | NPCC-US
3 | 79780004889 |  |  | BA | BA | [23 empty] | 2007-05-02 |  |  |  | 93000000 | NPCC-ON |  | NPCC-US
3 | 79780004894 |  |  | TOP | [18 empty] | TOP | [5 empty] | 2007-05-02 |  |  |  | 95300000 | NPCC-ON |  | NPCC-US
3 | 79780004905 |  |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-04-07 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780004911 |  |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-08-01 |  |  |  | 11300000 | NPCC-ON |  | NPCC-US
3 | 79780004917 |  |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-08-01 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780004927 |  |  | BA, PSE | BA | [9 empty] | PSE | [13 empty] | 2007-01-01 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780004931 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780004943 |  |  | BA, TSP | BA | [19 empty] | TSP |  |  |  | 2007-01-01 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780004949 |  |  | TSP | [20 empty] | TSP |  |  |  | 2007-01-01 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780004956 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780004964 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 11300000 | NPCC-ON |  | NPCC-US
3 | 79780004966 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780004982 |  |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780004993 |  |  | PSE, RC, TOP | [10 empty] | PSE | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780005029 |  |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780005056 |  |  | RC | [11 empty] | RC | [12 empty] | 2005-08-08 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780005065 |  |  | RC | [11 empty] | RC | [12 empty] | 2006-09-29 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780005074 |  |  | RC | [11 empty] | RC | [12 empty] | 2006-09-29 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780005084 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2006-11-02 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780005112 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 12300000 | NPCC-ON |  | NPCC-US
3 | 79780005114 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780005117 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780005124 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 16300000 | NPCC-ON |  | NPCC-US
3 | 79780005131 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2006-05-01 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780005141 |  |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2006-05-01 |  |  |  | 11300000 | NPCC-ON |  | NPCC-US
3 | 79780005144 |  |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2006-05-01 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780005208 |  |  | TOP | [18 empty] | TOP | [5 empty] | 2005-04-01 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780005270 | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780005274 | Where allowed by Standards CIP-002-3 through CIP-009-3, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780005277 | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780005280 | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780005284 | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780005294 | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780005298 | Where allowed by Standards CIP-002-4 through CIP-009-4, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780005301 | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780005304 | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780005308 | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780005321 | The Responsible Entity shall document test results. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780005326 | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780005333 | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780005336 | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-3 Requirement R5 and Standard CIP-004-3 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 51300000 | NPCC-ON |  | NPCC-US
3 | 79780005337 | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 52300000 | NPCC-ON |  | NPCC-US
3 | 79780005340 | Each password shall be changed at least annually, or more frequently based on risk. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 53300000 | NPCC-ON |  | NPCC-US
3 | 79780005346 | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780005350 | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 73000000 | NPCC-ON |  | NPCC-US
3 | 79780005352 | A review of controls for default accounts; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 83000000 | NPCC-ON |  | NPCC-US
3 | 79780005364 | The Responsible Entity shall document test results. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780005369 | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780005376 | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780005379 | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-4 Requirement R5 and Standard CIP-004-4 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 51300000 | NPCC-ON |  | NPCC-US
3 | 79780005380 | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 52300000 | NPCC-ON |  | NPCC-US
3 | 79780005383 | Each password shall be changed at least annually, or more frequently based on risk. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 53300000 | NPCC-ON |  | NPCC-US
3 | 79780005389 | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780005393 | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 73000000 | NPCC-ON |  | NPCC-US
3 | 79780005395 | A review of controls for default accounts; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 83000000 | NPCC-ON |  | NPCC-US
3 | 79780005601 | Include a description of how to identify the subset of SOLs that qualify as IROLs. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780005608 | Starting with all Facilities in service, the system’s response to a single Contingency, may include any of the following: |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780005620 | Level of detail of system models used to determine SOLs. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780005627 | Each Transmission Planner that works in the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780005632 | Include a description of how to identify the subset of SOLs that qualify as IROLs |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780005638 | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 22300000 | NPCC-ON |  | NPCC-US
3 | 79780005639 | In determining the system’s response to a single Contingency, the following shall be acceptable: |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780005643 | System reconfiguration through manual or automatic control or protection actions. |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 23300000 | NPCC-ON |  | NPCC-US
3 | 79780005648 | A process for determining which of the stability limits associated with the list of multiple contingencies (provided by the Planning Authority in accordance with FAC-014 Requirement 6) are applicable for use in the operating horizon given the actual or expected system conditions. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780005658 | Each Transmission Operator that operates in the Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780005663 | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780005687 | The source/sink or POR/POD identification and mapping to the model. |  | TSP | [20 empty] | TSP |  | 2017-04-01 | [5 empty] | 12300000 | NPCC-ON |  | NPCC-US
3 | 79780005700 | Any limiting Element/Contingency combination at least within its Reliability Coordinator’s Area that has been subjected to an Interconnection-wide congestion management procedure within the last 12 months, unless the limiting Element/Contingency combination is accounted for using another ATC methodology or was created to address temporary operating conditions. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780005705 | At a minimum, establish a list of Flowgates by creating, modifying, or deleting Flowgates that have been requested as part of R2.1.4 within thirty calendar days from the request. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780005713 | Updated at least once per month for AFC calculations for months two through 13. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780005720 | For external Flowgates, identified in R2.1.4, use the AFC provided by the Transmission Service Provider that calculates AFC for that Flowgate. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780005728 | The impact of all confirmed firm Point-to-Point Transmission Service expected to be scheduled, including roll-over rights for Firm Transmission Service contracts, for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780005736 | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 73000000 | NPCC-ON |  | NPCC-US
3 | 79780005746 | For monthly AFC, once per week. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 103000000 | NPCC-ON |  | NPCC-US
3 | 79780005755 | Generation resources that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12300000 | NPCC-ON |  | NPCC-US
3 | 79780005762 | The Cyber Asset is dial-up accessible. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780005767 | Generation resources that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12300000 | NPCC-ON |  | NPCC-US
3 | 79780005774 | The Cyber Asset is dial-up accessible. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780005782 | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780005791 | A requirement to review the agreement(s) at least every three years. (Retirement approved by FERC effective January 21, 2014.) | [26 empty] | 2014-11-13 |  |  |  | 91300000 | NPCC-ON |  | NPCC-US
3 | 79780005796 | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 92300000 | NPCC-ON |  | NPCC-US
3 | 79780005797 | Operations and maintenance coordination: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  |  | 93000000 | NPCC-ON |  | NPCC-US
3 | 79780005800 | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 93300000 | NPCC-ON |  | NPCC-US
3 | 79780005808 | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 94300000 | NPCC-ON |  | NPCC-US
3 | 79780005814 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category A of Table 1 (no contingencies). The specific elements selected (from each of the following categories) shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780005817 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780005829 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780005835 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category B of Table 1 (single contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780005838 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780005854 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780005860 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780005863 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780005879 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780005885 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780005888 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780005900 | Requirements to demonstrate that the RAS shall be designed so that a single RAS component failure, when the RAS was intended to operate, does not prevent the interconnected transmission system from meeting the performance requirements defined in Reliability Standards TPL-001-0, TPL-002-0, and TPL-003-0. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780005901 | Requirements to demonstrate that the RAS shall be designed so that a single RAS component failure, when the RAS was intended to operate, does not prevent the interconnected transmission system from meeting the performance requirements defined in Reliability Standards TPL-001-0, TPL-002-0, and TPL-003-0. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780005919 | Identification of RAS that were found not to comply with NERC standards and Regional Reliability Organization criteria. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780005925 | Modeling — Information on detection logic or relay settings that control operation of the RAS. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780005937 | Communications systems, where appropriate. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-04-01 |  | 2021-03-31 |  |  |  | 11300000 | NPCC-ON |  | NPCC-US
3 | 79780005940 | Summary of testing procedure. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-04-01 |  | 2021-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780005941 | Summary of testing procedure. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-01-25 |  | 2021-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780005949 | Corresponding voltage set points and overall scheme clearing times. | [26 empty] | 2014-11-13 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780005957 | Time delay from initiation to trip signal. | [26 empty] | 2014-11-13 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780006029 | Models all generation (may be either a single generator or multiple generators) that is greater than 20 MVA at the point of interconnection in the studied area. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 11300000 | NPCC-ON |  | NPCC-US
3 | 79780006162 | Physical security of BES Cyber Systems (CIP-006); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780006171 | Electronic access controls for external routable protocol connections and Dial-up Connectivity; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2016-06-30 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780006175 | The roles and responsibilities of Cyber Security Incident response groups or individuals. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.3. An example of evidence may include, but is not limited to, dated Cyber Security Incident response process(es) or procedure(s) that define roles and responsibilities (e.g., monitoring, reporting, initiating, documenting, etc.) of Cyber Security Incident response groups or individuals. | 2014-02-03 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780006179 | Retain records related to Reportable Cyber Security Incidents. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.3. An example of evidence may include, but is not limited to, dated documentation, such as security logs, police reports, emails, response forms or checklists, forensic analysis results, restoration records, and post-incident review notes related to Reportable Cyber Security Incidents. | 2014-02-03 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780006183 | Notify each person or group with a defined role in the Cyber Security Incident response plan of the updates to the Cyber Security Incident response plan based on any documented lessons learned. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | 31300000 | NPCC-ON |  | NPCC-US
3 | 79780006191 | For applicable patches identified in Part 2.2, within 35 calendar days of the evaluation completion, take one of the following actions:&lt;br/&gt;• Apply the applicable patches; or&lt;br/&gt;• Create a dated mitigation plan; or&lt;br/&gt;• Revise an existing mitigation plan. &lt;br/&gt;Mitigation plans shall include the Responsible Entity’s planned actions to mitigate the vulnerabilities addressed by each security patch and a timeframe to complete these mitigations. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780006195 | For those methods identified in Part 3.1 that use signatures or patterns, have a process for the update of the signatures or patterns. The process must address testing and installing the signatures or patterns. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780006198 | Where technically feasible, retain applicable event logs identified in Part 4.1 for at least the last 90 consecutive calendar days except under CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780006202 | Identify individuals who have authorized access to shared accounts. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780006209 | Detected malicious code. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 41300000 | NPCC-ON |  | NPCC-US
3 | 79780006221 | Any custom software installed; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 11300000 | NPCC-ON |  | NPCC-US
3 | 79780006225 | For a change that deviates from the existing baseline configuration, update the baseline configuration as necessary within 30 calendar days of completing the change. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780006229 | Document the results of the verification. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 14300000 | NPCC-ON |  | NPCC-US
3 | 79780006238 | Prior to adding a new applicable Cyber Asset to a production environment, perform an active vulnerability assessment of the new Cyber Asset, except for CIP Exceptional Circumstances and like replacements of the same type of Cyber Asset with a baseline configuration that models an existing baseline configuration of the previous or other existing Cyber Asset. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780006242 | Require inbound and outbound access permissions, including the reason for granting access, and deny all other access by default. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.3. An example of evidence may include, but is not limited to, a list of rules (firewall, access control lists, etc.) that demonstrate that only permitted access is allowed and that each access rule has a documented reason. | 2014-02-03 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780006247 | Require multi-factor authentication for all Interactive Remote Access sessions. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.3. An example of evidence may include, but is not limited to, architecture documents detailing the authentication factors used. &lt;br/&gt;Examples of authenticators may include, but are not limited to, &lt;br/&gt;• Something the individual knows such as passwords or PINs. This does not include User ID;&lt;br/&gt;• Something the individual has such as tokens, digital certificates, or smart cards; or &lt;br/&gt;• Something the individual is such as fingerprints, iris scans, or other biometric characteristics. | 2014-02-03 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780006250 | Where technically feasible, utilize two or more different physical access controls (this does not require two completely independent physical access control systems) to collectively allow unescorted physical access into Physical Security Perimeters to only those individuals who have authorized unescorted physical access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 1.3 An example of evidence may include, but is not limited to, language in the physical security plan that describes the Physical Security Perimeters and how unescorted physical access is controlled by two or more different methods and proof that unescorted physical access is restricted to only authorized individuals, such as a list of authorized individuals accompanied by access logs. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780006259 | Retain visitor logs for at least ninety calendar days. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 2.3 An example of evidence may include, but is not limited to, documentation showing logs have been retained for at least ninety calendar days. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780006263 | One or more processes for the backup and storage of information required to recover BES Cyber System functionality. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780006268 | Test each of the recovery plans referenced in Requirement R1 at least once every 36 calendar months through an operational exercise of the recovery plans in an environment representative of the production environment. &lt;br/&gt;&lt;br/&gt;An actual recovery response may substitute for an operational exercise. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780006272 | Notify each person or group with a defined role in the recovery plan of the updates to the recovery plan based on any documented lessons learned. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 31300000 | NPCC-ON |  | NPCC-US
3 | 79780006279 | Electronic access controls; | [23 empty] | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. |  |  | 2016-06-30 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780006297 | Require completion of the training specified in Part 2.1 at least once every 15 calendar months. | [23 empty] | Examples of evidence may include, but are not limited to, dated individual training records. |  |  | 2016-06-30 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780006302 | Criteria or process to evaluate criminal history records checks for authorizing access. | [23 empty] | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to evaluate criminal history records checks. |  |  | 2016-06-30 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780006308 | Access to designated storage locations, whether physical or electronic, for BES Cyber System Information. | [23 empty] | An example of evidence may include, but is not limited to, dated documentation of the process to authorize electronic access, unescorted physical access in a Physical Security Perimeter, and access to designated storage locations, whether physical or electronic, for BES Cyber System Information. |  |  | 2016-06-30 |  |  |  | 41300000 | NPCC-ON |  | NPCC-US
3 | 79780006310 | For electronic access, verify at least once every 15 calendar months that all user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and are those that the Responsible Entity determines are necessary. | [23 empty] | An example of evidence may include, but is not limited to, documentation of the review that includes all of the following: &lt;br/&gt;1. A dated listing of all accounts/account groups or roles within the system; &lt;br/&gt;2. A summary description of privileges associated with each group or role;&lt;br/&gt;3. Accounts assigned to the group or role; and&lt;br/&gt;4. Dated evidence showing verification of the privileges for the group are authorized and appropriate to the work function performed by people assigned to each account. |  |  | 2016-06-30 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780006314 | For termination actions, revoke the individual’s access to the designated storage locations for BES Cyber System Information, whether physical or electronic (unless already revoked according to Requirement R5.1), by the end of the next calendar day following the effective date of the termination action. | [23 empty] | An example of evidence may include, but is not limited to, workflow or sign-off form verifying access removal to designated physical areas or cyber systems containing BES Cyber System Information associated with the terminations and dated within the next calendar day of the termination action. |  |  | 2016-06-30 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780006319 | Identify each asset that contains a low impact BES Cyber System according to Attachment 1, Section 3, if any (a discrete list of low impact BES Cyber Systems is not required). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-12-26 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780006328 | Ambient conditions (for particular or average conditions or as they vary in real-time). |  | GO | [22 empty] | 2013-01-01 | [5 empty] | 22300000 | NPCC-ON |  | NPCC-US
3 | 79780006330 | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | GO | [22 empty] | 2011-11-17 | [5 empty] | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780006338 | Ambient conditions (for particular or average conditions or as they vary in real-time). |  | TO | [22 empty] | 2013-01-01 | [5 empty] | 32300000 | NPCC-ON |  | NPCC-US
3 | 79780006340 | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | TO | [22 empty] | 2011-11-17 | [5 empty] | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780006356 | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-11-19 |  | 2017-04-01 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780006362 | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-04-02 |  | 2017-04-01 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780006385 | If the unaffiliated verifying entity recommends that the Transmission Owner add a Transmission station(s) or Transmission substation(s) to, or remove a Transmission station(s) or Transmission substation(s) from, its identification under Requirement R1, the Transmission Owner shall either, within 60 calendar days of completion of the verification, for each recommended addition or removal of a Transmission station or Transmission substation:&lt;br/&gt;• Modify its identification under Requirement R1 consistent with the recommendation; or&lt;br/&gt;• Document the technical basis for not modifying the identification in accordance with the recommendation. |  | TO | [22 empty] | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:&lt;br/&gt;4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an &amp;quot;aggregate weighted value&amp;quot; exceeding 3000 according to the table below. The &amp;quot;aggregate weighted value&amp;quot; for a single station or substation is determined by summing the &amp;quot;weight value per line&amp;quot; shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;Voltage Value of a Line Weight Value per Line&lt;br/&gt;less than 200 kV (not applicable) (not applicable)&lt;br/&gt;200 kV to 299 kV 700&lt;br/&gt;300 kV to 499 kV 1300&lt;br/&gt;500 kV and above 0&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.&lt;br/&gt;4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. &lt;br/&gt;Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780006392 | Intelligence or threat warnings received from sources such as law enforcement, the Electric Reliability Organization (ERO), the Electricity Sector Information Sharing and Analysis Center (ES-ISAC), U.S. federal and/or Canadian governmental agencies, or their successors. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:&lt;br/&gt;4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an &amp;quot;aggregate weighted value&amp;quot; exceeding 3000 according to the table below. The &amp;quot;aggregate weighted value&amp;quot; for a single station or substation is determined by summing the &amp;quot;weight value per line&amp;quot; shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;Voltage Value of a Line Weight Value per Line&lt;br/&gt;less than 200 kV (not applicable) (not applicable)&lt;br/&gt;200 kV to 299 kV 700&lt;br/&gt;300 kV to 499 kV 1300&lt;br/&gt;500 kV and above 0&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.&lt;br/&gt;4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. &lt;br/&gt;Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780006396 | A timeline for executing the physical security enhancements and modifications specified in the physical security plan. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:&lt;br/&gt;4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an &amp;quot;aggregate weighted value&amp;quot; exceeding 3000 according to the table below. The &amp;quot;aggregate weighted value&amp;quot; for a single station or substation is determined by summing the &amp;quot;weight value per line&amp;quot; shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;Voltage Value of a Line Weight Value per Line&lt;br/&gt;less than 200 kV (not applicable) (not applicable)&lt;br/&gt;200 kV to 299 kV 700&lt;br/&gt;300 kV to 499 kV 1300&lt;br/&gt;500 kV and above 0&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.&lt;br/&gt;4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. &lt;br/&gt;Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780006403 | If the unaffiliated third party reviewer recommends changes to the evaluation performed under Requirement R4 or security plan(s) developed under Requirement R5, the Transmission Owner or Transmission Operator shall, within 60 calendar days of the completion of the unaffiliated third party review, for each recommendation:&lt;br/&gt;• Modify its evaluation or security plan(s) consistent with the recommendation; or&lt;br/&gt;• Document the reason(s) for not modifying the evaluation or security plan(s) consistent with the recommendation. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:&lt;br/&gt;4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an &amp;quot;aggregate weighted value&amp;quot; exceeding 3000 according to the table below. The &amp;quot;aggregate weighted value&amp;quot; for a single station or substation is determined by summing the &amp;quot;weight value per line&amp;quot; shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;Voltage Value of a Line Weight Value per Line&lt;br/&gt;less than 200 kV (not applicable) (not applicable)&lt;br/&gt;200 kV to 299 kV 700&lt;br/&gt;300 kV to 499 kV 1300&lt;br/&gt;500 kV and above 0&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.&lt;br/&gt;4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. &lt;br/&gt;Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780006422 | Request that the congestion management actions identified in Requirement R2, Part 2.1 be implemented by: 1.) Each Reliability Coordinator associated with a Sink Balancing Authority for which Interchange Transactions are to be curtailed, 2.) Each Reliability Coordinator associated with a Balancing Authority in the Eastern Interconnection for which Network Integration Transmission Service or Native Load is to be curtailed, and 3.) Each Reliability Coordinator associated with a Balancing Authority in the Eastern Interconnection for which its Market Flow is to be curtailed. |  | RC | [11 empty] | RC | [10 empty] | 2011-04-21 |  | 2016-03-31 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780006426 | Model structure and data including, but not limited to reactance, time constants, saturation factors, total rotational inertia, or equivalent data for the generator, |  | GO | [22 empty] | 2018-07-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following:&lt;br/&gt;4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: &lt;br/&gt;4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).&lt;br/&gt;4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.2 Generation in the Western Interconnection with the following characteristics:&lt;br/&gt;4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).&lt;br/&gt;4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.3 Generation in the ERCOT Interconnection with the following characteristics:&lt;br/&gt;4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).&lt;br/&gt;4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.4 For all Interconnections:&lt;br/&gt;• A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780006432 | For an otherwise stable simulation, a disturbance simulation results in the excitation control and plant volt/var control function model exhibiting positive damping. |  | TP | [19 empty] | TP |  |  | 2014-05-26 |  |  |  | 4.2. Facilities:&lt;br/&gt;For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following:&lt;br/&gt;4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: &lt;br/&gt;4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).&lt;br/&gt;4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.2 Generation in the Western Interconnection with the following characteristics:&lt;br/&gt;4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).&lt;br/&gt;4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.3 Generation in the ERCOT Interconnection with the following characteristics:&lt;br/&gt;4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).&lt;br/&gt;4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.4 For all Interconnections:&lt;br/&gt;• A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780006436 | A description of the turbine (e.g. for hydro turbine - Kaplan, Francis, or Pelton; for steam turbine - boiler type, normal fuel type, and turbine type; for gas turbine - the type and manufacturer; for variable energy plant - type and manufacturer), |  | GO | [22 empty] | 2014-07-01 |  |  |  | 4.2. Facilities&lt;br/&gt;For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred to as an “applicable unit” that meet the following:&lt;br/&gt;4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics:&lt;br/&gt;4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).&lt;br/&gt;4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.2 Generation in the Western Interconnection with the following characteristics:&lt;br/&gt;4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).&lt;br/&gt;4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.3 Generation in the ERCOT Interconnection with the following characteristics:&lt;br/&gt;4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).&lt;br/&gt;4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780006441 | For an otherwise stable simulation, a disturbance simulation results in the turbine/governor and load control or active power/frequency control model exhibiting positive damping. |  | TP | [19 empty] | TP |  |  | 2014-05-26 |  |  |  | 4.2. Facilities&lt;br/&gt;For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred to as an “applicable unit” that meet the following:&lt;br/&gt;4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics:&lt;br/&gt;4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).&lt;br/&gt;4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.2 Generation in the Western Interconnection with the following characteristics:&lt;br/&gt;4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).&lt;br/&gt;4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.3 Generation in the ERCOT Interconnection with the following characteristics:&lt;br/&gt;4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).&lt;br/&gt;4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780006445 | Emergency preparedness and operations |  | RC | [11 empty] | RC | [10 empty] | 2012-10-01 |  | 2019-06-30 |  |  |  | 11300000 | NPCC-ON |  | NPCC-US
3 | 79780006454 | System operations |  | TOP | [18 empty] | TOP |  |  |  | 2012-10-01 |  | 2019-06-30 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780006461 | System operations |  | BA | BA | [21 empty] | 2012-10-01 |  | 2019-06-30 |  |  |  | 31300000 | NPCC-ON |  | NPCC-US
3 | 79780006492 | &lt;p&gt;Voice communications.&lt;/p&gt; |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2013-07-01 |  | 2019-03-31 |  |  |  | 12300000 | NPCC-ON |  | NPCC-US
3 | 79780006495 | An Operating Process for keeping the backup functionality consistent with the primary control center. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780006509 | The conditions for terminating the Operating Procedure or Operating Process. |  | TOP | [18 empty] | TOP |  |  |  | 2015-04-01 | [5 empty] | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780006527 | Inform its Planning Coordinator of the need to exceed the stated tolerances of UFLS Attachment C, Table 2 or Table 3, and in the case of Attachment C, Table 2 only, the need to deviate from providing two stages of UFLS, if applicable, and |  | DP, DP-UFLS, TO |  | DP | [20 empty] | 2020-03-31 |  | 2020-03-31 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780006536 | Transmit the initial frequency trip setting and any changes to the setting and the technical basis for the settings to the Planning Coordinator. |  | DP-UFLS, GO |  | DP | [20 empty] | 2013-04-29 |  | 2020-03-31 |  |  |  | 193000000 | NPCC-ON |  | NPCC-US
3 | 79780006539 | A list of all generating units that may be tripped for underfrequency conditions above the appropriate generator underfrequency trip protection settings threshold curve in Figure 1, including the frequency trip threshold and time delay for each protection system. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2013-04-29 |  | 2020-03-31 |  |  |  | 203000000 | NPCC-ON |  | NPCC-US
3 | 79780006543 | Have compensatory load shedding, as provided by a Distribution Provider or Transmission Owner that is adequate to compensate for the loss of their generator due to early tripping. |  | DP-UFLS, GO |  | DP | [20 empty] | 2013-04-29 |  | 2020-03-31 |  |  |  | 163000000 | NPCC-ON |  | NPCC-US
3 | 79780006548 | A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780006551 | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780006554 | Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. |  | PCPA | [9 empty] | PA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  |  | 33300000 | NPCC-ON |  | NPCC-US
3 | 79780006557 | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780006564 | Format and schedule of UFLS data submittal |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 143000000 | NPCC-ON |  | NPCC-US
3 | 79780006569 | A statement that the assumptions and criteria used to perform the assessment are consistent with the Planning Coordinator’s planning practices. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-01-23 |  | 2020-12-14 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780006576 | Facilities consisting of one or more units connected to the BES at a common bus with total generation above 50 MVA gross nameplate rating. |  | PCPA | [9 empty] | PA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  |  | 330000 | NPCC-ON |  | NPCC-US
3 | 79780006579 | Facilities consisting of one or more units connected to the BES at a common bus with total generation above 50 MVA gross nameplate rating. |  | PCPA | [9 empty] | PA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  |  | 333000 | NPCC-ON |  | NPCC-US
3 | 79780006587 | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 330000 | NPCC-ON |  | NPCC-US
3 | 79780006590 | Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. |  | PCPA | [9 empty] | PA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  |  | 333000 | NPCC-ON |  | NPCC-US
3 | 79780006593 | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 430000 | NPCC-ON |  | NPCC-US
3 | 79780006625 | New planned Facilities and changes to existing Facilities |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-01-01 | [5 empty] | 11300000 | NPCC-ON |  | NPCC-US
3 | 79780006632 | P1 events in Table 1, with known outages modeled as in Requirement R1, Part 1.1.2, under those System peak or Off-Peak conditions when known outages are scheduled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780006637 | The short circuit analysis portion of the Planning Assessment shall be conducted annually addressing the Near-Term Transmission Planning Horizon and can be supported by current or past studies as qualified in Requirement R2, Part 2.6. The analysis shall be used to determine whether circuit breakers have interrupting capability for Faults that they will be expected to interrupt using the System short circuit model with any planned generation and Transmission Facilities in service which could impact the study area. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780006641 | Generator Operators that do not monitor the voltage at the location specified in their voltage schedule shall have a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2014-08-01 |  | 2015-05-28 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780006645 | Impedance data. |  | GO | [22 empty] | 2014-10-01 |  | 2015-05-28 |  |  |  | 51300000 | NPCC-ON |  | NPCC-US
3 | 79780006650 | For each of the studies described in Requirement R2, Parts 2.4.1 and 2.4.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in performance:&lt;br/&gt;• Load level, Load forecast, or dynamic Load model assumptions. &lt;br/&gt;• Expected transfers. &lt;br/&gt;• Expected in service dates of new or modified Transmission Facilities. &lt;br/&gt;• Reactive resource capability. &lt;br/&gt;• Generation additions, retirements, or other dispatch scenarios. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 24300000 | NPCC-ON |  | NPCC-US
3 | 79780006658 | If situations arise that are beyond the control of the Transmission Planner or Planning Coordinator that prevent the implementation of a Corrective Action Plan in the required timeframe, then the Transmission Planner or Planning Coordinator is permitted to utilize Non-Consequential Load Loss and curtailment of Firm Transmission Service to correct the situation that would normally not be permitted in Table 1, provided that the Transmission Planner or Planning Coordinator documents that they are taking actions to resolve the situation. The Transmission Planner or Planning Coordinator shall document the situation causing the problem, alternatives evaluated, and the use of Non-Consequential Load Loss or curtailment of Firm Transmission Service. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 27300000 | NPCC-ON |  | NPCC-US
3 | 79780006665 | Contingency analyses for Requirement R3, Parts 3.1 &amp;amp; 3.2 shall: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780006676 | For planning events P1 through P7: Power oscillations shall exhibit acceptable damping as established by the Planning Coordinator and Transmission Planner. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 41300000 | NPCC-ON |  | NPCC-US
3 | 79780006678 | Contingency analyses for Requirement R4, Parts 4.1 and 4.2 shall: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780006693 | System demand. |  | PCPA | [9 empty] | PA | [12 empty] | 2013-04-01 |  | 2020-12-14 |  |  |  | 14300000 | NPCC-ON |  | NPCC-US
3 | 79780006702 | The Purchasing-Selling Entity receives notification from a Reliability Coordinator or Transmission Operator to update the Confirmed Interchange. |  | PSE | [10 empty] | PSE | [11 empty] | 2015-01-01 | [5 empty] | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780006709 | Each Reliability Coordinator associated with each Balancing Authority included in the Arranged Interchange, |  | BA | BA | [21 empty] | 2014-06-30 |  | 2021-03-31 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780006720 | Each Distribution Provider within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780006726 | Each adjacent Transmission Operator synchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780006730 | Each Distribution Provider within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780006735 | Each Adjacent Balancing Authority. |  | BA | BA | [21 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780006744 | If the unaffiliated verifying entity recommends that the Transmission Owner add a Transmission station(s) or Transmission substation(s) to, or remove a Transmission station(s) or Transmission substation(s) from, its identification under Requirement R1, the Transmission Owner shall either, within 60 calendar days of completion of the verification, for each recommended addition or removal of a Transmission station or Transmission substation:&lt;br/&gt;• Modify its identification under Requirement R1 consistent with the recommendation; or&lt;br/&gt;• Document the technical basis for not modifying the identification in accordance with the recommendation. |  | TO | [22 empty] | 2015-10-01 |  | 2015-10-01 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780006749 | Intelligence or threat warnings received from sources such as law enforcement, the Electric Reliability Organization (ERO), the Electricity Sector Information Sharing and Analysis Center (ES-ISAC), U.S. federal and/or Canadian governmental agencies, or their successors. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780006752 | A timeline for executing the physical security enhancements and modifications specified in the physical security plan. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780006756 | If the unaffiliated third party reviewer recommends changes to the evaluation performed under Requirement R4 or security plan(s) developed under Requirement R5, the Transmission Owner or Transmission Operator shall, within 60 calendar days of the completion of the unaffiliated third party review, for each recommendation:&lt;br/&gt;• Modify its evaluation or security plan(s) consistent with the recommendation; or&lt;br/&gt;• Document the reason(s) for not modifying the evaluation or security plan(s) consistent with the recommendation. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780006760 | end-user Facilities. |  | TO | [22 empty] | 2014-11-06 |  | 2018-12-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780006767 | Steady-state, short-circuit, and dynamics studies, as necessary, to evaluate system performance under both normal and contingency conditions; and |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2014-11-06 |  | 2021-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780006777 | A request to provide any or all of the following actual data, as necessary: |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2015-04-27 |  | 2016-09-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780006781 | Monthly and annual Net Energy for Load in gigawatthours for the prior calendar year. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780006786 | Peak hour forecast Total Internal Demands (summer and winter) in megawatts for ten calendar years into the future. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 14300000 | NPCC-ON |  | NPCC-US
3 | 79780006792 | How Demand Side Management is addressed in the forecasts of its Peak Demand and annual Net Energy for Load. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 15300000 | NPCC-ON |  | NPCC-US
3 | 79780006800 | Case types or scenarios to be modeled; and |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-07-01 |  |  |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. |  | 12300000 | NPCC-ON |  | NPCC-US
3 | 79780006802 | Specifications for distribution or posting of the data requirements and reporting procedures so that they are available to those entities responsible for providing the data. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-07-01 |  |  |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780006807 | Guidelines the Planning Coordinator will use to determine unacceptable differences in performance under Part 1.1 or 1.2; and |  | PCPA | [9 empty] | PA | [12 empty] | 2014-05-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780006811 | Control of voltage, including the coordination of reactive resources. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-26 | [5 empty] | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780006816 | Distribute to all Reliability Coordinators that are required to take the indicated action(s) within 30 days of an update. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-26 | [5 empty] | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780006821 | Define the process to evaluate the impact of Transmission and generation outages within its Wide Area. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-26 | [5 empty] | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780006825 | A periodicity for providing data. |  | TOP | [18 empty] | TOP | [5 empty] | 2016-01-26 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780006829 | A periodicity for providing data. |  | BA | BA | [23 empty] | 2016-01-26 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780006833 | A periodicity for providing data. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-26 |  | 2021-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780006837 | A periodicity for providing data. |  | BA | BA | [21 empty] | 2016-01-26 |  | 2021-03-31 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780006841 | A mutually agreeable security protocol |  | BA, DP, GO, GOP, LSE, TO, TOP | BA | DP |  |  | GO | GOP |  | LSE | [9 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2021-03-31 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780006844 | Generator Operators that do not monitor the voltage at the location specified in their voltage schedule shall have a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-05-29 |  | 2017-09-25 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780006848 | Impedance data. |  | GO | [22 empty] | 2015-05-29 |  | 2017-09-25 |  |  |  | 51300000 | NPCC-ON |  | NPCC-US
3 | 79780006854 | Transmission system reconfiguration; |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 12300000 | NPCC-ON |  | NPCC-US
3 | 79780006862 | Managing generating resources in its Balancing Authority Area to address: |  | BA | BA | [21 empty] | 2017-04-01 | [5 empty] | 22300000 | NPCC-ON |  | NPCC-US
3 | 79780006876 | Notify each Balancing Authority and Transmission Operator of the results of its review, specifying any time frame for resubmittal of its Operating Plan(s) if revisions are identified. |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 31300000 | NPCC-ON |  | NPCC-US
3 | 79780006897 | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2014-11-04 |  | 2021-03-31 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780006902 | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 92300000 | NPCC-ON |  | NPCC-US
3 | 79780006903 | Operations and maintenance coordination |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2014-11-04 |  | 2021-03-31 |  |  |  | 93000000 | NPCC-ON |  | NPCC-US
3 | 79780006906 | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 93300000 | NPCC-ON |  | NPCC-US
3 | 79780006915 | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 94300000 | NPCC-ON |  | NPCC-US
3 | 79780006919 | One or more processes for the backup and storage of information required to recover BES Cyber System functionality. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.3. An example of evidence may include, but is not limited to, documentation of specific processes for the backup and storage of information required to recover BES Cyber System functionality. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780006924 | Test each of the recovery plans referenced in Requirement R1 at least once every 36 calendar months through an operational exercise of the recovery plans in an environment representative of the production environment. &lt;br/&gt;&lt;br/&gt;An actual recovery response may substitute for an operational exercise. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.3. Examples of evidence may include, but are not limited to, dated documentation of:&lt;br/&gt;• An operational exercise at least once every 36 calendar months between exercises, that demonstrates recovery in a representative environment; or&lt;br/&gt;• An actual recovery response that occurred within the 36 calendar month timeframe that exercised the recovery plans. | 2018-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780006929 | Notify each person or group with a defined role in the recovery plan of the updates to the recovery plan based on any documented lessons learned. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 31300000 | NPCC-ON |  | NPCC-US
3 | 79780006934 | A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780006937 | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: &lt;br/&gt;• Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES &lt;br/&gt;• Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES&lt;br/&gt;• Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780006940 | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780006951 | Format and schedule of UFLS data submittal |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 143000000 | NPCC-ON |  | NPCC-US
3 | 79780006962 | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall deliver training to its System Operators according to its training program. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | M1.3 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection System Operator training records showing the names of the people trained, the title of the training delivered, and the dates of delivery to show that it delivered the training, as specified in Requirement R1 part 1.3. | 2014-06-19 | [5 empty] | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780006967 | Each Transmission Owner shall deliver training to its personnel identified in Applicability Section 4.1.4.1 of this standard according to its training program. |  | TO | [21 empty] | M2.3 Each Transmission Owner shall have available for inspection training records showing the names of the people trained, the title of the training delivered, and the dates of delivery to show that it delivered the training, as specified in Requirement R2 part 2.3. | 2014-06-19 | [5 empty] | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780007045 | Electronic access controls for Low Impact External Routable Connectivity (LERC) and Dial-up Connectivity; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12300000 | NPCC-ON |  | NPCC-US
3 | 79780007049 | A periodicity for providing data. |  | RC | [11 empty] | RC | [10 empty] | 2017-01-01 |  | 2021-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780007053 | A mutually agreeable security protocol |  | BA, DP, GO, GOP, LSE, RC, TO, TOP | BA | DP |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2021-03-31 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780007056 | Planned or unplanned outage information. |  | RC | [11 empty] | RC | [12 empty] | 2016-01-26 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780007063 | Distribute to all Reliability Coordinators that are required to take the indicated action(s) within 30 days of an update. |  | RC | [11 empty] | RC | [9 empty] | 2.3 Distributed within 30 days of an update to all Reliability Coordinators that are required to take the indicated action(s).&lt;br/&gt;This evidence may include, but is not limited to dated documentation with confirmation of receipt, dated notice of acceptance or agreement to take specified actions, or dated electronic communications with confirmation of receipt and acceptance or agreement to take specified actions. (R2) |  |  | 2016-01-26 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780007067 | Transient stability limits; |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 11300000 | NPCC-ON |  | NPCC-US
3 | 79780007073 | Expected transmission uses; |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 12300000 | NPCC-ON |  | NPCC-US
3 | 79780007078 | Each methodology shall describe the process for including any reliability-related constraints that are requested to be included by another Transmission Operator, provided that (1) the request references this specific requirement, and (2) the requesting Transmission Operator includes those constraints in its TFC or TTC determination. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780007081 | A different method for determining whether requested constraints need to be included in the TFC or TTC determination may be used if agreed to by the Transmission Operators. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780007085 | Expected transmission uses; |  | TSP | [20 empty] | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780007095 | If not publicly posted on OASIS or its company website, the Transmission Service Provider’s effective: |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780007100 | If making available any requested data under parts 6.1 or 6.2 of this requirement is contrary to the Transmission Operator’s or Transmission Service Provider’s confidentiality, regulatory, or security requirements, the Transmission Operator or Transmission Service Provider shall not be required to make available that data; provided that, within 45 calendar days of the written request, it responds to the requesting registered entity specifying the data that is not being provided, on what basis and whether there are any options for resolving any of the confidentiality, regulatory or security concerns. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780007107 | Demand patterns |  | BA | BA | [21 empty] | 2016-01-26 | [5 empty] | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780007115 | The GMD Vulnerability Assessment shall be provided within 90 calendar days of completion to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners, and to any functional entity that submits a written request and has a reliability-related need. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780007131 | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and |  | GO, TO |  |  |  |  | GO | [17 empty] | 2021-01-01 |  | 2019-06-30 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780007135 | Be provided within 90 calendar days of completion to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), functional entities referenced in the Corrective Action Plan, and any functional entity that submits a written request and has a reliability-related need. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 73000000 | NPCC-ON |  | NPCC-US
3 | 79780007143 | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-05-13 |  | 2016-06-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780007147 | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-07-01 |  | 2016-06-30 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780007151 | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-05-29 |  | 2016-06-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780007155 | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2016-06-30 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780007165 | Re-evaluate all BES buses at least once every five calendar years in accordance with Part 1.1 and notify other owners, if any, in accordance with Part 1.2, and implement the re-evaluated list of BES buses as per the Implementation Plan. |  | TO | [22 empty] | 2015-11-24 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780007172 | Trigger settings for at least the following: |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780007180 | Each terminal of a high voltage direct current (HVDC) circuit with a nameplate rating greater than or equal to 300 MVA, on the alternating current (AC) portion of the converter. |  | PCPA, RC | [9 empty] | PA |  | RC | [10 empty] | 2016-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 51300000 | NPCC-ON |  | NPCC-US
3 | 79780007186 | Notify all owners of identified BES Elements, within 90-calendar days of completion of Part 5.1, that their respective BES Elements require DDR data when requested. |  | PCPA, RC | [9 empty] | PA |  | RC | [10 empty] | 2015-11-24 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780007190 | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. |  | TO | [22 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780007194 | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. |  | GO | [22 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 73000000 | NPCC-ON |  | NPCC-US
3 | 79780007204 | SER data will be provided in ASCII Comma Separated Value (CSV) format following Attachment 2. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 113000000 | NPCC-ON |  | NPCC-US
3 | 79780007211 | Electronic access controls; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780007222 | Any custom software installed; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 11300000 | NPCC-ON |  | NPCC-US
3 | 79780007226 | For a change that deviates from the existing baseline configuration, update the baseline configuration as necessary within 30 calendar days of completing the change. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.3. An example of evidence may include, but is not limited to, updated baseline documentation with a date that is within 30 calendar days of the date of the completion of the change. | 2016-03-31 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780007230 | Document the results of the verification. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 14300000 | NPCC-ON |  | NPCC-US
3 | 79780007239 | Prior to adding a new applicable Cyber Asset to a production environment, perform an active vulnerability assessment of the new Cyber Asset, except for CIP Exceptional Circumstances and like replacements of the same type of Cyber Asset with a baseline configuration that models an existing baseline configuration of the previous or other existing Cyber Asset. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.3. An example of evidence may include, but is not limited to, a document listing the date of the assessment (performed prior to the commissioning of the new Cyber Asset) and the output of any tools used to perform the assessment. | 2016-07-01 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780007245 | Require completion of the training specified in Part 2.1 at least once every 15 calendar months. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M.2.3. Examples of evidence may include, but are not limited to, dated individual training records. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780007261 | Access to designated storage locations, whether physical or electronic, for BES Cyber System Information. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 41300000 | NPCC-ON |  | NPCC-US
3 | 79780007263 | For electronic access, verify at least once every 15 calendar months that all user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and are those that the Responsible Entity determines are necessary. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.3. An example of evidence may include, but is not limited to, documentation of the review that includes all of the following: &lt;br/&gt;1. A dated listing of all accounts/account groups or roles within the system; &lt;br/&gt;2. A summary description of privileges associated with each group or role;&lt;br/&gt;3. Accounts assigned to the group or role; and&lt;br/&gt;4. Dated evidence showing verification of the privileges for the group are authorized and appropriate to the work function performed by people assigned to each account. | 2017-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780007267 | For termination actions, revoke the individual’s access to the designated storage locations for BES Cyber System Information, whether physical or electronic (unless already revoked according to Requirement R5.1), by the end of the next calendar day following the effective date of the termination action. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.3. An example of evidence may include, but is not limited to, workflow or sign-off form verifying access removal to designated physical areas or cyber systems containing BES Cyber System Information associated with the terminations and dated within the next calendar day of the termination action. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780007290 | For applicable patches identified in Part 2.2, within 35 calendar days of the evaluation completion, take one of the following actions:&lt;br/&gt;• Apply the applicable patches; or&lt;br/&gt;• Create a dated mitigation plan; or&lt;br/&gt;• Revise an existing mitigation plan. &lt;br/&gt;Mitigation plans shall include the Responsible Entity’s planned actions to mitigate the vulnerabilities addressed by each security patch and a timeframe to complete these mitigations. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.3. Examples of evidence may include, but are not limited to: &lt;br/&gt;• Records of the installation of the patch (e.g., exports from automated patch management tools that provide installation date, verification of BES Cyber System Component software revision, or registry exports that show software has been installed); or&lt;br/&gt;• A dated plan showing when and how the vulnerability will be addressed, to include documentation of the actions to be taken by the Responsible Entity to mitigate the vulnerabilities addressed by the security patch and a timeframe for the completion of these mitigations. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780007294 | For those methods identified in Part 3.1 that use signatures or patterns, have a process for the update of the signatures or patterns. The process must address testing and installing the signatures or patterns. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.3. An example of evidence may include, but is not limited to, documentation showing the process used for the update of signatures or patterns. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780007304 | Detected malicious code. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.1. Examples of evidence may include, but are not limited to, a paper or system generated listing of event types for which the BES Cyber System is capable of detecting and, for generated events, is configured to log. This listing must include the required types of events. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 41300000 | NPCC-ON |  | NPCC-US
3 | 79780007308 | Where technically feasible, retain applicable event logs identified in Part 4.1 for at least the last 90 consecutive calendar days except under CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.3. Examples of evidence may include, but are not limited to, documentation of the event log retention process and paper or system generated reports showing log retention configuration set at 90 days or greater. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780007312 | Identify individuals who have authorized access to shared accounts. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.3. An example of evidence may include, but is not limited to, listing of shared accounts and the individuals who have authorized access to each shared account. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780007341 | Where technically feasible, utilize two or more different physical access controls (this does not require two completely independent physical access control systems) to collectively allow unescorted physical access into Physical Security Perimeters to only those individuals who have authorized unescorted physical access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.3. An example of evidence may include, but is not limited to, language in the physical security plan that describes the Physical Security Perimeters and how unescorted physical access is controlled by two or more different methods and proof that unescorted physical access is restricted to only authorized individuals, such as a list of authorized individuals accompanied by access logs. | 2016-07-01 | [5 empty] | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780007351 | Retain visitor logs for at least ninety calendar days. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.3. An example of evidence may include, but is not limited to, documentation showing logs have been retained for at least ninety calendar days. | 2016-07-01 | [5 empty] | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780007355 | Polarizing currents and voltages, if used. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780007360 | Each Fault recorder shall be set to trigger for at least the following: |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780007363 | Monitored phase undervoltage set at 0.85 pu or greater. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 63300000 | NPCC-ON |  | NPCC-US
3 | 79780007392 | Teleprotection keying and receive |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 12300000 | NPCC-ON |  | NPCC-US
3 | 79780007403 | Major voltage sensitive areas. |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 72300000 | NPCC-ON |  | NPCC-US
3 | 79780007410 | Each DDR shall be set to trigger for at least one of the following (based on manufacturers’ equipment capabilities): |  | RC | [11 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 93000000 | NPCC-ON |  | NPCC-US
3 | 79780007413 | Delta Frequency (recommend 20 mHz change). |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 93300000 | NPCC-ON |  | NPCC-US
3 | 79780007417 | As a minimum, one phase current per monitored Element and two phase-to-neutral voltages of different Elements. One of the monitored voltages shall be of the same phase as the monitored current. |  | RC | [11 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 103000000 | NPCC-ON |  | NPCC-US
3 | 79780007422 | Monthly verification of communication channels used for accessing records remotely (if the entity relies on remote access and the channel is not monitored to a control center staffed around the clock, 24 hours a day, 7 days a week (24/7)). |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 143000000 | NPCC-ON |  | NPCC-US
3 | 79780007431 | Fault Recorder and DDR Files shall contain all monitored channels. SOE records shall contain station name, date, time resolved to milliseconds, SOE point name, status. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 163000000 | NPCC-ON |  | NPCC-US
3 | 79780007434 | Installation location. |  | GOP, RC, TOP | [5 empty] | GOP | [5 empty] | RC | [6 empty] | TOP |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  |  | 173000000 | NPCC-ON |  | NPCC-US
3 | 79780007443 | The Transmission Operator shall provide the criteria used to develop voltage schedules Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. |  | TOP | [18 empty] | TOP |  |  |  | 2014-08-01 |  | 2015-11-12 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780007474 | Each Distribution Provider within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780007480 | Physical security of BES Cyber Systems (CIP-006); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11300000 | NPCC-ON |  | NPCC-US
3 | 79780007491 | Each adjacent Transmission Operator synchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780007495 | Each Distribution Provider within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780007500 | Each Adjacent Balancing Authority. |  | BA | BA | [21 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780007514 | The Transmission Operator shall provide the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-25 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780007518 | Criteria or process to evaluate criminal history records checks for authorizing access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.3. An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to evaluate criminal history records checks. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780007529 | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-12-04 |  | 2016-06-30 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780007533 | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-07-01 |  | 2016-06-30 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780007538 | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-12-04 |  | 2017-04-01 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780007543 | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-07-01 |  | 2017-04-01 |  |  |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780007552 | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-11-19 |  | 2021-03-31 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Protection Systems for BES Elements, with the following exclusions:&lt;br/&gt;4.2.1.1 Non-protective functions that are embedded within a Protection System.&lt;br/&gt;4.2.1.2 Protective functions intended to operate as a control function during switching. &lt;br/&gt;4.2.1.3 Special Protection Systems (SPS).&lt;br/&gt;4.2.1.4 Remedial Action Schemes (RAS).&lt;br/&gt;4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.&lt;br/&gt;4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.&lt;br/&gt;4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780007558 | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-04-02 |  | 2021-03-31 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Protection Systems for BES Elements, with the following exclusions:&lt;br/&gt;4.2.1.1 Non-protective functions that are embedded within a Protection System.&lt;br/&gt;4.2.1.2 Protective functions intended to operate as a control function during switching. &lt;br/&gt;4.2.1.3 Special Protection Systems (SPS).&lt;br/&gt;4.2.1.4 Remedial Action Schemes (RAS).&lt;br/&gt;4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.&lt;br/&gt;4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.&lt;br/&gt;4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780007566 | For Protection System settings applied on BES Elements that electrically join Facilities owned by separate functional entities (Transmission Owners, Generator Owners, and Distribution Providers), provisions to: |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.1.3. Distribution Provider (that owns Protection Systems identified in the Facilities section 4.2 below)&lt;br/&gt;4.2. Facilities: Protection Systems installed to detect and isolate Faults on BES Elements. |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780007569 | Verify that identified coordination issue(s) associated with the proposed Protection System settings for the associated BES Elements are addressed prior to implementation. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.1.3. Distribution Provider (that owns Protection Systems identified in the Facilities section 4.2 below)&lt;br/&gt;4.2. Facilities: Protection Systems installed to detect and isolate Faults on BES Elements. |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780007583 | A request to provide any or all of the following actual data, as necessary: |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-02-18 |  | 2021-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780007587 | &lt;p&gt;Monthly and annual Net Energy for Load in gigawatthours for the prior calendar year.&lt;/p&gt; |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | &lt;p&gt;This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.”&lt;/p&gt; |  | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780007592 | &lt;p&gt;Peak hour forecast Total Internal Demands (summer and winter) in megawatts for ten calendar years into the future.&lt;/p&gt; |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | &lt;p&gt;This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.”&lt;/p&gt; |  | 14300000 | NPCC-ON |  | NPCC-US
3 | 79780007598 | &lt;p&gt;How Demand Side Management is addressed in the forecasts of its Peak Demand and annual Net Energy for Load.&lt;/p&gt; |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | &lt;p&gt;This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.”&lt;/p&gt; |  | 15300000 | NPCC-ON |  | NPCC-US
3 | 79780007610 | deploy Contingency Reserve, within system constraints, to respond to all Reportable Balancing Contingency Events, however, it is not subject to compliance with Requirement R1 part 1.1 if: |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2017-04-03 |  | 2017-12-31 |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780007628 | end-user Facilities |  | TO | [22 empty] | 2019-01-01 | [5 empty] | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780007631 | Procedures for confirming with those responsible for the reliability of affected systems of new or materially modified transmission Facilities are within a Balancing Authority Area’s metered boundaries. |  | TO | [22 empty] | 2019-01-01 | [5 empty] | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780007634 | Procedures for confirming with those responsible for the reliability of affected systems of new or materially modified generation Facilities are within a Balancing Authority Area’s metered boundaries. |  | GO | [22 empty] | 2019-01-01 | [5 empty] | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780007641 | An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:&lt;br/&gt;4.1.1. Applicable Transmission Owners&lt;br/&gt;4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.&lt;br/&gt;4.1.2. Applicable Generator Owners&lt;br/&gt;4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. &lt;br/&gt;4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.2.1. Each overhead transmission line operated at 200kV or higher.&lt;br/&gt;4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.&lt;br/&gt;4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.&lt;br/&gt;4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. &lt;br/&gt;4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:&lt;br/&gt;4.3.1.1. Operated at 200kV or higher; or&lt;br/&gt;4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or&lt;br/&gt;4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780007645 | An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage, |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:&lt;br/&gt;4.1.1. Applicable Transmission Owners&lt;br/&gt;4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.&lt;br/&gt;4.1.2. Applicable Generator Owners&lt;br/&gt;4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. &lt;br/&gt;4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.2.1. Each overhead transmission line operated at 200kV or higher.&lt;br/&gt;4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.&lt;br/&gt;4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.&lt;br/&gt;4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. &lt;br/&gt;4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:&lt;br/&gt;4.3.1.1. Operated at 200kV or higher; or&lt;br/&gt;4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or&lt;br/&gt;4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780007651 | Rescheduling work between growing seasons |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:&lt;br/&gt;4.1.1. Applicable Transmission Owners&lt;br/&gt;4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.&lt;br/&gt;4.1.2. Applicable Generator Owners&lt;br/&gt;4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. &lt;br/&gt;4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.2.1. Each overhead transmission line operated at 200kV or higher.&lt;br/&gt;4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.&lt;br/&gt;4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.&lt;br/&gt;4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. &lt;br/&gt;4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:&lt;br/&gt;4.3.1.1. Operated at 200kV or higher; or&lt;br/&gt;4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or&lt;br/&gt;4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 73000000 | NPCC-ON |  | NPCC-US
3 | 79780007667 | Uncontrolled separation shall not occur. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780007669 | For an ATC Path whose capacity is limited by contract, set TTC on the ATC Path at the lesser of the maximum allowable contract capacity or the reliability limit as determined by R2.1. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780007689 | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: |  | PCPA | [9 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 330000 | NPCC-ON |  | NPCC-US
3 | 79780007692 | Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. |  | PCPA | [9 empty] | PA | [12 empty] | 2015-10-01 |  | 2017-09-30 |  |  |  | 333000 | NPCC-ON |  | NPCC-US
3 | 79780007696 | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 430000 | NPCC-ON |  | NPCC-US
3 | 79780007727 | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. |  | TOP | [18 empty] | TOP |  |  |  | 2016-09-22 |  | 2018-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780007731 | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects its analysis functions. |  | BA | BA | [21 empty] | 2016-09-22 |  | 2018-03-31 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780007735 | Actions to address analysis quality issues affecting its Real-time Assessments. |  | TOP | [18 empty] | TOP |  |  |  | 2016-09-22 |  | 2018-03-31 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780007741 | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. |  | RC | [11 empty] | RC | [10 empty] | 2016-09-22 |  | 2018-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780007744 | Actions to address analysis quality issues affecting its Real-time Assessments. |  | RC | [11 empty] | RC | [10 empty] | 2016-09-22 |  | 2018-03-31 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780007753 | For limited impact RAS, the inadvertent operation of the RAS or the failure of the RAS to operate does not cause or contribute to BES Cascading, uncontrolled separation, angular instability, voltage instability, voltage collapse, or unacceptably damped oscillations. |  | PCPA | [9 empty] | PA | [12 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 41300000 | NPCC-ON |  | NPCC-US
3 | 79780007766 | The RAS was effective in mitigating BES performance issues it was designed to address. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 51300000 | NPCC-ON |  | NPCC-US
3 | 79780007773 | Notify each reviewing Reliability Coordinator if CAP actions or timetables change and when the CAP is completed. |  | DP, GO, PCPA, RC, TO |  | DP |  |  | GO |  |  |  |  | PA |  | RC | [10 empty] | 2017-11-27 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 73000000 | NPCC-ON |  | NPCC-US
3 | 79780007778 | Require its operating personnel that receive an oral two-party, person-to-person Operating Instruction to take one of the following actions: &lt;br/&gt;• Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct. &lt;br/&gt;• Request that the issuer reissue the Operating Instruction. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2015-06-22 | [5 empty] | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780007794 | Each Distribution Provider within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2016-10-28 | [5 empty] | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780007801 | Each adjacent Transmission Operator synchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2016-10-28 | [5 empty] | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780007806 | Each Distribution Provider within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2016-10-28 | [5 empty] | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780007812 | Each Adjacent Balancing Authority. |  | BA | BA | [21 empty] | 2016-10-28 | [5 empty] | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780007846 | Identify each asset that contains a low impact BES Cyber System according to Attachment 1, Section 3, if any (a discrete list of low impact BES Cyber Systems is not required). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-12-27 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency load shedding (UFLS) or undervoltage load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-002-5.1a: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780007854 | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. |  | RC | [11 empty] | RC | [10 empty] | 2016-12-14 | [5 empty] | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780007859 | Actions to address analysis quality issues affecting its Real-time Assessments. |  | RC | [11 empty] | RC | [10 empty] | 2016-12-14 | [5 empty] | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780007863 | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. |  | TOP | [18 empty] | TOP |  |  |  | 2016-12-14 | [5 empty] | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780007867 | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects its analysis functions. |  | BA | BA | [21 empty] | 2016-12-14 | [5 empty] | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780007872 | &lt;p&gt;Actions to address analysis quality issues affecting its Real-time Assessments.&lt;/p&gt; |  | TOP | [18 empty] | TOP |  |  |  | 2016-12-14 | [5 empty] | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780007891 | Interpersonal Communications. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2019-04-01 | [5 empty] | 12300000 | NPCC-ON |  | NPCC-US
3 | 79780007894 | An Operating Process for keeping the backup functionality consistent with the primary control center. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780007900 | Identification of the roles for personnel involved during the initiation and implementation of the Operating Plan for backup functionality. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2019-04-01 | [5 empty] | 16300000 | NPCC-ON |  | NPCC-US
3 | 79780007914 | Reporting requirements for the entities within the Reliability Coordinator Area during a restoration event. |  | RC | [11 empty] | RC | [10 empty] | 2018-03-26 | [5 empty] | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780007934 | Procedures for restoring interconnections with other Transmission Operators under the direction of its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780007950 | The capability of generating resources required to control voltages and frequency within acceptable operating limits. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780007956 | The minimum duration of each of the required tests. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 73000000 | NPCC-ON |  | NPCC-US
3 | 79780007960 | Building of cranking paths. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 83000000 | NPCC-ON |  | NPCC-US
3 | 79780007990 | Physical security of BES Cyber Systems (CIP-006); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11300000 | NPCC-ON |  | NPCC-US
3 | 79780008000 | Electronic access controls; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12300000 | NPCC-ON |  | NPCC-US
3 | 79780008025 | Monitor non-BES facilities within its Transmission Operator Area identified as necessary by the Transmission Operator; |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-17 |  | 2021-03-31 |  |  |  | 103000000 | NPCC-ON |  | NPCC-US
3 | 79780008045 | deploy Contingency Reserve, within system constraints, to respond to all Reportable Balancing Contingency Events, however, it is not subject to compliance with Requirement R1 part 1.1 if: |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2017-10-02 |  | 2019-03-31 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780008060 | The Transmission Operator shall provide the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. |  | TOP | [18 empty] | TOP |  |  |  | 2017-09-26 |  | 2018-12-31 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780008074 | Generator Operators that do not monitor the voltage at the location specified in their voltage schedule shall have a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2017-09-26 | [5 empty] | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780008082 | Impedance data. |  | GO | [22 empty] | 2017-09-26 | [5 empty] | 51300000 | NPCC-ON |  | NPCC-US
3 | 79780008090 | Notification by vendors when remote or onsite access should no longer be granted to vendor representatives; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and&lt;br/&gt;4.1.2.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and&lt;br/&gt;4.2.1.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers&lt;br/&gt;4.2.2.1. All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-013-1:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the identification and categorization process required by CIP-002-5, or any subsequent version of that Reliability Standard. |  | 12300000 | NPCC-ON |  | NPCC-US
3 | 79780008099 | Require inbound and outbound access permissions, including the reason for granting access, and deny all other access by default. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a list of rules (firewall, access control lists, etc.) that demonstrate that only permitted access is allowed and that each access rule has a documented reason. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-005-6:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780008105 | Require multi-factor authentication for all Interactive Remote Access sessions. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, architecture documents detailing the authentication factors used. &lt;br/&gt;Examples of authenticators may include, but are not limited to, &lt;br/&gt;• Something the individual knows such as passwords or PINs. This does not include User ID;&lt;br/&gt;• Something the individual has such as tokens, digital certificates, or smart cards; or &lt;br/&gt;• Something the individual is such as fingerprints, iris scans, or other biometric characteristics. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-005-6:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780008112 | Any custom software installed; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 11300000 | NPCC-ON |  | NPCC-US
3 | 79780008116 | For a change that deviates from the existing baseline configuration, update the baseline configuration as necessary within 30 calendar days of completing the change. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, updated baseline documentation with a date that is within 30 calendar days of the date of the completion of the change. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780008120 | Document the results of the verification. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 14300000 | NPCC-ON |  | NPCC-US
3 | 79780008134 | Prior to adding a new applicable Cyber Asset to a production environment, perform an active vulnerability assessment of the new Cyber Asset, except for CIP Exceptional Circumstances and like replacements of the same type of Cyber Asset with a baseline configuration that models an existing baseline configuration of the previous or other existing Cyber Asset. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a document listing the date of the assessment (performed prior to the commissioning of the new Cyber Asset) and the output of any tools used to perform the assessment. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780008168 | A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780008172 | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: &lt;br/&gt;• Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES &lt;br/&gt;• Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES&lt;br/&gt;• Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780008176 | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-3 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780008334 | The benchmark GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780008342 | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2019-06-30 |  |  |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780008347 | Include a timetable, subject to revision by the responsible entity in Part 7.4, for implementing the selected actions from Part 7.1. The timetable shall: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  |  | 73000000 | NPCC-ON |  | NPCC-US
3 | 79780008353 | Revisions to the selected actions in Part 7.1, if any, including utilization of Operating Procedures if applicable, and the updated timetable for implementing the selected actions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  |  | 74300000 | NPCC-ON |  | NPCC-US
3 | 79780008361 | If the analysis concludes there is Cascading caused by the supplemental GMD event described in Attachment 1, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  |  | 83000000 | NPCC-ON |  | NPCC-US
3 | 79780008370 | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2019-06-30 |  |  |  | 103000000 | NPCC-ON |  | NPCC-US
3 | 79780008399 | Emergency preparedness and operations |  | RC | [11 empty] | RC | [10 empty] | 2019-07-01 | [5 empty] | 11300000 | NPCC-ON |  | NPCC-US
3 | 79780008409 | System operations |  | TOP | [18 empty] | TOP |  |  |  | 2019-07-01 | [5 empty] | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780008417 | System operations |  | BA | BA | [21 empty] | 2019-07-01 | [5 empty] | 31300000 | NPCC-ON |  | NPCC-US
3 | 79780008425 | deploy Contingency Reserve, within system constraints, to respond to all Reportable Balancing Contingency Events, however, it is not subject to compliance with Requirement R1 part 1.1 if the Responsible Entity |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2019-04-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780008432 | If the Control Centers are owned or operated by different Responsible Entities, identification of the responsibilities of each Responsible Entity for applying security protection to the transmission of Real-time Assessment and Real-time monitoring data between those Control Centers. |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-04-13 |  |  |  | 4.2. Exemptions: The following are exempt from Reliability Standard CIP-012-1:&lt;br/&gt;4.2.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3. A Control Center that transmits to another Control Center Real-time Assessment or Real-time monitoring data pertaining only to the generation resource or Transmission station or substation co-located with the transmitting Control Center. |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780008442 | The Transmission Operator shall provide the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. |  | TOP | [18 empty] | TOP |  |  | For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | 2018-10-15 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780008455 | Real and reactive Load forecasts. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP | [8 empty] | 11300000 | NPCC-ON |  | NPCC-US
3 | 79780008462 | For each of the studies described in Requirement R2, Parts 2.1.1 and 2.1.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in System response :&lt;br/&gt;• Real and reactive forecasted Load. &lt;br/&gt;• Expected transfers. &lt;br/&gt;• Expected in service dates of new or modified Transmission Facilities. &lt;br/&gt;• Reactive resource capability. &lt;br/&gt;• Generation additions, retirements, or other dispatch scenarios. &lt;br/&gt;• Controllable Loads and Demand Side Management. &lt;br/&gt;• Duration or timing of known Transmission outages. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP | [8 empty] | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780008467 | The short circuit analysis portion of the Planning Assessment shall be conducted annually addressing the Near-Term Transmission Planning Horizon and can be supported by current or past studies as qualified in Requirement R2, Part 2.6. The analysis shall be used to determine whether circuit breakers have interrupting capability for Faults that they will be expected to interrupt using the System short circuit model with any planned generation and Transmission Facilities in service which could impact the study area. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-04-13 |  | 2020-06-10 |  |  |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780008471 | For each of the studies described in Requirement R2, Parts 2.4.1 and 2.4.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in performance:&lt;br/&gt;• Load level, Load forecast, or dynamic Load model assumptions. &lt;br/&gt;• Expected transfers. &lt;br/&gt;• Expected in service dates of new or modified Transmission Facilities. &lt;br/&gt;• Reactive resource capability. &lt;br/&gt;• Generation additions, retirements, or other dispatch scenarios. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP | [8 empty] | 24300000 | NPCC-ON |  | NPCC-US
3 | 79780008479 | If situations arise that are beyond the control of the Transmission Planner or Planning Coordinator that prevent the implementation of a Corrective Action Plan in the required timeframe, then the Transmission Planner or Planning Coordinator is permitted to utilize Non-Consequential Load Loss and curtailment of Firm Transmission Service to correct the situation that would normally not be permitted in Table 1, provided that the Transmission Planner or Planning Coordinator documents that they are taking actions to resolve the situation. The Transmission Planner or Planning Coordinator shall document the situation causing the problem, alternatives evaluated, and the use of Non-Consequential Load Loss or curtailment of Firm Transmission Service. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP | [8 empty] | 27300000 | NPCC-ON |  | NPCC-US
3 | 79780008493 | Contingency analyses for Requirement R3, Parts 3.1 and 3.2 shall: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-04-13 |  | 2020-06-10 |  |  |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780008509 | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each Quebec BES generator bus and associated generator step-up transformer high-side bus |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 13000 | NPCC-ON |  | NPCC-US
3 | 79780008513 | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 130000 | NPCC-ON |  | NPCC-US
3 | 79780008523 | &lt;p&gt;To provide notification per Requirement R4.&lt;/p&gt; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2021-01-01 |  |  |  | &lt;p&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes.&lt;/p&gt; |  | 12300000 | NPCC-ON |  | NPCC-US
3 | 79780008524 | &lt;p&gt;The roles and responsibilities of Cyber Security Incident response groups or individuals.&lt;/p&gt; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | &lt;p&gt;An example of evidence may include, but is not limited to, dated Cyber Security Incident response process(es) or procedure(s) that define roles and responsibilities (e.g., monitoring, reporting, initiating, documenting, etc.) of Cyber Security Incident response groups or individuals.&lt;/p&gt; | 2019-06-20 |  |  |  | &lt;p&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes.&lt;/p&gt; |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780008529 | &lt;p&gt;Retain records related to Reportable Cyber Security Incidents and Cyber Security Incidents that attempted to compromise a system identified in the “Applicable Systems” column for this Part as per the Cyber Security Incident response plan(s) under Requirement R1.&lt;/p&gt; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | &lt;p&gt;An example of evidence may include, but is not limited to, dated documentation, such as security logs, police reports, emails, response forms or checklists, forensic analysis results, restoration records, and post-incident review notes related to Reportable Cyber Security Incidents and a Cyber Security Incident that is determined to be an attempt to compromise a system identified in the “Applicable Systems” column.&lt;/p&gt; | 2019-06-20 |  |  |  | &lt;p&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes.&lt;/p&gt; |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780008535 | &lt;p&gt;Notify each person or group with a defined role in the Cyber Security Incident response plan of the updates to the Cyber Security Incident response plan based on any documented lessons learned.&lt;/p&gt; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2021-01-01 |  |  |  | &lt;p&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes.&lt;/p&gt; |  | 31300000 | NPCC-ON |  | NPCC-US
3 | 79780008542 | &lt;p&gt;The level of intrusion that was achieved or attempted.&lt;/p&gt; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2021-01-01 |  |  |  | &lt;p&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes.&lt;/p&gt; |  | 41300000 | NPCC-ON |  | NPCC-US
3 | 79780008544 | &lt;p&gt;Provide updates, if any, within 7 calendar days of determination of new or changed attribute information required in Part 4.1.&lt;/p&gt; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | &lt;p&gt;Examples of evidence may include, but are not limited to, dated documentation of submissions to the E-ISAC and NCCIC.&lt;/p&gt; | 2019-06-20 |  |  |  | &lt;p&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes.&lt;/p&gt; |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780008556 | The benchmark GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2020-10-05 |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780008567 | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2020-10-05 |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780008572 | Include a timetable, subject to revision by the responsible entity in Part 7.4, for implementing the selected actions from Part 7.1. The timetable shall: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2020-10-05 |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 73000000 | NPCC-ON |  | NPCC-US
3 | 79780008579 | Revisions to the selected actions in Part 7.1, if any, including utilization of Operating Procedures if applicable, and the updated timetable for implementing the selected actions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 74300000 | NPCC-ON |  | NPCC-US
3 | 79780008584 | If the analysis concludes there is Cascading caused by the supplemental GMD event described in Attachment 1, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2020-10-05 |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 83000000 | NPCC-ON |  | NPCC-US
3 | 79780008600 | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2020-10-05 |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 103000000 | NPCC-ON |  | NPCC-US
3 | 79780008683 | Physical security of BES Cyber Systems (CIP-006); | [28 empty] | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service &lt;br/&gt;&lt;br/&gt;equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11300000 | NPCC-ON |  | NPCC-US
3 | 79780008693 | Electronic access controls; | [28 empty] | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service &lt;br/&gt;&lt;br/&gt;equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12300000 | NPCC-ON |  | NPCC-US
3 | 79780008702 | Format and schedule of UFLS data submittal |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 143000000 | NPCC-ON |  | NPCC-US
3 | 79780008727 | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | GO | [28 empty] | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780008731 | Ambient conditions (for particular or average conditions or as they vary in real-time). |  | GO | [28 empty] | 22300000 | NPCC-ON |  | NPCC-US
3 | 79780008737 | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | TO | [28 empty] | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780008742 | Ambient conditions (for particular or average conditions or as they vary in real-time). |  | TO | [28 empty] | 32300000 | NPCC-ON |  | NPCC-US
3 | 79780008749 | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Protection Systems for BES Elements, with the following exclusions:&lt;br/&gt;4.2.1.1 Non-protective functions that are embedded within a Protection System.&lt;br/&gt;4.2.1.2 Protective functions intended to operate as a control function during switching. &lt;br/&gt;4.2.1.3 Special Protection Systems (SPS).&lt;br/&gt;4.2.1.4 Remedial Action Schemes (RAS).&lt;br/&gt;4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.&lt;br/&gt;4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.&lt;br/&gt;4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780008754 | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Protection Systems for BES Elements, with the following exclusions:&lt;br/&gt;4.2.1.1 Non-protective functions that are embedded within a Protection System.&lt;br/&gt;4.2.1.2 Protective functions intended to operate as a control function during switching. &lt;br/&gt;4.2.1.3 Special Protection Systems (SPS).&lt;br/&gt;4.2.1.4 Remedial Action Schemes (RAS).&lt;br/&gt;4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.&lt;br/&gt;4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.&lt;br/&gt;4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 21300000 | NPCC-ON |  | NPCC-US
3 | 79780008774 | Monitor non-BES facilities within its Transmission Operator Area identified as necessary by the Transmission Operator; |  | TOP | [18 empty] | TOP |  |  |  | 2021-04-01 | [5 empty] | 103000000 | NPCC-ON |  | NPCC-US
3 | 79780008808 | The Transmission Operator shall provide the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. |  | TOP | [18 empty] | TOP | [5 empty] | 2020-05-14 |  |  |  | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780008911 | Each Planning Coordinator in Ontario, Québec and the Maritime Provinces shall arrange for compensatory load shedding, in accordance with Attachment A and as provided by a Distribution Provider or Transmission Owner, that is adequate to compensate for the loss of generator(s) due to early tripping that is within the UFLS island identified by the Planning Coordinator in Requirement R2. |  | PCPA | [9 empty] | PA | [12 empty] | 2020-02-18 |  |  |  | 4.1.3. Distribution Providers that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators&lt;br/&gt;4.1.4. Transmission Owners that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators |  | 133000000 | NPCC-ON |  | NPCC-US
3 | 79780008915 | Transmit the initial frequency trip setting and any changes to the setting and the technical basis for the settings to the Planning Coordinator. |  | GO | [22 empty] | 2020-02-18 |  |  |  | 4.1.3. Distribution Providers that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators&lt;br/&gt;4.1.4. Transmission Owners that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators |  | 163000000 | NPCC-ON |  | NPCC-US
3 | 79780008989 | The benchmark GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780008997 | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 63000000 | NPCC-ON |  | NPCC-US
3 | 79780009002 | Include a timetable, subject to approval for any extension sought under Part 7.4, for implementing the selected actions from Part 7.1. The timetable shall: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 73000000 | NPCC-ON |  | NPCC-US
3 | 79780009015 | If the analysis concludes there is Cascading caused by the supplemental GMD event described in Attachment 1, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 83000000 | NPCC-ON |  | NPCC-US
3 | 79780009016 | The supplemental GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 83000000 | NPCC-ON |  | NPCC-US
3 | 79780009024 | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 103000000 | NPCC-ON |  | NPCC-US
3 | 79780009028 | Updated timetable for implementing the selected actions in Part 7.1. | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 74300000 | NPCC-ON |  | NPCC-US
3 | 79780009032 | Include a timetable, subject to approval for any extension sought under Part 11.4, for implementing the selected actions from Part 11.1. The timetable shall: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 113000000 | NPCC-ON |  | NPCC-US
3 | 79780009038 | Updated timetable for implementing the selected actions in Part 11.1. | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 114300000 | NPCC-ON |  | NPCC-US
3 | 79780009060 | Steady-state, short-circuit, and dynamics studies, as necessary, to evaluate system performance under both normal and contingency conditions; and |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2021-04-01 |  |  |  | Applicable Generator Owner: Generator Owner with a fully executed Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780009069 | A periodicity for providing data. |  | RC | [11 empty] | RC | [10 empty] | 2021-04-01 | [5 empty] | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780009075 | A mutually agreeable security protocol |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2021-04-01 | [5 empty] | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780009079 | A request to provide any or all of the following actual data, as necessary: |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780009083 | Monthly and annual Net Energy for Load in gigawatthours for the prior calendar year. | [24 empty] | 2021-04-01 | [5 empty] | 13300000 | NPCC-ON |  | NPCC-US
3 | 79780009088 | Peak hour forecast Total Internal Demands (summer and winter) in megawatts for ten calendar years into the future. | [24 empty] | 2021-04-01 | [5 empty] | 14300000 | NPCC-ON |  | NPCC-US
3 | 79780009104 | Guidelines the Planning Coordinator will use to determine unacceptable differences in performance under Part 1.1 or 1.2; and |  | PCPA | [9 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780009113 | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. |  | BA, DP, GO, GOP, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  |  |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780009123 | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 92300000 | NPCC-ON |  | NPCC-US
3 | 79780009124 | Operations and maintenance coordination |  | BA, DP, GO, GOP, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  |  |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 93000000 | NPCC-ON |  | NPCC-US
3 | 79780009127 | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 93300000 | NPCC-ON |  | NPCC-US
3 | 79780009135 | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 94300000 | NPCC-ON |  | NPCC-US
3 | 79780009173 | A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. |  | PCPA | [9 empty] | PA | [16 empty] | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780009177 | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: &lt;br/&gt;• Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES &lt;br/&gt;• Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES&lt;br/&gt;• Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. |  | PCPA | [9 empty] | PA | [16 empty] | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780009181 | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1. |  | PCPA | [9 empty] | PA | [16 empty] | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 43000000 | NPCC-ON |  | NPCC-US
3 | 79780009200 | Format and schedule of UFLS data submittal |  | PCPA | [9 empty] | PA | [16 empty] | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 143000000 | NPCC-ON |  | NPCC-US
3 | 79780009207 | A periodicity for providing data. |  | TOP | [18 empty] | TOP |  |  |  | 2021-04-01 | [5 empty] | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780009212 | A periodicity for providing data. |  | BA | BA | [21 empty] | 2021-04-01 | [5 empty] | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780009219 | A mutually agreeable security protocol |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  |  | 2021-04-01 | [5 empty] | 53000000 | NPCC-ON |  | NPCC-US
3 | 79780009256 | 1.3. Identify each asset that contains a low impact BES Cyber System according to Attachment 1, Section 3, if any (a discrete list of low impact BES Cyber Systems is not required). |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [5 empty] | 2021-02-04 |  |  |  | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780009311 | The short circuit analysis portion of the Planning Assessment shall be conducted annually addressing the Near-Term Transmission Planning Horizon and can be supported by current or past studies as qualified in Requirement R2, Part 2.6. The analysis shall be used to determine whether circuit breakers have interrupting capability for Faults that they will be expected to interrupt using the System short circuit model with any planned generation and Transmission Facilities in service which could impact the study area. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780009331 | Contingency analyses for Requirement R3, Parts 3.1 and 3.2 shall: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 33000000 | NPCC-ON |  | NPCC-US
3 | 79780009453 | Require inbound and outbound access permissions, including the reason for granting access, and deny all other access by default. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780009458 | Require multi-factor authentication for all Interactive Remote Access sessions. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 23000000 | NPCC-ON |  | NPCC-US
3 | 79780009471 | For a change that deviates from the existing baseline configuration, update the baseline configuration as necessary within 30 calendar days of completing the change. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 13000000 | NPCC-ON |  | NPCC-US
3 | 79780009487 | Prior to adding a new applicable Cyber Asset to a production environment, perform an active vulnerability assessment of the new Cyber Asset, except for CIP Exceptional Circumstances and like replacements of the same type of Cyber Asset with a baseline configuration that models an existing baseline configuration of the previous or other existing Cyber Asset |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 33000000 | NPCC-ON |  | NPCC-US
3. | 1026 | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  | IRO-005-2 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1053 | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  | IRO-005-3a R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1075 | The Interconnection-wide transmission loading relief procedure for use in ERCOT is provided as Section 7 of the ERCOT Protocols, posted at: http://www.ercot.com/tac/retailisoadhoccommittee/protocols/keydocs/draftercotprotocols.htm. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-04-22 |  |  | IRO-006-3 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1083 | The Interconnection-wide transmission loading relief procedure for use in ERCOT is provided as Section 7 of the ERCOT Protocols, posted at: http://www.ercot.com/mktrules/protocols/current.html |  | RC | [11 empty] | RC | [10 empty] | 2009-04-23 |  | 2009-12-09 |  |  | IRO-006-4 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1101 | Timeframe and periodicity for providing data and information (based on its hardware and software requirements, and the time needed to do its Operational Planning Analyses). |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2009-08-05 |  |  | IRO-010-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1109 | Planned or unplanned outage information. |  | RC | [11 empty] | RC | [9 empty] | M1.1.3 Planned or unplanned outage information. | 2007-06-18 |  | 2017-03-31 |  |  |  | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1122 | Be reviewed, at least once every three years, and updated if needed. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  | IRO-014-1 R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1133 | If the involved Reliability Coordinators cannot agree on the solution, the more conservative solution shall be implemented. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2017-03-31 |  |  | IRO-016-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1139 | An accounting for the ultimate points of power injection (sources) and power extraction (sinks) in TTC and ATC calculations. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-001-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1144 | Monthly values for months 2 through 13 at least once per month. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 15300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1154 | Monthly values for at least the next 12 months (months 2-13). |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-001-1 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1160 | The identity of the Transmission Operators and Transmission Service Providers from which the Transmission Service Provider receives data for use in calculating ATC or AFC. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-001-1 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1166 | How outages from other Transmission Service Providers that can not be mapped to the Transmission model used to calculate transfer or Flowgate capability are addressed. |  | TSP | [20 empty] | TSP |  |  |  | 2010-09-16 |  |  |  | 36300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1170 | Each Transmission Operator associated with the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-001-1 R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1180 | Monthly values, once per week. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-001-1 R8. | 83000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1185 | If the Transmission Service Provider does not use the data requested in its transfer or Flowgate capability calculations, and does not maintain that data, it shall not be required to make that data available. |  | TSP | [20 empty] | TSP |  |  |  | 2010-09-16 |  |  |  | 91300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1193 | The manner in which the response will be communicated (e.g., email, letter, telephone, etc). |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-003-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1200 | Require that generation unit outages considered in a Transmission Service Provider’s CBM calculation be restricted to those units within the Transmission Service Provider’s system. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-004-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1211 | The procedure for a Load-Serving Entity or Balancing Authority to use Transmission capacity set aside as CBM, including the manner in which the Transmission Service Provider will manage situations where the requested use of CBM exceeds the amount of CBM available. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1234 | The Load of the “energy deficient entity” is located within the TransmissionService Provider’s area. |  | TP, TSP | [19 empty] | TP | TSP |  | 2010-02-08 |  |  |  | 4.5. Transmission Planners, when their associated Transmission Service Provider has elected to maintain CBM. |  | 91000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1239 | Require review of the consistency of the Transmission Service Provider’s CBM components with its published planning criteria. A CBM value is considered consistent with published planning criteria if the components that comprise CBM are addressed in the planning criteria. The methodology used to determine and apply CBM does not have to involve the same mechanics as the planning process, but the same uncertainties must be considered and any simplifying assumptions explained. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-005-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1246 | Describe the conditions under which CBM may be available as Non-Firm Transmission Service. |  | TSP | [20 empty] | TSP |  | 2007-06-18 |  | 2009-05-12 |  |  | MOD-006-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1251 | Describe the conditions under which CBM may be available as Non-Firm Transmission Service. |  | TSP | [20 empty] | TSP |  | 2009-05-13 |  | 2011-03-31 |  |  | MOD-006-0.1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1257 | Amount of CBM used. |  | TSP | [20 empty] | TSP |  | 2007-06-18 |  | 2011-03-31 |  |  | MOD-007-0 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1261 | Specify the uncertainties accounted for in TRM and the methods used to determine their impacts on the TRM values. Any component of uncertainty, other than those identified in MOD-008-0_R1.3.1 through MOD-008-0_R1.3.7, shall benefit the interconnected transmission systems as a whole before they shall be permitted to be included in TRM calculations. The components of uncertainty identified in MOD-008-0_R1.3.1 through MOD-008-0_R1.3.7, if applied, shall be accounted for solely in TRM and not CBM. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-008-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1264 | Variations in facility Loadings due to balancing of generation within a Balancing Authority Area. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1276 | The identification of the TRM calculation used for the following time periods: |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  |  |  |  | MOD-008-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1279 | Beyond day-ahead and pre-schedule, up to thirteen months ahead. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 | [5 empty] | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1287 | Require review of the consistency of the Transmission Service Provider’s TRM components with its published planning criteria. A TRM value is considered consistent with published planning criteria if the same components that comprise TRM are also addressed in the planning criteria. The methodology used to determine and apply TRM does not have to involve the same mechanics as the planning process, but the same uncertainties must be considered and any simplifying assumption explained. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-009-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1296 | AC Transmission Line or Circuit (overhead and underground): nominal voltage, impedance, line charging, Normal and Emergency Ratings (consistent with methodologies defined and Ratings supplied per Reliability Standard FAC-004-0 and FAC-005-0 ) equipment status, and metering locations. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | MOD-011-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1310 | Device specific dynamics data shall be reported for dynamic devices, including, among others, static VAR controllers, high voltage direct current systems, flexible AC transmission systems, and static compensators. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | MOD-013-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1337 | Monthly peak hour forecast demands in MW and Net Energy for Load in GWh for the next two years. |  | LSE, PCPA, RP | [7 empty] | LSE |  | PA |  |  |  | RP | [8 empty] | 2007-06-18 |  | 2009-05-12 |  |  | MOD-017-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 134 | Month end Inadvertent Adjustments are 100% Primary Inadvertent Interchange and shall be added to the appropriate On- or Off-Peak accumulated Primary Inadvertent Interchange, unless such adjustments can be pinpointed to specific hours in which case R4.2 applies. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2014-03-31 |  |  | BAL-004-WECC-01 R4. | 43000000 | WECC-US | [5 empty] | WECC-US
3. | 1342 | Monthly peak hour forecast demands in MW and Net Energy for Load in GWh for the next two years. |  | LSE, PCPA, RP | [7 empty] | LSE |  | PA |  |  |  | RP | [8 empty] | 2009-05-13 |  | 2016-06-30 |  |  | MOD-017-0.1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1347 | Items (MOD-018-0_R 1.1) and (MOD-018-0_R 1.2) shall be addressed as described in the reporting procedures developed for Standard MOD-016-1_R 1. |  | LSE, PCPA, RP, TP | [7 empty] | LSE |  | PA |  |  |  | RP | [5 empty] | TP |  |  | 2007-06-18 |  | 2016-06-30 |  |  | MOD-018-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1358 | Acceptable methods for model and data verification, including any applicable conditions under which the data should be verified. Such methods can include use of manufacturer data, commissioning data, performance tracking, and testing, etc. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | MOD-024-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1363 | Method of verification, including date and conditions. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 15300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1369 | Acceptable methods for model and data verification, including any applicable conditions under which the data should be verified. Such methods can include use of commissioning data, performance tracking, engineering analysis, testing, etc. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | MOD-025-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1374 | Verified Reactive Power of auxiliary loads. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 15300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1381 | Any contractual obligations for allocation of TTC. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2013-09-30 |  |  | MOD-028-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1386 | The source/sink or POR/POD identification and mapping to the model. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2013-09-30 |  |  |  | 15300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 139 | Each Load-Serving Entity with load operating in an Interconnection shall ensure that those loads are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2008-08-26 |  |  | BAL-005-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1393 | Facility Ratings specified by the Generator Owners and Transmission Owners. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | MOD-028-1 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1398 | Unit commitment and dispatch order, to include all designated network resources and other resources that are committed or have the legal obligation to run, (within or out of economic dispatch) as they are expected to run. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2013-09-30 |  |  |  | 31300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1402 | Unit commitment and dispatch order, to include all designated network resources and other resources that are committed or have the legal obligation to run, (within or out of economic dispatch) as they are expected to run. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2013-09-30 |  |  |  | 32300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1406 | Include, for each time period, the Firm Transmission Service expected to be scheduled as specified in the ATCID (filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers) for the Transmission Service Provider, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed modeling the source and sink as follows: - If the source, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the source. - If the source, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the source, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source. - If the sink, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point shall as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the sink. - If the sink, as specified in the ATCID, has been identified in the reservation and the point can not be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is to be delivered as the sink. - If the sink, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is being delivered as the sink. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | MOD-028-1 R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1410 | Within 24 hours of the unexpected outage of a 500 kV or higher transmission Facility or a transformer with a low-side voltage of 200 kV or higher for TTCs in effect during the anticipated duration of the outage, provided such outage is expected to last 24 hours or longer. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | MOD-028-1 R5. | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1414 | Use (as the TTC) the lesser of: The sum of the incremental Transfer Capability and the impacts of Firm Transmission Services, as specified in the Transmission Service Provider’s ATCID, that were included in the study model, or The sum of Facility Ratings of all ties comprising the ATC Path. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | MOD-028-1 R6. | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1426 | Any other Transmission Operator area linked to the Transmission Operator’s area by joint operating agreement. (Equivalent representation is allowed.) |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 11130000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1429 | Models all generation (may be either a single generator or multiple generators) that is greater than 20 MVA at the point of interconnection in the studied area. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1441 | Uncontrolled separation shall not occur. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1443 | For an ATC Path whose capacity is limited by contract, set TTC on the ATC Path at the lesser of the maximum allowable contract capacity or the reliability limit as determined by R2.1. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-029-1 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 145 | Balancing Authorities shall install common metering equipment where Dynamic Schedules or Pseudo-Ties are implemented between two or more Balancing Authorities to deliver the output of Jointly Owned Units or to serve remote load. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2008-08-26 |  |  | BAL-005-0 R12. | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1460 | The source/sink or POR/POD identification and mapping to the model. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 12300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1465 | For monthly AFC, once per week. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | MOD-030-1 R10. | 103000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1475 | Any limiting Element/Contingency combination at least within the Transmission model identified in R3.4 and R3.5 that has been subjected to an Interconnection-wide congestion management procedure within the last 12 months, unless the limiting Element/Contingency combination is accounted for using another ATC methodology. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1480 | At a minimum, establish the list of Flowgates to create, modify, or delete external Flowgates that have been requested as part of R2.1.4 within thirty calendar days from the request. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | MOD-030-1 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1488 | Updated at least once per month for AFC calculations for months two through 13. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | MOD-030-1 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1495 | For external Flowgates, identified in R2.1.4, use the AFC provided by the Transmission Service Provider that calculates AFC for that Flowgate. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | MOD-030-1 R5. | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1503 | The impact of all confirmed firm Point-to-Point Transmission Service expected to be scheduled, including roll-over rights for Firm Transmission Service contracts, for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | MOD-030-1 R6. | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1511 | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | MOD-030-1 R7. | 73000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1523 | The source/sink or POR/POD identification and mapping to the model. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 12300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1528 | For monthly AFC, once per week. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R10. | 103000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1535 | If any limiting element is kept within its limit for its associated worst Contingency by operating within the limits of another Flowgate, then no new Flowgate needs to be established for such limiting elements or Contingencies. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21130000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1539 | If any limiting element is kept within its limit for its associated worst Contingency by operating within the limits of another Flowgate, then no new Flowgate needs to be established for such limiting elements or Contingencies. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21230000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1540 | Any limiting Element/Contingency combination at least within its Reliability Coordinator’s Area that has been subjected to an Interconnection-wide congestion management procedure within the last 12 months, unless the limiting Element/Contingency combination is accounted for using another ATC methodology or was created to address temporary operating conditions. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1545 | At a minimum, establish a list of Flowgates by creating, modifying, or deleting Flowgates that have been requested as part of R2.1.4 within thirty calendar days from the request. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1553 | Updated at least once per month for AFC calculations for months two through 13. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1560 | For external Flowgates, identified in R2.1.4, use the AFC provided by the Transmission Service Provider that calculates AFC for that Flowgate. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R5. | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1568 | The impact of all confirmed firm Point-to-Point Transmission Service expected to be scheduled, including roll-over rights for Firm Transmission Service contracts, for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R6. | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1576 | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R7. | 73000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1589 | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2008-11-26 |  | 2010-03-31 |  |  | NUC-001-1 R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1598 | A requirement to review the agreement(s) at least every three years. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 91300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1603 | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 92300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1604 | Operations and maintenance coordination: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2008-11-26 |  | 2010-03-31 |  |  | NUC-001-1 R9. | 93000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1607 | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 93300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1615 | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 94300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1626 | The training program must include training time for all Transmission Operator and Balancing Authority operating personnel to ensure their operating proficiency. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-03-31 |  |  | PER-002-0 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 164 | Each Load-Serving Entity with load operating in an Interconnection shall ensure that those loads are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2009-05-13 |  | 2012-09-12 |  |  | BAL-005-0.1b R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1643 | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall deliver the training established in R1.2. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | M1.3 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection System Operator training records showing the names of the people trained, the title of the training delivered and the dates of delivery to show that it delivered the training, as specified in R1.3. | 2013-04-01 |  | 2016-06-30 |  |  | PER-005-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1669 | Electrical quantities to be recorded for each monitored element shall be sufficient to determine the following: |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1672 | Polarizing currents and voltages, if used. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 21330000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1678 | Event triggering requirements. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 22300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1683 | Electrical quantities to be recorded for each monitored element shall be sufficient to determine the following: |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 31300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1692 | Timetable for response to data request. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | PRC-002-1 R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 170 | Balancing Authorities shall install common metering equipment where Dynamic Schedules or Pseudo-Ties are implemented between two or more Balancing Authorities to deliver the output of Jointly Owned Units or to serve remote load. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2009-05-13 |  | 2012-09-12 |  |  | BAL-005-0.1b R12. | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1701 | Process for review, analysis follow up, and documentation of Corrective Action Plans for Misoperations. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | PRC-003-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1716 | If the Protection System or RAS has a Security-Based or Dependability-Based Misoperation and a FEPS and FERAS is not in service to ensure BES reliability, Transmission Owners or Generator Owners shall repair and place back in service within 22 hours the Protection System or RAS that misoperated. If this cannot be done, then Transmission Owners and Generator Owners shall perform the following. |  | GO, TO, TOP |  |  |  |  | GO | [12 empty] | TO | TOP |  |  | M2.3 The Transmission Owners and Generation Owners shall have evidence that they repaired the Protection System or RAS that misoperated within 22 hours following identification of the Protection System or RAS Misoperation. | 2011-06-27 |  | 2017-03-31 |  |  | PRC-004-WECC-1 R2. | 23000000 | WECC-US | [5 empty] | WECC-US
3. | 1738 | Intentional and total tripping time delays. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  |  | 12300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1744 | A Regional Reliability Organization UFLS program database. This database shall be updated as specified in the Regional Reliability Organization program (but at least every five years) and shall include sufficient information to model the UFLS program in dynamic simulations of the interconnected transmission systems. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  | PRC-006-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1758 | A simulation of the event. |  | DP, LSE, TO, TOP |  | DP | [5 empty] | LSE | [9 empty] | TO | TOP |  |  |  | 2007-06-18 |  | 2013-09-30 |  |  | PRC-009-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1765 | A review of the voltage set points and timing. |  | DP, LSE, TO, TOP |  | DP | [5 empty] | LSE | [9 empty] | TO | TOP |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  |  | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1771 | Communications systems, where appropriate. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2027-03-31 |  |  |  | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1774 | Summary of testing procedure. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2027-03-31 |  |  | PRC-011-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1782 | Requirements to demonstrate that the SPS shall be designed so that a single SPS component failure, when the SPS was intended to operate, does not prevent the interconnected transmission system from meeting the performance requirements defined in Reliability Standards TPL-001-0, TPL-002-0, and TPL-003-0. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  | PRC-012-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1793 | Modeling — Information on detection logic or relay settings that control operation of the SPS. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  | PRC-013-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1800 | Identification of SPSs that were found not to comply with NERC standards and Regional Reliability Organization criteria. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  | PRC-014-0 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1816 | Communications systems, where appropriate. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1819 | Summary of testing procedure. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2007-06-18 |  | 2017-03-31 |  |  | PRC-017-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1831 | Installation location. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2022-06-30 |  |  | PRC-018-1 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1845 | Corresponding voltage set points and overall scheme clearing times. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  | PRC-020-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1853 | Time delay from initiation to trip signal. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2017-03-31 |  |  | PRC-021-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1860 | A simulation of the event, if deemed appropriate by the Regional Reliability Organization. For most events, analysis of sequence of events may be sufficient and dynamic simulations may not be needed. |  | DP, LSE, TOP |  | DP | [5 empty] | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | PRC-022-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1871 | Include a relay setting component of 87% of the current calculated in R1.12.2 in the Facility Rating determination for the circuit. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  |  | 20500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1874 | Set transmission line relays so they do not operate at or below 115% of the maximum theoretical power transfer capability (using a 90-degree angle between the sending-end and receiving-end voltages and either reactance or complex impedance) of the circuit (expressed in amperes) using one of the following to perform the power transfer calculation: |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  | PRC-023-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1888 | The Planning Coordinator shall provide a list of facilities to its Reliability Coordinators, Transmission Owners, Generator Owners, and Distribution Providers within 30 days of the establishment of the initial list and within 30 days of any changes to the list. |  | PCPA | [9 empty] | PA | [12 empty] | 2011-11-17 |  | 2012-06-30 |  |  | PRC-023-1 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 189 | Each Load-Serving Entity with load operating in an Interconnection shall ensure that those loads are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2008-08-27 |  | 2009-05-12 |  |  | BAL-005-0b R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1901 | When time does not permit such notifications and coordination, or when immediate action is required to prevent a hazard to the public, lengthy customer service interruption, or damage to facilities, the Generator Operator shall notify the Transmission Operator, and the Transmission Operator shall notify its Reliability Coordinator and adjacent Transmission Operators, at the earliest possible time. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-11-20 |  |  | TOP-001-1 R7. | 73000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 195 | Balancing Authorities shall install common metering equipment where Dynamic Schedules or Pseudo-Ties are implemented between two or more Balancing Authorities to deliver the output of Jointly Owned Units or to serve remote load. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2008-08-27 |  | 2009-05-12 |  |  | BAL-005-0b R12. | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1952 | Such information shall be available by 1200 Central Standard Time for the Eastern Interconnection and 1200 Pacific Standard Time for the Western Interconnection. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-09-30 |  |  | TOP-003-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1959 | Such information shall be available by 1200 Central Standard Time for the Eastern Interconnection and 1200 Pacific Standard Time for the Western Interconnection. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-05-23 |  | 2017-03-31 |  |  | TOP-003-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1971 | Switching transmission elements. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-01-21 |  |  | TOP-004-1 R6. | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 1983 | Planned outages of transmission elements. |  | TOP | [18 empty] | TOP |  |  |  | 2009-01-22 |  | 2017-03-31 |  |  | TOP-004-2 R6. | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2036 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category A of Table 1 (no contingencies). The specific elements selected (from each of the following categories) shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  | TPL-001-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2039 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2051 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2057 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category A of Table 1 (no contingencies). The specific elements selected (from each of the following categories) shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  | TPL-001-0.1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2060 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2072 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2078 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category B of Table 1 (single contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | TPL-002-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2084 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2097 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2103 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories,, showing system performance following Category B of Table 1 (single contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | TPL-002-0a R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2109 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2122 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2128 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | TPL-003-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2134 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2147 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2153 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | TPL-003-0a R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2159 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2172 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2178 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  | TPL-004-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2181 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 219 | A Balancing Authority shall make after-the-fact corrections to the agreed-to daily and monthly accounting data only as needed to reflect actual operating conditions (e.g. a meter being used for control was sending bad data). Changes or corrections based on non-reliability considerations shall not be reflected in the Balancing Authority’s Inadvertent Interchange. After-the-fact corrections to scheduled or actual values will not be accepted without agreement of the Adjacent Balancing Authority(ies). |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  | BAL-006-1 R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2194 | Other system conditions as deemed appropriate by the Regional Reliability Organization. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  |  | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2196 | Longer-term planning horizons (years six through ten). Assessment shall focus on the analysis of trends in resources and transmission Adequacy, other industry trends and developments, and reliability concerns. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | TPL-005-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 22 | The permissible mix of Operating Reserve - Spinning and Operating Reserve - Supplemental that may be included in Contingency Reserve. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  | BAL-002-0 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2202 | Evaluations of emergency response preparedness. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | TPL-005-0 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2209 | Demand-Side resources and their characteristics (program ratings, effects on annual system loads and load shapes, contractual arrangements, and program durations.) |  | RRO | [14 empty] | RRO | [9 empty] | 2009-04-15 |  |  | TPL-006-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2257 | Impedance data. |  | GO | [22 empty] | 2007-08-02 |  | 2008-08-26 |  |  |  | 41300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2272 | Impedance data. |  | GO | [22 empty] | 2009-05-13 |  | 2010-09-15 |  |  |  | 41300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2287 | Impedance data. |  | GO | [22 empty] | 2010-09-16 |  | 2013-06-30 |  |  |  | 41300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 229 | A Balancing Authority shall make after-the-fact corrections to the agreed-to daily and monthly accounting data only as needed to reflect actual operating conditions (e.g. a meter being used for control was sending bad data). Changes or corrections based on non-reliability considerations shall not be reflected in the Balancing Authority’s Inadvertent Interchange. After-the-fact corrections to scheduled or actual values will not be accepted without agreement of the Adjacent Balancing Authority(ies). |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-03-31 |  |  | BAL-006-1.1 R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2302 | Impedance data. |  | GO | [22 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 41300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2310 | AVR exhibits instability due to abnormal system configuration. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-06-27 |  | 2015-03-31 |  |  | VAR-002-WECC-1 R1. | 13000000 | WECC-US | [5 empty] | WECC-US
3. | 2324 | PSS exhibits instability due to abnormal system configuration. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-06-27 |  | 2015-03-31 |  |  | VAR-501-WECC-1 R1. | 13000000 | WECC-US | [5 empty] | WECC-US
3. | 2337 | The Interconnection-wide transmission loading relief procedure for use in ERCOT is provided as Section 7 of the ERCOT Protocols, posted at: http://www.ercot.com/mktrules/protocols/current.html |  | RC | [11 empty] | RC | [10 empty] | 2009-12-10 |  | 2011-06-30 |  |  | IRO-006-4.1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2349 | Demand-Side resources and their characteristics (program ratings, effects on annual system loads and load shapes, contractual arrangements, and program durations.) |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | TPL-006-0.1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2359 | Generation resources that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 12300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2368 | The Cyber Asset is dial-up accessible. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-002-2 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2373 | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-003-2 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2377 | Where allowed by Standards CIP-002-2 through CIP-009-2, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-003-2 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2382 | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-003-2 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2386 | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-003-2 R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2392 | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-003-2 R5. | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2400 | The proper handling of Critical Cyber Asset information; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 22300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2402 | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-004-2 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2406 | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-004-2 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2413 | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-005-2 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2420 | The Responsible Entity shall implement and maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-005-2 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2425 | The review process for authorization rights, in accordance with Standard CIP-004-2 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 25300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2434 | The discovery of all access points to the Electronic Security Perimeter; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-005-2 R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2440 | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-005-2 R5. | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2444 | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  | CIP-006-2 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2461 | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  | CIP-006-2 R8. | 83000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2465 | The Responsible Entity shall document test results. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | CIP-007-2 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2469 | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | CIP-007-2 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2480 | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-2 Requirement R5 and Standard CIP-004-2 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 51300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2484 | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 52300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2485 | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | CIP-007-2 R5. | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2488 | Each password shall be changed at least annually, or more frequently based on risk. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 53300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 249 | Generation resources that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 12300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2492 | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | CIP-007-2 R6. | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2498 | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | CIP-007-2 R7. | 73000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2502 | A review of controls for default accounts; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | CIP-007-2 R8. | 83000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2508 | Process for reporting Cyber Security Incidents to the Electricity Sector Information Sharing and Analysis Center (ES-ISAC). The Responsible Entity must ensure that all reportable Cyber Security Incidents are reported to the ES-ISAC either directly or through an intermediary. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-008-2 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2526 | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  | NUC-001-2 R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2535 | A requirement to review the agreement(s) at least every three years. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2014-01-21 |  |  |  | 91300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2540 | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 92300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2541 | Operations and maintenance coordination: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  | NUC-001-2 R9. | 93000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2544 | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 93300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2552 | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 94300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2559 | Develop, maintain, and implement a set of plans for load shedding. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  | EOP-001-2 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2563 | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  | EOP-001-2 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2570 | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  | EOP-001-2 R6. | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2575 | Procedures for restoring interconnections with other Transmission Operators under the direction of the Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | EOP-005-2 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 258 | The Cyber Asset is dial-up accessible. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-002-1 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2585 | Building of cranking paths. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | EOP-005-2 R10. | 103000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2608 | The capability of generating resources required to control voltages and frequency within acceptable operating limits. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | EOP-005-2 R6. | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2616 | The minimum duration of each of the required tests. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | EOP-005-2 R9. | 93000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2620 | Descriptions of the elements of coordination between individual Transmission Operator restoration plans. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  | EOP-006-2 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 263 | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-003-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2650 | The Responsible Entity shall document test results. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | CIP-007-2a R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2655 | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | CIP-007-2a R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2662 | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | CIP-007-2a R5. | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2665 | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-2 Requirement R5 and Standard CIP-004-2 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 51300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2666 | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 52300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2669 | Each password shall be changed at least annually, or more frequently based on risk. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 53300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 267 | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-003-1 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2675 | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | CIP-007-2a R6. | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2679 | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | CIP-007-2a R7. | 73000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2681 | A review of controls for default accounts; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | CIP-007-2a R8. | 83000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2689 | Include a description of how to identify the subset of SOLs that qualify as IROLs. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | FAC-010-2.1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2692 | Starting with all Facilities in service, the system’s response to a single Contingency, may include any of the following: |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | FAC-010-2.1 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2698 | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 22300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2704 | Level of detail of system models used to determine SOLs. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | FAC-010-2.1 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 271 | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-003-1 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2711 | Each Transmission Planner that works in the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | FAC-010-2.1 R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2718 | Generation resources that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | 12300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2727 | The Cyber Asset is dial-up accessible. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. | CIP-002-3 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2732 | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | CIP-003-3 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2736 | Where allowed by Standards CIP-002-3 through CIP-009-3, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | CIP-003-3 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2741 | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | CIP-003-3 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2745 | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | CIP-003-3 R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 275 | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-003-1 R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2751 | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | CIP-003-3 R5. | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2759 | The proper handling of Critical Cyber Asset information; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2012-12-11 |  |  |  | 22300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2761 | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2012-12-11 |  |  | CIP-004-3 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2765 | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2012-12-11 |  |  | CIP-004-3 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2772 | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | CIP-005-3 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2779 | The Responsible Entity shall implement and maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | CIP-005-3 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2784 | The review process for authorization rights, in accordance with Standard CIP-004-3 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2011-02-01 |  |  |  | 25300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2793 | The discovery of all access points to the Electronic Security Perimeter; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | CIP-005-3 R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2799 | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | CIP-005-3 R5. | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2803 | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  | CIP-006-3 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 281 | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-003-1 R5. | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2822 | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  | CIP-006-3 R8. | 83000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2826 | The Responsible Entity shall document test results. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-007-3a R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2830 | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-007-3a R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2841 | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-3 Requirement R5 and Standard CIP-004-3 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 51300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2845 | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 52300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2846 | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-007-3a R5. | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2849 | Each password shall be changed at least annually, or more frequently based on risk. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 53300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2853 | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-007-3a R6. | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2859 | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-007-3a R7. | 73000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2863 | A review of controls for default accounts; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-007-3a R8. | 83000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2869 | Process for reporting Cyber Security Incidents to the Electricity Sector Information Sharing and Analysis Center (ES-ISAC). The Responsible Entity must ensure that all reportable Cyber Security Incidents are reported to the ES-ISAC either directly or through an intermediary. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | CIP-008-3 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 289 | The proper handling of Critical Cyber Asset information; and, |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 22300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2895 | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  | CIP-006-2b R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2901 | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  | CIP-006-2b R8. | 83000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 291 | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-004-1 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2916 | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | CIP-006-2c R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2922 | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | CIP-006-2c R8. | 83000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2934 | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1b R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2940 | Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1b R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2946 | Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R2.3. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1b R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2949 | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1b R6. | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 295 | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-004-1 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2957 | Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R2.3. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | CIP-006-1c R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2965 | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | CIP-006-1c R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2969 | Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | CIP-006-1c R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2974 | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | CIP-006-1c R6. | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2991 | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  | CIP-006-3c R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 2999 | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  | CIP-006-3c R8. | 83000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3011 | Monthly values for at least the next 12 months (months 2-13). |  | TSP | [20 empty] | TSP | M2.3 - - There has been at least the next 12 months of monthly values calculated at all times (Months 2-13). | 2010-09-16 |  |  |  |  | MOD-001-1a R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3012 | The identity of the Transmission Operators and Transmission Service Providers from which the Transmission Service Provider receives data for use in calculating ATC or AFC. |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  |  |  |  | MOD-001-1a R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 302 | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | CIP-005-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3020 | How outages from other Transmission Service Providers that can not be mapped to the Transmission model used to calculate transfer or Flowgate capability are addressed. |  | TSP | [20 empty] | TSP |  | 2011-04-01 | [5 empty] | 36300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3023 | Each Transmission Operator associated with the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  |  |  |  | MOD-001-1a R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3031 | Monthly values, once per week. |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  |  |  |  | MOD-001-1a R8. | 83000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3056 | Models all generation (may be either a single generator or multiple generators) that is greater than 20 MVA at the point of interconnection in the studied area. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3059 | Any other Transmission Operator area linked to the Transmission Operator’s area by joint operating agreement. (Equivalent representation is allowed.) |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 11130000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3060 | For an ATC Path whose capacity is limited by contract, set TTC on the ATC Path at the lesser of the maximum allowable contract capacity or the reliability limit as determined by R2.1. |  | TOP | [18 empty] | TOP |  |  |  | 2010-09-16 |  | 2017-03-31 |  |  | MOD-029-1a R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3070 | Uncontrolled separation shall not occur. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3076 | Timeframe and periodicity for providing data and information (based on its hardware and software requirements, and the time needed to do its Operational Planning Analyses). |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2017-03-31 |  |  | IRO-010-1a R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 309 | The Responsible Entity shall maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-005-1 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 314 | The review process for authorization rights, in accordance with Standard CIP-004 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 25300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3157 | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. | CIP-005-3a R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3165 | The Responsible Entity shall implement and maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. | CIP-005-3a R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3170 | The review process for authorization rights, in accordance with Standard CIP-004-3 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. |  | 25300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3176 | The discovery of all access points to the Electronic Security Perimeter; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. | CIP-005-3a R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3182 | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. | CIP-005-3a R5. | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3188 | The permissible mix of Operating Reserve – Spinning and Operating Reserve – Supplemental that may be included in Contingency Reserve. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  | BAL-002-1 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3211 | A Balancing Authority shall make after-the-fact corrections to the agreed-to daily and monthly accounting data only as needed to reflect actual operating conditions (e.g. a meter being used for control was sending bad data). Changes or corrections based on non-reliability considerations shall not be reflected in the Balancing Authority’s Inadvertent Interchange. After-the-fact corrections to scheduled or actual values will not be accepted without agreement of the Adjacent Balancing Authority(ies). |  | BA | BA | [21 empty] | 2011-04-01 |  | 2018-12-31 |  |  | BAL-006-2 R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3221 | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-003-4 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3225 | Where allowed by Standards CIP-002-4 through CIP-009-4, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-003-4 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 323 | The discovery of all access points to the Electronic Security Perimeter; |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | CIP-005-1 R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3230 | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-003-4 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3234 | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-003-4 R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3240 | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-003-4 R5. | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3248 | The proper handling of Critical Cyber Asset information; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2012-12-11 |  |  |  | 22300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3250 | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2012-12-11 |  |  | CIP-004-4 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3254 | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2012-12-11 |  |  | CIP-004-4 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3261 | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-005-4a R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3268 | The Responsible Entity shall implement and maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-005-4a R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3273 | The review process for authorization rights, in accordance with Standard CIP-004-4 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 25300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3282 | The discovery of all access points to the Electronic Security Perimeter; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-005-4a R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3288 | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-005-4a R5. | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 329 | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-005-1 R5. | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3292 | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-006-4c R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3311 | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-006-4c R8. | 83000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3315 | The Responsible Entity shall document test results. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-007-4a R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3319 | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-007-4a R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 333 | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-006-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3330 | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-4 Requirement R5 and Standard CIP-004-4 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 51300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3334 | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 52300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3335 | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-007-4a R5. | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3338 | Each password shall be changed at least annually, or more frequently based on risk. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 53300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3342 | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-007-4a R6. | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3348 | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-007-4a R7. | 73000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3352 | A review of controls for default accounts; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-007-4a R8. | 83000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3358 | Process for reporting Cyber Security Incidents to the Electricity Sector Information Sharing and Analysis Center (ES-ISAC). The Responsible Entity must ensure that all reportable Cyber Security Incidents are reported to the ES-ISAC either directly or through an intermediary. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-008-4 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3378 | Interrupting interruptible load and exports. |  | BA | BA | [21 empty] | 2011-01-10 |  | 2012-09-12 |  |  | EOP-002-3 R6. | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3389 | The Reliability Coordinator shall use EEA 1 to forecast the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  | RC | [11 empty] | RC | [10 empty] | 2011-01-10 |  | 2012-09-12 |  |  | EOP-002-3 R9. | 93000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3410 | Evidence that the parties involved in the assessment have coordinated and cooperated on the assessment of the reliability impacts of new facilities on the interconnected transmission systems. While these studies may be performed independently, the results shall be jointly evaluated and coordinated by the entities involved. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [14 empty] | 2011-01-10 |  | 2015-12-31 |  |  | FAC-002-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3424 | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  | IRO-005-2a R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 343 | Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-006-1 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3455 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category A of Table 1 (no contingencies). The specific elements selected (from each of the following categories) shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | TPL-001-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3458 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3470 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3476 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories,, showing system performance following Category B of Table 1 (single contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | TPL-002-0b R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3482 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3495 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3501 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category B of Table 1 (single contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | TPL-002-1b R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3507 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 351 | Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R2.3. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-006-1 R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3520 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3526 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | TPL-003-1a R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3532 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3545 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3551 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | TPL-004-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3554 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 356 | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-006-1 R6. | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 360 | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1a R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3621 | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | CIP-005-1a R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3629 | The Responsible Entity shall maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | CIP-005-1a R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3634 | The review process for authorization rights, in accordance with Standard CIP-004 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 25300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3640 | The discovery of all access points to the Electronic Security Perimeter; |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | CIP-005-1a R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3646 | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | CIP-005-1a R5. | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3652 | Communication links connecting discrete Electronic Security Perimeters shall not be considered part of the Electronic Security Perimeter. However, end points of these communication links within the Electronic Security Perimeter(s) shall be considered access points to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | CIP-005-2a R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3660 | The Responsible Entity shall implement and maintain a procedure for securing dial-up access to the Electronic Security Perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | CIP-005-2a R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3665 | The review process for authorization rights, in accordance with Standard CIP-004-2 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 25300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3671 | The discovery of all access points to the Electronic Security Perimeter; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | CIP-005-2a R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3677 | The Responsible Entity shall retain electronic access logs for at least ninety calendar days. Logs related to reportable incidents shall be kept in accordance with the requirements of Standard CIP-008-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | CIP-005-2a R5. | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3696 | Each Load-Serving Entity with load operating in an Interconnection shall ensure that those loads are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP | [5 empty] | 2008-04-15 |  |  | BAL-005-0a R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 370 | Security Personnel: Personnel responsible for controlling physical access who may reside on-site or at a monitoring station. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1a R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3700 | Balancing Authorities shall install common metering equipment where Dynamic Schedules or Pseudo-Ties are implemented between two or more Balancing Authorities to deliver the output of Jointly Owned Units or to serve remote load. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP | [5 empty] | 2008-04-15 |  |  | BAL-005-0a R12. | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 378 | Manual Logging: A log book or sign-in sheet, or other record of physical access maintained by security or other personnel authorized to control and monitor physical access as specified in Requirement R2.3. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1a R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3807 | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  | IRO-005-3 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3821 | When time does not permit such notifications and coordination, or when immediate action is required to prevent a hazard to the public, lengthy customer service interruption, or damage to facilities, the Generator Operator shall notify the Transmission Operator, and the Transmission Operator shall notify its Reliability Coordinator and adjacent Transmission Operators, at the earliest possible time. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-11-21 |  | 2017-03-31 |  |  | TOP-001-1a R7. | 73000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 383 | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1a R6. | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3835 | Develop, maintain, and implement a set of plans for load shedding. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | EOP-001-0b R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3838 | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | EOP-001-0b R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3843 | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | EOP-001-0b R7. | 73000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3853 | Develop, maintain, and implement a set of plans for load shedding. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | EOP-001-2b R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3855 | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | EOP-001-2b R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3860 | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | EOP-001-2b R6. | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 387 | The Responsible Entity shall document test results. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-007-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3904 | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | CIP-006-2a R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 391 | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure or an acceptance of risk. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | CIP-007-1 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3910 | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | CIP-006-2a R8. | 83000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3925 | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  | CIP-006-3a R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3933 | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  | CIP-006-3a R8. | 83000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3963 | Any contractual obligations for allocation of TTC. |  | TSP | [20 empty] | TSP |  | 2013-09-27 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | MOD-028-2 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3968 | The source/sink or POR/POD identification and mapping to the model. |  | TSP | [20 empty] | TSP |  | 2013-10-01 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 15300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3975 | Facility Ratings specified by the Generator Owners and Transmission Owners. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | MOD-028-2 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3980 | A daily load forecast for TTCs used in ATC calculations for days two through 31. |  | TOP | [18 empty] | TOP |  |  |  | 2013-10-01 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 31300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3986 | Include, for each time period, the Firm Transmission Service expected to be scheduled as specified in the ATCID (filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers) for the Transmission Service Provider, all adjacent Transmission Service Providers, and any Transmission Service Providers with which coordination agreements have been executed modeling the source and sink as follows:- If the source, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point as the source.- If the source, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the source.- If the source, as specified in the ATCID, has been identified in the reservation and the point cannot be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source.- If the source, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider from which the power is to be received as the source.- If the sink, as specified in the ATCID, has been identified in the reservation and it is discretely modeled in the Transmission Service Provider’s Transmission model, use the discretely modeled point shall as the sink.- If the sink, as specified in the ATCID, has been identified in the reservation and the point can be mapped to an “equivalence” or “aggregate representation” in the Transmission Service Provider’s Transmission model, use the modeled equivalence or aggregate as the sink.- If the sink, as specified in the ATCID, has been identified in the reservation and the point can not be mapped to a discretely modeled point, an “equivalence,” or an “aggregate representation” in the Transmission Service Provider’s Transmission model, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is to be delivered as the sink.- If the sink, as specified in the ATCID, has not been identified in the reservation, use the immediately adjacent Balancing Authority associated with the Transmission Service Provider to which the power is being delivered as the sink. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | MOD-028-2 R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3990 | Within 24 hours of the unexpected outage of a 500 kV or higher transmission Facility or a transformer with a low-side voltage of 200 kV or higher for TTCs in effect during the anticipated duration of the outage, provided such outage is expected to last 24 hours or longer. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | MOD-028-2 R5. | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 3994 | Use (as the TTC) the lesser of:- The sum of the incremental Transfer Capability and the impacts of Firm Transmission Services, as specified in the Transmission Service Provider’s ATCID, that were included in the study model, or- The sum of Facility Ratings of all ties comprising the ATC Path. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | MOD-028-2 R6. | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 402 | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003 Requirement R5 and Standard CIP-004 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 51300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4037 | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-006-3d R8. | 83000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4043 | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-006-3d R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 406 | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 52300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4064 | Processes, tools, and procedures to monitor physical access to the perimeter(s). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-006-4d R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 407 | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-007-1 R5. | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4072 | Retention of outage records regarding access controls, logging, and monitoring for a minimum of one calendar year. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-006-4d R8. | 83000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4091 | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  | EOP-001-2.1b R6. | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4093 | Develop, maintain, and implement a set of plans for load shedding. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  | EOP-001-2.1b R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4097 | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  | EOP-001-2.1b R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 410 | Each password shall be changed at least annually, or more frequently based on risk. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 53300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4117 | Each Load-Serving Entity with load operating in an Interconnection shall ensure that those loads are included within the metered boundaries of a Balancing Authority Area. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2012-09-13 |  | 2018-12-31 |  |  | BAL-005-0.2b R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4121 | Balancing Authorities shall install common metering equipment where Dynamic Schedules or Pseudo-Ties are implemented between two or more Balancing Authorities to deliver the output of Jointly Owned Units or to serve remote load. |  | BA, GOP, LSE, TOP | BA |  |  |  |  | GOP |  | LSE | [10 empty] | TOP |  |  |  | 2012-09-13 |  | 2018-12-31 |  |  | BAL-005-0.2b R12. | 123000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4132 | Develop, maintain, and implement a set of plans for load shedding. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  | EOP-001-0.1b R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4138 | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  | EOP-001-0.1b R7. | 73000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 414 | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | CIP-007-1 R6. | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4140 | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  | EOP-001-0.1b R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4183 | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  | IRO-005-3.1a R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4198 | Interrupting interruptible load and exports. |  | BA | BA | [21 empty] | 2012-09-13 |  | 2017-03-31 |  |  | EOP-002-3.1 R6. | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 42 | If the Sink Balancing Authority is designating an Interchange Transaction(s) as part of its Contingency Reserve either Spinning or Non-Spinning, the Source Balancing Authority shall increase its Contingency Reserves equal in amount and type, to the capacity transaction(s) where the Sink Balancing Authority is designating the transaction(s) as a resource to meet its Contingency Reserve requirements. These types of transactions could be designated as either spinning or non-spinning reserves. If designated as Spinning Reserves, all of the requirements of section R2.1 & R2.2 must be met. |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2010-11-26 |  |  | BAL-002-WECC-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 420 | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-007-1 R7. | 73000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4207 | The Reliability Coordinator shall use EEA 1 to forecast the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  | EOP-002-3.1 R9. | 93000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4219 | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP | M4.3 The Transmission Entity informed the Nuclear Plant Generator Operator when it became aware it lost the capability to assess the operation of the electric system affecting the NPIRs. (Requirement 4.3) | 2013-04-01 |  | 2015-12-31 |  |  |  | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4224 | Operations and maintenance coordination: |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 93000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4225 | A requirement to review the agreement(s) at least every three years. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2014-01-21 |  |  |  | 91300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4231 | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 92300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4234 | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 93300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 424 | A review of controls for default accounts; and, |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | CIP-007-1 R8. | 83000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4241 | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 94300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4254 | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  | NUC-001-2.1 R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4259 | Operations and maintenance coordination: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  | NUC-001-2.1 R9. | 93000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 430 | Process for reporting Cyber Security Incidents to the Electricity Sector Information Sharing and Analysis Center (ES ISAC). The Responsible Entity must ensure that all reportable Cyber Security Incidents are reported to the ES ISAC either directly or through an intermediary. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-008-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4344 | Generation resources that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 12300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4346 | The Cyber Asset is dial-up accessible. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-002-3a R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4369 | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-004-3 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4371 | The proper handling of Critical Cyber Asset information; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 22300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4376 | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-004-3 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4385 | The Responsible Entity shall maintain documentation that training is conducted at least annually, including the date the training was completed and attendance records. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2014-02-03 |  |  | CIP-004-4 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4387 | The proper handling of Critical Cyber Asset information; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 22300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4392 | The Responsible Entity shall document the results of personnel risk assessments of its personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets, and that personnel risk assessments of contractor and service vendor personnel with such access are conducted pursuant to Standard CIP-004-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2014-02-03 |  |  | CIP-004-4 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4409 | Impedance data. |  | GO | [22 empty] | 2013-07-01 |  | 2014-09-30 |  |  |  | 41300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4444 | The permissible mix of Operating Reserve – Spinning and Operating Reserve – Supplemental that may be included in Contingency Reserve. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  | BAL-002-1a R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 445 | With other Reliability Coordinators, Transmission Operators, and Balancing Authorities as necessary to maintain reliability. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-05-12 |  |  | COM-001-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4465 | Each Balancing Authority shall inform its Reliability Coordinator of all generation resources available for use. |  | BA | BA | [23 empty] | 2015-03-18 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 455 | With other Reliability Coordinators, Transmission Operators, and Balancing Authorities as necessary to maintain reliability. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2009-05-13 |  | 2015-09-30 |  |  | COM-001-1.1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4557 | The Cyber Asset is dial-up accessible. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-002-3a R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4567 | Generation resources that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 12300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4584 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category A of Table 1 (no contingencies). The specific elements selected (from each of the following categories) shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | TPL-001-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4594 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4598 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4625 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories,, showing system performance following Category B of Table 1 (single contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | TPL-002-0b R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4640 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4644 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4650 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | TPL-003-0a R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4665 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4669 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4674 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | TPL-004-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4678 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4690 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | TPL-003-0a R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 470 | Develop, maintain, and implement a set of plans for load shedding. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  | EOP-001-0 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4705 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4709 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4719 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | TPL-003-0a R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4726 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4736 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4739 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | TPL-004-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4743 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 475 | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  | EOP-001-0 R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4756 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | TPL-004-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4764 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4802 | A Balancing Authority shall make after-the-fact corrections to the agreed-to daily andmonthly accounting data only as needed to reflect actual operating conditions (e.g. ameter being used for control was sending bad data). Changes or corrections based onnon-reliability considerations shall not be reflected in the Balancing Authority’sInadvertent Interchange. After-the-fact corrections to scheduled or actual values willnot be accepted without agreement of the Adjacent Balancing Authority(ies). |  | BA | BA | [23 empty] | 2006-05-01 |  |  |  | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4811 | With other Reliability Coordinators, Transmission Operators, and BalancingAuthorities as necessary to maintain reliability. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 482 | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  | EOP-001-0 R7. | 73000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4822 | The Transmission Operator anticipates initiating a 3% or greater voltage reduction,public appeals for load curtailments, or firm load shedding for other than localproblems. |  | TOP | [18 empty] | TOP | [5 empty] | 2006-11-01 |  |  |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4831 | The Reliability Coordinator shall use EEA 1 to forecast the change of the priority oftransmission service of an Interchange Transaction on the system from Priority 6 toPriority 7. |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 103000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4840 | Interrupting interruptible load and exports. |  | BA | BA | [23 empty] | 2006-11-01 |  |  |  | 73000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4857 | Interrupting interruptible load and exports. |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4868 | The Reliability Coordinator shall use EEA 1 to forecast the change of the priority oftransmission service of an Interchange Transaction on the system from Priority 6 toPriority 7. |  | RC | [11 empty] | RC | [12 empty] | 2007-01-01 |  |  |  | 93000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 488 | Develop, maintain, and implement a set of plans for load shedding. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  | EOP-001-1 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4889 | The affected Balancing Authorities, working with their Reliability Coordinator(s), shall immediately review the Interchange Schedules between those Balancing Authority Areas or fragments of those Balancing Authority Areas within the separated area and make adjustments as needed to facilitate the restoration. The affected Balancing Authorities shall make all attempts to maintain the adjusted Interchange Schedules, whether generation control is manual or automatic. |  | BA | BA | [23 empty] | 2007-05-02 |  |  |  | 93000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4894 | Reliability Coordinator(s) and adjacent areas are notified and Reliability Coordinator approval is given. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-05-02 |  |  |  | 95300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 49 | Interchange Transactions designated by the source Balancing Authority as non-spinning contingency reserve; |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2010-11-26 |  |  | BAL-002-WECC-1 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4905 | Annual work plan. |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-04-07 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4911 | Series and shunt reactive elements |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-08-01 |  |  |  | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4917 | In cases where protection systems and control settings constitute a loading limit on afacility, this limit shall become the Rating for that facility. |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-08-01 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4927 | All Dynamic Schedules at the expected average MW profile for each hour. |  | BA, PSE | BA | [9 empty] | PSE | [13 empty] | 2007-01-01 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 493 | The tasks to be coordinated with and among adjacent Transmission Operators and Balancing Authorities. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  | EOP-001-1 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4931 | All bilateral inadvertent interchange payback. |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4943 | Transmission Service Provider(s) on the Schedule Path |  | BA, TSP | BA | [19 empty] | TSP |  |  |  | 2007-01-01 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4949 | Energy profile fits within OASIS reservation. |  | TSP | [20 empty] | TSP |  |  |  | 2007-01-01 |  |  |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4956 | Ramp (ability of generation maneuverability to accommodate). |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4964 | Ramp start time and duration (Balancing Authorities shall use the Ramp duration established for their Interconnection unless they agree to an alternative Ramp duration.) Default Ramps durations are as follows:• Default Ramp duration for the Eastern Interconnection shall be 10 minutes equally across the Interchange Schedule start and end times.• Default Ramp duration for the Western Interconnection shall be 20 minutes equally across the Interchange Schedule start and end times.• Ramp durations for Interchange Schedules implemented for compliance with NERC’s Disturbance Control Standard (recovery from a disturbance condition) and Interchange Transaction curtailment in response to line loading relief procedures may be shorter than the above defaults, but must be identical for the Sending Balancing Authority and Receiving Balancing Authority. |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4966 | Balancing Authorities that implement Interchange Schedules that cross an Interconnection boundary shall use the same start time and Ramp durations. |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4982 | SOL or IROL potential or actual limit violation. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 4993 | A Reliability Coordinator or Transmission Operator determines the deviation, regardless of magnitude, to be a reliability concern and notifies the Purchasing-Selling Entity of that determination and the reasons. |  | PSE, RC, TOP | [10 empty] | PSE | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 500 | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  | EOP-001-1 R6. | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5029 | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5056 | The Interconnection-wide transmission loading relief procedure for use in ERCOT isprovided as Section 7 of the ERCOT Protocols, posted at:http://www.ercot.com/tac/retailisoadhoccommittee/protocols/keydocs/draftercotprotocols.htm. |  | RC | [11 empty] | RC | [12 empty] | 2005-08-08 |  |  |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5065 | The Interconnection-wide transmission loading relief procedure for use in ERCOT isprovided as Section 7 of the ERCOT Protocols, posted at:http://www.ercot.com/tac/retailisoadhoccommittee/protocols/keydocs/draftercotprotocols.htm. |  | RC | [11 empty] | RC | [12 empty] | 2006-09-29 |  |  |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5074 | The Interconnection-wide transmission loading relief procedure for use inERCOT is provided as Section 7 of the ERCOT Protocols, posted at:http://www.ercot.com/tac/retailisoadhoccommittee/protocols/keydocs/draftercotprotocols.htm. |  | RC | [11 empty] | RC | [12 empty] | 2006-09-29 |  |  |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5084 | Dynamics data representing electrical demand characteristics as a function of frequency and voltage. |  | RRO | [14 empty] | RRO | [9 empty] | 2006-11-02 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 510 | Interrupting interruptible load and exports. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  | EOP-002-2 R6. | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5112 | Data format requirements. |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 12300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5114 | Monitoring, recording, and reporting capabilities of the equipment. |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5117 | Frequency. |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5124 | Generators. |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 16300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5131 | Process for review, follow up, and documentation of corrective action plans for misoperations. |  | RRO | [14 empty] | RRO | [9 empty] | 2006-05-01 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5141 | Communications systems, where appropriate. |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2006-05-01 |  |  |  | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5144 | Summary of testing procedure. |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2006-05-01 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5208 | Switching transmission elements. |  | TOP | [18 empty] | TOP | [5 empty] | 2005-04-01 |  |  |  | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 521 | The Reliability Coordinator shall use EEA 1 to forecast the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-05-12 |  |  | EOP-002-2 R9. | 93000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5270 | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | CIP-003-3 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5274 | Where allowed by Standards CIP-002-3 through CIP-009-3, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | CIP-003-3 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5277 | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | CIP-003-3 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5280 | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | CIP-003-3 R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5284 | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | CIP-003-3 R5. | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5294 | Annual review and approval of the cyber security policy by the senior manager assigned pursuant to R2. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-003-4 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5298 | Where allowed by Standards CIP-002-4 through CIP-009-4, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-003-4 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5301 | Authorized exceptions to the cyber security policy must be reviewed and approved annually by the senior manager or delegate(s) to ensure the exceptions are still required and valid. Such review and approval shall be documented. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-003-4 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5304 | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-003-4 R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5308 | The Responsible Entity shall assess and document at least annually the processes for controlling access privileges to protected information. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-003-4 R5. | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 531 | Interrupting interruptible load and exports. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-09-30 |  |  | EOP-002-2.1 R6. | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5321 | The Responsible Entity shall document test results. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-007-3a R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5326 | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-007-3a R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5333 | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-007-3a R5. | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5336 | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-3 Requirement R5 and Standard CIP-004-3 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 51300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5337 | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 52300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5340 | Each password shall be changed at least annually, or more frequently based on risk. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 53300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5346 | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-007-3a R6. | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5350 | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-007-3a R7. | 73000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5352 | A review of controls for default accounts; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-007-3a R8. | 83000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5364 | The Responsible Entity shall document test results. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-007-4a R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5369 | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-007-4a R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5376 | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-007-4a R5. | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5379 | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-4 Requirement R5 and Standard CIP-004-4 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 51300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5380 | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 52300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5383 | Each password shall be changed at least annually, or more frequently based on risk. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 53300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5389 | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-007-4a R6. | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5393 | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-007-4a R7. | 73000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5395 | A review of controls for default accounts; and, |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-007-4a R8. | 83000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 542 | The Reliability Coordinator shall use EEA 1 to forecast the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  | RC | [11 empty] | RC | [10 empty] | 2009-05-13 |  | 2011-09-30 |  |  | EOP-002-2.1 R9. | 93000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 557 | Under certain adverse conditions, e.g., severe weather, it may not be possible to assess the damage caused by a disturbance and issue a written Interconnection Reliability Operating Limit and Preliminary Disturbance Report within 24 hours. In such cases, the affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load-Serving Entity shall promptly notify its Regional Reliability Organization(s) and NERC, and verbally provide as much information as is available at that time. The affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load-Serving Entity shall then provide timely, periodic verbal updates until adequate information is available to issue a written Preliminary Disturbance Report. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-12-31 |  |  | EOP-004-1 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5601 | Include a description of how to identify the subset of SOLs that qualify as IROLs. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5620 | Level of detail of system models used to determine SOLs. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5627 | Each Transmission Planner that works in the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5632 | Include a description of how to identify the subset of SOLs that qualify as IROLs |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5638 | In determining the system’s response to a single Contingency, the following shall be acceptable: |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 22300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5648 | A process for determining which of the stability limits associated with the list of multiple contingencies (provided by the Planning Authority in accordance with FAC-014 Requirement 6) are applicable for use in the operating horizon given the actual or expected system conditions. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5658 | Each Transmission Operator that operates in the Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5663 | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 567 | The affected Balancing Authorities, working with their Reliability Coordinator(s), shall immediately review the Interchange Schedules between those Balancing Authority Areas or fragments of those Balancing Authority Areas within the separated area and make adjustments as needed to facilitate the restoration. The affected Balancing Authorities shall make all attempts to maintain the adjusted Interchange Schedules, whether generation control is manual or automatic. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2013-06-30 |  |  | EOP-005-1 R11. | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5687 | The source/sink or POR/POD identification and mapping to the model. |  | TSP | [20 empty] | TSP |  | 2017-04-01 | [5 empty] | 12300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5694 | If any limiting element is kept within its limit for its associated worst Contingency by operating within the limits of another Flowgate, then no new Flowgate needs to be established for such limiting elements or Contingencies. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 21130000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5699 | If any limiting element is kept within its limit for its associated worst Contingency by operating within the limits of another Flowgate, then no new Flowgate needs to be established for such limiting elements or Contingencies. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 21230000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5700 | Any limiting Element/Contingency combination at least within its Reliability Coordinator’s Area that has been subjected to an Interconnection-wide congestion management procedure within the last 12 months, unless the limiting Element/Contingency combination is accounted for using another ATC methodology or was created to address temporary operating conditions. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5705 | At a minimum, establish a list of Flowgates by creating, modifying, or deleting Flowgates that have been requested as part of R2.1.4 within thirty calendar days from the request. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5713 | Updated at least once per month for AFC calculations for months two through 13. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 572 | Reliability Coordinator(s) and adjacent areas are notified and Reliability Coordinator approval is given. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  |  | 115300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5720 | For external Flowgates, identified in R2.1.4, use the AFC provided by the Transmission Service Provider that calculates AFC for that Flowgate. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5728 | The impact of all confirmed firm Point-to-Point Transmission Service expected to be scheduled, including roll-over rights for Firm Transmission Service contracts, for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5736 | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 73000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5746 | For monthly AFC, once per week. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 103000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5755 | Generation resources that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5762 | The Cyber Asset is dial-up accessible. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5767 | Generation resources that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5774 | The Cyber Asset is dial-up accessible. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5782 | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  |  | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5791 | A requirement to review the agreement(s) at least every three years. (Retirement approved by FERC effective January 21, 2014.) | [26 empty] | 2014-11-13 |  |  |  | 91300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5796 | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 92300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5797 | Operations and maintenance coordination: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  |  | 93000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5800 | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 93300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5808 | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 94300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5814 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category A of Table 1 (no contingencies). The specific elements selected (from each of the following categories) shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5817 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5829 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5835 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category B of Table 1 (single contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5838 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5854 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5860 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category C of Table 1 (multiple contingencies). The specific elements selected (from each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5863 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5879 | Consider lead times necessary to implement plans. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5885 | Be supported by a current or past study and/or system simulation testing that addresses each of the following categories, showing system performance following Category D contingencies of Table I. The specific elements selected (from within each of the following categories) for inclusion in these studies and simulations shall be acceptable to the associated Regional Reliability Organization(s). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5888 | Be conducted annually unless changes to system conditions do not warrant such analyses. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5900 | Requirements to demonstrate that the RAS shall be designed so that a single RAS component failure, when the RAS was intended to operate, does not prevent the interconnected transmission system from meeting the performance requirements defined in Reliability Standards TPL-001-0, TPL-002-0, and TPL-003-0. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5901 | Requirements to demonstrate that the RAS shall be designed so that a single RAS component failure, when the RAS was intended to operate, does not prevent the interconnected transmission system from meeting the performance requirements defined in Reliability Standards TPL-001-0, TPL-002-0, and TPL-003-0. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 591 | Blackstart unit testing requirements including, but not limited to: |  | RRO | [14 empty] | RRO | [7 empty] | 2011-05-23 |  | 2011-05-23 |  |  | EOP-007-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5919 | Identification of RAS that were found not to comply with NERC standards and Regional Reliability Organization criteria. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5925 | Modeling — Information on detection logic or relay settings that control operation of the RAS. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5937 | Communications systems, where appropriate. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-04-01 |  | 2027-03-31 |  |  |  | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 594 | Minimum duration of tests. |  | RRO | [14 empty] | RRO | [9 empty] | 2011-05-23 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5940 | Summary of testing procedure. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-04-01 |  | 2027-03-31 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5941 | Summary of testing procedure. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-01-25 |  | 2027-03-31 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5949 | Corresponding voltage set points and overall scheme clearing times. | [26 empty] | 2014-11-13 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5957 | Time delay from initiation to trip signal. | [26 empty] | 2014-11-13 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 5991 | If the Protection System or RAS has a Security-Based or Dependability-Based Misoperation and a FEPS and FERAS is not in service to ensure BES reliability, Transmission Owners or Generator Owners shall repair and place back in service within 22 hours the Protection System or RAS that misoperated. If this cannot be done, then Transmission Owners and Generator Owners shall perform the following. |  | GO, TO |  |  |  |  | GO | [16 empty] | M2.3 The Transmission Owners and Generation Owners shall have evidence that they repaired the Protection System or RAS that misoperated within 22 hours following identification of the Protection System or RAS Misoperation. | 2016-01-25 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf..4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. |  | 23000000 | WECC-US | [5 empty] | WECC-US
3. | 600 | The contingency plan must address monitoring and control of critical transmission facilities, generation control, voltage control, time and frequency control, control of critical substation devices, and logging of significant power system events. The plan shall list the critical facilities. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | EOP-008-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6027 | Any other Transmission Operator area linked to the Transmission Operator’s area by joint operating agreement. (Equivalent representation is allowed.) |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 11130000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 611 | End-user facilities. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  | FAC-001-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6162 | Physical security of BES Cyber Systems (CIP-006); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6171 | Electronic access controls for external routable protocol connections and Dial-up Connectivity; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2016-06-30 |  |  |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6175 | The roles and responsibilities of Cyber Security Incident response groups or individuals. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.3. An example of evidence may include, but is not limited to, dated Cyber Security Incident response process(es) or procedure(s) that define roles and responsibilities (e.g., monitoring, reporting, initiating, documenting, etc.) of Cyber Security Incident response groups or individuals. | 2014-02-03 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6179 | Retain records related to Reportable Cyber Security Incidents. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.3. An example of evidence may include, but is not limited to, dated documentation, such as security logs, police reports, emails, response forms or checklists, forensic analysis results, restoration records, and post-incident review notes related to Reportable Cyber Security Incidents. | 2014-02-03 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6183 | Notify each person or group with a defined role in the Cyber Security Incident response plan of the updates to the Cyber Security Incident response plan based on any documented lessons learned. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | 31300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6191 | For applicable patches identified in Part 2.2, within 35 calendar days of the evaluation completion, take one of the following actions:• Apply the applicable patches; or• Create a dated mitigation plan; or• Revise an existing mitigation plan. Mitigation plans shall include the Responsible Entity’s planned actions to mitigate the vulnerabilities addressed by each security patch and a timeframe to complete these mitigations. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6195 | For those methods identified in Part 3.1 that use signatures or patterns, have a process for the update of the signatures or patterns. The process must address testing and installing the signatures or patterns. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6198 | Where technically feasible, retain applicable event logs identified in Part 4.1 for at least the last 90 consecutive calendar days except under CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6202 | Identify individuals who have authorized access to shared accounts. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6209 | Detected malicious code. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 41300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6221 | Any custom software installed; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6225 | For a change that deviates from the existing baseline configuration, update the baseline configuration as necessary within 30 calendar days of completing the change. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6229 | Document the results of the verification. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 14300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 623 | Voltage level and MW and MVAR capacity or demand at point of connection. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6238 | Prior to adding a new applicable Cyber Asset to a production environment, perform an active vulnerability assessment of the new Cyber Asset, except for CIP Exceptional Circumstances and like replacements of the same type of Cyber Asset with a baseline configuration that models an existing baseline configuration of the previous or other existing Cyber Asset. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6242 | Require inbound and outbound access permissions, including the reason for granting access, and deny all other access by default. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.3. An example of evidence may include, but is not limited to, a list of rules (firewall, access control lists, etc.) that demonstrate that only permitted access is allowed and that each access rule has a documented reason. | 2014-02-03 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6247 | Require multi-factor authentication for all Interactive Remote Access sessions. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.3. An example of evidence may include, but is not limited to, architecture documents detailing the authentication factors used. Examples of authenticators may include, but are not limited to, • Something the individual knows such as passwords or PINs. This does not include User ID;• Something the individual has such as tokens, digital certificates, or smart cards; or • Something the individual is such as fingerprints, iris scans, or other biometric characteristics. | 2014-02-03 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6250 | Where technically feasible, utilize two or more different physical access controls (this does not require two completely independent physical access control systems) to collectively allow unescorted physical access into Physical Security Perimeters to only those individuals who have authorized unescorted physical access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 1.3 An example of evidence may include, but is not limited to, language in the physical security plan that describes the Physical Security Perimeters and how unescorted physical access is controlled by two or more different methods and proof that unescorted physical access is restricted to only authorized individuals, such as a list of authorized individuals accompanied by access logs. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6259 | Retain visitor logs for at least ninety calendar days. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 2.3 An example of evidence may include, but is not limited to, documentation showing logs have been retained for at least ninety calendar days. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6263 | One or more processes for the backup and storage of information required to recover BES Cyber System functionality. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6268 | Test each of the recovery plans referenced in Requirement R1 at least once every 36 calendar months through an operational exercise of the recovery plans in an environment representative of the production environment. An actual recovery response may substitute for an operational exercise. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6272 | Notify each person or group with a defined role in the recovery plan of the updates to the recovery plan based on any documented lessons learned. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 31300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6297 | Require completion of the training specified in Part 2.1 at least once every 15 calendar months. | [23 empty] | Examples of evidence may include, but are not limited to, dated individual training records. |  |  | 2016-06-30 |  |  |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6302 | Criteria or process to evaluate criminal history records checks for authorizing access. | [23 empty] | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to evaluate criminal history records checks. |  |  | 2016-06-30 |  |  |  | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6310 | For electronic access, verify at least once every 15 calendar months that all user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and are those that the Responsible Entity determines are necessary. | [23 empty] | An example of evidence may include, but is not limited to, documentation of the review that includes all of the following: 1. A dated listing of all accounts/account groups or roles within the system; 2. A summary description of privileges associated with each group or role;3. Accounts assigned to the group or role; and4. Dated evidence showing verification of the privileges for the group are authorized and appropriate to the work function performed by people assigned to each account. |  |  | 2016-06-30 |  |  |  | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6314 | For termination actions, revoke the individual’s access to the designated storage locations for BES Cyber System Information, whether physical or electronic (unless already revoked according to Requirement R5.1), by the end of the next calendar day following the effective date of the termination action. | [23 empty] | An example of evidence may include, but is not limited to, workflow or sign-off form verifying access removal to designated physical areas or cyber systems containing BES Cyber System Information associated with the terminations and dated within the next calendar day of the termination action. |  |  | 2016-06-30 |  |  |  | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6319 | Identify each asset that contains a low impact BES Cyber System according to Attachment 1, Section 3, if any (a discrete list of low impact BES Cyber Systems is not required). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-12-26 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6328 | Ambient conditions (for particular or average conditions or as they vary in real-time). |  | GO | [22 empty] | 2013-01-01 |  | 2021-09-30 |  |  |  | 22300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6330 | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | GO | [22 empty] | 2011-11-17 |  | 2021-09-30 |  |  |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6338 | Ambient conditions (for particular or average conditions or as they vary in real-time). |  | TO | [22 empty] | 2013-01-01 |  | 2021-09-30 |  |  |  | 32300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 634 | Evidence that the parties involved in the assessment have coordinated and cooperated on the assessment of the reliability impacts of new facilities on the interconnected transmission systems. While these studies may be performed independently, the results shall be jointly evaluated and coordinated by the entities involved. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [14 empty] | 2007-06-18 |  | 2011-09-30 |  |  | FAC-002-0 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6340 | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | TO | [22 empty] | 2011-11-17 |  | 2021-09-30 |  |  |  | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6356 | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-11-19 |  | 2017-04-01 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6362 | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-04-02 |  | 2017-04-01 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6370 | If a generating unit/generating facility has not participated in a minimum of (8) eight FMEs in a 12-month period, its performance shall be based on a rolling eight FME average response. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [16 empty] | 2014-01-16 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01.4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. |  | 23000000 | TXRE-US |  |  |  |  | TXRE-US
3. | 6385 | If the unaffiliated verifying entity recommends that the Transmission Owner add a Transmission station(s) or Transmission substation(s) to, or remove a Transmission station(s) or Transmission substation(s) from, its identification under Requirement R1, the Transmission Owner shall either, within 60 calendar days of completion of the verification, for each recommended addition or removal of a Transmission station or Transmission substation:• Modify its identification under Requirement R1 consistent with the recommendation; or• Document the technical basis for not modifying the identification in accordance with the recommendation. |  | TO | [22 empty] | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.Voltage Value of a Line Weight Value per Lineless than 200 kV (not applicable) (not applicable)200 kV to 299 kV 700300 kV to 499 kV 1300500 kV and above 04.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6392 | Intelligence or threat warnings received from sources such as law enforcement, the Electric Reliability Organization (ERO), the Electricity Sector Information Sharing and Analysis Center (ES-ISAC), U.S. federal and/or Canadian governmental agencies, or their successors. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.Voltage Value of a Line Weight Value per Lineless than 200 kV (not applicable) (not applicable)200 kV to 299 kV 700300 kV to 499 kV 1300500 kV and above 04.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6396 | A timeline for executing the physical security enhancements and modifications specified in the physical security plan. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.Voltage Value of a Line Weight Value per Lineless than 200 kV (not applicable) (not applicable)200 kV to 299 kV 700300 kV to 499 kV 1300500 kV and above 04.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6403 | If the unaffiliated third party reviewer recommends changes to the evaluation performed under Requirement R4 or security plan(s) developed under Requirement R5, the Transmission Owner or Transmission Operator shall, within 60 calendar days of the completion of the unaffiliated third party review, for each recommendation:• Modify its evaluation or security plan(s) consistent with the recommendation; or• Document the reason(s) for not modifying the evaluation or security plan(s) consistent with the recommendation. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.Voltage Value of a Line Weight Value per Lineless than 200 kV (not applicable) (not applicable)200 kV to 299 kV 700300 kV to 499 kV 1300500 kV and above 04.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6422 | Request that the congestion management actions identified in Requirement R2, Part 2.1 be implemented by: 1.) Each Reliability Coordinator associated with a Sink Balancing Authority for which Interchange Transactions are to be curtailed, 2.) Each Reliability Coordinator associated with a Balancing Authority in the Eastern Interconnection for which Network Integration Transmission Service or Native Load is to be curtailed, and 3.) Each Reliability Coordinator associated with a Balancing Authority in the Eastern Interconnection for which its Market Flow is to be curtailed. |  | RC | [11 empty] | RC | [10 empty] | 2011-04-21 |  | 2016-03-31 |  |  |  | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US | MRO-US | NPCC-US | RF-US | SERC-US
3. | 6426 | Model structure and data including, but not limited to reactance, time constants, saturation factors, total rotational inertia, or equivalent data for the generator, |  | GO | [22 empty] | 2018-07-01 |  |  |  | 4.2. Facilities:For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following:4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).4.2.2 Generation in the Western Interconnection with the following characteristics:4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.3 Generation in the ERCOT Interconnection with the following characteristics:4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.4 For all Interconnections:• A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6432 | For an otherwise stable simulation, a disturbance simulation results in the excitation control and plant volt/var control function model exhibiting positive damping. |  | TP | [19 empty] | TP |  |  | 2014-05-26 |  |  |  | 4.2. Facilities:For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following:4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).4.2.2 Generation in the Western Interconnection with the following characteristics:4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.3 Generation in the ERCOT Interconnection with the following characteristics:4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.4 For all Interconnections:• A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. |  | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6436 | A description of the turbine (e.g. for hydro turbine - Kaplan, Francis, or Pelton; for steam turbine - boiler type, normal fuel type, and turbine type; for gas turbine - the type and manufacturer; for variable energy plant - type and manufacturer), |  | GO | [22 empty] | 2014-07-01 |  |  |  | 4.2. FacilitiesFor the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred to as an “applicable unit” that meet the following:4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics:4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).4.2.2 Generation in the Western Interconnection with the following characteristics:4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.3 Generation in the ERCOT Interconnection with the following characteristics:4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6441 | For an otherwise stable simulation, a disturbance simulation results in the turbine/governor and load control or active power/frequency control model exhibiting positive damping. |  | TP | [19 empty] | TP |  |  | 2014-05-26 |  |  |  | 4.2. FacilitiesFor the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred to as an “applicable unit” that meet the following:4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics:4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).4.2.2 Generation in the Western Interconnection with the following characteristics:4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.3 Generation in the ERCOT Interconnection with the following characteristics:4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). |  | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6445 | Emergency preparedness and operations |  | RC | [11 empty] | RC | [10 empty] | 2012-10-01 |  | 2019-06-30 |  |  |  | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 645 | All personnel directly involved in the design and implementation of the TVMP shall hold appropriate qualifications and training, as defined by the Transmission Owner, to perform their duties. |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  | FAC-003-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6454 | System operations |  | TOP | [18 empty] | TOP |  |  |  | 2012-10-01 |  | 2019-06-30 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6461 | System operations |  | BA | BA | [21 empty] | 2012-10-01 |  | 2019-06-30 |  |  |  | 31300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6467 | For digital and electronic Governors, once frequency deviation has exceeded the Governor deadband from 60.000 Hz, the Governor setting shall follow the slope derived from the formula below.(see standard for formula) where MWGCS is the maximum megawatt control range of the Governor control system. For mechanical Governors, droop will be proportional from the deadband by design. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [16 empty] | 2014-01-16 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01.4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. |  | 63000000 | TXRE-US |  |  |  |  | TXRE-US
3. | 6470 | A generating unit/generating facility’s initial Primary Frequency Response performance during an FME may be excluded from the rolling average calculation due to a legitimate operating condition that prevented normal Primary Frequency Response performance. Examples of legitimate operating conditions that may support exclusion of FMEs include: Operation at or near auxiliary equipment operating limits (such as boilerfeed pumps, condensate pumps, pulverizers, and forced draft fans); Data telemetry failure. The Compliance Enforcement Authority may request raw data from the GO as a substitute. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [16 empty] | 2014-04-01 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01.4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. |  | 93000000 | TXRE-US |  |  |  |  | TXRE-US
3. | 6471 | A generating unit/generating facility’s initial Primary Frequency Response performance during an FME may be excluded from the rolling average calculation due to a legitimate operating condition that prevented normal Primary Frequency Response performance. Examples of legitimate operating conditions that may support exclusion of FMEs include: Operation at or near auxiliary equipment operating limits (such as boilerfeed pumps, condensate pumps, pulverizers, and forced draft fans); Data telemetry failure. The Compliance Enforcement Authority may request raw data from the GO as a substitute. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [16 empty] | 2014-01-16 |  | 2020-06-30 |  |  |  | 93000000 | TXRE-US |  |  |  |  | TXRE-US
3. | 6474 | A generating unit/generating facility’s sustained Primary Frequency Response performance during an FME may be excluded from the rolling average calculation due to a legitimate operating condition that preventednormal Primary Frequency Response performance. Examples of legitimate operating conditions that may support exclusion of FMEs include: Operation at or near auxiliary equipment operating limits (such as boilerfeed pumps, condensate pumps, pulverizers, and forced draft fans); Data telemetry failure. The Compliance Enforcement Authority may request raw data from the GO as a substitute. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [16 empty] | 2014-01-16 |  | 2020-06-30 |  | Exemptions: 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL- 001-TRE-01.4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-01. 4.2.3 Any generators that are not required by the BA to provide primary frequency response are exempt from this standard. |  | 103000000 | TXRE-US |  |  |  |  | TXRE-US
3. | 6477 | Based on real-time hourly load and generating energy values averaged over each Clock Hour (excluding Qualifying Facilities covered in 18 C.F.R.§ 292.101, as addressed in FERC Order 464). |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | 1.3 Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates compliance with Requirement R1, Part 1.3. Evidence of compliance with Requirement R1, Part 1.3 may include, but is not limited to, documentation that Contingency Reserve amounts are based upon load and generating data averaged over each Clock Hour and excludes Qualifying Facilities covered in 18 C.F.R.§ 292.101, as addressed in FERC Order 464. | 2014-01-28 |  | 2017-01-23 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity.4.2.1. The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group.4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | 13000000 | WECC-US | [5 empty] | WECC-US
3. | 6487 | Automatic Time Error Correction term (IATEC). |  | BA | BA | [21 empty] | 2013-10-16 |  | 2018-09-30 |  |  |  | 43000000 | WECC-US | [5 empty] | WECC-US
3. | 6492 | Voice communications. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2013-07-01 |  | 2019-03-31 |  |  |  | 12300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6495 | An Operating Process for keeping the backup functionality consistent with the primary control center. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6501 | Identification of the roles for personnel involved during the initiation and implementation of the Operating Plan for backup functionality. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2013-07-01 |  | 2019-03-31 |  |  |  | 16300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6509 | The conditions for terminating the Operating Procedure or Operating Process. |  | TOP | [18 empty] | TOP |  |  |  | 2015-04-01 | [5 empty] | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 652 | The outage information provided by the Transmission Owner to the RRO, or the RRO’s designee, shall include at a minimum: the name of the circuit(s) outaged, the date, time and duration of the outage; a description of the cause of the outage; other pertinent comments; and any countermeasures taken by the Transmission Owner. |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  | FAC-003-1 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6527 | Inform its Planning Coordinator of the need to exceed the stated tolerances of UFLS Attachment C, Table 2 or Table 3, and in the case of Attachment C, Table 2 only, the need to deviate from providing two stages of UFLS, if applicable, and |  | DP, DP-UFLS, TO |  | DP | [20 empty] | 2020-03-31 |  | 2020-03-31 |  |  |  | 53000000 | NPCC-US |  | NPCC-US
3. | 6536 | Transmit the initial frequency trip setting and any changes to the setting and the technical basis for the settings to the Planning Coordinator. |  | DP-UFLS, GO |  | DP | [20 empty] | 2013-04-29 |  | 2020-03-31 |  |  |  | 193000000 | NPCC-US |  | NPCC-US
3. | 6539 | A list of all generating units that may be tripped for underfrequency conditions above the appropriate generator underfrequency trip protection settings threshold curve in Figure 1, including the frequency trip threshold and time delay for each protection system. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2013-04-29 |  | 2020-03-31 |  |  |  | 203000000 | NPCC-US |  | NPCC-US
3. | 6543 | Have compensatory load shedding, as provided by a Distribution Provider or Transmission Owner that is adequate to compensate for the loss of their generator due to early tripping. |  | DP-UFLS, GO |  | DP | [20 empty] | 2013-04-29 |  | 2020-03-31 |  |  |  | 163000000 | NPCC-US |  | NPCC-US
3. | 6548 | A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6551 | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6554 | Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. |  | PCPA | [9 empty] | PA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  |  | 33300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6557 | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 656 | Category 3 — Fall-ins: Outages caused by vegetation falling into lines from outside the ROW. |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  |  | 34300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6564 | Format and schedule of UFLS data submittal |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 143000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6569 | A statement that the assumptions and criteria used to perform the assessment are consistent with the Planning Coordinator’s planning practices. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-01-23 |  | 2020-12-14 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6579 | Facilities consisting of one or more units connected to the BES at a common bus with total generation above 50 MVA gross nameplate rating. |  | PCPA | [9 empty] | PA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  |  | 333000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6587 | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 330000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6590 | Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. |  | PCPA | [9 empty] | PA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  |  | 333000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6593 | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 430000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6603 | The highest frequency set point for relays used to arrest frequency decline shall be no lower than 59.3 Hz and not higher than 59.5 Hz. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2013-02-25 |  | 2017-12-31 |  |  |  | 23000000 | SERC-US |  |  |  | SERC-US
3. | 6611 | The amount of total UFLS load of all steps combined shall be within -1.0 and +5.0 of the percentage specified by the Planning Coordinator for the total UFLS load in the UFLS scheme. |  | DP, DP-UFLS, TO |  | DP | [20 empty] | 2015-10-01 |  | 2017-12-31 |  |  |  | 43000000 | SERC-US |  |  |  | SERC-US
3. | 6616 | Amount of previous year actual or estimated load associated with each set point, both in percent and in MW. The percentage and the Load demand (MW) shall be based on the time coincident with the previous year actual Peak Demand. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2013-02-25 |  | 2017-12-31 |  |  |  | 73000000 | SERC-US |  |  |  | SERC-US
3. | 6621 | Maximum generator net MW that could be tripped automatically due to an underfrequency or overfrequency condition. |  | DP-UFLS, GO |  | DP | [20 empty] | 2013-02-25 |  | 2017-12-31 |  |  |  | 83000000 | SERC-US |  |  |  | SERC-US
3. | 6625 | New planned Facilities and changes to existing Facilities |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-01-01 | [5 empty] | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6632 | P1 events in Table 1, with known outages modeled as in Requirement R1, Part 1.1.2, under those System peak or Off-Peak conditions when known outages are scheduled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6637 | The short circuit analysis portion of the Planning Assessment shall be conducted annually addressing the Near-Term Transmission Planning Horizon and can be supported by current or past studies as qualified in Requirement R2, Part 2.6. The analysis shall be used to determine whether circuit breakers have interrupting capability for Faults that they will be expected to interrupt using the System short circuit model with any planned generation and Transmission Facilities in service which could impact the study area. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6641 | Generator Operators that do not monitor the voltage at the location specified in their voltage schedule shall have a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2014-08-01 |  | 2015-05-28 |  |  |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6645 | Impedance data. |  | GO | [22 empty] | 2014-10-01 |  | 2015-05-28 |  |  |  | 51300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6650 | For each of the studies described in Requirement R2, Parts 2.4.1 and 2.4.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in performance:• Load level, Load forecast, or dynamic Load model assumptions. • Expected transfers. • Expected in service dates of new or modified Transmission Facilities. • Reactive resource capability. • Generation additions, retirements, or other dispatch scenarios. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 24300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6658 | If situations arise that are beyond the control of the Transmission Planner or Planning Coordinator that prevent the implementation of a Corrective Action Plan in the required timeframe, then the Transmission Planner or Planning Coordinator is permitted to utilize Non-Consequential Load Loss and curtailment of Firm Transmission Service to correct the situation that would normally not be permitted in Table 1, provided that the Transmission Planner or Planning Coordinator documents that they are taking actions to resolve the situation. The Transmission Planner or Planning Coordinator shall document the situation causing the problem, alternatives evaluated, and the use of Non-Consequential Load Loss or curtailment of Firm Transmission Service. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 27300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6665 | Contingency analyses for Requirement R3, Parts 3.1 & 3.2 shall: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6676 | For planning events P1 through P7: Power oscillations shall exhibit acceptable damping as established by the Planning Coordinator and Transmission Planner. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 41300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6678 | Contingency analyses for Requirement R4, Parts 4.1 and 4.2 shall: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6682 | Tripping of Transmission lines and transformers where transient swings cause Protection System operation based on generic or actual relay models. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 43130000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6693 | System demand. |  | PCPA | [9 empty] | PA | [12 empty] | 2013-04-01 |  | 2020-12-14 |  |  |  | 14300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6702 | The Purchasing-Selling Entity receives notification from a Reliability Coordinator or Transmission Operator to update the Confirmed Interchange. |  | PSE | [10 empty] | PSE | [11 empty] | 2014-11-26 |  | 2020-12-14 |  |  |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6709 | Each Reliability Coordinator associated with each Balancing Authority included in the Arranged Interchange, |  | BA | BA | [21 empty] | 2014-06-30 |  | 2021-03-31 |  |  |  | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6720 | Each Distribution Provider within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  |  | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6726 | Each adjacent Transmission Operator synchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  |  | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6730 | Each Distribution Provider within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6735 | Each Adjacent Balancing Authority. |  | BA | BA | [21 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6744 | If the unaffiliated verifying entity recommends that the Transmission Owner add a Transmission station(s) or Transmission substation(s) to, or remove a Transmission station(s) or Transmission substation(s) from, its identification under Requirement R1, the Transmission Owner shall either, within 60 calendar days of completion of the verification, for each recommended addition or removal of a Transmission station or Transmission substation:• Modify its identification under Requirement R1 consistent with the recommendation; or• Document the technical basis for not modifying the identification in accordance with the recommendation. |  | TO | [22 empty] | 2015-10-01 |  | 2015-10-01 |  |  |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6749 | Intelligence or threat warnings received from sources such as law enforcement, the Electric Reliability Organization (ERO), the Electricity Sector Information Sharing and Analysis Center (ES-ISAC), U.S. federal and/or Canadian governmental agencies, or their successors. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  |  | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6752 | A timeline for executing the physical security enhancements and modifications specified in the physical security plan. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  |  | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6756 | If the unaffiliated third party reviewer recommends changes to the evaluation performed under Requirement R4 or security plan(s) developed under Requirement R5, the Transmission Owner or Transmission Operator shall, within 60 calendar days of the completion of the unaffiliated third party review, for each recommendation:• Modify its evaluation or security plan(s) consistent with the recommendation; or• Document the reason(s) for not modifying the evaluation or security plan(s) consistent with the recommendation. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  |  | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6760 | end-user Facilities. |  | TO | [22 empty] | 2014-11-06 |  | 2018-12-31 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6767 | Steady-state, short-circuit, and dynamics studies, as necessary, to evaluate system performance under both normal and contingency conditions; and |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2014-11-06 |  | 2021-03-31 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6777 | A request to provide any or all of the following actual data, as necessary: |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2015-04-27 |  | 2016-09-30 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6781 | Monthly and annual Net Energy for Load in gigawatthours for the prior calendar year. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6786 | Peak hour forecast Total Internal Demands (summer and winter) in megawatts for ten calendar years into the future. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 14300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6792 | How Demand Side Management is addressed in the forecasts of its Peak Demand and annual Net Energy for Load. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 15300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6800 | Case types or scenarios to be modeled; and |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-07-01 |  |  |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. |  | 12300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6802 | Specifications for distribution or posting of the data requirements and reporting procedures so that they are available to those entities responsible for providing the data. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-07-01 |  |  |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6807 | Guidelines the Planning Coordinator will use to determine unacceptable differences in performance under Part 1.1 or 1.2; and |  | PCPA | [9 empty] | PA | [12 empty] | 2014-05-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6811 | Control of voltage, including the coordination of reactive resources. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-26 | [5 empty] | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6816 | Distribute to all Reliability Coordinators that are required to take the indicated action(s) within 30 days of an update. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-26 | [5 empty] | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6821 | Define the process to evaluate the impact of Transmission and generation outages within its Wide Area. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-26 | [5 empty] | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6825 | A periodicity for providing data. |  | TOP | [18 empty] | TOP | [5 empty] | 2016-01-26 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6829 | A periodicity for providing data. |  | BA | BA | [23 empty] | 2016-01-26 |  |  |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6833 | A periodicity for providing data. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-26 |  | 2021-03-31 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6837 | A periodicity for providing data. |  | BA | BA | [21 empty] | 2016-01-26 |  | 2021-03-31 |  |  |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6841 | A mutually agreeable security protocol |  | BA, DP, GO, GOP, LSE, TO, TOP | BA | DP |  |  | GO | GOP |  | LSE | [9 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2021-03-31 |  |  |  | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6844 | Generator Operators that do not monitor the voltage at the location specified in their voltage schedule shall have a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-05-29 |  | 2017-09-25 |  |  |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6848 | Impedance data. |  | GO | [22 empty] | 2015-05-29 |  | 2017-09-25 |  |  |  | 51300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6853 | Transmission system reconfiguration; |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 12200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6854 | Transmission system reconfiguration; |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 12300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6862 | Managing generating resources in its Balancing Authority Area to address: |  | BA | BA | [21 empty] | 2017-04-01 | [5 empty] | 22300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6865 | fuel switching capabilities; and |  | BA | BA | [21 empty] | 2017-04-01 | [5 empty] | 22330000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6876 | Notify each Balancing Authority and Transmission Operator of the results of its review, specifying any time frame for resubmittal of its Operating Plan(s) if revisions are identified. |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 31300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6897 | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2014-11-04 |  | 2021-03-31 |  |  |  | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 690 | Consideration of the following: |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2012-12-31 |  |  | FAC-008-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6902 | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 92300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6903 | Operations and maintenance coordination |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2014-11-04 |  | 2021-03-31 |  |  |  | 93000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6906 | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 93300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6915 | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 94300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6919 | One or more processes for the backup and storage of information required to recover BES Cyber System functionality. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.3. An example of evidence may include, but is not limited to, documentation of specific processes for the backup and storage of information required to recover BES Cyber System functionality. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6924 | Test each of the recovery plans referenced in Requirement R1 at least once every 36 calendar months through an operational exercise of the recovery plans in an environment representative of the production environment. An actual recovery response may substitute for an operational exercise. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.3. Examples of evidence may include, but are not limited to, dated documentation of:• An operational exercise at least once every 36 calendar months between exercises, that demonstrates recovery in a representative environment; or• An actual recovery response that occurred within the 36 calendar month timeframe that exercised the recovery plans. | 2018-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6929 | Notify each person or group with a defined role in the recovery plan of the updates to the recovery plan based on any documented lessons learned. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 31300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 693 | Ambient conditions. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2012-12-31 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6934 | A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6937 | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: • Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES • Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES• Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6940 | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6951 | Format and schedule of UFLS data submittal |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 143000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6962 | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall deliver training to its System Operators according to its training program. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | M1.3 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection System Operator training records showing the names of the people trained, the title of the training delivered, and the dates of delivery to show that it delivered the training, as specified in Requirement R1 part 1.3. | 2014-06-19 | [5 empty] | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 6967 | Each Transmission Owner shall deliver training to its personnel identified in Applicability Section 4.1.4.1 of this standard according to its training program. |  | TO | [21 empty] | M2.3 Each Transmission Owner shall have available for inspection training records showing the names of the people trained, the title of the training delivered, and the dates of delivery to show that it delivered the training, as specified in Requirement R2 part 2.3. | 2014-06-19 | [5 empty] | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 703 | Include a description of how to identify the subset of SOLs that qualify as IROLs. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-010-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7045 | Electronic access controls for Low Impact External Routable Connectivity (LERC) and Dial-up Connectivity; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7049 | A periodicity for providing data. |  | RC | [11 empty] | RC | [10 empty] | 2017-01-01 |  | 2021-03-31 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7053 | A mutually agreeable security protocol |  | BA, DP, GO, GOP, LSE, RC, TO, TOP | BA | DP |  |  | GO | GOP |  | LSE |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2021-03-31 |  |  |  | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7056 | Planned or unplanned outage information. |  | RC | [11 empty] | RC | [12 empty] | 2016-01-26 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7063 | Distribute to all Reliability Coordinators that are required to take the indicated action(s) within 30 days of an update. |  | RC | [11 empty] | RC | [9 empty] | 2.3 Distributed within 30 days of an update to all Reliability Coordinators that are required to take the indicated action(s).This evidence may include, but is not limited to dated documentation with confirmation of receipt, dated notice of acceptance or agreement to take specified actions, or dated electronic communications with confirmation of receipt and acceptance or agreement to take specified actions. (R2) |  |  | 2016-01-26 |  |  |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7067 | Transient stability limits; |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7073 | Expected transmission uses; |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 12300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7078 | Each methodology shall describe the process for including any reliability-related constraints that are requested to be included by another Transmission Operator, provided that (1) the request references this specific requirement, and (2) the requesting Transmission Operator includes those constraints in its TFC or TTC determination. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7081 | A different method for determining whether requested constraints need to be included in the TFC or TTC determination may be used if agreed to by the Transmission Operators. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7085 | Expected transmission uses; |  | TSP | [20 empty] | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 709 | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-07-01 |  | 2009-04-28 |  |  |  | 22300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7095 | If not publicly posted on OASIS or its company website, the Transmission Service Provider’s effective: |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 710 | Starting with all Facilities in service, the system’s response to a single Contingency, may include any of the following: |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-010-1 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7100 | If making available any requested data under parts 6.1 or 6.2 of this requirement is contrary to the Transmission Operator’s or Transmission Service Provider’s confidentiality, regulatory, or security requirements, the Transmission Operator or Transmission Service Provider shall not be required to make available that data; provided that, within 45 calendar days of the written request, it responds to the requesting registered entity specifying the data that is not being provided, on what basis and whether there are any options for resolving any of the confidentiality, regulatory or security concerns. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7107 | Demand patterns |  | BA | BA | [21 empty] | 2016-01-26 | [5 empty] | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7115 | The GMD Vulnerability Assessment shall be provided within 90 calendar days of completion to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners, and to any functional entity that submits a written request and has a reliability-related need. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities:4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 713 | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-07-01 |  | 2009-04-28 |  |  |  | 23300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7131 | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and |  | GO, TO |  |  |  |  | GO | [17 empty] | 2021-01-01 |  | 2019-06-30 |  | 4.2. Facilities:4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7135 | Be provided within 90 calendar days of completion to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), functional entities referenced in the Corrective Action Plan, and any functional entity that submits a written request and has a reliability-related need. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2022-01-01 |  | 2019-06-30 |  | 4.2. Facilities:4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 73000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7143 | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-05-13 |  | 2016-06-30 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7147 | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-07-01 |  | 2016-06-30 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7151 | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-05-29 |  | 2016-06-30 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7155 | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2016-06-30 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7165 | Re-evaluate all BES buses at least once every five calendar years in accordance with Part 1.1 and notify other owners, if any, in accordance with Part 1.2, and implement the re-evaluated list of BES buses as per the Implementation Plan. |  | TO | [22 empty] | 2015-11-24 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7172 | Trigger settings for at least the following: |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7180 | Each terminal of a high voltage direct current (HVDC) circuit with a nameplate rating greater than or equal to 300 MVA, on the alternating current (AC) portion of the converter. |  | PCPA, RC | [9 empty] | PA |  | RC | [10 empty] | 2016-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 51300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7186 | Notify all owners of identified BES Elements, within 90-calendar days of completion of Part 5.1, that their respective BES Elements require DDR data when requested. |  | PCPA, RC | [9 empty] | PA |  | RC | [10 empty] | 2015-11-24 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7190 | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. |  | TO | [22 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7194 | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. |  | GO | [22 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 73000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 720 | Level of detail of system models used to determine SOLs. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-010-1 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7204 | SER data will be provided in ASCII Comma Separated Value (CSV) format following Attachment 2. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7211 | Electronic access controls; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7222 | Any custom software installed; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7226 | For a change that deviates from the existing baseline configuration, update the baseline configuration as necessary within 30 calendar days of completing the change. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.3. An example of evidence may include, but is not limited to, updated baseline documentation with a date that is within 30 calendar days of the date of the completion of the change. | 2016-03-31 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7230 | Document the results of the verification. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 14300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7239 | Prior to adding a new applicable Cyber Asset to a production environment, perform an active vulnerability assessment of the new Cyber Asset, except for CIP Exceptional Circumstances and like replacements of the same type of Cyber Asset with a baseline configuration that models an existing baseline configuration of the previous or other existing Cyber Asset. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.3. An example of evidence may include, but is not limited to, a document listing the date of the assessment (performed prior to the commissioning of the new Cyber Asset) and the output of any tools used to perform the assessment. | 2016-07-01 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7245 | Require completion of the training specified in Part 2.1 at least once every 15 calendar months. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M.2.3. Examples of evidence may include, but are not limited to, dated individual training records. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7261 | Access to designated storage locations, whether physical or electronic, for BES Cyber System Information. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 41300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7263 | For electronic access, verify at least once every 15 calendar months that all user accounts, user account groups, or user role categories, and their specific, associated privileges are correct and are those that the Responsible Entity determines are necessary. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.3. An example of evidence may include, but is not limited to, documentation of the review that includes all of the following: 1. A dated listing of all accounts/account groups or roles within the system; 2. A summary description of privileges associated with each group or role;3. Accounts assigned to the group or role; and4. Dated evidence showing verification of the privileges for the group are authorized and appropriate to the work function performed by people assigned to each account. | 2017-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7267 | For termination actions, revoke the individual’s access to the designated storage locations for BES Cyber System Information, whether physical or electronic (unless already revoked according to Requirement R5.1), by the end of the next calendar day following the effective date of the termination action. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.3. An example of evidence may include, but is not limited to, workflow or sign-off form verifying access removal to designated physical areas or cyber systems containing BES Cyber System Information associated with the terminations and dated within the next calendar day of the termination action. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 727 | Each Transmission Planner that works in the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-010-1 R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7290 | For applicable patches identified in Part 2.2, within 35 calendar days of the evaluation completion, take one of the following actions:• Apply the applicable patches; or• Create a dated mitigation plan; or• Revise an existing mitigation plan. Mitigation plans shall include the Responsible Entity’s planned actions to mitigate the vulnerabilities addressed by each security patch and a timeframe to complete these mitigations. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.3. Examples of evidence may include, but are not limited to: • Records of the installation of the patch (e.g., exports from automated patch management tools that provide installation date, verification of BES Cyber System Component software revision, or registry exports that show software has been installed); or• A dated plan showing when and how the vulnerability will be addressed, to include documentation of the actions to be taken by the Responsible Entity to mitigate the vulnerabilities addressed by the security patch and a timeframe for the completion of these mitigations. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7294 | For those methods identified in Part 3.1 that use signatures or patterns, have a process for the update of the signatures or patterns. The process must address testing and installing the signatures or patterns. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.3. An example of evidence may include, but is not limited to, documentation showing the process used for the update of signatures or patterns. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7304 | Detected malicious code. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.1. Examples of evidence may include, but are not limited to, a paper or system generated listing of event types for which the BES Cyber System is capable of detecting and, for generated events, is configured to log. This listing must include the required types of events. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 41300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7308 | Where technically feasible, retain applicable event logs identified in Part 4.1 for at least the last 90 consecutive calendar days except under CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.3. Examples of evidence may include, but are not limited to, documentation of the event log retention process and paper or system generated reports showing log retention configuration set at 90 days or greater. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7312 | Identify individuals who have authorized access to shared accounts. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.3. An example of evidence may include, but is not limited to, listing of shared accounts and the individuals who have authorized access to each shared account. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 732 | Include a description of how to identify the subset of SOLs that qualify as IROLs. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | FAC-010-2 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7341 | Where technically feasible, utilize two or more different physical access controls (this does not require two completely independent physical access control systems) to collectively allow unescorted physical access into Physical Security Perimeters to only those individuals who have authorized unescorted physical access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.3. An example of evidence may include, but is not limited to, language in the physical security plan that describes the Physical Security Perimeters and how unescorted physical access is controlled by two or more different methods and proof that unescorted physical access is restricted to only authorized individuals, such as a list of authorized individuals accompanied by access logs. | 2016-07-01 | [5 empty] | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7351 | Retain visitor logs for at least ninety calendar days. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.3. An example of evidence may include, but is not limited to, documentation showing logs have been retained for at least ninety calendar days. | 2016-07-01 | [5 empty] | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7355 | Polarizing currents and voltages, if used. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 53000000 | NPCC-US |  | NPCC-US
3. | 7360 | Each Fault recorder shall be set to trigger for at least the following: |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 63000000 | NPCC-US |  | NPCC-US
3. | 7363 | Monitored phase undervoltage set at 0.85 pu or greater. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 63300000 | NPCC-US |  | NPCC-US
3. | 738 | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 22300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 739 | Starting with all Facilities in service, the system’s response to a single Contingency, may include any of the following: |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | FAC-010-2 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7392 | Teleprotection keying and receive |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 12300000 | NPCC-US |  | NPCC-US
3. | 7403 | Major voltage sensitive areas. |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 72300000 | NPCC-US |  | NPCC-US
3. | 7410 | Each DDR shall be set to trigger for at least one of the following (based on manufacturers’ equipment capabilities): |  | RC | [11 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 93000000 | NPCC-US |  | NPCC-US
3. | 7413 | Delta Frequency (recommend 20 mHz change). |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 93300000 | NPCC-US |  | NPCC-US
3. | 7417 | As a minimum, one phase current per monitored Element and two phase-to-neutral voltages of different Elements. One of the monitored voltages shall be of the same phase as the monitored current. |  | RC | [11 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 103000000 | NPCC-US |  | NPCC-US
3. | 7422 | Monthly verification of communication channels used for accessing records remotely (if the entity relies on remote access and the channel is not monitored to a control center staffed around the clock, 24 hours a day, 7 days a week (24/7)). |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 143000000 | NPCC-US |  | NPCC-US
3. | 7431 | Fault Recorder and DDR Files shall contain all monitored channels. SOE records shall contain station name, date, time resolved to milliseconds, SOE point name, status. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 163000000 | NPCC-US |  | NPCC-US
3. | 7434 | Installation location. |  | GOP, RC, TOP | [5 empty] | GOP | [5 empty] | RC | [6 empty] | TOP |  |  |  | 2011-10-20 |  | 2016-07-01 |  |  |  | 173000000 | NPCC-US |  | NPCC-US
3. | 7443 | The Transmission Operator shall provide the criteria used to develop voltage schedules Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. |  | TOP | [18 empty] | TOP |  |  |  | 2014-08-01 |  | 2015-11-12 |  |  |  | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7474 | Each Distribution Provider within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  |  | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7480 | Physical security of BES Cyber Systems (CIP-006); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 749 | Level of detail of system models used to determine SOLs. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | FAC-010-2 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7491 | Each adjacent Transmission Operator synchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  |  | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7495 | Each Distribution Provider within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7500 | Each Adjacent Balancing Authority. |  | BA | BA | [21 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7514 | The Transmission Operator shall provide the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-25 |  |  |  | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7518 | Criteria or process to evaluate criminal history records checks for authorizing access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.3. An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process to evaluate criminal history records checks. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7529 | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-12-04 |  | 2016-06-30 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7533 | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-07-01 |  | 2016-06-30 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7538 | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-12-04 |  | 2017-04-01 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7543 | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-07-01 |  | 2017-04-01 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7552 | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2015-11-19 |  | 2021-03-31 |  | 4.2. Facilities:4.2.1 Protection Systems for BES Elements, with the following exclusions:4.2.1.1 Non-protective functions that are embedded within a Protection System.4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS).4.2.1.4 Remedial Action Schemes (RAS).4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7558 | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-04-02 |  | 2021-03-31 |  | 4.2. Facilities:4.2.1 Protection Systems for BES Elements, with the following exclusions:4.2.1.1 Non-protective functions that are embedded within a Protection System.4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS).4.2.1.4 Remedial Action Schemes (RAS).4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 756 | Each Transmission Planner that works in the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | FAC-010-2 R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7566 | For Protection System settings applied on BES Elements that electrically join Facilities owned by separate functional entities (Transmission Owners, Generator Owners, and Distribution Providers), provisions to: |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.1.3. Distribution Provider (that owns Protection Systems identified in the Facilities section 4.2 below)4.2. Facilities: Protection Systems installed to detect and isolate Faults on BES Elements. |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7569 | Verify that identified coordination issue(s) associated with the proposed Protection System settings for the associated BES Elements are addressed prior to implementation. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.1.3. Distribution Provider (that owns Protection Systems identified in the Facilities section 4.2 below)4.2. Facilities: Protection Systems installed to detect and isolate Faults on BES Elements. |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7583 | A request to provide any or all of the following actual data, as necessary: |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-02-18 |  | 2021-03-31 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7587 | Monthly and annual Net Energy for Load in gigawatthours for the prior calendar year. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7592 | Peak hour forecast Total Internal Demands (summer and winter) in megawatts for ten calendar years into the future. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” |  | 14300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7598 | How Demand Side Management is addressed in the forecasts of its Peak Demand and annual Net Energy for Load. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” |  | 15300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 761 | Include a description of how to identify the subset of SOLs that qualify as IROLs. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-011-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7610 | deploy Contingency Reserve, within system constraints, to respond to all Reportable Balancing Contingency Events, however, it is not subject to compliance with Requirement R1 part 1.1 if: |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2017-04-03 |  | 2017-12-31 |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7628 | end-user Facilities |  | TO | [22 empty] | 2019-01-01 | [5 empty] | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7631 | Procedures for confirming with those responsible for the reliability of affected systems of new or materially modified transmission Facilities are within a Balancing Authority Area’s metered boundaries. |  | TO | [22 empty] | 2019-01-01 | [5 empty] | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7634 | Procedures for confirming with those responsible for the reliability of affected systems of new or materially modified generation Facilities are within a Balancing Authority Area’s metered boundaries. |  | GO | [22 empty] | 2019-01-01 | [5 empty] | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7641 | An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:4.1.1. Applicable Transmission Owners4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.4.1.2. Applicable Generator Owners4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.2.1. Each overhead transmission line operated at 200kV or higher.4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:4.3.1.1. Operated at 200kV or higher; or4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7645 | An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation-related Sustained Outage, |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:4.1.1. Applicable Transmission Owners4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.4.1.2. Applicable Generator Owners4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.2.1. Each overhead transmission line operated at 200kV or higher.4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:4.3.1.1. Operated at 200kV or higher; or4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7650 | Rescheduling work between growing seasons |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:4.1.1. Applicable Transmission Owners4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.4.1.2. Applicable Generator Owners4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.2.1. Each overhead transmission line operated at 200kV or higher.4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:4.3.1.1. Operated at 200kV or higher; or4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 72000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7667 | Uncontrolled separation shall not occur. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7669 | For an ATC Path whose capacity is limited by contract, set TTC on the ATC Path at the lesser of the maximum allowable contract capacity or the reliability limit as determined by R2.1. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 767 | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. |  | RC | [11 empty] | RC | [10 empty] | 2008-10-01 |  | 2009-04-28 |  |  |  | 22300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 768 | In determining the system’s response to a single Contingency, the following shall be acceptable: |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-011-1 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7689 | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: |  | PCPA | [9 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 330000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7692 | Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. |  | PCPA | [9 empty] | PA | [12 empty] | 2015-10-01 |  | 2017-09-30 |  |  |  | 333000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7696 | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 430000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 771 | System reconfiguration through manual or automatic control or protection actions. |  | RC | [11 empty] | RC | [10 empty] | 2008-10-01 |  | 2009-04-28 |  |  |  | 23300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7716 | AVR exhibits instability due to abnormal system configuration. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2015-03-03 |  | 2018-09-05 |  |  |  | 13000000 | WECC-US | [5 empty] | WECC-US
3. | 7727 | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. |  | TOP | [18 empty] | TOP |  |  |  | 2016-09-22 |  | 2018-03-31 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7731 | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects its analysis functions. |  | BA | BA | [21 empty] | 2016-09-22 |  | 2018-03-31 |  |  |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7735 | Actions to address analysis quality issues affecting its Real-time Assessments. |  | TOP | [18 empty] | TOP |  |  |  | 2016-09-22 |  | 2018-03-31 |  |  |  | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7741 | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. |  | RC | [11 empty] | RC | [10 empty] | 2016-09-22 |  | 2018-03-31 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7744 | Actions to address analysis quality issues affecting its Real-time Assessments. |  | RC | [11 empty] | RC | [10 empty] | 2016-09-22 |  | 2018-03-31 |  |  |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7753 | For limited impact RAS, the inadvertent operation of the RAS or the failure of the RAS to operate does not cause or contribute to BES Cascading, uncontrolled separation, angular instability, voltage instability, voltage collapse, or unacceptably damped oscillations. |  | PCPA | [9 empty] | PA | [12 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 41300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7757 | Applicable Facility Ratings shall not be exceeded. |  | PCPA | [9 empty] | PA | [12 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 41430000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 776 | A process for determining which of the stability limits associated with the list of multiple contingencies (provided by the Planning Authority in accordance with FAC-014 Requirement 6) are applicable for use in the operating horizon given the actual or expected system conditions. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-011-1 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7766 | The RAS was effective in mitigating BES performance issues it was designed to address. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 51300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7773 | Notify each reviewing Reliability Coordinator if CAP actions or timetables change and when the CAP is completed. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-11-27 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 73000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7778 | Require its operating personnel that receive an oral two-party, person-to-person Operating Instruction to take one of the following actions: • Repeat, not necessarily verbatim, the Operating Instruction and receive confirmation from the issuer that the response was correct. • Request that the issuer reissue the Operating Instruction. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2015-06-22 | [5 empty] | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7794 | Each Distribution Provider within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2016-10-28 | [5 empty] | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7801 | Each adjacent Transmission Operator synchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2016-10-28 | [5 empty] | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7806 | Each Distribution Provider within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2016-10-28 | [5 empty] | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7812 | Each Adjacent Balancing Authority. |  | BA | BA | [21 empty] | 2016-10-28 | [5 empty] | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7830 | PSS exhibits instability due to abnormal system configuration. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-04-01 |  | 2017-06-30 |  |  |  | 13000000 | WECC-US | [5 empty] | WECC-US
3. | 7846 | Identify each asset that contains a low impact BES Cyber System according to Attachment 1, Section 3, if any (a discrete list of low impact BES Cyber Systems is not required). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-12-27 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency load shedding (UFLS) or undervoltage load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-002-5.1a: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 785 | Each Transmission Operator that operates in the Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-011-1 R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7854 | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. |  | RC | [11 empty] | RC | [10 empty] | 2016-12-14 | [5 empty] | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7859 | Actions to address analysis quality issues affecting its Real-time Assessments. |  | RC | [11 empty] | RC | [10 empty] | 2016-12-14 | [5 empty] | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7863 | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects Real-time Assessments. |  | TOP | [18 empty] | TOP |  |  |  | 2016-12-14 | [5 empty] | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7867 | Actions to address Real-time data quality issues with the entity(ies) responsible for providing the data when data quality affects its analysis functions. |  | BA | BA | [21 empty] | 2016-12-14 | [5 empty] | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7872 | Actions to address analysis quality issues affecting its Real-time Assessments. |  | TOP | [18 empty] | TOP |  |  |  | 2016-12-14 | [5 empty] | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7877 | Based on real-time hourly load and generating energy values averaged over each Clock Hour (excluding Qualifying Facilities covered in 18 C.F.R.§ 292.101, as addressed in FERC Order 464). |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Part 1.3. Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates compliance with Requirement R1, Part 1.3. Evidence of compliance with Requirement R1, Part 1.3 may include, but is not limited to, documentation that Contingency Reserve amounts are based upon load and generating data averaged over each Clock Hour and excludes Qualifying Facilities covered in 18 C.F.R.§ 292.101, as addressed in FERC Order 464. | 2017-01-24 |  | 2021-06-27 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity.4.2.1.The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group.4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | 13000000 | WECC-US | [5 empty] | WECC-US
3. | 7891 | Interpersonal Communications. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2019-04-01 | [5 empty] | 12300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7894 | An Operating Process for keeping the backup functionality consistent with the primary control center. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 790 | Include a description of how to identify the subset of SOLs that qualify as IROLs. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | FAC-011-2 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7900 | Identification of the roles for personnel involved during the initiation and implementation of the Operating Plan for backup functionality. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2019-04-01 | [5 empty] | 16300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7914 | Reporting requirements for the entities within the Reliability Coordinator Area during a restoration event. |  | RC | [11 empty] | RC | [10 empty] | 2018-03-26 | [5 empty] | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7934 | Procedures for restoring interconnections with other Transmission Operators under the direction of its Reliability Coordinator. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7950 | The capability of generating resources required to control voltages and frequency within acceptable operating limits. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7956 | The minimum duration of each of the required tests. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 73000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 796 | Single pole block, with Normal Clearing, in a monopolar or bipolar high voltage direct current system. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 22300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7960 | Building of cranking paths. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 83000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 797 | In determining the system’s response to a single Contingency, the following shall be acceptable: |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | FAC-011-2 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 7979 | PSS gain shall be set to between 1/3 and 1/2 of maximum practical gain. |  | GO | [22 empty] | 2017-04-28 |  | 2017-09-25 |  |  |  | 33000000 | WECC-US | [5 empty] | WECC-US
3. | 7990 | Physical security of BES Cyber Systems (CIP-006); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 800 | System reconfiguration through manual or automatic control or protection actions. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 23300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8000 | Electronic access controls; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8025 | Monitor non-BES facilities within its Transmission Operator Area identified as necessary by the Transmission Operator; |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-17 |  | 2021-03-31 |  |  |  | 103000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8045 | deploy Contingency Reserve, within system constraints, to respond to all Reportable Balancing Contingency Events, however, it is not subject to compliance with Requirement R1 part 1.1 if: |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2017-10-02 |  | 2019-03-31 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 805 | A process for determining which of the stability limits associated with the list of multiple contingencies (provided by the Planning Authority in accordance with FAC-014 Requirement 6) are applicable for use in the operating horizon given the actual or expected system conditions. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | FAC-011-2 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8060 | The Transmission Operator shall provide the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. |  | TOP | [18 empty] | TOP |  |  |  | 2017-09-26 |  | 2018-12-31 |  |  |  | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8074 | Generator Operators that do not monitor the voltage at the location specified in their voltage schedule shall have a methodology for converting the scheduled voltage specified by the Transmission Operator to the voltage point being monitored by the Generator Operator. |  | GOP | [5 empty] | GOP | [16 empty] | 2017-09-26 | [5 empty] | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8082 | Impedance data. |  | GO | [22 empty] | 2017-09-26 | [5 empty] | 51300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8090 | Notification by vendors when remote or onsite access should no longer be granted to vendor representatives; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and4.1.2.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and4.2.1.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers4.2.2.1. All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-013-1:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the identification and categorization process required by CIP-002-5, or any subsequent version of that Reliability Standard. |  | 12300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8099 | Require inbound and outbound access permissions, including the reason for granting access, and deny all other access by default. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a list of rules (firewall, access control lists, etc.) that demonstrate that only permitted access is allowed and that each access rule has a documented reason. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-005-6:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8105 | Require multi-factor authentication for all Interactive Remote Access sessions. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, architecture documents detailing the authentication factors used. Examples of authenticators may include, but are not limited to, • Something the individual knows such as passwords or PINs. This does not include User ID;• Something the individual has such as tokens, digital certificates, or smart cards; or • Something the individual is such as fingerprints, iris scans, or other biometric characteristics. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-005-6:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8112 | Any custom software installed; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8116 | For a change that deviates from the existing baseline configuration, update the baseline configuration as necessary within 30 calendar days of completing the change. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, updated baseline documentation with a date that is within 30 calendar days of the date of the completion of the change. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8120 | Document the results of the verification. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 14300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8134 | Prior to adding a new applicable Cyber Asset to a production environment, perform an active vulnerability assessment of the new Cyber Asset, except for CIP Exceptional Circumstances and like replacements of the same type of Cyber Asset with a baseline configuration that models an existing baseline configuration of the previous or other existing Cyber Asset. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a document listing the date of the assessment (performed prior to the commissioning of the new Cyber Asset) and the output of any tools used to perform the assessment. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 814 | Each Transmission Operator that operates in the Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | FAC-011-2 R4. | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8142 | The highest frequency set point for relays used to arrest frequency decline shall be no lower than 59.3 Hz and not higher than 59.5 Hz. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2017-10-16 | [5 empty] | 23000000 | SERC-US |  |  |  | SERC-US
3. | 8151 | The amount of total UFLS load of all steps combined shall be within -1.0 and +5.0 of the percentage specified by the Planning Coordinator for the total UFLS load in the UFLS scheme. |  | DP, DP-UFLS, TO |  | DP | [20 empty] | 2017-10-16 | [5 empty] | 43000000 | SERC-US |  |  |  | SERC-US
3. | 8159 | Amount of previous year actual or estimated load associated with each set point, both in percent and in MW. The percentage and the Load demand (MW) shall be based on the time coincident with the previous year actual Peak Demand. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-16 | [5 empty] | 73000000 | SERC-US |  |  |  | SERC-US
3. | 8163 | Maximum generator net MW that could be tripped automatically due to an underfrequency or overfrequency condition. |  | DP-UFLS, GO |  | DP | [20 empty] | 2017-10-16 | [5 empty] | 83000000 | SERC-US |  |  |  | SERC-US
3. | 8168 | A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8172 | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: • Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES • Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES• Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8176 | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-3 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 819 | A description of how each of the following is addressed, including any reliability margins applied to reflect uncertainty with projected BES conditions: |  | PCPA, RC | [9 empty] | PA |  | RC | [12 empty] | 2013-03-31 |  |  | FAC-012-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8204 | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 330000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8207 | Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 333000 | WECC-US | [5 empty] | WECC-US
3. | 8211 | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-3 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 430000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 822 | Generation dispatch |  | PCPA, RC | [9 empty] | PA |  | RC | [12 empty] | 2013-03-31 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8229 | Include the following subject matter and documentation of its use: |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-16 | [5 empty] | 13000000 | RF-US |  |  | RF-US
3. | 8233 | Load diversity. |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 13130000 | RF-US |  |  | RF-US
3. | 8240 | Modeling assumptions of firm capacity purchases from and sales to entities outside the Planning Coordinator area. |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 13230000 | RF-US |  |  | RF-US
3. | 8244 | Transmission limitations that prevent the delivery of generation reserves |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 13300000 | RF-US |  |  | RF-US
3. | 8250 | Environmental or regulatory restrictions of resource availability. |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 14300000 | RF-US |  |  | RF-US
3. | 8262 | The documentation as specified per requirement R2.1 and R2.2 shall be publicly posted no later than 30 calendar days prior to the beginning of Year One. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-16 | [5 empty] | 23000000 | RF-US |  |  | RF-US
3. | 8269 | PSS gain shall be set to between 1/3 and 1/2 of maximum practical gain. |  | GO | [22 empty] | 2017-09-26 |  |  |  | 5. Facilities: This standard applies to synchronous generators, connected to the Bulk Electric System, that meet the definition of Commercial Operation. |  | 33000000 | WECC-US | [5 empty] | WECC-US
3. | 827 | Each Transmission Operator that operates in the Reliability Coordinator Area. |  | RC | [11 empty] | RC | [12 empty] | 2013-03-31 |  |  | FAC-012-1 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 831 | Each Reliability Coordinator and Transmission Operator that operates any portion of the Planning Authority’s Planning Authority Area. |  | PCPA | [9 empty] | PA | [14 empty] | 2013-03-31 |  |  | FAC-012-1 R3. | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8334 | The benchmark GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  |  | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8342 | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2019-06-30 |  |  |  | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8347 | Include a timetable, subject to revision by the responsible entity in Part 7.4, for implementing the selected actions from Part 7.1. The timetable shall: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  |  | 73000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8353 | Revisions to the selected actions in Part 7.1, if any, including utilization of Operating Procedures if applicable, and the updated timetable for implementing the selected actions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  |  | 74300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8361 | If the analysis concludes there is Cascading caused by the supplemental GMD event described in Attachment 1, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  |  | 83000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8370 | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2019-06-30 |  |  |  | 103000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8383 | Automatic Time Error Correction term (IATEC). |  | BA | BA | [21 empty] | 2018-05-30 | [5 empty] | 43000000 | WECC-US | [5 empty] | WECC-US
3. | 8399 | Emergency preparedness and operations |  | RC | [11 empty] | RC | [10 empty] | 2019-07-01 | [5 empty] | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8409 | System operations |  | TOP | [18 empty] | TOP |  |  |  | 2019-07-01 | [5 empty] | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8417 | System operations |  | BA | BA | [21 empty] | 2019-07-01 | [5 empty] | 31300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8425 | deploy Contingency Reserve, within system constraints, to respond to all Reportable Balancing Contingency Events, however, it is not subject to compliance with Requirement R1 part 1.1 if the Responsible Entity |  | BA, RSG | BA | [15 empty] | RSG | [5 empty] | 2019-04-01 |  |  |  | 4.1.1.1. A Balancing Authority that is a member of a Reserve Sharing Group is the Responsible Entity only in periods during which the Balancing Authority is not in active status under the applicable agreement or governing rules for the Reserve Sharing Group. |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8432 | If the Control Centers are owned or operated by different Responsible Entities, identification of the responsibilities of each Responsible Entity for applying security protection to the transmission of Real-time Assessment and Real-time monitoring data between those Control Centers. |  | BA, GO, GOP, RC, TO, TOP | BA |  |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-04-13 |  |  |  | 4.2. Exemptions: The following are exempt from Reliability Standard CIP-012-1:4.2.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.2. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3. A Control Center that transmits to another Control Center Real-time Assessment or Real-time monitoring data pertaining only to the generation resource or Transmission station or substation co-located with the transmitting Control Center. |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8442 | The Transmission Operator shall provide the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. |  | TOP | [18 empty] | TOP |  |  | For part 5.3, the Transmission Operator shall have evidence it provided the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) within 30 days of receiving a request by a Generator Operator. | 2018-10-15 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 845 | The associated Contingency(ies). |  | RC | [11 empty] | RC | [10 empty] | 2009-01-01 |  | 2009-04-28 |  |  |  | 51300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8455 | Real and reactive Load forecasts. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  |  | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8462 | For each of the studies described in Requirement R2, Parts 2.1.1 and 2.1.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in System response :• Real and reactive forecasted Load. • Expected transfers. • Expected in service dates of new or modified Transmission Facilities. • Reactive resource capability. • Generation additions, retirements, or other dispatch scenarios. • Controllable Loads and Demand Side Management. • Duration or timing of known Transmission outages. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8467 | The short circuit analysis portion of the Planning Assessment shall be conducted annually addressing the Near-Term Transmission Planning Horizon and can be supported by current or past studies as qualified in Requirement R2, Part 2.6. The analysis shall be used to determine whether circuit breakers have interrupting capability for Faults that they will be expected to interrupt using the System short circuit model with any planned generation and Transmission Facilities in service which could impact the study area. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-04-13 |  | 2020-06-10 |  |  |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8471 | For each of the studies described in Requirement R2, Parts 2.4.1 and 2.4.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in performance:• Load level, Load forecast, or dynamic Load model assumptions. • Expected transfers. • Expected in service dates of new or modified Transmission Facilities. • Reactive resource capability. • Generation additions, retirements, or other dispatch scenarios. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  |  | 24300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8479 | If situations arise that are beyond the control of the Transmission Planner or Planning Coordinator that prevent the implementation of a Corrective Action Plan in the required timeframe, then the Transmission Planner or Planning Coordinator is permitted to utilize Non-Consequential Load Loss and curtailment of Firm Transmission Service to correct the situation that would normally not be permitted in Table 1, provided that the Transmission Planner or Planning Coordinator documents that they are taking actions to resolve the situation. The Transmission Planner or Planning Coordinator shall document the situation causing the problem, alternatives evaluated, and the use of Non-Consequential Load Loss or curtailment of Firm Transmission Service. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  |  | 27300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 848 | The Planning Authority shall provide its SOLs (including the subset of SOLs that are IROLs) to adjacent Planning Authorities, and to Transmission Planners, Transmission Service Providers, Transmission Operators and Reliability Coordinators that work within its Planning Authority Area. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-014-1 R5. | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8493 | Contingency analyses for Requirement R3, Parts 3.1 and 3.2 shall: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-04-13 |  | 2020-06-10 |  |  |  | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8509 | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each Quebec BES generator bus and associated generator step-up transformer high-side bus |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 13000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8513 | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 130000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8523 | To provide notification per Requirement R4. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | 12300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8524 | The roles and responsibilities of Cyber Security Incident response groups or individuals. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, dated Cyber Security Incident response process(es) or procedure(s) that define roles and responsibilities (e.g., monitoring, reporting, initiating, documenting, etc.) of Cyber Security Incident response groups or individuals. | 2019-06-20 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8529 | Retain records related to Reportable Cyber Security Incidents and Cyber Security Incidents that attempted to compromise a system identified in the “Applicable Systems” column for this Part as per the Cyber Security Incident response plan(s) under Requirement R1. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, dated documentation, such as security logs, police reports, emails, response forms or checklists, forensic analysis results, restoration records, and post-incident review notes related to Reportable Cyber Security Incidents and a Cyber Security Incident that is determined to be an attempt to compromise a system identified in the “Applicable Systems” column. | 2019-06-20 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8535 | Notify each person or group with a defined role in the Cyber Security Incident response plan of the updates to the Cyber Security Incident response plan based on any documented lessons learned. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | 31300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8542 | The level of intrusion that was achieved or attempted. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2021-01-01 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | 41300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8544 | Provide updates, if any, within 7 calendar days of determination of new or changed attribute information required in Part 4.1. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, dated documentation of submissions to the E-ISAC and NCCIC. | 2019-06-20 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8556 | The benchmark GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2020-10-05 |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8567 | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2020-10-05 |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8572 | Include a timetable, subject to revision by the responsible entity in Part 7.4, for implementing the selected actions from Part 7.1. The timetable shall: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2020-10-05 |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 73000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8579 | Revisions to the selected actions in Part 7.1, if any, including utilization of Operating Procedures if applicable, and the updated timetable for implementing the selected actions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 74300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8584 | If the analysis concludes there is Cascading caused by the supplemental GMD event described in Attachment 1, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2020-10-05 |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 83000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8600 | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2020-10-05 |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 103000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8608 | The Responsible Entity shall document test results. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 13000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC | MRO-US | NPCC-US |  |  |  | WECC-US
3. | 8612 | In the case where unused ports and services cannot be disabled due to technical limitations, the Responsible Entity shall document compensating measure(s) applied to mitigate risk exposure. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 23000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC | MRO-US | NPCC-US |  |  |  | WECC-US
3. | 8623 | The Responsible Entity shall review, at least annually, user accounts to verify access privileges are in accordance with Standard CIP-003-3 Requirement R5 and Standard CIP-004-3 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 51300000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC | MRO-US | NPCC-US |  |  |  | WECC-US
3. | 8627 | Where such accounts must be shared, the Responsible Entity shall have a policy for managing the use of such accounts that limits access to only those with authorization, an audit trail of the account use (automated or manual), and steps for securing the account in the event of personnel changes (for example, change in assignment or termination). |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 52300000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC | MRO-US | NPCC-US |  |  |  | WECC-US
3. | 8628 | At a minimum, the Responsible Entity shall require and use passwords, subject to the following, as technically feasible: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 53000000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC | MRO-US | NPCC-US |  |  |  | WECC-US
3. | 8631 | Each password shall be changed at least annually, or more frequently based on risk. | [30 empty] | 53300000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC | MRO-US | NPCC-US |  |  |  | WECC-US
3. | 8635 | The Responsible Entity shall maintain logs of system events related to cyber security, where technically feasible, to support incident response as required in Standard CIP-008-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 63000000 | MRO-MB | MRO-US
3. | 8641 | The Responsible Entity shall maintain records that such assets were disposed of or redeployed in accordance with documented procedures. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 73000000 | MRO-MB | MRO-US
3. | 8645 | A review of controls for default accounts; and, | [30 empty] | 83000000 | MRO-MB | MRO-US
3. | 8648 | Include a timetable, subject to revision by the responsible entity in Part 7.4, for implementing the selected actions from Part 7.1. The timetable shall: | This Variance replaces Requirement R7, Part 7.3 | [23 empty] | 2019-07-01 |  |  |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 730000 | MRO-MB, MRO-SK, NPCC-NB, NPCC-NS, NPCC-ON, NPCC-QC, WECC-AB, WECC-BC | MRO-US | NPCC-US |  |  |  | WECC-US
3. | 8660 | A method to determine Contingencies included in analyses and assessments; | [24 empty] | 2020-01-01 |  | 2021-03-31 |  | ApplicabilityAs used in this WECC Regional Variance, Reliability Coordinator is specific to those Reliability Coordinators providing Reliability Coordinator service(s) to entities operating within the Western Interconnection, regardless of where the Reliability Coordinator may be located. |  | 730000 | WECC-US | [5 empty] | WECC-US
3. | 8674 | A method to determine Contingencies included in analyses and assessments; |  | RC | [11 empty] | RC | [10 empty] | 2021-04-01 | [5 empty] | 730000 | WECC-US | [5 empty] | WECC-US
3. | 8683 | Physical security of BES Cyber Systems (CIP-006); |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8693 | Electronic access controls; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8702 | Format and schedule of UFLS data submittal |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 143000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8727 | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | GO | [24 empty] | 2021-02-04 |  |  |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8731 | Ambient conditions (for particular or average conditions or as they vary in real-time). |  | GO | [24 empty] | 2021-02-04 |  |  |  | 22300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8737 | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | TO | [24 empty] | 2021-02-04 |  |  |  | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8742 | Ambient conditions (for particular or average conditions or as they vary in real-time). |  | TO | [24 empty] | 2021-02-04 |  |  |  | 32300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8749 | The BES interrupting device owner identified that its Protection System component(s) caused the BES interrupting device(s) operation or was caused by manual intervention in response to its Protection System failure to operate. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.2. Facilities:4.2.1 Protection Systems for BES Elements, with the following exclusions:4.2.1.1 Non-protective functions that are embedded within a Protection System.4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS).4.2.1.4 Remedial Action Schemes (RAS).4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8754 | The BES interrupting device owner has determined that its Protection System component(s) did not cause the BES interrupting device(s) operation or cannot determine whether its Protection System components caused the BES interrupting device(s) operation. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.2. Facilities:4.2.1 Protection Systems for BES Elements, with the following exclusions:4.2.1.1 Non-protective functions that are embedded within a Protection System.4.2.1.2 Protective functions intended to operate as a control function during switching. 4.2.1.3 Special Protection Systems (SPS).4.2.1.4 Remedial Action Schemes (RAS).4.2.1.5 Protection Systems of individual dispersed power producing resources identified under Inclusion I4 of the BES definition where the Misoperations affected an aggregate nameplate rating of less than or equal to 75 MVA of BES Facilities.4.2.2 Underfrequency load shedding (UFLS) that is intended to trip one or more BES Elements.4.2.3 Undervoltage load shedding (UVLS) that is intended to trip one or more BES Elements. |  | 21300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8774 | Monitor non-BES facilities within its Transmission Operator Area identified as necessary by the Transmission Operator; |  | TOP | [18 empty] | TOP |  |  |  | 2021-04-01 | [5 empty] | 103000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8808 | The Transmission Operator shall provide the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. |  | TOP | [18 empty] | TOP | [5 empty] | 2020-05-14 |  |  |  | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8841 | Based on real-time hourly load and generating energy values averaged over each Clock Hour (excluding Qualifying Facilities covered in 18 C.F.R.§ 292.101, as addressed in FERC Order 464). |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Part 1.3Each Balancing Authority and each Reserve Sharing Group will have dated documentation that demonstrates compliance with Requirement R1, Part 1.3. Evidence of compliance with Requirement R1, Part 1.3 may include, but is not limited to, documentation that Contingency Reserve amounts are based upon load and generating data averaged over each Clock Hour and excludes Qualifying Facilities covered in 18 C.F.R.§ 292.101, as addressed in FERC Order 464. | 2021-06-28 |  |  |  | 4.1.2.1 The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group.4.1.2.2 The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | 13000000 | WECC-US | [5 empty] | WECC-US
3. | 8911 | Each Planning Coordinator in Ontario, Québec and the Maritime Provinces shall arrange for compensatory load shedding, in accordance with Attachment A and as provided by a Distribution Provider or Transmission Owner, that is adequate to compensate for the loss of generator(s) due to early tripping that is within the UFLS island identified by the Planning Coordinator in Requirement R2. |  | PCPA | [9 empty] | PA | [12 empty] | 2020-02-18 |  |  |  | 4.1.3. Distribution Providers that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators4.1.4. Transmission Owners that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators |  | 133000000 | NPCC-US |  | NPCC-US
3. | 8915 | Transmit the initial frequency trip setting and any changes to the setting and the technical basis for the settings to the Planning Coordinator. |  | GO | [22 empty] | 2020-02-18 |  |  |  | 4.1.3. Distribution Providers that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators4.1.4. Transmission Owners that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators |  | 163000000 | NPCC-US |  | NPCC-US
3. | 895 | A Reliability Coordinator or Transmission Operator determines the deviation, regardless of magnitude, to be a reliability concern and notifies the Purchasing-Selling Entity of that determination and the reasons. |  | RC, TOP | [11 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2008-08-26 |  |  | INT-004-1 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8989 | The benchmark GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 8997 | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 63000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 900 | A Reliability Coordinator or Transmission Operator determines the deviation, regardless of magnitude, to be a reliability concern and notifies the Purchasing-Selling Entity of that determination and the reasons. |  | PSE | [10 empty] | PSE | [11 empty] | 2008-08-27 |  | 2014-09-30 |  |  | INT-004-2 R2. | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9002 | Include a timetable, subject to approval for any extension sought under Part 7.4, for implementing the selected actions from Part 7.1. The timetable shall: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 73000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9015 | If the analysis concludes there is Cascading caused by the supplemental GMD event described in Attachment 1, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 83000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9016 | The supplemental GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 83000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9024 | Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 103000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9028 | Updated timetable for implementing the selected actions in Part 7.1. | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 74300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9032 | Include a timetable, subject to approval for any extension sought under Part 11.4, for implementing the selected actions from Part 11.1. The timetable shall: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 113000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9038 | Updated timetable for implementing the selected actions in Part 11.1. | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 114300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9045 | Updated timetable for implementing the selected actions in Part 7.1. | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 743000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9054 | Updated timetable for implementing the selected actions in Part 11.1. | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 2043000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9060 | Steady-state, short-circuit, and dynamics studies, as necessary, to evaluate system performance under both normal and contingency conditions; and |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2021-04-01 |  |  |  | Applicable Generator Owner: Generator Owner with a fully executed Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9069 | A periodicity for providing data. |  | RC | [11 empty] | RC | [10 empty] | 2021-04-01 | [5 empty] | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9075 | A mutually agreeable security protocol |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2021-04-01 | [5 empty] | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9079 | A request to provide any or all of the following actual data, as necessary: |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9083 | Monthly and annual Net Energy for Load in gigawatthours for the prior calendar year. | [24 empty] | 2021-04-01 | [5 empty] | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9088 | Peak hour forecast Total Internal Demands (summer and winter) in megawatts for ten calendar years into the future. | [24 empty] | 2021-04-01 | [5 empty] | 14300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9104 | Guidelines the Planning Coordinator will use to determine unacceptable differences in performance under Part 1.1 or 1.2; and |  | PCPA | [9 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 911 | Scheduling path (proper connectivity of Adjacent Balancing Authorities). |  | BA | BA | [21 empty] | 2007-06-18 |  | 2008-08-26 |  |  |  | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9113 | Inform the Nuclear Plant Generator Operator when the ability to assess the operation of the electric system affecting NPIRs is lost. |  | BA, DP, GO, GOP, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  |  |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9123 | Types of planning and operational analyses performed specifically to support the NPIRs, including the frequency of studies and types of Contingencies and scenarios required. | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 92300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9124 | Operations and maintenance coordination |  | BA, DP, GO, GOP, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  |  |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 93000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9127 | Coordination of testing, calibration and maintenance of on-site and off-site power supply systems and related components. | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 93300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9135 | Provisions for coordinating investigations of causes of unplanned events affecting the NPIRs and developing solutions to minimize future risk of such events. | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 94300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9141 | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each Quebec BES generator bus and associated generator step-up transformer high-side bus |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 330000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9145 | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 430000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9153 | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 330000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9156 | Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. | [26 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 333000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9160 | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1. |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 430000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 917 | Scheduling path (proper connectivity of Adjacent Balancing Authorities). |  | BA | BA | [21 empty] | 2008-08-27 |  | 2010-06-30 |  |  |  | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9173 | A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9177 | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: • Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES • Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES• Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9181 | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-4 - Attachment 1. |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 43000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9200 | Format and schedule of UFLS data submittal |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 143000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9207 | A periodicity for providing data. |  | TOP | [18 empty] | TOP |  |  |  | 2021-04-01 | [5 empty] | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9212 | A periodicity for providing data. |  | BA | BA | [21 empty] | 2021-04-01 | [5 empty] | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9219 | A mutually agreeable security protocol |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  |  | 2021-04-01 | [5 empty] | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 923 | Scheduling path (proper connectivity of Adjacent Balancing Authorities). |  | BA | BA | [21 empty] | 2010-07-01 |  | 2014-09-30 |  |  |  | 11300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9231 | If a generating unit/generating facility has not participated in a minimum of (8) eight FMEs in a 12-month period, its performance shall be based on a rolling eight FME average response. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [16 empty] | 2020-05-19 |  |  |  | 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL001-TRE-2. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-2. 4.2.3 Any generators that are not required by the Balancing Authority to provide primary frequency response are exempt from this standard. |  | 23000000 | TXRE-US |  |  |  |  | TXRE-US
3. | 9238 | For digital and electronic Governors, once frequency deviation has exceeded the Governor deadband from 60.000 Hz, the Governor setting shall follow the slope derived from the formula below.(see standard for formula) where MWGCS is the maximum megawatt control range of the Governor control system. For mechanical Governors, droop will be proportional from the deadband by design. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [16 empty] | 2020-05-19 |  |  |  | 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL001-TRE-2. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-2. 4.2.3 Any generators that are not required by the Balancing Authority to provide primary frequency response are exempt from this standard. |  | 63000000 | TXRE-US |  |  |  |  | TXRE-US
3. | 9244 | A generating unit/generating facility’s initial Primary Frequency Response performance during an FME may be excluded from the rolling average calculation by the Balancing Authority due to a legitimate operating condition that prevented normal Primary Frequency Response performance. Examples of legitimate operating conditions that may support exclusion of FMEs include, but are not limited to: • Operation at or near auxiliary equipment operating limits (such as boiler feed pumps, condensate pumps, • Data telemetry failure. The Balancing Authority may request raw data from the Generator Owner as a substitute. pulverizers, and forced draft fans); |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [16 empty] | 2020-05-19 |  |  |  | 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL001-TRE-2. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-2. 4.2.3 Any generators that are not required by the Balancing Authority to provide primary frequency response are exempt from this standard. |  | 93000000 | TXRE-US |  |  |  |  | TXRE-US
3. | 9248 | A generating unit/generating facility’s sustained Primary Frequency Response performance during an FME may be excluded from the rolling average calculation by the Balancing Authority due to a legitimate operating condition that prevented normal Primary Frequency Response performance. Examples of legitimate operating conditions that may support exclusion of FMEs include, , but are not limited to:• Operation at or near auxiliary equipment operating limits (such as boiler feed pumps, condensate pumps, pulverizers, and forced draft fans);• Data telemetry failure. The Balancing Authority may request raw data from the Generator Owner as a substitute. |  | BA, GO, GOP | BA |  |  |  | GO | GOP | [16 empty] | 2020-05-19 |  |  |  | 4.2.1 Existing generating facilities regulated by the U.S. Nuclear Regulatory Commission prior to the Effective Date are exempt from Standard BAL001-TRE-2. 4.2.2 Generating units/generating facilities while operating in synchronous condenser mode are exempt from Standard BAL-001-TRE-2. 4.2.3 Any generators that are not required by the Balancing Authority to provide primary frequency response are exempt from this standard. |  | 103000000 | TXRE-US |  |  |  |  | TXRE-US
3. | 9256 | 1.3. Identify each asset that contains a low impact BES Cyber System according to Attachment 1, Section 3, if any (a discrete list of low impact BES Cyber Systems is not required). |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [5 empty] | 2021-02-04 |  |  |  | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 928 | The following are defined: |  | IA | [6 empty] | IA | [15 empty] | 2007-06-18 |  | 2014-09-30 |  |  | INT-007-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 931 | Ramp start and stop times. |  | IA | [6 empty] | IA | [15 empty] | 2007-06-18 |  | 2014-09-30 |  |  |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9311 | The short circuit analysis portion of the Planning Assessment shall be conducted annually addressing the Near-Term Transmission Planning Horizon and can be supported by current or past studies as qualified in Requirement R2, Part 2.6. The analysis shall be used to determine whether circuit breakers have interrupting capability for Faults that they will be expected to interrupt using the System short circuit model with any planned generation and Transmission Facilities in service which could impact the study area. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9331 | Contingency analyses for Requirement R3, Parts 3.1 and 3.2 shall: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9359 | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: |  | PCPA | [9 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 330000 | WECC-US | [5 empty] | WECC-US
3. | 9370 | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-5 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 430000 | WECC-US | [5 empty] | WECC-US
3. | 9453 | Require inbound and outbound access permissions, including the reason for granting access, and deny all other access by default. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9458 | Require multi-factor authentication for all Interactive Remote Access sessions. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9471 | For a change that deviates from the existing baseline configuration, update the baseline configuration as necessary within 30 calendar days of completing the change. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 9487 | Prior to adding a new applicable Cyber Asset to a production environment, perform an active vulnerability assessment of the new Cyber Asset, except for CIP Exceptional Circumstances and like replacements of the same type of Cyber Asset with a baseline configuration that models an existing baseline configuration of the previous or other existing Cyber Asset |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 33000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | 999 | Current post-contingency element conditions (voltage, thermal, or stability), including any applicable mitigation plans to alleviate SOL or IROL violations, including the plan’s viability and scope. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  | IRO-005-1 R1. | 13000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-04-12-0000007 | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | GO | [22 empty] | 2021-10-01 | [5 empty] | 22300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-04-12-0000017 | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | GO | [22 empty] | 2021-10-01 | [5 empty] | 32300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-05-26-0000003 | Identification of the roles for personnel involved during the initiation and implementation of the Operating Plan for backup functionality. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  |  | 16003000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-08-0000003 | Undervoltage inhibit setting shall be less than or equal to 85 percent of nominal voltage. |  | DP, TO |  | DP | [22 empty] | 2013-11-07 |  |  |  | 10300000 | SPPRE-US
3. | RP-2021-06-08-0000006 | The intentional relay time delay for UFLS shall be less than or equal to 30 cycles. |  | DP, TO |  | DP | [22 empty] | 2013-11-07 |  |  |  | 20300000 | SPPRE-US
3. | RP-2021-06-08-0000010 | Total relay operating time of each location (time required for the relay to reliably sense the frequency + intentional delay time (if any)) |  | DP, TO |  | DP | [22 empty] | 2013-11-07 |  |  |  | 50300000 | SPPRE-US
3. | RP-2021-06-08-0000018 | Total relay operating time of each location (time required for the relay to reliably sense the frequency + intentional delay time (if any)) |  | GO | [24 empty] | 2013-11-07 |  |  |  | 60300000 | SPPRE-US
3. | RP-2021-06-08-0000025 | Time delay from initiation to trip signal |  | DP, TO |  | DP | [22 empty] | 2014-11-13 |  |  |  | 10300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-09-0000006 | When time does not permit such notifications and coordination, or when immediateaction is required to prevent a hazard to the public, lengthy customer serviceinterruption, or damage to facilities, the Generator Operator shall notify theTransmission Operator, and the Transmission Operator shall notify its ReliabilityCoordinator and adjacent Transmission Operators, at the earliest possible time. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 70300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-09-0000007 | When time does not permit such notifications and coordination, or whenimmediate action is required to prevent a hazard to the public, lengthycustomer service interruption, or damage to facilities, the Generator Operatorshall notify the Transmission Operator, and the Transmission Operator shallnotify its Reliability Coordinator and adjacent Transmission Operators, at theearliest possible time. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-11-20 |  |  |  | 70300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-14-0000009 | Where allowed by Standards CIP-002-2 through CIP-009-2, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 22300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-14-0000010 | Where allowed by Standards CIP-002-4 through CIP-009-4, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 22300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-14-0000011 | Where allowed by Standards CIP-002-4 through CIP-009-4, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 20300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-15-0000026 | With other Reliability Coordinators, Transmission Operators, and BalancingAuthorities as necessary to maintain reliability. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 10300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-16-0000009 | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | GO | [24 empty] | 2011-05-24 |  |  |  | 20300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-16-0000019 | A statement that a Facility Rating shall respect the most limiting applicable Equipment Rating of the individual equipment that comprises that Facility. |  | TO | [24 empty] | 2011-05-24 |  |  |  | 30300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-16-0000034 | Include the following subject matter and documentation of its use: |  | PCPA | [9 empty] | PA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  |  | 10300000 | RF-US |  |  | RF-US
3. | RP-2021-06-16-0000046 | The documentation as specified per requirement R2.1 and R2.2 shall be publicly posted no later than 30 calendar days prior to the beginning of Year One. |  | PCPA | [9 empty] | PA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  |  | 20300000 | RF-US |  |  | RF-US
3. | RP-2021-06-16-0000049 | Where allowed by Standards CIP-002-3 through CIP-009-3, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  |  |  | 20300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-16-0000050 | Where allowed by Standards CIP-002-3 through CIP-009-3, the senior manager may delegate authority for specific actions to a named delegate or delegates. These delegations shall be documented in the same manner as R2.1 and R2.2, and approved by the senior manager. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | 20300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-17-0000015 | Where technically feasible, utilize twoor more different physical accesscontrols (this does not require twocompletely independent physicalaccess control systems) to collectivelyallow unescorted physical access intoPhysical Security Perimeters to onlythose individuals who have authorizedunescorted physical access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 10300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-18-0000002 | Where technically feasible, retain applicable event logs identified in Part 4.1 for at least the last 90 consecutive calendar days except under CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 40300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-18-0000017 | With other Reliability Coordinators, Transmission Operators, and BalancingAuthorities as necessary to maintain reliability. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2009-05-13 |  | 2015-09-30 |  |  |  | 10300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-21-0000002 | The Transmission Operator and Balancing Authority shall coordinate transmission and generator maintenance schedules to maximize capacity or conserve the fuel in short supply. (This includes water for hydro generators.) |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2013-07-01 |  | 2017-03-31 |  |  |  | 60300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-21-0000006 | End-user Facilities |  | TO | [22 empty] | 2013-11-25 |  | 2015-12-31 |  |  |  | 10300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-22-0000003 | Timeframe and periodicity for providing data and information (based on itshardware and software requirements, and the time needed to do its OperationalPlanning Analyses). |  | RC | [11 empty] | RC | [12 empty] | 2009-08-05 |  |  |  | 10300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-22-0000004 | Timeframe and periodicity for providing data and information (based on itshardware and software requirements, and the time needed to do its OperationalPlanning Analyses). |  | RC | [11 empty] | RC | [10 empty] | 2011-10-01 |  | 2017-03-31 |  |  |  | 10300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-22-0000032 | Updated at least once per month for AFC calculations for months two through 13. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 30300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-23-0000009 | Timetable for response to data request. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 40300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-23-0000012 | Shunt capacitors, shunt reactors. |  | TO | [22 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 20300000 | NPCC-US |  | NPCC-US
3. | RP-2021-06-23-0000034 | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following: |  | PCPA | [9 empty] | PA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  |  | 30300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-23-0000037 | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-1 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  |  | 40300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-23-0000043 | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-2 - Attachment 1. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-10-01 |  | 2017-09-30 |  |  |  | 40300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-24-0000002 | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two secondscumulatively per simulated event, and shall not exceed 1.10 per unit for longerthan 45 seconds cumulatively per simulated event at each generator bus andgenerator step-up transformer high-side bus associated with each of thefollowing: Individual generating units greater than 20 MVA (gross nameplate rating)directly connected to the BES Generating plants/facilities greater than 75 MVA (gross aggregate nameplaterating) directly connected to the BES Facilities consisting of one or more units connected to the BES at a commonbus with total generation above 75 MVA gross nameplate rating. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 30300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-24-0000005 | Underfrequency trip settings of any facility consisting of one or more unitsconnected to the BES at a common bus with total generation above 75 MVA(gross nameplate rating) that trip above the Generator Underfrequency TripModeling curve in PRC-006-3 - Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 40300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-24-0000009 | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two secondscumulatively per simulated event, and shall not exceed 1.10 per unit for longerthan 45 seconds cumulatively per simulated event at each generator bus andgenerator step-up transformer high-side bus associated with each of thefollowing: Individual generating units greater than 20 MVA (gross nameplate rating)directly connected to the BES Generating plants/facilities greater than 75 MVA (gross aggregate nameplaterating) directly connected to the BES Facilities consisting of one or more units connected to the BES at a commonbus with total generation above 75 MVA gross nameplate rating. |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 30300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-24-0000012 | Underfrequency trip settings of any facility consisting of one or more unitsconnected to the BES at a common bus with total generation above 75 MVA(gross nameplate rating) that trip above the Generator Underfrequency TripModeling curve in PRC-006-4 - Attachment 1. |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 40300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-24-0000015 | Format and schedule of UFLS data submittal |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 140300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-24-0000017 | Transmit the initial frequency trip setting and any changes to the settingand the technical basis for the settings to the Planning Coordinator. |  | DP-UFLS, GO |  | DP | [20 empty] | 2015-07-01 |  | 2020-03-31 |  |  |  | 190300000 | NPCC-US |  | NPCC-US
3. | RP-2021-06-24-0000027 | Time delay from initiation to trip signal. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 10300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-24-0000028 | When time does not permit such notifications and coordination, or whenimmediate action is required to prevent a hazard to the public, lengthycustomer service interruption, or damage to facilities, the Generator Operatorshall notify the Transmission Operator, and the Transmission Operator shallnotify its Reliability Coordinator and adjacent Transmission Operators, at theearliest possible time. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-11-21 |  | 2017-03-31 |  |  |  | 70300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-24-0000032 | The short circuit analysis portion of the Planning Assessment shall beconducted annually addressing the Near-Term Transmission Planning Horizonand can be supported by current or past studies as qualified in RequirementR2, Part 2.6. The analysis shall be used to determine whether circuit breakershave interrupting capability for Faults that they will be expected to interruptusing the System short circuit model with any planned generation andTransmission Facilities in service which could impact the study area. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-07-01 |  | 2020-06-10 |  |  |  | 20300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-24-0000045 | Contingency analyses for Requirement R4, Parts 4.1 and 4.2 shall : |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-07-01 |  | 2020-06-10 |  |  |  | 40300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-24-0000062 | The Transmission Operator shall provide the criteria used to develop voltage schedules ReactivePower schedule (which is either a range or a target value with an associated tolerance band) tothe Generator Operator within 30 days of receiving a request. |  | TOP | [18 empty] | TOP |  |  |  | 2014-10-01 |  | 2015-11-12 |  |  |  | 50300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-24-0000065 | The Transmission Operator shall provide the criteria used to develop voltage schedules orReactive Power schedule (which is either a range or a target value with an associated toleranceband) to the Generator Operator within 30 days of receiving a request. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-25 |  |  |  | 50300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-24-0000068 | The Transmission Operator shall provide the criteria used to develop voltage schedules orReactive Power schedule (which is either a range or a target value with an associatedtolerance band) to the Generator Operator within 30 days of receiving a request. |  | TOP | [18 empty] | TOP |  |  |  | 2017-09-26 |  | 2018-12-31 |  |  |  | 50300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-24-0000071 | The Transmission Operator shall provide the criteria used to develop voltageschedules or Reactive Power schedule (which is either a range or a target valuewith an associated tolerance band) to the Generator Operator within 30 daysof receiving a request. |  | TOP | [18 empty] | TOP | [5 empty] | 2020-05-14 |  |  |  | 50300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-24-0000111 | Generating unit(s) cold weather data, to include: |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 70300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-24-0000123 | Provisions for notification of BES generating unit(s) during local forecasted cold weather to include: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 10300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-24-0000137 | A mutually agreeable security protocol |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 30300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-24-0000140 | Provisions for notification of BES generating unit(s) during local forecasted cold weather to include: |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 10300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-24-0000154 | Provisions for notification of BES generating unit(s) status during local forecasted cold weather to include: |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 20300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-24-0000169 | A mutually agreeable security protocol |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 50300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-30-0000009 | Where technically feasible, utilize two or more different physical access controls (this does not require two completely independent physical access control systems) to collectively allow unescorted physical access into Physical Security Perimeters to only those individuals who have authorized unescorted physical access. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 | [5 empty] | 10300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-06-30-0000011 | Where technically feasible, retain applicable event logs identified in Part 4.1 for at least the last 90 consecutive calendar days except under CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 40300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-01-0000013 | Starting with all Facilities in service, the system’s response to a single Contingency, may include any of the following: |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 22300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-02-0000003 | The Planning Authority shall provide its SOLs (including the subset of SOLs that are IROLs) to adjacent Planning Authorities, and to Transmission Planners, Transmission Service Providers, Transmission Operators and Reliability Coordinators that work within its Planning Authority Area. |  | PCPA, RC, TOP, TP | [9 empty] | PA |  | RC | [6 empty] | TOP | TP |  |  | 2009-04-29 | [5 empty] | 51400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-07-0000004 | Within 24 hours of the unexpected outage of a 500 kV or higher transmission Facility or a transformer with a low-side voltage of 200 kV or higher for TTCs in effect during the anticipated duration of the outage, provided such outage is expected to last 24 hours or longer. |  | TOP | [18 empty] | TOP |  |  |  | 2013-10-01 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 50300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-07-0000005 | Use (as the TTC) the lesser of:  The sum of the incremental Transfer Capability and the impacts of Firm Transmission Services, as specified in the Transmission Service Provider’s ATCID, that were included in the study model, or  The sum of Facility Ratings of all ties comprising the ATC Path. |  | TOP | [18 empty] | TOP |  |  |  | 2013-10-01 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 60300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-07-0000023 | Updated at least once per month for AFC calculations for months two through 13. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 30300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-08-0000004 | Trigger settings for at least the following: |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  | Entities shall be at least 50 percent compliant within four (4) years of the effective date of PRC-002-2 and fully compliant within six (6) years of the effective date.Entities that own only one (1) identified BES bus, BES Element, or generating unit shall be fully compliant within six (6) years of the effective date.Entities shall be 100 percent compliant with a re-evaluated list from Requirement R1 or R5 within three (3) years following the notification by the TO or the Responsible Entity that re-evaluated the list. | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 40300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-09-0000003 | A single island that includes all portions of the BES in either the Regional Entity area or the Interconnection in which the Planning Coordinator’s area resides. If a Planning Coordinator’s area resides in multiple Regional Entity areas, each of those Regional Entity areas shall be identified as an island. Planning Coordinators may adjust island boundaries to differ from Regional Entity area boundaries by mutual consent where necessary for the sole purpose of producing contiguous regional islands more suitable for simulation. |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2021-04-01 |  |  |  | UFLS entities shall mean all entities that are responsible for the ownership,operation, or control of UFLS equipment as required by the UFLS programestablished by the Planning Coordinators. Such entities may include one ormore of the following: 4.2.1 Transmission Owners4.2.2 Distribution Providers4.2.3 UFLS-Only Distribution Providers4.3. Transmission Owners that own Elements identified in the UFLS programestablished by the Planning Coordinators. |  | 20300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-09-0000006 | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each generator bus and generator step-up transformer high-side bus associated with each of the following:• Individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES• Generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES• Facilities consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA gross nameplate rating. |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2021-04-01 |  |  |  | UFLS entities shall mean all entities that are responsible for the ownership,operation, or control of UFLS equipment as required by the UFLS programestablished by the Planning Coordinators. Such entities may include one ormore of the following: 4.2.1 Transmission Owners4.2.2 Distribution Providers4.2.3 UFLS-Only Distribution Providers4.3. Transmission Owners that own Elements identified in the UFLS programestablished by the Planning Coordinators. |  | 30300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-09-0000009 | Underfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip above the Generator Underfrequency Trip Modeling curve in PRC-006-5 - Attachment 1. |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2021-04-01 |  |  |  | UFLS entities shall mean all entities that are responsible for the ownership,operation, or control of UFLS equipment as required by the UFLS programestablished by the Planning Coordinators. Such entities may include one ormore of the following: 4.2.1 Transmission Owners4.2.2 Distribution Providers4.2.3 UFLS-Only Distribution Providers4.3. Transmission Owners that own Elements identified in the UFLS programestablished by the Planning Coordinators. |  | 40300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-09-0000018 | Format and schedule of UFLS data submittal |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2021-04-01 |  |  |  | UFLS entities shall mean all entities that are responsible for the ownership,operation, or control of UFLS equipment as required by the UFLS programestablished by the Planning Coordinators. Such entities may include one ormore of the following: 4.2.1 Transmission Owners4.2.2 Distribution Providers4.2.3 UFLS-Only Distribution Providers4.3. Transmission Owners that own Elements identified in the UFLS programestablished by the Planning Coordinators. |  | 140300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-09-0000023 | Volts per Hz (V/Hz) shall not exceed 1.18 per unit for longer than two seconds cumulatively per simulated event, and shall not exceed 1.10 per unit for longer than 45 seconds cumulatively per simulated event at each Quebec BES generator bus and associated generator step-up transformer high-side bus |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2021-04-01 |  |  |  | UFLS entities shall mean all entities that are responsible for the ownership,operation, or control of UFLS equipment as required by the UFLS programestablished by the Planning Coordinators. Such entities may include one ormore of the following: 4.2.1 Transmission Owners4.2.2 Distribution Providers4.2.3 UFLS-Only Distribution Providers4.3. Transmission Owners that own Elements identified in the UFLS programestablished by the Planning Coordinators. |  | 68030300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-09-0000030 | Transmit the initial frequency trip setting and any changes to the setting and the technical basis for the settings to the Planning Coordinator. |  | GO | [22 empty] | 2020-02-18 |  |  |  | 4.1.3. Distribution Providers that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators4.1.4. Transmission Owners that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators |  | 160300000 | NPCC-US |  | NPCC-US
3. | RP-2021-07-09-0000049 | The short circuit analysis portion of the Planning Assessment shall be conducted annually addressing the Near-Term Transmission Planning Horizon and can be supported by current or past studies as qualified in Requirement R2, Part 2.6. The analysis shall be used to determine whether circuit breakers have interrupting capability for Faults that they will be expected to interrupt using the System short circuit model with any planned generation and Transmission Facilities in service which could impact the study area. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 20300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-12-0000037 | Contingency analyses for Requirement R4, Parts 4.1 and 4.2 shall : |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 40300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-12-0000047 | Updated timetable for implementing the selected actions in Part 7.1 |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP | [6 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 68740300000
3. | RP-2021-07-12-0000048 | Updated timetable for implementing the selected actions in Part 11.1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP | [6 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 69140300000
3. | RP-2021-07-12-0000059 | The Transmission Operator shall provide the criteria used to develop voltage schedules or Reactive Power schedule (which is either a range or a target value with an associated tolerance band) to the Generator Operator within 30 days of receiving a request. |  | TOP | [18 empty] | TOP |  |  |  | 2019-01-01 |  |  |  | 4.2. Generator Operators within the Western Interconnection (for the WECC Variance) |  | 50300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-13-0000003 | Monitor non-BES facilities within its Transmission Operator Area identified as necessary by the Transmission Operator; |  | BA, DP, GOP, TOP | BA | DP |  |  |  | GOP | [12 empty] | TOP | [9 empty] | 100300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-13-0000009 | Require that System Voltage Limits are greater than or equal to in-service BES relay settings for undervoltage load shedding systems and Undervoltage Load Shedding Programs; |  | RC | [11 empty] | RC | [16 empty] | 30300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-13-0000018 | Describe how the Reliability Coordinator establishes stability limits when there is an impact to more than one Transmission Operator in its Reliability Coordinator Area or other Reliability Coordinator Areas. |  | RC | [11 empty] | RC | [16 empty] | 40300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-13-0000026 | Describe the method(s) for identifying which, if any, of the Contingency events provided by the Planning Coordinator or Transmission Planner in accordance with FAC-014-3, Requirement R7, to use in determining stability limits. |  | RC | [11 empty] | RC | [16 empty] | 50300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-13-0000037 | System performance for applicable Contingencies identified in Part 5.2 demonstrates that: instability, Cascading, or uncontrolled separation that adversely impact the reliability of the Bulk Electric System does not occur. |  | RC | [11 empty] | RC | [16 empty] | 60300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-13-0000064 | Each impacted Transmission Operator within its Reliability Coordinator Area, the value of the stability limits established pursuant to Requirement R4 and each IROL established pursuant to Requirement R1, in an agreed upon time frame necessary for inclusion in the Transmission Operator’s Operational Planning Analyses, Real- time monitoring, and Real-time Assessments. |  | RC, TOP, TP | [11 empty] | RC | [6 empty] | TOP | TP | [8 empty] | 50300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-13-0000070 | The associated stability criteria violation requiring the Corrective Action Plan (e.g. violation of transient voltage response criteria or damping rate criteria); |  | RC, TOP, TP | [11 empty] | RC | [6 empty] | TOP | TP | [8 empty] | 70300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-13-0000075 | An encroachment due to the blowing together of applicable lines and vegetation located inside the ROW that caused a vegetation‐related Sustained Outage,Footnote: Multiple Sustained Outages on an individual line, if caused by the same vegetation, will be reported as one outage regardless of the actual number of outages within a 24‐hour period. |  | GO, TO |  |  |  |  | GO | [23 empty] | 10300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-13-0000081 | Rescheduling work between growing seasons |  | GO, TO |  |  |  |  | GO | [23 empty] | 70300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-15-0000003 | Re-evaluate all BES buses at least once every five calendar years in accordance with Part 1.1 and notify other owners, if any, in accordance with Part 1.2, and implement the re-evaluated list of BES buses as per the Implementation Plan. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 10300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-15-0000010 | Trigger settings for at least the following: |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 40300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-15-0000024 | Notify all owners of identified BES Elements, within 90-calendar days of completion of Part 5.1, that their respective BES Elements require DDR data when requested. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 50300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-15-0000028 | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 60300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-15-0000032 | Real Power and Reactive Power flows expressed on a three phase basis corresponding to all circuits where current measurements are required. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 70300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-07-15-0000042 | SER data will be provided in ASCII Comma Separated Value (CSV) format following Attachment 2. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 110300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-08-12-0000003 | Identify each asset that contains a low impact BES Cyber System according to Attachment 1, Section 3, if any (a discrete list of low impact BES Cyber Systems is not required). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2014-02-03 |  |  |  | 10300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-08-13-0000002 | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 20300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-08-13-0000003 | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 40300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3. | RP-2021-08-13-0000008 | The Responsible Entity shall, at least annually, assess adherence to its Critical Cyber Asset information protection program, document the assessment results, and implement an action plan to remediate deficiencies identified during the assessment. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 40300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1. | 5608 | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1. | 5639 | Planned or controlled interruption of electric supply to radial customers or some local network customers connected to or supplied by the Faulted Facility or by the affected area. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 23000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1. | RP-2021-06-16-0000025 | This process shall address the need to modify these limits, to modify the list of limits, and to modify the list of associated multiple contingencies. |  | RC | [11 empty] | RC | [10 empty] | 2008-10-01 |  | 2009-04-28 |  |  |  | 33100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1. | RP-2021-06-16-0000035 | Load forecast characteristics: • Median (50:50) forecast peak Load. • Load forecast uncertainty (reflects variability in the Load forecast due to weather and regional economic forecasts). • Load diversity. • Seasonal Load variations. • Daily demand modeling assumptions (firm, interruptible). • Contractual arrangements concerning curtailable/Interruptible Demand. |  | PCPA | [9 empty] | PA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  |  | 13100000 | RF-US |  |  | RF-US
3.1. | RP-2021-06-23-0000023 | When a FEPS is not available, the Transmission Owners shall remove the associated Element from service. |  | GO, TO, TOP |  |  |  |  | GO | [12 empty] | TO | TOP |  |  |  | 2011-10-01 |  | 2017-03-31 |  |  |  | 23100000 | WECC-US | [5 empty] | WECC-US
3.1. | RP-2021-06-24-0000019 | This does not apply to UFLS relays with time delay of one second or longerand a higher frequency setpoint applied to prevent the frequency fromstalling at less than 60 Hz when recovering from an underfrequency event. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2014-04-01 |  | 2017-12-31 |  |  |  | 23100000 | SERC-US |  |  |  | SERC-US
3.1. | RP-2021-06-24-0000046 | Simulate the removal of all elements that the Protection System andother automatic controls are expected to disconnect for eachContingency without operator intervention. The analyses shallinclude the impact of subsequent: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-07-01 |  | 2020-06-10 |  |  |  | 43100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1. | RP-2021-06-24-0000112 | Generating unit(s) operating limitations in cold weather to include: |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 73100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1. | RP-2021-06-24-0000133 | Operating limitations based on: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 10400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1. | RP-2021-06-24-0000141 | Operating limitations based on: |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1. | RP-2021-06-24-0000155 | Operating limitations based on: |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 23100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1. | RP-2021-07-02-0000002 | This process shall address the need to modify these limits, to modify the list of limits, and to modify the list of associated multiple contingencies. |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 33100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1. | RP-2021-07-09-0000031 | This does not apply to UFLS relays with time delay of one second or longer and a higher frequency setpoint applied to prevent the frequency from stalling atlessthan 60 Hz when recovering from an underfrequency event. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 23100000 | SERC-US |  |  |  | SERC-US
3.1. | RP-2021-07-12-0000025 | Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 33100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1. | RP-2021-07-12-0000038 | Simulate the removal of all elements that the Protection System and other automatic controls are expected to disconnect for each Contingency without operator intervention. The analyses shall include the impact of subsequent: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 43100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1. | RP-2021-07-15-0000011 | Neutral (residual) overcurrent. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 43100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.1. | RP-2021-06-24-0000037 | Tripping of generators where simulations show generatorbus voltages or high side of the generation step up (GSU)voltages are less than known or assumed minimumgenerator steady state or ride through voltage limitations.Include in the assessment any assumptions made. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-07-01 |  | 2020-06-10 |  |  |  | 61100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.1. | RP-2021-06-24-0000047 | Successful high speed (less than one second) reclosing andunsuccessful high speed reclosing into a Fault where highspeed reclosing is utilized. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-07-01 |  | 2020-06-10 |  |  |  | 71100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.1. | RP-2021-06-24-0000113 | capability and availability; |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 101100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.1. | RP-2021-06-24-0000134 | capability and availability; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 10500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.1. | RP-2021-06-24-0000142 | capability and availability; |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 41100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.1. | RP-2021-06-24-0000156 | capability and availability; |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 51100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.1. | RP-2021-07-09-0000050 | Tripping of generators where simulations show generator bus voltages or high side of the generation step up (GSU) voltages are less than known or assumed minimum generator steady state or ride through voltage limitations. Include in the assessment any assumptions made. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 61100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.1. | RP-2021-07-12-0000026 | Tripping of generators where simulations show generator bus voltages or high side of the generation step up (GSU) voltages are less than known or assumed minimum generator steady state or ride through voltage limitations. Include in the assessment any assumptions made. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 61100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.1. | RP-2021-07-12-0000039 | Successful high speed (less than one second) reclosing and unsuccessful high speed reclosing into a Fault where high speed reclosing is utilized. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 71100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.2. | RP-2021-06-24-0000038 | Tripping of Transmission elements where relay loadabilitylimits are exceeded. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-07-01 |  | 2020-06-10 |  |  |  | 61200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.2. | RP-2021-06-24-0000048 | Tripping of generators where simulations show generatorbus voltages or high side of the GSU voltages are less thanknown or assumed generator low voltage ride throughcapability. Include in the assessment any assumptionsmade. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-07-01 |  | 2020-06-10 |  |  |  | 71200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.2. | RP-2021-06-24-0000114 | fuel supply and inventory concerns; |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 101200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.2. | RP-2021-06-24-0000124 | fuel supply and inventory concerns; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 13100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.2. | RP-2021-06-24-0000143 | fuel supply and inventory concerns; |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 41200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.2. | RP-2021-06-24-0000157 | fuel supply and inventory concerns; |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 51200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.2. | RP-2021-07-09-0000051 | Tripping of Transmission elements where relay loadability limits are exceeded. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 61200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.2. | RP-2021-07-09-0000054 | Tripping of generators where simulations show generator bus voltages or high side of the GSU voltages are less than known or assumed generator low voltage ride through capability. Include in the assessment any assumptions made. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 71200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.2. | RP-2021-07-12-0000027 | Tripping of Transmission elements where relay loadability limits are exceeded. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 61200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.2. | RP-2021-07-12-0000040 | Tripping of generators where simulations show generator bus voltages or high side of the GSU voltages are less than known or assumed generator low voltage ride through capability. Include in the assessment any assumptions made. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 71200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.3. | RP-2021-06-24-0000049 | Tripping of Transmission lines and transformers wheretransient swings cause Protection System operation basedon generic or actual relay models. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-07-01 |  | 2020-06-10 |  |  |  | 71300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.3. | RP-2021-06-24-0000115 | fuel switching capabilities; and |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 101300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.3. | RP-2021-06-24-0000120 | current cold weather performance temperature determined by an engineering analysis. |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 101300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.3. | RP-2021-06-24-0000129 | fuel switching capabilities; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.3. | RP-2021-06-24-0000144 | fuel switching capabilities; and |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 41300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.3. | RP-2021-06-24-0000158 | fuel switching capabilities; and |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 51300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.3. | RP-2021-07-09-0000055 | Tripping of Transmission lines and transformers where transient swings cause Protection System operation based on generic or actual relay models. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 71300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.3. | RP-2021-07-12-0000041 | Tripping of Transmission lines and transformers where transient swings cause Protection System operation based on generic or actual relay models. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 71300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.4. | RP-2021-06-24-0000116 | environmental constraints. |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 101400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.4. | RP-2021-06-24-0000125 | environmental constraints |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 41100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.4. | RP-2021-06-24-0000145 | environmental constraints |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 41400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.1.4. | RP-2021-06-24-0000159 | environmental constraints. |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 51400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.2. | 5641 | Interruption of other network customers, (a) only if the system has already been adjusted, or is being adjusted, following at least one prior outage, or (b) if the real-time operating conditions are more adverse than anticipated in the corresponding studies |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 23100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.2. | RP-2021-06-16-0000036 | Resource characteristics: • Historic resource performance and any projected changes • Seasonal resource ratings • Modeling assumptions of firm capacity purchases from and sales to entities outside the Planning Coordinator area. • Resource planned outage schedules, deratings, and retirements. • Modeling assumptions of intermittent and energy limited resource such as wind and cogeneration. • Criteria for including planned resource additions in the analysis |  | PCPA | [9 empty] | PA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  |  | 13200000 | RF-US |  |  | RF-US
3.2. | RP-2021-06-23-0000024 | When FERAS is not available, then |  | GO, TO, TOP |  |  |  |  | GO | [12 empty] | TO | TOP |  |  |  | 2011-10-01 |  | 2017-03-31 |  |  |  | 23200000 | WECC-US | [5 empty] | WECC-US
3.2. | RP-2021-06-24-0000050 | Simulate the expected automatic operation of existing and planneddevices designed to provide dynamic control of electrical systemquantities when such devices impact the study area. These devicesmay include equipment such as generation exciter control and power system stabilizers, static var compensators, power flow controllers,and DC Transmission controllers. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-07-01 |  | 2020-06-10 |  |  |  | 43200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.2. | RP-2021-06-24-0000117 | Generating unit(s) minimum: |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 73200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.2. | RP-2021-06-24-0000126 | Generating unit(s) minimum: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 41200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.2. | RP-2021-06-24-0000146 | Generating unit(s) minimum: |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 13200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.2. | RP-2021-06-24-0000160 | Generating unit(s) minimum: |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 23200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.2. | RP-2021-07-01-0000014 | System reconfiguration through manual or automatic control or protection actions. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 23100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.2. | RP-2021-07-12-0000028 | Simulate the expected automatic operation of existing and planned devices designed to provide steady state control of electrical system quantities when such devices impact the study area. These devices may include equipment such as phase-shifting transformers, load tap changing transformers, and switched capacitors and inductors. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 33200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.2. | RP-2021-07-12-0000042 | Simulate the expected automatic operation of existing and planned devices designed to provide dynamic control of electrical system quantities when such devices impact the study area. These devices may include equipment such as generation exciter control and power system stabilizers, static var compensators, power flow controllers, and DC Transmission controllers. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 43200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.2. | RP-2021-07-15-0000012 | Phase undervoltage or overcurrent. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 43200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.2.1. | RP-2021-06-24-0000118 | design temperature; or |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 102100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.2.1. | RP-2021-06-24-0000127 | design temperature; or |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 41300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.2.1. | RP-2021-06-24-0000147 | design temperature; or |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 42100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.2.1. | RP-2021-06-24-0000161 | design temperature; or |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 52100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.2.2. | RP-2021-06-23-0000025 | Transmission Operators shall adjust the SOL and operate the facilities within established limits. |  | GO, TO, TOP |  |  |  |  | GO | [12 empty] | TO | TOP |  |  |  | 2011-10-01 |  | 2017-03-31 |  |  |  | 52200000 | WECC-US | [5 empty] | WECC-US
3.2.2. | RP-2021-06-23-0000028 | Transmission Operators shall adjust the SOL and operate the facilities within established limits. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2017-04-01 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf..4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. |  | 52200000 | WECC-US | [5 empty] | WECC-US
3.2.2. | RP-2021-06-24-0000119 | historical operating temperature; or |  | BA, GO, GOP, RC, TO | BA |  |  |  | GO | GOP | [5 empty] | RC | [14 empty] | For the purpose of this standard, the term “generating unit” means all Bulk Electric System generators. |  | 102200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.2.2. | RP-2021-06-24-0000128 | historical operating temperature; or |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 41400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.2.2. | RP-2021-06-24-0000148 | historical operating temperature; or |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 42200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.2.2. | RP-2021-06-24-0000162 | historical operating temperature; or |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 52200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.2.3. | RP-2021-06-24-0000130 | current cold weather performance temperature determined by anengineering analysis. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 42100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.2.3. | RP-2021-06-24-0000149 | current cold weather performance temperature determined by an engineering analysis. |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 42300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.2.3. | RP-2021-06-24-0000163 | current cold weather performance temperature determined by an engineering analysis. |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 52300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.3. | 5642 | System reconfiguration through manual or automatic control or protection actions. |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 23200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.3. | 6576 | Facilities consisting of one or more units connected to the BES at a common bus with total generation above 50 MVA gross nameplate rating. |  | PCPA | [9 empty] | PA | [12 empty] | 2013-10-01 |  | 2015-09-30 |  |  |  | 330000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.3. | RP-2021-06-16-0000023 | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-07-01 |  | 2009-04-28 |  |  |  | 23300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.3. | RP-2021-06-16-0000037 | Transmission limitations that prevent the delivery of generation reserves |  | PCPA | [9 empty] | PA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  |  | 13300000 | RF-US |  |  | RF-US
3.3. | RP-2021-06-29-0000006 | Transmission limitations that prevent the delivery of generation reserves |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 13300000 | RF-US |  |  | RF-US
3.3. | RP-2021-07-09-0000047 | Verify that identified coordination issue(s) associated with the proposed Protection System settings for the associated BES Elements are addressed prior to implementation. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.1.3. Distribution Provider (that owns Protection Systems identified in the Facilities section 4.2 below)4.2. Facilities: Protection Systems installed to detect and isolate Faults on BES Elements. |  | 13300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
3.3.1. | RP-2021-06-16-0000038 | Criteria for including planned Transmission Facility additions in the analysis |  | PCPA | [9 empty] | PA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  |  | 43100000 | RF-US |  |  | RF-US
3.4. | RP-2021-06-16-0000039 | Assistance from other interconnected systems including multi-area assessment considering Transmission limitations into the study area. |  | PCPA | [9 empty] | PA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  |  | 13400000 | RF-US |  |  | RF-US
4 | 79780000023 | The procedure for applying Contingency Reserve in practice. |  | RRO, RSG | [14 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780000250 | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 12400000 | NPCC-ON |  | NPCC-US
4 | 79780000290 | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 22400000 | NPCC-ON |  | NPCC-US
4 | 79780000303 | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780000310 | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780000315 | The controls used to secure dial-up accessible connections. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 25400000 | NPCC-ON |  | NPCC-US
4 | 79780000324 | A review of controls for default accounts, passwords, and network management community strings; and, |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  |  | 44000000 | NPCC-ON |  | NPCC-US
4 | 79780000334 | Procedures for the appropriate use of physical access controls as described in Requirement R3 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780000344 | Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780000361 | Procedures for the appropriate use of physical access controls as described in Requirement R3 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780000371 | Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780000415 | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780000425 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  |  | 84000000 | NPCC-ON |  | NPCC-US
4 | 79780000431 | Process for updating the Cyber Security Incident response plan within ninety calendar days of any changes. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780000446 | Where applicable, these facilities shall be redundant and diversely routed. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780000456 | Where applicable, these facilities shall be redundant and diversely routed. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2009-05-13 |  | 2015-09-30 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780000471 | Develop, maintain, and implement a set of plans for system restoration. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780000476 | Staffing levels for the emergency. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  |  | 44000000 | NPCC-ON |  | NPCC-US
4 | 79780000483 | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  |  | 74000000 | NPCC-ON |  | NPCC-US
4 | 79780000489 | Develop, maintain, and implement a set of plans for system restoration. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780000494 | Staffing levels for the emergency. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780000501 | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780000511 | Requesting emergency assistance from other Balancing Authorities. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780000522 | The Reliability Coordinator shall use EEA 2 to announce the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | 94000000 | NPCC-ON |  | NPCC-US
4 | 79780000532 | Requesting emergency assistance from other Balancing Authorities. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-09-30 |  |  |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780000543 | The Reliability Coordinator shall use EEA 2 to announce the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  | RC | [11 empty] | RC | [10 empty] | 2009-05-13 |  | 2011-09-30 |  |  |  | 94000000 | NPCC-ON |  | NPCC-US
4 | 79780000558 | If, in the judgment of the Regional Reliability Organization, after consultation with the Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load-Serving Entity in which a disturbance occurred, a final report is required, the affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load-Serving Entity shall prepare this report within 60 days. As a minimum, the final report shall have a discussion of the events and its cause, the conclusions reached, and recommendations to prevent recurrence of this type of event. The report shall be subject to Regional Reliability Organization approval. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-12-31 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780000568 | The affected Transmission Operators shall give high priority to restoration of off-site power to nuclear stations. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  |  | 114000000 | NPCC-ON |  | NPCC-US
4 | 79780000573 | Load is shed in neighboring areas, if required, to permit successful interconnected system restoration. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  |  | 115400000 | NPCC-ON |  | NPCC-US
4 | 79780000595 | A requirement to review and update the Regional BCP at least every five years. |  | RRO | [14 empty] | RRO | [7 empty] | 2011-05-23 |  | 2011-05-23 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780000601 | The plan shall include procedures and responsibilities for maintaining basic voice communication capabilities with other areas. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780000624 | Breaker duty and surge protection. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 21400000 | NPCC-ON |  | NPCC-US
4 | 79780000635 | Evidence that the assessment included steady-state, short-circuit, and dynamics studies as necessary to evaluate system performance in accordance with Reliability Standard TPL-001-0. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [14 empty] | 2007-06-18 |  | 2011-09-30 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780000646 | Each Transmission Owner shall develop mitigation measures to achieve sufficient clearances for the protection of the transmission facilities when it identifies locations on the ROW where the Transmission Owner is restricted from attaining the clearances specified in Requirement 1.2.1. |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780000653 | An outage shall be categorized as one of the following: |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780000694 | Operating limitations. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2012-12-31 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780000714 | Starting with all facilities in service and following any of the multiple Contingencies identified in Reliability Standard TPL-003 the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading Outages or uncontrolled separation shall not occur. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780000721 | Allowed uses of Special Protection Systems or Remedial Action Plans. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780000742 | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780000750 | Allowed uses of Special Protection Systems or Remedial Action Plans. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780000772 | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780000778 | Level of detail of system models used to determine SOLs. |  | RC | [11 empty] | RC | [10 empty] | 2008-05-29 |  | 2009-04-28 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780000801 | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780000807 | Level of detail of system models used to determine SOLs. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780000823 | Current and projected transmission uses |  | PCPA, RC | [9 empty] | PA |  | RC | [12 empty] | 2013-03-31 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780000846 | The type of limitation represented by the IROL (e.g., voltage collapse, angular stability). |  | RC | [11 empty] | RC | [10 empty] | 2009-01-01 |  | 2009-04-28 |  |  |  | 51400000 | NPCC-ON |  | NPCC-US
4 | 79780000849 | The Transmission Planner shall provide its SOLs (including the subset of SOLs that are IROLs) to its Planning Authority, Reliability Coordinators, Transmission Operators, and Transmission Service Providers that work within its Transmission Planning Area and to adjacent Transmission Planners. |  | TP | [19 empty] | TP |  |  | 2008-02-08 |  | 2009-04-28 |  |  |  | 54000000 | NPCC-ON |  | NPCC-US
4 | 79780000862 | The type of limitation represented by the IROL (e.g., voltage collapse, angular stability). |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 | [5 empty] | 51400000 | NPCC-ON |  | NPCC-US
4 | 79780000865 | The Transmission Planner shall provide its SOLs (including the subset of SOLs that are IROLs) to its Planning Authority, Reliability Coordinators, Transmission Operators, and Transmission Service Providers that work within its Transmission Planning Area and to adjacent Transmission Planners. |  | TP | [19 empty] | TP |  |  | 2009-04-29 | [5 empty] | 54000000 | NPCC-ON |  | NPCC-US
4 | 79780000932 | Interchange duration. |  | IA | [6 empty] | IA | [15 empty] | 2007-06-18 |  | 2014-09-30 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780000933 | Each Balancing Authority and Transmission Service Provider that received the Arranged Interchange information from the Interchange Authority for reliability assessment has provided approval. |  | IA | [6 empty] | IA | [15 empty] | 2007-06-18 |  | 2014-09-30 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001000 | System real and reactive reserves (actual versus required). |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001027 | System real and reactive reserves (actual versus required). |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001054 | System real and reactive reserves (actual versus required). |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001102 | Process for data provision when automated Real-Time system operating data is unavailable. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2009-08-05 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001110 | Voltage control, including the coordination of reactive resources for voltage control. |  | RC | [11 empty] | RC | [9 empty] | M1.1.4 Voltage control, including the coordination of reactive resources for voltage&lt;br/&gt;control. | 2007-06-18 |  | 2017-03-31 |  |  |  | 11400000 | NPCC-ON |  | NPCC-US
4 | 79780001140 | A description of how incomplete or so-called partial path transmission reservations are addressed. (Incomplete or partial path transmission reservations are those for which all transmission reservations necessary to complete the transmission path from ultimate source to ultimate sink are not identifiable due to differing reservation priorities, durations, or because the reservations have not all been made.) |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001161 | The identity of the Transmission Service Providers and Transmission Operators to which it provides data for use in calculating transfer or Flowgate capability. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780001171 | Each Planning Coordinator adjacent to the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 44000000 | NPCC-ON |  | NPCC-US
4 | 79780001194 | What recourse a customer has if the response is deemed unsatisfactory. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001201 | Require that CBM be preserved only on the Transmission Service Provider’s System where the Load-Serving Entity’s Load is located (i.e., CBM is an import quantity only). |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001240 | Require CBM values to be periodically updated (at least annually) and available to the Regional Reliability Organizations, NERC, and transmission users. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001265 | Forecast uncertainty in transmission system topology. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780001270 | Describe the conditions, if any, under which TRM may be available to the market as Non-Firm Transmission Service. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001288 | Require TRM values to be periodically updated (at least prior to each season — winter, spring, summer, and fall), as necessary, and made available to the Regional Reliability Organizations, NERC, and transmission users. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001297 | DC Transmission Line (overhead and underground): line parameters, Normal and Emergency Ratings, control parameters, rectifier data, and inverter data. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001311 | Dynamics data representing electrical Demand characteristics as a function of frequency and voltage. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001338 | Annual Peak hour forecast demands (summer and winter) in MW and annual Net Energy for load in GWh for at least five years and up to ten years into the future, as requested. |  | LSE, PCPA, RP | [7 empty] | LSE |  | PA |  |  |  | RP | [8 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001343 | Annual Peak hour forecast demands (summer and winter) in MW and annual Net Energy for load in GWh for at least five years and up to ten years into the future, as requested. |  | LSE, PCPA, RP | [7 empty] | LSE |  | PA |  |  |  | RP | [8 empty] | 2009-05-13 |  | 2016-06-30 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001359 | Periodicity and schedule of model and data verification and reporting. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001370 | Periodicity and schedule of model and data verification and reporting. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001375 | Method of verification, including date and conditions. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 15400000 | NPCC-ON |  | NPCC-US
4 | 79780001382 | A description of the manner in which Contingencies are identified for use in the TTC process. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2013-09-30 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001387 | If the Transmission Service Provider’s ATC calculation process involves a grouping of generation, the ATCID must identify how these generators participate in the group. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2013-09-30 |  |  |  | 15400000 | NPCC-ON |  | NPCC-US
4 | 79780001415 | For ATC Paths whose capacity uses jointly-owned or allocated Facilities, limit TTC for each Transmission Service Provider so the TTC does not exceed each Transmission Service Provider’s contractual rights. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780001430 | Models phase shifters in non-regulating mode, unless otherwise specified in the Available Transfer Capability Implementation Document (ATCID). |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 11400000 | NPCC-ON |  | NPCC-US
4 | 79780001444 | For an ATC Path whose TTC varies due to simultaneous interaction with one or more other paths, develop a nomogram describing the interaction of the paths and the resulting TTC under specified conditions |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780001461 | If the Transmission Service Provider’s AFC calculation process involves a grouping of generators, the ATCID must identify how these generators participate in the group. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 12400000 | NPCC-ON |  | NPCC-US
4 | 79780001476 | Any limiting Element/Contingency combination within the Transmission model that has been requested to be included by any other Transmission Service Provider using the Flowgate Methodology or Area Interchange Methodology, where: |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 21400000 | NPCC-ON |  | NPCC-US
4 | 79780001481 | Establish the TFC of each of the defined Flowgates as equal to: - For thermal limits, the System Operating Limit (SOL) of the Flowgate. - For voltage or stability limits, the flow that will respect the SOL of the Flowgate. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780001489 | Contains modeling data and system topology for the Facilities within its Reliability Coordinator’s Area. Equivalent representation of radial lines and Facilities161kV or below is allowed. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780001504 | The impact of any confirmed firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, including roll-over rights for Firm Transmission Service contracts having a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780001512 | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 74000000 | NPCC-ON |  | NPCC-US
4 | 79780001524 | If the Transmission Service Provider’s AFC calculation process involves a grouping of generators, the ATCID must identify how these generators participate in the group. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 12400000 | NPCC-ON |  | NPCC-US
4 | 79780001541 | Any limiting Element/Contingency combination within the Transmission model that has been requested to be included by any other Transmission Service Provider using the Flowgate Methodology or Area Interchange Methodology, where: |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21400000 | NPCC-ON |  | NPCC-US
4 | 79780001546 | Establish the TFC of each of the defined Flowgates as equal to: - For thermal limits, the System Operating Limit (SOL) of the Flowgate. - For voltage or stability limits, the flow that will respect the SOL of the Flowgate. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780001554 | Contains modeling data and system topology for the Facilities within its Reliability Coordinator’s Area. Equivalent representation of radial lines and Facilities161kV or below is allowed. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780001569 | The impact of any confirmed firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, including roll-over rights for Firm Transmission Service contracts having a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780001577 | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 74000000 | NPCC-ON |  | NPCC-US
4 | 79780001599 | A dispute resolution mechanism. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 91400000 | NPCC-ON |  | NPCC-US
4 | 79780001608 | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 93400000 | NPCC-ON |  | NPCC-US
4 | 79780001612 | Communications and training: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2008-11-26 |  | 2010-03-31 |  |  |  | 94000000 | NPCC-ON |  | NPCC-US
4 | 79780001616 | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 94400000 | NPCC-ON |  | NPCC-US
4 | 79780001627 | Training staff must be identified, and the staff must be competent in both knowledge of system operations and instructional capabilities. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-03-31 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780001644 | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall conduct an annual evaluation of the training program established in R1, to identify any needed changes to the training program and shall implement the changes identified. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection evidence (such as instructor observations, trainee feedback, supervisor feedback, course evaluations, learning assessments, or internalaudit results) that it performed an annual training program evaluation, as specified in R1.4 | 2013-04-01 |  | 2016-06-30 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001673 | Frequency. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 21340000 | NPCC-ON |  | NPCC-US
4 | 79780001693 | Provision for reporting Disturbance data in a format which is capable of being viewed, read and analyzed with a generic COMTRADE1 analysis tool, |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 44000000 | NPCC-ON |  | NPCC-US
4 | 79780001702 | Identification of the Regional Reliability Organization group responsible for the procedures and the process for approval of the procedures. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001739 | Generation protection. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  |  | 12400000 | NPCC-ON |  | NPCC-US
4 | 79780001745 | Assessment and documentation of the effectiveness of the design and implementation of the Regional UFLS program. This assessment shall be conducted periodically and shall (at least every five years or as required by changes in system conditions) include, but not be limited to: |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001759 | A summary of the findings. |  | DP, LSE, TO, TOP |  | DP | [5 empty] | LSE | [9 empty] | TO | TOP |  |  |  | 2007-06-18 |  | 2013-09-30 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001772 | Batteries. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2021-03-31 |  |  |  | 11400000 | NPCC-ON |  | NPCC-US
4 | 79780001775 | Schedule for system testing. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2021-03-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001783 | Requirements to demonstrate that the inadvertent operation of an SPS shall meet the same performance requirement (TPL-001-0, TPL-002-0, and TPL-003-0) as that required of the contingency for which it was designed, and not exceed TPL-003-0. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001801 | Discussion of any coordination problems found between a SPS and other protection and control systems. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780001817 | Batteries. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 11400000 | NPCC-ON |  | NPCC-US
4 | 79780001820 | Schedule for system testing. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001832 | Operational status. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2022-06-30 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780001846 | Time delay from initiation to trip signal. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001854 | Breaker operating times. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001861 | A summary of the findings. |  | DP, LSE, TOP |  | DP | [5 empty] | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001877 | Set transmission line relays on series compensated transmission lines so they do not operate at or below the maximum power transfer capability of the line, determined as the greater of:&lt;br/&gt;- 115% of the highest emergency rating of the series capacitor.&lt;br/&gt;- 115% of the maximum power transfer capability of the circuit (expressed in amperes), calculated in accordance with R1.3, using the full line inductive reactance. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780001972 | Planned outages of transmission elements. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-01-21 |  |  |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780001984 | Responding to IROL and SOL violations. |  | TOP | [18 empty] | TOP |  |  |  | 2009-01-22 |  | 2017-03-31 |  |  |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780002040 | Have established normal (pre-contingency) operating procedures in place. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780002046 | Address any planned upgrades needed to meet the performance requirements of Category A. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780002061 | Have established normal (pre-contingency) operating procedures in place. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780002067 | Address any planned upgrades needed to meet the performance requirements of Category A. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780002085 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780002091 | Address any planned upgrades needed to meet the performance requirements of Category B of Table I. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780002110 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780002116 | Address any planned upgrades needed to meet the performance requirements of Category B of Table I. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780002135 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780002141 | Address any planned upgrades needed to meet the performance requirements of Category C. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780002160 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780002166 | Address any planned upgrades needed to meet the performance requirements of Category C. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780002182 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780002188 | Consider all contingencies applicable to Category D. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780002197 | Inter-Regional reliability assessments to demonstrate that the performance of these systems is in compliance with NERC Reliability Standards TPL-001-0, TPL-002-0, TPL-003-0, TPL-004-0 and respective Regional transmission and generation criteria. These assessments shall also identify key reliability issues and the risks and uncertainties affecting Adequacy and Security. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780002203 | Adequacy of fuel supply and hydro conditions. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780002210 | Supply-side resources and their characteristics (existing and planned generator units, Ratings, performance characteristics, fuel types and availability, and real and reactive capabilities.) |  | RRO | [14 empty] | RRO | [9 empty] | 2009-04-15 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780002258 | The +/- voltage range with step-change in % for load-tap changing transformers. |  | GO | [22 empty] | 2007-08-02 |  | 2008-08-26 |  |  |  | 41400000 | NPCC-ON |  | NPCC-US
4 | 79780002273 | The +/- voltage range with step-change in % for load-tap changing transformers. |  | GO | [22 empty] | 2009-05-13 |  | 2010-09-15 |  |  |  | 41400000 | NPCC-ON |  | NPCC-US
4 | 79780002288 | The +/- voltage range with step-change in % for load-tap changing transformers. |  | GO | [22 empty] | 2010-09-16 |  | 2013-06-30 |  |  |  | 41400000 | NPCC-ON |  | NPCC-US
4 | 79780002303 | The +/- voltage range with step-change in % for load-tap changing transformers. |  | GO | [22 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 41400000 | NPCC-ON |  | NPCC-US
4 | 79780002350 | Supply-side resources and their characteristics (existing and planned generator units, Ratings, performance characteristics, fuel types and availability, and real and reactive capabilities.) |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780002360 | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 12400000 | NPCC-ON |  | NPCC-US
4 | 79780002378 | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780002401 | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 22400000 | NPCC-ON |  | NPCC-US
4 | 79780002414 | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780002421 | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780002426 | The controls used to secure dial-up accessible connections. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 25400000 | NPCC-ON |  | NPCC-US
4 | 79780002435 | A review of controls for default accounts, passwords, and network management community strings; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 44000000 | NPCC-ON |  | NPCC-US
4 | 79780002445 | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780002493 | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780002503 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  |  | 84000000 | NPCC-ON |  | NPCC-US
4 | 79780002509 | Process for updating the Cyber Security Incident response plan within thirty calendar days of any changes. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780002536 | A dispute resolution mechanism. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2014-01-21 |  |  |  | 91400000 | NPCC-ON |  | NPCC-US
4 | 79780002545 | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 93400000 | NPCC-ON |  | NPCC-US
4 | 79780002549 | Communications and training: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 94000000 | NPCC-ON |  | NPCC-US
4 | 79780002553 | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 94400000 | NPCC-ON |  | NPCC-US
4 | 79780002564 | Staffing levels for the emergency. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780002571 | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780002576 | Identification of each Blackstart Resource and its characteristics including but not limited to the following: the name of the Blackstart Resource, location, megawatt and megavar capacity, and type of unit. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780002586 | Synchronizing (re-energized sections of the System). |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  |  | 104000000 | NPCC-ON |  | NPCC-US
4 | 79780002621 | Descriptions of the elements of coordination of restoration plans with neighboring Reliability Coordinators. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780002673 | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780002682 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  |  | 84000000 | NPCC-ON |  | NPCC-US
4 | 79780002695 | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780002705 | Allowed uses of Special Protection Systems or Remedial Action Plans. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780002719 | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | 12400000 | NPCC-ON |  | NPCC-US
4 | 79780002737 | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780002760 | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2012-12-11 |  |  |  | 22400000 | NPCC-ON |  | NPCC-US
4 | 79780002773 | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780002780 | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780002785 | The controls used to secure dial-up accessible connections. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2011-02-01 |  |  |  | 25400000 | NPCC-ON |  | NPCC-US
4 | 79780002794 | A review of controls for default accounts, passwords, and network management community strings; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  |  | 44000000 | NPCC-ON |  | NPCC-US
4 | 79780002804 | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780002854 | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780002864 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 84000000 | NPCC-ON |  | NPCC-US
4 | 79780002870 | Process for updating the Cyber Security Incident response plan within thirty calendar days of any changes. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780002892 | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780002913 | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780002929 | Procedures for the appropriate use of physical access controls as described in Requirement R3 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780002939 | Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780002967 | Procedures for the appropriate use of physical access controls as described in Requirement R3 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780002968 | Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780002992 | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780003015 | The identity of the Transmission Service Providers and Transmission Operators to which it provides data for use in calculating transfer or Flowgate capability. |  | TSP | [20 empty] | TSP |  | 2010-09-16 | [5 empty] | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780003025 | Each Planning Coordinator adjacent to the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-09-16 | [5 empty] | 44000000 | NPCC-ON |  | NPCC-US
4 | 79780003055 | Models phase shifters in non-regulating mode, unless otherwise specified in the Available Transfer Capability Implementation Document (ATCID). |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 11400000 | NPCC-ON |  | NPCC-US
4 | 79780003062 | For an ATC Path whose TTC varies due to simultaneous interaction with one or more other paths, develop a nomogram describing the interaction of the paths and the resulting TTC under specified conditions |  | TOP | [18 empty] | TOP |  |  |  | 2010-09-16 |  | 2017-03-31 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780003077 | Process for data provision when automated Real-Time system operating data is unavailable. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2017-03-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780003158 | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780003164 | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780003169 | The controls used to secure dial-up accessible connections. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | 25400000 | NPCC-ON |  | NPCC-US
4 | 79780003178 | A review of controls for default accounts, passwords, and network management community strings; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | 44000000 | NPCC-ON |  | NPCC-US
4 | 79780003189 | The procedure for applying Contingency Reserve in practice. |  | RRO, RSG | [14 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780003226 | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780003249 | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2012-12-11 |  |  |  | 22400000 | NPCC-ON |  | NPCC-US
4 | 79780003262 | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780003269 | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780003274 | The controls used to secure dial-up accessible connections. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 25400000 | NPCC-ON |  | NPCC-US
4 | 79780003283 | A review of controls for default accounts, passwords, and network management community strings; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 44000000 | NPCC-ON |  | NPCC-US
4 | 79780003293 | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780003343 | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780003353 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 84000000 | NPCC-ON |  | NPCC-US
4 | 79780003359 | Process for updating the Cyber Security Incident response plan within thirty calendar days of any changes. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780003379 | Requesting emergency assistance from other Balancing Authorities. |  | BA | BA | [21 empty] | 2011-01-10 |  | 2012-09-12 |  |  |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780003390 | The Reliability Coordinator shall use EEA 2 to announce the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  | RC | [11 empty] | RC | [10 empty] | 2011-01-10 |  | 2012-09-12 |  |  |  | 94000000 | NPCC-ON |  | NPCC-US
4 | 79780003411 | Evidence that the assessment included steady-state, short-circuit, and dynamics studies as necessary to evaluate system performance under both normal and contingency conditions in accordance with Reliability Standards TPL-001-0, TPL-002-0, and TPL-003-0. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [14 empty] | 2011-01-10 |  | 2015-12-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780003425 | System real and reactive reserves (actual versus required). |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780003459 | Have established normal (pre-contingency) operating procedures in place. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780003465 | Address any planned upgrades needed to meet the performance requirements of Category A. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780003483 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780003489 | Address any planned upgrades needed to meet the performance requirements of Category B of Table I. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780003508 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780003514 | Address any planned upgrades needed to meet the performance requirements of Category B of Table I. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780003533 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780003539 | Address any planned upgrades needed to meet the performance requirements of Category C. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780003555 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780003561 | Consider all contingencies applicable to Category D. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780003622 | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780003628 | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780003633 | The controls used to secure dial-up accessible connections. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 25400000 | NPCC-ON |  | NPCC-US
4 | 79780003642 | A review of controls for default accounts, passwords, and network management community strings; and, |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 44000000 | NPCC-ON |  | NPCC-US
4 | 79780003653 | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780003659 | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780003664 | The controls used to secure dial-up accessible connections. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 25400000 | NPCC-ON |  | NPCC-US
4 | 79780003673 | A review of controls for default accounts, passwords, and network management community strings; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  |  | 44000000 | NPCC-ON |  | NPCC-US
4 | 79780003810 | System real and reactive reserves (actual versus required). |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780003833 | Develop, maintain, and implement a set of plans for system restoration. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780003839 | Staffing levels for the emergency. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  |  | 44000000 | NPCC-ON |  | NPCC-US
4 | 79780003844 | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  |  | 74000000 | NPCC-ON |  | NPCC-US
4 | 79780003856 | Staffing levels for the emergency. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780003861 | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780003901 | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780003926 | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780003964 | A description of the manner in which Contingencies are identified for use in the TTC process. |  | TSP | [20 empty] | TSP |  | 2013-09-27 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780003969 | If the Transmission Service Provider’s ATC calculation process involves a grouping of generation, the ATCID must identify how these generators participate in the group. |  | TSP | [20 empty] | TSP |  | 2013-10-01 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 15400000 | NPCC-ON |  | NPCC-US
4 | 79780003981 | A monthly load forecast for TTCs used in ATC calculations for months two through 13 months TTCs. |  | TOP | [18 empty] | TOP |  |  |  | 2013-10-01 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 31400000 | NPCC-ON |  | NPCC-US
4 | 79780003995 | For ATC Paths whose capacity uses jointly-owned or allocated Facilities, limit TTC for each Transmission Service Provider so the TTC does not exceed each Transmission Service Provider’s contractual rights. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780004042 | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780004065 | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780004089 | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780004098 | Staffing levels for the emergency. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780004134 | Develop, maintain, and implement a set of plans for system restoration. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780004137 | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  |  | 74000000 | NPCC-ON |  | NPCC-US
4 | 79780004141 | Staffing levels for the emergency. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  |  | 44000000 | NPCC-ON |  | NPCC-US
4 | 79780004186 | System real and reactive reserves (actual versus required). |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780004199 | Requesting emergency assistance from other Balancing Authorities. |  | BA | BA | [21 empty] | 2012-09-13 |  | 2017-03-31 |  |  |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780004208 | The Reliability Coordinator shall use EEA 2 to announce the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  |  | 94000000 | NPCC-ON |  | NPCC-US
4 | 79780004221 | Communications and training: |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 94000000 | NPCC-ON |  | NPCC-US
4 | 79780004226 | A dispute resolution mechanism. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2014-01-21 |  |  |  | 91400000 | NPCC-ON |  | NPCC-US
4 | 79780004233 | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 93400000 | NPCC-ON |  | NPCC-US
4 | 79780004242 | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 94400000 | NPCC-ON |  | NPCC-US
4 | 79780004256 | Communications and training: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 94000000 | NPCC-ON |  | NPCC-US
4 | 79780004343 | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 12400000 | NPCC-ON |  | NPCC-US
4 | 79780004372 | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:&lt;br/&gt;&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 22400000 | NPCC-ON |  | NPCC-US
4 | 79780004388 | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 22400000 | NPCC-ON |  | NPCC-US
4 | 79780004410 | The +/- voltage range with step-change in % for load-tap changing transformers. |  | GO | [22 empty] | 2013-07-01 |  | 2014-09-30 |  |  |  | 41400000 | NPCC-ON |  | NPCC-US
4 | 79780004449 | The procedure for applying Contingency Reserve in practice. |  | RRO, RSG | [14 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780004564 | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 12400000 | NPCC-ON |  | NPCC-US
4 | 79780004585 | Address any planned upgrades needed to meet the performance requirements of Category A. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780004589 | Have established normal (pre-contingency) operating procedures in place. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780004627 | Address any planned upgrades needed to meet the performance requirements of Category B of Table I. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780004639 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780004652 | Address any planned upgrades needed to meet the performance requirements of Category C. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780004664 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780004677 | Consider all contingencies applicable to Category D. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780004686 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780004692 | Address any planned upgrades needed to meet the performance requirements of Category C. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780004704 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780004718 | Address any planned upgrades needed to meet the performance requirements of Category C. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780004727 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780004742 | Consider all contingencies applicable to Category D. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780004751 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780004755 | Consider all contingencies applicable to Category D. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780004760 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780004812 |  |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780004841 |  |  | BA | BA | [23 empty] | 2006-11-01 |  |  |  | 74000000 | NPCC-ON |  | NPCC-US
4 | 79780004848 |  |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 104000000 | NPCC-ON |  | NPCC-US
4 | 79780004858 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780004869 |  |  | RC | [11 empty] | RC | [12 empty] | 2007-01-01 |  |  |  | 94000000 | NPCC-ON |  | NPCC-US
4 | 79780004890 |  |  | TOP | [18 empty] | TOP | [5 empty] | 2007-05-02 |  |  |  | 94000000 | NPCC-ON |  | NPCC-US
4 | 79780004895 |  |  | TOP | [18 empty] | TOP | [5 empty] | 2007-05-02 |  |  |  | 95400000 | NPCC-ON |  | NPCC-US
4 | 79780004912 |  |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-08-01 |  |  |  | 11400000 | NPCC-ON |  | NPCC-US
4 | 79780004918 |  |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-08-01 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780004944 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780004950 |  |  | TSP | [20 empty] | TSP |  |  |  | 2007-01-01 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780004957 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780004983 |  |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780005030 |  |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780005085 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2006-11-02 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780005113 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 12400000 | NPCC-ON |  | NPCC-US
4 | 79780005118 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780005119 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780005132 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2006-05-01 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780005142 |  |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2006-05-01 |  |  |  | 11400000 | NPCC-ON |  | NPCC-US
4 | 79780005145 |  |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2006-05-01 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780005209 |  |  | TOP | [18 empty] | TOP | [5 empty] | 2005-04-01 |  |  |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780005273 | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780005297 | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780005344 | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780005353 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 84000000 | NPCC-ON |  | NPCC-US
4 | 79780005387 | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780005396 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 84000000 | NPCC-ON |  | NPCC-US
4 | 79780005612 | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780005621 | Allowed uses of Remedial Action Schemes. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780005644 | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780005650 | Level of detail of system models used to determine SOLs. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780005664 | System real and reactive reserves (actual versus required). |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780005688 | If the Transmission Service Provider’s AFC calculation process involves a grouping of generators, the ATCID must identify how these generators participate in the group. |  | TSP | [20 empty] | TSP |  | 2017-04-01 | [5 empty] | 12400000 | NPCC-ON |  | NPCC-US
4 | 79780005701 | Any limiting Element/Contingency combination within the Transmission model that has been requested to be included by any other Transmission Service Provider using the Flowgate Methodology or Area Interchange Methodology, where: |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 21400000 | NPCC-ON |  | NPCC-US
4 | 79780005706 | Establish the TFC of each of the defined Flowgates as equal to: &lt;br/&gt;- For thermal limits, the System Operating Limit (SOL) of the Flowgate. &lt;br/&gt;&lt;br/&gt;- For voltage or stability limits, the flow that will respect the SOL of the Flowgate |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780005714 | Contains modeling data and system topology for the Facilities within its Reliability Coordinator’s Area. Equivalent representation of radial lines and Facilities161kV or below is allowed. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780005729 | The impact of any confirmed firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, including roll-over rights for Firm Transmission Service contracts having a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. (Footnote: A percentage less than that used in the Interconnection-wide congestion management procedure may be utilized.) |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780005737 | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 74000000 | NPCC-ON |  | NPCC-US
4 | 79780005756 | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12400000 | NPCC-ON |  | NPCC-US
4 | 79780005768 | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12400000 | NPCC-ON |  | NPCC-US
4 | 79780005792 | A dispute resolution mechanism. (Retirement approved by FERC effective January 21, 2014.) | [26 empty] | 2014-11-13 |  |  |  | 91400000 | NPCC-ON |  | NPCC-US
4 | 79780005801 | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 93400000 | NPCC-ON |  | NPCC-US
4 | 79780005805 | Communications and training: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  |  | 94000000 | NPCC-ON |  | NPCC-US
4 | 79780005809 | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 94400000 | NPCC-ON |  | NPCC-US
4 | 79780005818 | Have established normal (pre-contingency) operating procedures in place. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780005824 | Address any planned upgrades needed to meet the performance requirements of Category A. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780005839 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780005848 | Address any planned upgrades needed to meet the performance requirements of Category B of Table I. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780005864 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780005873 | Address any planned upgrades needed to meet the performance requirements of Category C. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780005889 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780005895 | Consider all contingencies applicable to Category D. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780005902 | Requirements to demonstrate that the inadvertent operation of a RAS shall meet the same performance requirement (TPL-001-0, TPL-002-0, and TPL-003-0) as that required of the contingency for which it was designed, and not exceed TPL-003-0. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780005920 | Discussion of any coordination problems found between a RAS and other protection and control systems. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780005938 | Batteries. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-04-01 |  | 2021-03-31 |  |  |  | 11400000 | NPCC-ON |  | NPCC-US
4 | 79780005942 | Schedule for system testing. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-01-25 |  | 2021-03-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780005950 | Time delay from initiation to trip signal. | [26 empty] | 2014-11-13 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780005958 | Breaker operating times. | [26 empty] | 2014-11-13 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780006030 | Models phase shifters in non-regulating mode, unless otherwise specified in the Available Transfer Capability Implementation Document (ATCID). |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 11400000 | NPCC-ON |  | NPCC-US
4 | 79780006163 | System security management (CIP-007); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780006172 | Incident response to a Cyber Security Incident. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2016-06-30 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780006176 | Incident handling procedures for Cyber Security Incidents. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.4. An example of evidence may include, but is not limited to, dated Cyber Security Incident response process(es) or procedure(s) that address incident handling (e.g., containment, eradication, recovery/incident resolution). | 2014-02-03 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780006192 | For each mitigation plan created or revised in Part 2.3, implement the plan within the timeframe specified in the plan, unless a revision to the plan or an extension to the timeframe specified in Part 2.3 is approved by the CIP Senior Manager or delegate. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780006199 | Review a summarization or sampling of logged events as determined by the Responsible Entity at intervals no greater than 15 calendar days to identify undetected Cyber Security Incidents. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 44000000 | NPCC-ON |  | NPCC-US
4 | 79780006203 | Change known default passwords, per Cyber Asset capability |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 54000000 | NPCC-ON |  | NPCC-US
4 | 79780006222 | Any logical network accessible ports; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 11400000 | NPCC-ON |  | NPCC-US
4 | 79780006226 | For a change that deviates from the existing baseline configuration: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780006239 | Document the results of the assessments conducted according to Parts 3.1, 3.2, and 3.3 and the action plan to remediate or mitigate vulnerabilities identified in the assessments including the planned date of completing the action plan and the execution status of any remediation or mitigation action items. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780006243 | Where technically feasible, perform authentication when establishing Dial-up Connectivity with applicable Cyber Assets. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.4. An example of evidence may include, but is not limited to, a documented process that describes how the Responsible Entity is providing authenticated access through each dial-up connection. | 2014-02-03 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780006251 | Monitor for unauthorized access through a physical access point into a Physical Security Perimeter. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 1.4 An example of evidence may include, but is not limited to, documentation of controls that monitor for unauthorized access through a physical access point into a Physical Security Perimeter. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780006264 | One or more processes to verify the successful completion of the backup processes in Part 1.3 and to address any backup failures. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780006280 | The visitor control program; | [23 empty] | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. |  |  | 2016-06-30 |  |  |  | 21400000 | NPCC-ON |  | NPCC-US
4 | 79780006303 | Criteria or process for verifying that personnel risk assessments performed for contractors or service vendors are conducted according to Parts 3.1 through 3.3. | [23 empty] | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s criteria or process for verifying contractors or service vendors personnel risk assessments. |  |  | 2016-06-30 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780006311 | Verify at least once every 15 calendar months that access to the designated storage locations for BES Cyber System Information, whether physical or electronic, are correct and are those that the Responsible Entity determines are necessary for performing assigned work functions. | [23 empty] | An example of evidence may include, but is not limited to, the documentation of the review that includes all of the following:&lt;br/&gt;1. A dated listing of authorizations for BES Cyber System information;&lt;br/&gt;2. Any privileges associated with the authorizations; and &lt;br/&gt;3. Dated evidence showing a verification of the authorizations and any privileges were confirmed correct and the minimum necessary for performing assigned work functions. |  |  | 2016-06-30 |  |  |  | 44000000 | NPCC-ON |  | NPCC-US
4 | 79780006315 | For termination actions, revoke the individual’s non-shared user accounts (unless already revoked according to Parts 5.1 or 5.3) within 30 calendar days of the effective date of the termination action. | [23 empty] | An example of evidence may include, but is not limited to, workflow or sign-off form showing access removal for any individual BES Cyber Assets and software applications as determined necessary to completing the revocation of access and dated within thirty calendar days of the termination actions. |  |  | 2016-06-30 |  |  |  | 54000000 | NPCC-ON |  | NPCC-US
4 | 79780006329 | Operating limitations. (Footnote: Such as temporary de-ratings of impaired equipment in accordance with good utility practice.) |  | GO | [22 empty] | 2013-01-01 | [5 empty] | 22400000 | NPCC-ON |  | NPCC-US
4 | 79780006331 | The process by which the Rating of equipment that comprises a Facility is determined. |  | GO | [22 empty] | 2011-11-17 | [5 empty] | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780006339 | Operating limitations. (Footnote: Such as temporary de-ratings of impaired equipment in accordance with good utility practice.) |  | TO | [22 empty] | 2013-01-01 | [5 empty] | 32400000 | NPCC-ON |  | NPCC-US
4 | 79780006341 | The process by which the Rating of equipment that comprises a Facility is determined. |  | TO | [22 empty] | 2011-11-17 | [5 empty] | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780006386 | Each Transmission Owner shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party verifier and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. |  | TO | [22 empty] | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:&lt;br/&gt;4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an &amp;quot;aggregate weighted value&amp;quot; exceeding 3000 according to the table below. The &amp;quot;aggregate weighted value&amp;quot; for a single station or substation is determined by summing the &amp;quot;weight value per line&amp;quot; shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;Voltage Value of a Line Weight Value per Line&lt;br/&gt;less than 200 kV (not applicable) (not applicable)&lt;br/&gt;200 kV to 299 kV 700&lt;br/&gt;300 kV to 499 kV 1300&lt;br/&gt;500 kV and above 0&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.&lt;br/&gt;4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. &lt;br/&gt;Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780006397 | Provisions to evaluate evolving physical threats, and their corresponding security measures, to the Transmission station(s), Transmission substation(s), or primary control center(s). |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:&lt;br/&gt;4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an &amp;quot;aggregate weighted value&amp;quot; exceeding 3000 according to the table below. The &amp;quot;aggregate weighted value&amp;quot; for a single station or substation is determined by summing the &amp;quot;weight value per line&amp;quot; shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;Voltage Value of a Line Weight Value per Line&lt;br/&gt;less than 200 kV (not applicable) (not applicable)&lt;br/&gt;200 kV to 299 kV 700&lt;br/&gt;300 kV to 499 kV 1300&lt;br/&gt;500 kV and above 0&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.&lt;br/&gt;4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. &lt;br/&gt;Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 54000000 | NPCC-ON |  | NPCC-US
4 | 79780006404 | Each Transmission Owner and Transmission Operator shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party reviewer and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:&lt;br/&gt;4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an &amp;quot;aggregate weighted value&amp;quot; exceeding 3000 according to the table below. The &amp;quot;aggregate weighted value&amp;quot; for a single station or substation is determined by summing the &amp;quot;weight value per line&amp;quot; shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.&lt;br/&gt;Voltage Value of a Line Weight Value per Line&lt;br/&gt;less than 200 kV (not applicable) (not applicable)&lt;br/&gt;200 kV to 299 kV 700&lt;br/&gt;300 kV to 499 kV 1300&lt;br/&gt;500 kV and above 0&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;&lt;br/&gt;4.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.&lt;br/&gt;4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. &lt;br/&gt;Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780006427 | Model structure and data for the excitation control system, including the closed loop voltage regulator if a closed loop voltage regulator is installed or the model structure and data for the plant volt/var control function system, |  | GO | [22 empty] | 2018-07-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following:&lt;br/&gt;4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: &lt;br/&gt;4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).&lt;br/&gt;4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.2 Generation in the Western Interconnection with the following characteristics:&lt;br/&gt;4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).&lt;br/&gt;4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.3 Generation in the ERCOT Interconnection with the following characteristics:&lt;br/&gt;4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).&lt;br/&gt;4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.4 For all Interconnections:&lt;br/&gt;• A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. |  | 21400000 | NPCC-ON |  | NPCC-US
4 | 79780006437 | Model structure and data for turbine/governor and load control or active power/frequency control, and |  | GO | [22 empty] | 2014-07-01 |  |  |  | 4.2. Facilities&lt;br/&gt;For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred to as an “applicable unit” that meet the following:&lt;br/&gt;4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics:&lt;br/&gt;4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).&lt;br/&gt;4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.2 Generation in the Western Interconnection with the following characteristics:&lt;br/&gt;4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).&lt;br/&gt;4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.3 Generation in the ERCOT Interconnection with the following characteristics:&lt;br/&gt;4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).&lt;br/&gt;4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). |  | 21400000 | NPCC-ON |  | NPCC-US
4 | 79780006446 | System operations |  | RC | [11 empty] | RC | [10 empty] | 2012-10-01 |  | 2019-06-30 |  |  |  | 11400000 | NPCC-ON |  | NPCC-US
4 | 79780006455 | Protection and control |  | TOP | [18 empty] | TOP |  |  |  | 2012-10-01 |  | 2019-06-30 |  |  |  | 21400000 | NPCC-ON |  | NPCC-US
4 | 79780006462 | Interchange scheduling and coordination |  | BA | BA | [21 empty] | 2012-10-01 |  | 2019-06-30 |  |  |  | 31400000 | NPCC-ON |  | NPCC-US
4 | 79780006493 | &lt;p&gt;Power source(s).&lt;/p&gt; |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2013-07-01 |  | 2019-03-31 |  |  |  | 12400000 | NPCC-ON |  | NPCC-US
4 | 79780006496 | Operating Procedures, including decision authority, for use in determining when to implement the Operating Plan for backup functionality |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780006528 | Provide its Planning Coordinator with an analysis demonstrating that no alternative load shedding solution is available that would allow the Distribution Provider or Transmission Owner to comply with UFLS Attachment C Table 2 or Attachment C Table 3. |  | DP, DP-UFLS, TO |  | DP | [20 empty] | 2016-01-01 |  | 2020-03-31 |  |  |  | 54000000 | NPCC-ON |  | NPCC-US
4 | 79780006540 | The location and amount of additional elements to be switched for voltage control that are coordinated with UFLS program tripping. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2013-04-29 |  | 2020-03-31 |  |  |  | 204000000 | NPCC-ON |  | NPCC-US
4 | 79780006558 | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 44000000 | NPCC-ON |  | NPCC-US
4 | 79780006570 | A description of how each of the following assumptions and criteria used in performing the assessment are addressed: |  | PCPA | [9 empty] | PA | [12 empty] | 2012-01-23 |  | 2020-12-14 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780006594 | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 440000 | NPCC-ON |  | NPCC-US
4 | 79780006626 | Real and reactive Load forecasts |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-01-01 | [5 empty] | 11400000 | NPCC-ON |  | NPCC-US
4 | 79780006633 | For each of the studies described in Requirement R2, Parts 2.1.1 and 2.1.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in System response :&lt;br/&gt;-Real and reactive forecasted Load.&lt;br/&gt;-Expected transfers.&lt;br/&gt;-Expected in service dates of new or modified Transmission Facilities.&lt;br/&gt;-Generation additions, retirements, or other dispatch scenarios.&lt;br/&gt;-Controllable Loads and Demand Side Management.&lt;br/&gt;-Duration or timing of known Transmission outages. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 21400000 | NPCC-ON |  | NPCC-US
4 | 79780006638 | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed annually and be supported by current or past studies as qualified in Requirement R2, Part2.6. The following studies are required: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780006659 | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 27400000 | NPCC-ON |  | NPCC-US
4 | 79780006670 | Those planning events in Table 1, that are expected to produce more severe System impacts on its portion of the BES, shall be identified and a list of those Contingencies to be evaluated for System performance in Requirement R3, Part 3.1 created. The rationale for those Contingencies selected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780006684 | Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES, shall be identified, and a list created of those Contingencies to be evaluated in Requirement R4, Part 4.1. The rationale for those Contingencies selected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 44000000 | NPCC-ON |  | NPCC-US
4 | 79780006694 | Current approved and projected Transmission uses. |  | PCPA | [9 empty] | PA | [12 empty] | 2013-04-01 |  | 2020-12-14 |  |  |  | 14400000 | NPCC-ON |  | NPCC-US
4 | 79780006710 | Each Transmission Service Provider included in the Arranged Interchange, and |  | BA | BA | [21 empty] | 2014-06-30 |  | 2021-03-31 |  |  |  | 54000000 | NPCC-ON |  | NPCC-US
4 | 79780006721 | Each Generator Operator within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780006727 | Each adjacent Transmission Operator asynchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  |  | 44000000 | NPCC-ON |  | NPCC-US
4 | 79780006731 | Each Generator Operator that operates Facilities within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 54000000 | NPCC-ON |  | NPCC-US
4 | 79780006745 | Each Transmission Owner shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party verifier and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. |  | TO | [22 empty] | 2015-10-01 |  | 2015-10-01 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780006753 | Provisions to evaluate evolving physical threats, and their corresponding security measures, to the Transmission station(s), Transmission substation(s), or primary control center(s). |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  |  | 54000000 | NPCC-ON |  | NPCC-US
4 | 79780006757 | Each Transmission Owner and Transmission Operator shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party reviewer and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780006768 | Study assumptions, system performance, alternatives considered, and coordinated recommendations. While these studies may be performed independently, the results shall be evaluated and coordinated by the entities involved. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2014-11-06 |  | 2021-03-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780006782 | Monthly and annual peak hour controllable and dispatchable Demand Side Management under the control or supervision of the System Operator in megawatts for the prior calendar year. Three values shall be reported for each hour: 1) the committed megawatts (the amount under control or supervision), 2) the dispatched megawatts (the amount, if any, activated for use by the System Operator), and 3) the realized megawatts (the amount of actual demand reduction). |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780006783 | A request to provide any or all of the following forecast data, as necessary: |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2015-04-27 |  | 2016-09-30 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780006787 | Annual forecast Net Energy for Load in gigawatthours for ten calendar years into the future. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 14400000 | NPCC-ON |  | NPCC-US
4 | 79780006793 | How the controllable and dispatchable Demand Side Management forecast compares to actual controllable and dispatchable Demand Side Management for the prior calendar year and, if applicable, how the assumptions and methods for future forecasts were adjusted. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 15400000 | NPCC-ON |  | NPCC-US
4 | 79780006801 | A schedule for submission of data at least once every 13 calendar months. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-07-01 |  |  |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. |  | 12400000 | NPCC-ON |  | NPCC-US
4 | 79780006808 | Guidelines to resolve the unacceptable differences in performance identified under Part 1.3. |  | PCPA | [9 empty] | PA | [12 empty] | 2014-05-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780006812 | Exchange of information including planned and unplanned outage information to support its Operational Planning Analyses and Real-time Assessments. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-26 | [5 empty] | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780006822 | Define the process to coordinate the resolution of identified outage conflicts with its Transmission Operators and Balancing Authorities, and other Reliability Coordinators. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-26 | [5 empty] | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780006826 | The deadline by which the respondent is to provide the indicated data. |  | TOP | [18 empty] | TOP | [5 empty] | 2016-01-26 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780006830 | The deadline by which the respondent is to provide the indicated data. |  | BA | BA | [23 empty] | 2016-01-26 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780006834 | The deadline by which the respondent is to provide the indicated data. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-26 |  | 2021-03-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780006838 | The deadline by which the respondent is to provide the indicated data. |  | BA | BA | [21 empty] | 2016-01-26 |  | 2021-03-31 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780006855 | Redispatch of generation request; |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 12400000 | NPCC-ON |  | NPCC-US
4 | 79780006866 | environmental constraints. |  | BA | BA | [21 empty] | 2017-04-01 | [5 empty] | 22340000 | NPCC-ON |  | NPCC-US
4 | 79780006867 | Public appeals for voluntary Load reductions; |  | BA | BA | [21 empty] | 2017-04-01 | [5 empty] | 22400000 | NPCC-ON |  | NPCC-US
4 | 79780006907 | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 93400000 | NPCC-ON |  | NPCC-US
4 | 79780006911 | Communications and training Administrative elements: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2014-11-04 |  | 2021-03-31 |  |  |  | 94000000 | NPCC-ON |  | NPCC-US
4 | 79780006916 | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 94400000 | NPCC-ON |  | NPCC-US
4 | 79780006920 | One or more processes to verify the successful completion of the backup processes in Part 1.3 and to address any backup failures. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.4. An example of evidence may include, but is not limited to, logs, workflow or other documentation confirming that the backup process completed successfully and backup failures, if any, were addressed. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780006941 | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 44000000 | NPCC-ON |  | NPCC-US
4 | 79780006963 | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct an evaluation each calendar year of the training program established in Requirement R1 to identify any needed changes to the training program and shall implement the changes identified. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | M1.4 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection evidence (such as instructor observations, trainee feedback, supervisor feedback, course evaluations, learning assessments, or internal audit results) that it performed an evaluation of its training program each calendar year, as specified in Requirement R1 part 1.4. | 2014-06-19 | [5 empty] | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780006968 | Each Transmission Owner shall conduct an evaluation each calendar year of the training program established in Requirement R2 to identify any needed changes to the training program and shall implement the changes identified. |  | TO | [21 empty] | M2.4 Each Transmission Owner shall have available for inspection evidence (such as instructor observations, trainee feedback, supervisor feedback, course evaluations, learning assessments, or internal audit results) that it performed an evaluation of its training program each calendar year, as specified in Requirement R2 part 2.4. | 2014-06-19 | [5 empty] | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780007046 | Cyber Security Incident response |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12400000 | NPCC-ON |  | NPCC-US
4 | 79780007050 | The deadline by which the respondent is to provide the indicated data. |  | RC | [11 empty] | RC | [10 empty] | 2017-01-01 |  | 2021-03-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780007057 | Control of voltage, including the coordination of reactive resources. |  | RC | [11 empty] | RC | [12 empty] | 2016-01-26 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780007068 | Voltage stability limits; and |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 11400000 | NPCC-ON |  | NPCC-US
4 | 79780007074 | Planned outages; |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 12400000 | NPCC-ON |  | NPCC-US
4 | 79780007086 | Planned outages; |  | TSP | [20 empty] | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 21400000 | NPCC-ON |  | NPCC-US
4 | 79780007109 | Capacity and energy reserve requirements, including deliverability capability |  | BA | BA | [21 empty] | 2016-01-26 | [5 empty] | 44000000 | NPCC-ON |  | NPCC-US
4 | 79780007132 | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2021-01-01 |  | 2019-06-30 |  | 4.2. Facilities:&lt;br/&gt;4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780007181 | One or more BES Elements that are part of an Interconnection Reliability Operating Limit (IROL). |  | PCPA, RC | [9 empty] | PA |  | RC | [10 empty] | 2016-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 51400000 | NPCC-ON |  | NPCC-US
4 | 79780007187 | Re-evaluate all BES Elements at least once every five calendar years in accordance with Parts 5.1 and 5.2, and notify owners in accordance with Part 5.3 to implement the re-evaluated list of BES Elements as per the Implementation Plan. |  | PCPA, RC | [9 empty] | PA |  | RC | [10 empty] | 2015-11-24 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 54000000 | NPCC-ON |  | NPCC-US
4 | 79780007191 | Frequency of any one of the voltage(s) in Requirement R6, Part 6.1. |  | TO | [22 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780007195 | Frequency of at least one of the voltages in Requirement R7, Part 7.1. |  | GO | [22 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 74000000 | NPCC-ON |  | NPCC-US
4 | 79780007205 | FR and DDR data will be provided in electronic files that are formatted in conformance with C37.111, (IEEE Standard for Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 or later. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 114000000 | NPCC-ON |  | NPCC-US
4 | 79780007212 | The visitor control program; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21400000 | NPCC-ON |  | NPCC-US
4 | 79780007223 | Any logical network accessible ports; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 11400000 | NPCC-ON |  | NPCC-US
4 | 79780007227 | For a change that deviates from the existing baseline configuration: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.4. An example of evidence may include, but is not limited to, a list of cyber security controls verified or tested along with the dated test results. | 2016-03-31 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780007240 | Document the results of the assessments conducted according to Parts 3.1, 3.2, and 3.3 and the action plan to remediate or mitigate vulnerabilities identified in the assessments including the planned date of completing the action plan and the execution status of any remediation or mitigation action items. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.4. An example of evidence may include, but is not limited to, a document listing the results or the review or assessment, a list of action items, documented proposed dates of completion for the action plan, and records of the status of the action items (such as minutes of a status meeting, updates in a work order system, or a spreadsheet tracking the action items). | 2016-07-01 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780007264 | Verify at least once every 15 calendar months that access to the designated storage locations for BES Cyber System Information, whether physical or electronic, are correct and are those that the Responsible Entity determines are necessary for performing assigned work functions. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.4. An example of evidence may include, but is not limited to, the documentation of the review that includes all of the following:&lt;br/&gt;1. A dated listing of authorizations for BES Cyber System information;&lt;br/&gt;2. Any privileges associated with the authorizations; and &lt;br/&gt;3. Dated evidence showing a verification of the authorizations and any privileges were confirmed correct and the minimum necessary for performing assigned work functions. | 2017-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 44000000 | NPCC-ON |  | NPCC-US
4 | 79780007268 | For termination actions, revoke the individual’s non-shared user accounts (unless already revoked according to Parts 5.1 or 5.3) within 30 calendar days of the effective date of the termination action. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.4 An example of evidence may include, but is not limited to, workflow or sign-off form showing access removal for any individual BES Cyber Assets and software applications as determined necessary to completing the revocation of access and dated within thirty calendar days of the termination actions. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 54000000 | NPCC-ON |  | NPCC-US
4 | 79780007291 | For each mitigation plan created or revised in Part 2.3, implement the plan within the timeframe specified in the plan, unless a revision to the plan or an extension to the timeframe specified in Part 2.3 is approved by the CIP Senior Manager or delegate. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.4. An example of evidence may include, but is not limited to, records of implementation of mitigations. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780007309 | Review a summarization or sampling of logged events as determined by the Responsible Entity at intervals no greater than 15 calendar days to identify undetected Cyber Security Incidents. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.4. Examples of evidence may include, but are not limited to, documentation describing the review, any findings from the review (if any), and dated documentation showing the review occurred. | 2016-07-15 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 44000000 | NPCC-ON |  | NPCC-US
4 | 79780007313 | Change known default passwords, per Cyber Asset capability |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.4. Examples of evidence may include, but are not limited to:&lt;br/&gt;• Records of a procedure that passwords are changed when new devices are in production; or&lt;br/&gt;• Documentation in system manuals or other vendor documents showing default vendor passwords were generated pseudo-randomly and are thereby unique to the device. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 54000000 | NPCC-ON |  | NPCC-US
4 | 79780007342 | Monitor for unauthorized access through a physical access point into a Physical Security Perimeter. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.4. An example of evidence may include, but is not limited to, documentation of controls that monitor for unauthorized access through a physical access point into a Physical Security Perimeter. | 2016-07-01 | [5 empty] | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780007356 | Frequency. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 54000000 | NPCC-ON |  | NPCC-US
4 | 79780007364 | Document additional triggers and deviations from the settings in 6.3.2 and 6.3.3 when local conditions dictate. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780007404 | Major transmission interfaces. |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 72400000 | NPCC-ON |  | NPCC-US
4 | 79780007414 | Oscillation of Frequency. |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 93400000 | NPCC-ON |  | NPCC-US
4 | 79780007418 | Frequency. |  | RC | [11 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 104000000 | NPCC-ON |  | NPCC-US
4 | 79780007423 | Monthly verification of time synchronization (if the loss of time synchronization is not monitored to a 24/7 control center). |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 144000000 | NPCC-ON |  | NPCC-US
4 | 79780007435 | Operational Status.Operational Status. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 174000000 | NPCC-ON |  | NPCC-US
4 | 79780007475 | Each Generator Operator within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780007481 | System security management (CIP-007); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11400000 | NPCC-ON |  | NPCC-US
4 | 79780007492 | Each adjacent Transmission Operator asynchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  |  | 44000000 | NPCC-ON |  | NPCC-US
4 | 79780007496 | Each Generator Operator that operates Facilities within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 54000000 | NPCC-ON |  | NPCC-US
4 | 79780007519 | Criteria or process for verifying that personnel risk assessments performed for contractors or service vendors are conducted according to Parts 3.1 through 3.3. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.4. An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s criteria or process for verifying contractors or service vendors personnel risk assessments. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780007570 | Communicate with the other owner(s) of the electrically joined Facilities regarding revised Protection System settings resulting from unforeseen circumstances that arise during implementation or commissioning, Misoperation investigations, maintenance activities, or emergency replacements required as a result of Protection System component failure. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.1.3. Distribution Provider (that owns Protection Systems identified in the Facilities section 4.2 below)&lt;br/&gt;4.2. Facilities: Protection Systems installed to detect and isolate Faults on BES Elements. |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780007588 | &lt;p&gt;Monthly and annual peak hour controllable and dispatchable Demand Side Management under the control or supervision of the System Operator in megawatts for the prior calendar year. Three values shall be reported for each hour: 1) the committed megawatts (the amount under control or supervision), 2) the dispatched megawatts (the amount, if any, activated for use by the System Operator), and 3) the realized megawatts (the amount of actual demand reduction).&lt;/p&gt; |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | &lt;p&gt;This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.”&lt;/p&gt; |  | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780007589 | A request to provide any or all of the following forecast data, as necessary: |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-02-18 |  | 2021-03-31 |  |  |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780007593 | &lt;p&gt;Annual forecast Net Energy for Load in gigawatthours for ten calendar years into the future.&lt;/p&gt; |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | &lt;p&gt;This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.”&lt;/p&gt; |  | 14400000 | NPCC-ON |  | NPCC-US
4 | 79780007599 | &lt;p&gt;How the controllable and dispatchable Demand Side Management forecast compares to actual controllable and dispatchable Demand Side Management for the prior calendar year and, if applicable, how the assumptions and methods for future forecasts were adjusted.&lt;/p&gt; |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | &lt;p&gt;This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.”&lt;/p&gt; |  | 15400000 | NPCC-ON |  | NPCC-US
4 | 79780007642 | An encroachment due to vegetation growth into the MVCD that caused a vegetation-related Sustained Outage. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:&lt;br/&gt;4.1.1. Applicable Transmission Owners&lt;br/&gt;4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.&lt;br/&gt;4.1.2. Applicable Generator Owners&lt;br/&gt;4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. &lt;br/&gt;4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.2.1. Each overhead transmission line operated at 200kV or higher.&lt;br/&gt;4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.&lt;br/&gt;4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.&lt;br/&gt;4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. &lt;br/&gt;4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:&lt;br/&gt;4.3.1.1. Operated at 200kV or higher; or&lt;br/&gt;4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or&lt;br/&gt;4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780007646 | An encroachment due to vegetation growth into the line MVCD that caused a vegetation-related Sustained Outage. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:&lt;br/&gt;4.1.1. Applicable Transmission Owners&lt;br/&gt;4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.&lt;br/&gt;4.1.2. Applicable Generator Owners&lt;br/&gt;4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. &lt;br/&gt;4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.2.1. Each overhead transmission line operated at 200kV or higher.&lt;br/&gt;4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.&lt;br/&gt;4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.&lt;br/&gt;4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. &lt;br/&gt;4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:&lt;br/&gt;4.3.1.1. Operated at 200kV or higher; or&lt;br/&gt;4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or&lt;br/&gt;4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780007652 | Crew or contractor availability/Mutual assistance agreements |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:&lt;br/&gt;4.1.1. Applicable Transmission Owners&lt;br/&gt;4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.&lt;br/&gt;4.1.2. Applicable Generator Owners&lt;br/&gt;4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. &lt;br/&gt;4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.2.1. Each overhead transmission line operated at 200kV or higher.&lt;br/&gt;4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.&lt;br/&gt;4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.&lt;br/&gt;4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. &lt;br/&gt;4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:&lt;br/&gt;4.3.1.1. Operated at 200kV or higher; or&lt;br/&gt;4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or&lt;br/&gt;4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 74000000 | NPCC-ON |  | NPCC-US
4 | 79780007670 | For an ATC Path whose TTC varies due to simultaneous interaction with one or more other paths, develop a nomogram describing the interaction of the paths and the resulting TTC under specified conditions. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780007697 | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 440000 | NPCC-ON |  | NPCC-US
4 | 79780007754 | Except for limited impact RAS, the possible inadvertent operation of the RAS, resulting from any single RAS component malfunction satisfies all of the following: |  | PCPA | [9 empty] | PA | [12 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 41400000 | NPCC-ON |  | NPCC-US
4 | 79780007767 | The RAS operation resulted in any unintended or adverse BES response. |  | DP, GO, PCPA, RC, TO |  | DP |  |  | GO |  |  |  |  | PA |  | RC | [10 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 51400000 | NPCC-ON |  | NPCC-US
4 | 79780007779 | Require its operating personnel that issue a written or oral single-party to multiple-party burst Operating Instruction to confirm or verify that the Operating Instruction was received by at least one receiver of the Operating Instruction. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2015-06-22 | [5 empty] | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780007795 | Each Generator Operator within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2016-10-28 | [5 empty] | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780007802 | Each adjacent Transmission Operator asynchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2016-10-28 | [5 empty] | 44000000 | NPCC-ON |  | NPCC-US
4 | 79780007807 | Each Generator Operator that operates Facilities within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2016-10-28 | [5 empty] | 54000000 | NPCC-ON |  | NPCC-US
4 | 79780007892 | Power source(s). |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2019-04-01 | [5 empty] | 12400000 | NPCC-ON |  | NPCC-US
4 | 79780007895 | Operating Procedures, including decision authority, for use in determining when to implement the Operating Plan for backup functionality. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780007915 | Criteria for sharing information regarding restoration with neighboring Reliability Coordinators and with Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2018-03-26 | [5 empty] | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780007935 | Identification of each Blackstart Resource and its characteristics including but not limited to the following: the name of the Blackstart Resource, location, megawatt and megavar capacity, and type of unit. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780007961 | Synchronizing (re-energized sections of the System). |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 84000000 | NPCC-ON |  | NPCC-US
4 | 79780007992 | System security management (CIP-007); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11400000 | NPCC-ON |  | NPCC-US
4 | 79780008001 | Cyber Security Incident response; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12400000 | NPCC-ON |  | NPCC-US
4 | 79780008026 | Obtain and utilize status, voltages, and flow data for Facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator; |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-17 |  | 2021-03-31 |  |  |  | 104000000 | NPCC-ON |  | NPCC-US
4 | 79780008091 | Disclosure by vendors of known vulnerabilities related to the products or services provided to the Responsible Entity; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and&lt;br/&gt;4.1.2.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and&lt;br/&gt;4.2.1.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers&lt;br/&gt;4.2.2.1. All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-013-1:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the identification and categorization process required by CIP-002-5, or any subsequent version of that Reliability Standard. |  | 12400000 | NPCC-ON |  | NPCC-US
4 | 79780008100 | Where technically feasible, perform authentication when establishing Dial-up Connectivity with applicable Cyber Assets. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a documented process that describes how the Responsible Entity is providing authenticated access through each dial-up connection. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-005-6:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780008106 | Have one or more methods for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation of the methods used to determine active vendor remote access (including Interactive Remote Access and system-to-system remote access), such as: &lt;br/&gt;• Methods for accessing logged or monitoring information to determine active vendor remote access sessions;&lt;br/&gt;• Methods for monitoring activity (e.g. connection tables or rule hit counters in a firewall, or user activity monitoring) or open ports (e.g. netstat or related commands to display currently active ports) to determine active system to system remote access sessions; or&lt;br/&gt;• Methods that control vendor initiation of remote access such as vendors calling and requesting a second factor in order to initiate remote access. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-005-6:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780008113 | Any logical network accessible ports; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 11400000 | NPCC-ON |  | NPCC-US
4 | 79780008117 | For a change that deviates from the existing baseline configuration: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a list of cyber security controls verified or tested along with the dated test results. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780008135 | Document the results of the assessments conducted according to Parts 3.1, 3.2, and 3.3 and the action plan to remediate or mitigate vulnerabilities identified in the assessments including the planned date of completing the action plan and the execution status of any remediation or mitigation action items. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a document listing the results or the review or assessment, a list of action items, documented proposed dates of completion for the action plan, and records of the status of the action items (such as minutes of a status meeting, updates in a work order system, or a spreadsheet tracking the action items). | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780008177 | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-3 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 44000000 | NPCC-ON |  | NPCC-US
4 | 79780008343 | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2019-06-30 |  |  |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780008350 | Be revised if situations beyond the control of the responsible entity determined in Requirement R1 prevent implementation of the CAP within the timetable for implementation provided in Part 7.3. The revised CAP shall document the following, and be updated at least once every 12 calendar months until implemented: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  |  | 74000000 | NPCC-ON |  | NPCC-US
4 | 79780008362 | The supplemental GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  |  | 84000000 | NPCC-ON |  | NPCC-US
4 | 79780008371 | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2019-06-30 |  |  |  | 104000000 | NPCC-ON |  | NPCC-US
4 | 79780008400 | System operations |  | RC | [11 empty] | RC | [10 empty] | 2019-07-01 | [5 empty] | 11400000 | NPCC-ON |  | NPCC-US
4 | 79780008410 | Protection and control |  | TOP | [18 empty] | TOP |  |  |  | 2019-07-01 | [5 empty] | 21400000 | NPCC-ON |  | NPCC-US
4 | 79780008418 | Interchange scheduling and coordination |  | BA | BA | [21 empty] | 2019-07-01 | [5 empty] | 31400000 | NPCC-ON |  | NPCC-US
4 | 79780008456 | Known commitments for Firm Transmission Service and Interchange. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP | [8 empty] | 11400000 | NPCC-ON |  | NPCC-US
4 | 79780008463 | When known outage(s) of generation or Transmission Facility(ies) are planned in the Near-Term Planning Horizon, the impact of selected known outages on System performance shall be assessed. These known outage(s) shall be selected for assessment consistent with a documented outage coordination procedure or technical rationale by the Planning Coordinator or Transmission Planner. Known outage(s) shall not be excluded solely based upon outage duration. The assessment shall be performed for the P0 and P1 categories identified in Table 1 with the System peak or Off-Peak conditions that the System is expected to experience when the known outage(s) are planned. This assessment shall include, at a minimum known outages expected to produce more severe System impacts on the Planning Coordinator or Transmission Planner’s portion of the BES. Past or current studies may support the selection of known outage(s), if the study(s) has comparable post-Contingency System conditions and configuration such as those following P3 or P6 category events in Table 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP | [8 empty] | 21400000 | NPCC-ON |  | NPCC-US
4 | 79780008468 | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed annually and be supported by current or past studies as qualified in Requirement R2, Part2.6. The following studies are required: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-04-13 |  | 2020-06-10 |  |  |  | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780008472 | When known outage(s) of generation or Transmission Facility(ies) are planned in the Near-Term Planning Horizon, the impact of selected known outages on System performance shall be assessed. These known outage(s) shall be selected for assessment consistent with a documented outage coordination procedure or technical rationale by the Planning Coordinator or Transmission Planner. Known outage(s) shall not be excluded solely based upon outage duration. The assessment shall be performed for the P1 categories identified in Table 1 with the System peak or Off-Peak conditions that the System is expected to experience when the known outage(s) are planned. This assessment shall include, at a minimum, those known outages expected to produce more severe System impacts on the Planning Coordinator or Transmission Planner’s portion of the BES. Past or current studies may support the selection of known outage(s), if the study(s) has comparable post-Contingency System conditions and configuration such as those following P3 or P6 category events in Table 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP | [8 empty] | 24400000 | NPCC-ON |  | NPCC-US
4 | 79780008480 | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP | [8 empty] | 27400000 | NPCC-ON |  | NPCC-US
4 | 79780008498 | Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES shall be identified, and a list of those Contingencies to be evaluated for System performance in Requirement R3, Part 3.1 created. The rationale for those Contingencies selected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-04-13 |  | 2020-06-10 |  |  |  | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780008525 | &lt;p&gt;Incident handling procedures for Cyber Security Incidents.&lt;/p&gt; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | &lt;p&gt;An example of evidence may include, but is not limited to, dated Cyber Security Incident response process(es) or procedure(s) that address incident handling (e.g., containment, eradication, recovery/incident resolution).&lt;/p&gt; | 2019-06-20 |  |  |  | &lt;p&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes.&lt;/p&gt; |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780008568 | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2020-10-05 |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780008573 | Be revised if situations beyond the control of the responsible entity determined in Requirement R1 prevent implementation of the CAP within the timetable for implementation provided in Part 7.3. The revised CAP shall document the following, and be updated at least once every 12 calendar months until implemented: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2020-10-05 |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 74000000 | NPCC-ON |  | NPCC-US
4 | 79780008585 | The supplemental GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2020-10-05 |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 84000000 | NPCC-ON |  | NPCC-US
4 | 79780008601 | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2020-10-05 |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 104000000 | NPCC-ON |  | NPCC-US
4 | 79780008684 | System security management (CIP-007); | [28 empty] | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service &lt;br/&gt;&lt;br/&gt;equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11400000 | NPCC-ON |  | NPCC-US
4 | 79780008694 | Cyber Security Incident response; | [28 empty] | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service &lt;br/&gt;&lt;br/&gt;equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12400000 | NPCC-ON |  | NPCC-US
4 | 79780008728 | The process by which the Rating of equipment that comprises a Facility is determined. |  | GO | [28 empty] | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780008732 | Operating limitations. |  | GO | [28 empty] | 22400000 | NPCC-ON |  | NPCC-US
4 | 79780008738 | The process by which the Rating of equipment that comprises a Facility is determined. |  | TO | [28 empty] | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780008743 | Operating limitations. |  | TO | [28 empty] | 32400000 | NPCC-ON |  | NPCC-US
4 | 79780008775 | Obtain and utilize status, voltages, and flow data for Facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator; |  | TOP | [18 empty] | TOP |  |  |  | 2021-04-01 | [5 empty] | 104000000 | NPCC-ON |  | NPCC-US
4 | 79780008912 | Each Generator Owner in the ISO-NE Planning Coordinator area and in NYISO Planning Coordinator area shall arrange for compensatory load shedding, in accordance with Attachment B and as provided by a Distribution Provider or Transmission Owner, that is adequate to compensate for the loss of generator(s) due to early tripping that is within the UFLS island identified by the Planning Coordinator in Requirement R2. |  | GO | [22 empty] | 2020-02-18 |  |  |  | 4.1.3. Distribution Providers that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators&lt;br/&gt;4.1.4. Transmission Owners that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators |  | 134000000 | NPCC-ON |  | NPCC-US
4 | 79780008998 | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 64000000 | NPCC-ON |  | NPCC-US
4 | 79780009005 | Be submitted to the Compliance Enforcement Authority (CEA) with a request for extension of time if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. The submitted CAP shall document the following: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 74000000 | NPCC-ON |  | NPCC-US
4 | 79780009025 | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 104000000 | NPCC-ON |  | NPCC-US
4 | 79780009035 | Be submitted to the CEA with a request for extension of time if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. The submitted CAP shall document the following: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 114000000 | NPCC-ON |  | NPCC-US
4 | 79780009061 | Study assumptions, system performance, alternatives considered, and coordinated recommendations. While these studies may be performed independently, the results shall be evaluated and coordinated by the entities involved. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2021-04-01 |  |  |  | Applicable Generator Owner: Generator Owner with a fully executed Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. |  | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780009070 | The deadline by which the respondent is to provide the indicated data. |  | RC | [11 empty] | RC | [10 empty] | 2021-04-01 | [5 empty] | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780009084 | Monthly and annual peak hour controllable and dispatchable Demand Side Management under the control or supervision of the System Operator in megawatts for the prior calendar year. Three values shall be reported for each hour: 1) the committed megawatts (the amount under control or supervision), 2) the dispatched megawatts (the amount, if any, activated for use by the System Operator), and 3) the realized megawatts (the amount of actual demand reduction). | [24 empty] | 2021-04-01 | [5 empty] | 13400000 | NPCC-ON |  | NPCC-US
4 | 79780009085 | A request to provide any or all of the following forecast data, as necessary: |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780009089 | Annual forecast Net Energy for Load in gigawatthours for ten calendar years into the future. | [24 empty] | 2021-04-01 | [5 empty] | 14400000 | NPCC-ON |  | NPCC-US
4 | 79780009105 | Guidelines to resolve the unacceptable differences in performance identified under Part 1.3. |  | PCPA | [9 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780009128 | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 93400000 | NPCC-ON |  | NPCC-US
4 | 79780009132 | Communications and training Administrative elements: |  | BA, DP, GO, GOP, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  |  |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 94000000 | NPCC-ON |  | NPCC-US
4 | 79780009136 | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 94400000 | NPCC-ON |  | NPCC-US
4 | 79780009182 | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-4 — Attachment 1. |  | PCPA | [9 empty] | PA | [16 empty] | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 44000000 | NPCC-ON |  | NPCC-US
4 | 79780009208 | The deadline by which the respondent is to provide the indicated data. |  | TOP | [18 empty] | TOP |  |  |  | 2021-04-01 | [5 empty] | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780009213 | The deadline by which the respondent is to provide the indicated data. |  | BA | BA | [21 empty] | 2021-04-01 | [5 empty] | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780009312 | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed annually and be supported by current or past studies as qualified in Requirement R2, Part2.6. The following studies are required: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780009336 | Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES shall be identified, and a list of those Contingencies to be evaluated for System performance in Requirement R3, Part 3.1 created. The rationale for those Contingencies selected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 34000000 | NPCC-ON |  | NPCC-US
4 | 79780009454 | Where technically feasible, perform authentication when establishing Dial-up Connectivity with applicable Cyber Assets. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780009459 | Have one or more methods for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access). |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 24000000 | NPCC-ON |  | NPCC-US
4 | 79780009472 | For a change that deviates from the existing baseline configuration: |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 14000000 | NPCC-ON |  | NPCC-US
4 | 79780009488 | Document the results of the assessments conducted according to Parts 3.1, 3.2, and 3.3 and the action plan to remediate or mitigate vulnerabilities identified in the assessments including the planned date of completing the action plan and the execution status of any remediation or mitigation action items. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 34000000 | NPCC-ON |  | NPCC-US
4. | 1000 | System real and reactive reserves (actual versus required). |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  | IRO-005-1 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1027 | System real and reactive reserves (actual versus required). |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  | IRO-005-2 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1054 | System real and reactive reserves (actual versus required). |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  | IRO-005-3a R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1102 | Process for data provision when automated Real-Time system operating data is unavailable. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2009-08-05 |  |  | IRO-010-1 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1110 | Voltage control, including the coordination of reactive resources for voltage control. |  | RC | [11 empty] | RC | [9 empty] | M1.1.4 Voltage control, including the coordination of reactive resources for voltagecontrol. | 2007-06-18 |  | 2017-03-31 |  |  |  | 11400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1140 | A description of how incomplete or so-called partial path transmission reservations are addressed. (Incomplete or partial path transmission reservations are those for which all transmission reservations necessary to complete the transmission path from ultimate source to ultimate sink are not identifiable due to differing reservation priorities, durations, or because the reservations have not all been made.) |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-001-0 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1161 | The identity of the Transmission Service Providers and Transmission Operators to which it provides data for use in calculating transfer or Flowgate capability. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-001-1 R3. | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1171 | Each Planning Coordinator adjacent to the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-001-1 R4. | 44000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1194 | What recourse a customer has if the response is deemed unsatisfactory. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-003-0 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1201 | Require that CBM be preserved only on the Transmission Service Provider’s System where the Load-Serving Entity’s Load is located (i.e., CBM is an import quantity only). |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-004-0 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1240 | Require CBM values to be periodically updated (at least annually) and available to the Regional Reliability Organizations, NERC, and transmission users. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-005-0 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1265 | Forecast uncertainty in transmission system topology. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1270 | Describe the conditions, if any, under which TRM may be available to the market as Non-Firm Transmission Service. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-008-0 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1288 | Require TRM values to be periodically updated (at least prior to each season — winter, spring, summer, and fall), as necessary, and made available to the Regional Reliability Organizations, NERC, and transmission users. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-009-0 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1297 | DC Transmission Line (overhead and underground): line parameters, Normal and Emergency Ratings, control parameters, rectifier data, and inverter data. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | MOD-011-0 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1311 | Dynamics data representing electrical Demand characteristics as a function of frequency and voltage. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | MOD-013-1 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1338 | Annual Peak hour forecast demands (summer and winter) in MW and annual Net Energy for load in GWh for at least five years and up to ten years into the future, as requested. |  | LSE, PCPA, RP | [7 empty] | LSE |  | PA |  |  |  | RP | [8 empty] | 2007-06-18 |  | 2009-05-12 |  |  | MOD-017-0 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1343 | Annual Peak hour forecast demands (summer and winter) in MW and annual Net Energy for load in GWh for at least five years and up to ten years into the future, as requested. |  | LSE, PCPA, RP | [7 empty] | LSE |  | PA |  |  |  | RP | [8 empty] | 2009-05-13 |  | 2016-06-30 |  |  | MOD-017-0.1 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 135 | Each BA in the Western Interconnection shall synchronize its Time Error to the nearest 0.001 seconds of the system Time Error by comparing its reading at the designated time each day to the reading broadcast by the Interconnection Time Monitor. Any difference shall be applied as an adjustment to its current Time Error. |  | BA | BA | [21 empty] | 2009-06-29 |  | 2014-03-31 |  |  | BAL-004-WECC-01 R4. | 44000000 | WECC-US | [5 empty] | WECC-US
4. | 1359 | Periodicity and schedule of model and data verification and reporting. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | MOD-024-1 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1370 | Periodicity and schedule of model and data verification and reporting. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | MOD-025-1 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1375 | Method of verification, including date and conditions. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 15400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1382 | A description of the manner in which Contingencies are identified for use in the TTC process. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2013-09-30 |  |  | MOD-028-1 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1387 | If the Transmission Service Provider’s ATC calculation process involves a grouping of generation, the ATCID must identify how these generators participate in the group. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2013-09-30 |  |  |  | 15400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1415 | For ATC Paths whose capacity uses jointly-owned or allocated Facilities, limit TTC for each Transmission Service Provider so the TTC does not exceed each Transmission Service Provider’s contractual rights. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2013-09-30 |  |  | MOD-028-1 R6. | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1430 | Models phase shifters in non-regulating mode, unless otherwise specified in the Available Transfer Capability Implementation Document (ATCID). |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 11400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1444 | For an ATC Path whose TTC varies due to simultaneous interaction with one or more other paths, develop a nomogram describing the interaction of the paths and the resulting TTC under specified conditions |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-029-1 R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1461 | If the Transmission Service Provider’s AFC calculation process involves a grouping of generators, the ATCID must identify how these generators participate in the group. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 12400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1476 | Any limiting Element/Contingency combination within the Transmission model that has been requested to be included by any other Transmission Service Provider using the Flowgate Methodology or Area Interchange Methodology, where: |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 21400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1481 | Establish the TFC of each of the defined Flowgates as equal to: - For thermal limits, the System Operating Limit (SOL) of the Flowgate. - For voltage or stability limits, the flow that will respect the SOL of the Flowgate. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | MOD-030-1 R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1489 | Contains modeling data and system topology for the Facilities within its Reliability Coordinator’s Area. Equivalent representation of radial lines and Facilities161kV or below is allowed. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | MOD-030-1 R3. | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1504 | The impact of any confirmed firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, including roll-over rights for Firm Transmission Service contracts having a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | MOD-030-1 R6. | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1512 | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | MOD-030-1 R7. | 74000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1524 | If the Transmission Service Provider’s AFC calculation process involves a grouping of generators, the ATCID must identify how these generators participate in the group. |  | TSP | [20 empty] | TSP |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 12400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1541 | Any limiting Element/Contingency combination within the Transmission model that has been requested to be included by any other Transmission Service Provider using the Flowgate Methodology or Area Interchange Methodology, where: |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 21400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1546 | Establish the TFC of each of the defined Flowgates as equal to: - For thermal limits, the System Operating Limit (SOL) of the Flowgate. - For voltage or stability limits, the flow that will respect the SOL of the Flowgate. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1554 | Contains modeling data and system topology for the Facilities within its Reliability Coordinator’s Area. Equivalent representation of radial lines and Facilities161kV or below is allowed. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R3. | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1569 | The impact of any confirmed firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, including roll-over rights for Firm Transmission Service contracts having a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R6. | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1577 | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R7. | 74000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1599 | A dispute resolution mechanism. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 91400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1608 | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 93400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1612 | Communications and training: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2008-11-26 |  | 2010-03-31 |  |  | NUC-001-1 R9. | 94000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1616 | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 94400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1627 | Training staff must be identified, and the staff must be competent in both knowledge of system operations and instructional capabilities. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-03-31 |  |  | PER-002-0 R3. | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1644 | Each Reliability Coordinator, Balancing Authority and Transmission Operator shall conduct an annual evaluation of the training program established in R1, to identify any needed changes to the training program and shall implement the changes identified. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection evidence (such as instructor observations, trainee feedback, supervisor feedback, course evaluations, learning assessments, or internalaudit results) that it performed an annual training program evaluation, as specified in R1.4 | 2013-04-01 |  | 2016-06-30 |  |  | PER-005-1 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1673 | Frequency. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 21340000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1693 | Provision for reporting Disturbance data in a format which is capable of being viewed, read and analyzed with a generic COMTRADE1 analysis tool, |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | PRC-002-1 R4. | 44000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1702 | Identification of the Regional Reliability Organization group responsible for the procedures and the process for approval of the procedures. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | PRC-003-1 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1721 | If the Protection System or RAS has a Dependability-Based Misoperation but has one or more FEPS or FERAS that operated correctly, the associated Element or transmission path may remain in service without removing from service the Protection System or RAS |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-06-27 |  | 2017-03-31 |  |  | PRC-004-WECC-1 R2. | 24000000 | WECC-US | [5 empty] | WECC-US
4. | 1739 | Generation protection. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  |  | 12400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1745 | Assessment and documentation of the effectiveness of the design and implementation of the Regional UFLS program. This assessment shall be conducted periodically and shall (at least every five years or as required by changes in system conditions) include, but not be limited to: |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  | PRC-006-0 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1759 | A summary of the findings. |  | DP, LSE, TO, TOP |  | DP | [5 empty] | LSE | [9 empty] | TO | TOP |  |  |  | 2007-06-18 |  | 2013-09-30 |  |  | PRC-009-0 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1772 | Batteries. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2027-03-31 |  |  |  | 11400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1775 | Schedule for system testing. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2027-03-31 |  |  | PRC-011-0 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1783 | Requirements to demonstrate that the inadvertent operation of an SPS shall meet the same performance requirement (TPL-001-0, TPL-002-0, and TPL-003-0) as that required of the contingency for which it was designed, and not exceed TPL-003-0. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  | PRC-012-0 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1801 | Discussion of any coordination problems found between a SPS and other protection and control systems. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  | PRC-014-0 R3. | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1817 | Batteries. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 11400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1820 | Schedule for system testing. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2007-06-18 |  | 2017-03-31 |  |  | PRC-017-0 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1832 | Operational status. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2022-06-30 |  |  | PRC-018-1 R3. | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1846 | Time delay from initiation to trip signal. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  | PRC-020-1 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1854 | Breaker operating times. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2017-03-31 |  |  | PRC-021-1 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1861 | A summary of the findings. |  | DP, LSE, TOP |  | DP | [5 empty] | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | PRC-022-1 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1877 | Set transmission line relays on series compensated transmission lines so they do not operate at or below the maximum power transfer capability of the line, determined as the greater of:- 115% of the highest emergency rating of the series capacitor.- 115% of the maximum power transfer capability of the circuit (expressed in amperes), calculated in accordance with R1.3, using the full line inductive reactance. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  | PRC-023-1 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1972 | Planned outages of transmission elements. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-01-21 |  |  | TOP-004-1 R6. | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 1984 | Responding to IROL and SOL violations. |  | TOP | [18 empty] | TOP |  |  |  | 2009-01-22 |  | 2017-03-31 |  |  | TOP-004-2 R6. | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2040 | Have established normal (pre-contingency) operating procedures in place. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2046 | Address any planned upgrades needed to meet the performance requirements of Category A. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  | TPL-001-0 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2061 | Have established normal (pre-contingency) operating procedures in place. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2067 | Address any planned upgrades needed to meet the performance requirements of Category A. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  | TPL-001-0.1 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2085 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2091 | Address any planned upgrades needed to meet the performance requirements of Category B of Table I. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | TPL-002-0 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2110 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2116 | Address any planned upgrades needed to meet the performance requirements of Category B of Table I. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | TPL-002-0a R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2135 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2141 | Address any planned upgrades needed to meet the performance requirements of Category C. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | TPL-003-0 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2160 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2166 | Address any planned upgrades needed to meet the performance requirements of Category C. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | TPL-003-0a R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2182 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2188 | Consider all contingencies applicable to Category D. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  | TPL-004-0 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2197 | Inter-Regional reliability assessments to demonstrate that the performance of these systems is in compliance with NERC Reliability Standards TPL-001-0, TPL-002-0, TPL-003-0, TPL-004-0 and respective Regional transmission and generation criteria. These assessments shall also identify key reliability issues and the risks and uncertainties affecting Adequacy and Security. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | TPL-005-0 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2203 | Adequacy of fuel supply and hydro conditions. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | TPL-005-0 R3. | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2210 | Supply-side resources and their characteristics (existing and planned generator units, Ratings, performance characteristics, fuel types and availability, and real and reactive capabilities.) |  | RRO | [14 empty] | RRO | [9 empty] | 2009-04-15 |  |  | TPL-006-0 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2258 | The +/- voltage range with step-change in % for load-tap changing transformers. |  | GO | [22 empty] | 2007-08-02 |  | 2008-08-26 |  |  |  | 41400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2273 | The +/- voltage range with step-change in % for load-tap changing transformers. |  | GO | [22 empty] | 2009-05-13 |  | 2010-09-15 |  |  |  | 41400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2288 | The +/- voltage range with step-change in % for load-tap changing transformers. |  | GO | [22 empty] | 2010-09-16 |  | 2013-06-30 |  |  |  | 41400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 23 | The procedure for applying Contingency Reserve in practice. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  | BAL-002-0 R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2303 | The +/- voltage range with step-change in % for load-tap changing transformers. |  | GO | [22 empty] | 2008-08-27 |  | 2009-05-12 |  |  |  | 41400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2311 | Due to component failure, the AVR may be out of service up to 60 consecutive days for repair per incident. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-06-27 |  | 2015-03-31 |  |  | VAR-002-WECC-1 R1. | 14000000 | WECC-US | [5 empty] | WECC-US
4. | 2325 | Unit is operating in the synchronous condenser mode (very near zero real power level). |  | GOP | [5 empty] | GOP | [16 empty] | 2011-06-27 |  | 2015-03-31 |  |  | VAR-501-WECC-1 R1. | 14000000 | WECC-US | [5 empty] | WECC-US
4. | 2350 | Supply-side resources and their characteristics (existing and planned generator units, Ratings, performance characteristics, fuel types and availability, and real and reactive capabilities.) |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | TPL-006-0.1 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2360 | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 12400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2378 | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-003-2 R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2401 | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 22400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2414 | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-005-2 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2421 | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-005-2 R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2426 | The controls used to secure dial-up accessible connections. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 25400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2435 | A review of controls for default accounts, passwords, and network management community strings; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-005-2 R4. | 44000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2445 | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  | CIP-006-2 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2493 | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | CIP-007-2 R6. | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 250 | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 12400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2503 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | CIP-007-2 R8. | 84000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2509 | Process for updating the Cyber Security Incident response plan within thirty calendar days of any changes. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-008-2 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2536 | A dispute resolution mechanism. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2014-01-21 |  |  |  | 91400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2545 | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 93400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2549 | Communications and training: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  | NUC-001-2 R9. | 94000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2553 | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 94400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2564 | Staffing levels for the emergency. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  | EOP-001-2 R3. | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2571 | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-05-23 |  | 2011-12-14 |  |  | EOP-001-2 R6. | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2576 | Identification of each Blackstart Resource and its characteristics including but not limited to the following: the name of the Blackstart Resource, location, megawatt and megavar capacity, and type of unit. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | EOP-005-2 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2586 | Synchronizing (re-energized sections of the System). |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | EOP-005-2 R10. | 104000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2621 | Descriptions of the elements of coordination of restoration plans with neighboring Reliability Coordinators. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  | EOP-006-2 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2673 | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | CIP-007-2a R6. | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2682 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | CIP-007-2a R8. | 84000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2695 | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | FAC-010-2.1 R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2705 | Allowed uses of Special Protection Systems or Remedial Action Plans. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | FAC-010-2.1 R3. | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2719 | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | 12400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2737 | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | CIP-003-3 R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2760 | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2012-12-11 |  |  |  | 22400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2773 | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | CIP-005-3 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2780 | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | CIP-005-3 R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2785 | The controls used to secure dial-up accessible connections. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2011-02-01 |  |  |  | 25400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2794 | A review of controls for default accounts, passwords, and network management community strings; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | CIP-005-3 R4. | 44000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2804 | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  | CIP-006-3 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2854 | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-007-3a R6. | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2864 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-007-3a R8. | 84000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2870 | Process for updating the Cyber Security Incident response plan within thirty calendar days of any changes. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | CIP-008-3 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2892 | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  | CIP-006-2b R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 290 | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 22400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2913 | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | CIP-006-2c R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2929 | Procedures for the appropriate use of physical access controls as described in Requirement R3 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1b R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2939 | Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1b R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2967 | Procedures for the appropriate use of physical access controls as described in Requirement R3 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | CIP-006-1c R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2968 | Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | CIP-006-1c R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 2992 | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  | CIP-006-3c R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3015 | The identity of the Transmission Service Providers and Transmission Operators to which it provides data for use in calculating transfer or Flowgate capability. |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  |  |  |  | MOD-001-1a R3. | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3025 | Each Planning Coordinator adjacent to the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  |  |  |  | MOD-001-1a R4. | 44000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 303 | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | CIP-005-1 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3055 | Models phase shifters in non-regulating mode, unless otherwise specified in the Available Transfer Capability Implementation Document (ATCID). |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 11400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3062 | For an ATC Path whose TTC varies due to simultaneous interaction with one or more other paths, develop a nomogram describing the interaction of the paths and the resulting TTC under specified conditions |  | TOP | [18 empty] | TOP |  |  |  | 2010-09-16 |  | 2017-03-31 |  |  | MOD-029-1a R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3077 | Process for data provision when automated Real-Time system operating data is unavailable. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2017-03-31 |  |  | IRO-010-1a R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 310 | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | CIP-005-1 R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 315 | The controls used to secure dial-up accessible connections. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 25400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3158 | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. | CIP-005-3a R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3164 | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. | CIP-005-3a R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3169 | The controls used to secure dial-up accessible connections. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. |  | 25400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3178 | A review of controls for default accounts, passwords, and network management community strings; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. | CIP-005-3a R4. | 44000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3189 | The procedure for applying Contingency Reserve in practice. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  | BAL-002-1 R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3226 | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-003-4 R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 324 | A review of controls for default accounts, passwords, and network management community strings; and, |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | CIP-005-1 R4. | 44000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3249 | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2012-12-11 |  |  |  | 22400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3262 | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-005-4a R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3269 | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-005-4a R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3274 | The controls used to secure dial-up accessible connections. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 25400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3283 | A review of controls for default accounts, passwords, and network management community strings; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-005-4a R4. | 44000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3293 | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-006-4c R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 334 | Procedures for the appropriate use of physical access controls as described in Requirement R3 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-006-1 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3343 | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-007-4a R6. | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3353 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-007-4a R8. | 84000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3359 | Process for updating the Cyber Security Incident response plan within thirty calendar days of any changes. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-008-4 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3379 | Requesting emergency assistance from other Balancing Authorities. |  | BA | BA | [21 empty] | 2011-01-10 |  | 2012-09-12 |  |  | EOP-002-3 R6. | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3390 | The Reliability Coordinator shall use EEA 2 to announce the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  | RC | [11 empty] | RC | [10 empty] | 2011-01-10 |  | 2012-09-12 |  |  | EOP-002-3 R9. | 94000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3411 | Evidence that the assessment included steady-state, short-circuit, and dynamics studies as necessary to evaluate system performance under both normal and contingency conditions in accordance with Reliability Standards TPL-001-0, TPL-002-0, and TPL-003-0. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [14 empty] | 2011-01-10 |  | 2015-12-31 |  |  | FAC-002-1 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3425 | System real and reactive reserves (actual versus required). |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  | IRO-005-2a R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 344 | Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-006-1 R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3459 | Have established normal (pre-contingency) operating procedures in place. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3465 | Address any planned upgrades needed to meet the performance requirements of Category A. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | TPL-001-1 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3483 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3489 | Address any planned upgrades needed to meet the performance requirements of Category B of Table I. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | TPL-002-0b R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3508 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3514 | Address any planned upgrades needed to meet the performance requirements of Category B of Table I. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | TPL-002-1b R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3533 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3539 | Address any planned upgrades needed to meet the performance requirements of Category C. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | TPL-003-1a R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3555 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3561 | Consider all contingencies applicable to Category D. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | TPL-004-1 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 361 | Procedures for the appropriate use of physical access controls as described in Requirement R3 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1a R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3622 | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | CIP-005-1a R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3628 | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | CIP-005-1a R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3633 | The controls used to secure dial-up accessible connections. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 25400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3642 | A review of controls for default accounts, passwords, and network management community strings; and, |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | CIP-005-1a R4. | 44000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3653 | Any non-critical Cyber Asset within a defined Electronic Security Perimeter shall be identified and protected pursuant to the requirements of Standard CIP-005-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | CIP-005-2a R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3659 | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | CIP-005-2a R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3664 | The controls used to secure dial-up accessible connections. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 25400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3673 | A review of controls for default accounts, passwords, and network management community strings; |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | CIP-005-2a R4. | 44000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 371 | Other Authentication Devices: Biometric, keypad, token, or other equivalent devices that control physical access to the Critical Cyber Assets. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1a R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3810 | System real and reactive reserves (actual versus required). |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  | IRO-005-3 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3833 | Develop, maintain, and implement a set of plans for system restoration. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | EOP-001-0b R3. | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3839 | Staffing levels for the emergency. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | EOP-001-0b R4. | 44000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3844 | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | EOP-001-0b R7. | 74000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3856 | Staffing levels for the emergency. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | EOP-001-2b R3. | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3861 | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2011-12-15 |  | 2012-09-12 |  |  | EOP-001-2b R6. | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3901 | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | CIP-006-2a R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3926 | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  | CIP-006-3a R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3964 | A description of the manner in which Contingencies are identified for use in the TTC process. |  | TSP | [20 empty] | TSP |  | 2013-09-27 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | MOD-028-2 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3969 | If the Transmission Service Provider’s ATC calculation process involves a grouping of generation, the ATCID must identify how these generators participate in the group. |  | TSP | [20 empty] | TSP |  | 2013-10-01 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 15400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3981 | A monthly load forecast for TTCs used in ATC calculations for months two through 13 months TTCs. |  | TOP | [18 empty] | TOP |  |  |  | 2013-10-01 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 31400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 3995 | For ATC Paths whose capacity uses jointly-owned or allocated Facilities, limit TTC for each Transmission Service Provider so the TTC does not exceed each Transmission Service Provider’s contractual rights. |  | TOP | [18 empty] | TOP |  |  |  | 2013-09-27 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | MOD-028-2 R6. | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4042 | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-006-3d R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4065 | Appropriate use of physical access controls as described in Requirement R4 including visitor pass management, response to loss, and prohibition of inappropriate use of physical access controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-006-4d R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4089 | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  | EOP-001-2.1b R6. | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4098 | Staffing levels for the emergency. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2017-03-31 |  |  | EOP-001-2.1b R3. | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4134 | Develop, maintain, and implement a set of plans for system restoration. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  | EOP-001-0.1b R3. | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4137 | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  | EOP-001-0.1b R7. | 74000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4141 | Staffing levels for the emergency. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2012-09-13 |  | 2013-06-30 |  |  | EOP-001-0.1b R4. | 44000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 415 | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-007-1 R6. | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4186 | System real and reactive reserves (actual versus required). |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  | IRO-005-3.1a R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4199 | Requesting emergency assistance from other Balancing Authorities. |  | BA | BA | [21 empty] | 2012-09-13 |  | 2017-03-31 |  |  | EOP-002-3.1 R6. | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4208 | The Reliability Coordinator shall use EEA 2 to announce the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  | EOP-002-3.1 R9. | 94000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4221 | Communications and training: |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 94000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4226 | A dispute resolution mechanism. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2014-01-21 |  |  |  | 91400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4233 | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 93400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4242 | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 94400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 425 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | CIP-007-1 R8. | 84000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4256 | Communications and training: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  | NUC-001-2.1 R9. | 94000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 431 | Process for updating the Cyber Security Incident response plan within ninety calendar days of any changes. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-008-1 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4343 | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 12400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4372 | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-12-12 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-004-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 22400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4388 | Action plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 22400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4410 | The +/- voltage range with step-change in % for load-tap changing transformers. |  | GO | [22 empty] | 2013-07-01 |  | 2014-09-30 |  |  |  | 41400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4449 | The procedure for applying Contingency Reserve in practice. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  | BAL-002-1a R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 446 | Where applicable, these facilities shall be redundant and diversely routed. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-05-12 |  |  | COM-001-1 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 456 | Where applicable, these facilities shall be redundant and diversely routed. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2009-05-13 |  | 2015-09-30 |  |  | COM-001-1.1 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4564 | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 12400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4585 | Address any planned upgrades needed to meet the performance requirements of Category A. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | TPL-001-1 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4589 | Have established normal (pre-contingency) operating procedures in place. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4627 | Address any planned upgrades needed to meet the performance requirements of Category B of Table I. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | TPL-002-0b R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4639 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4652 | Address any planned upgrades needed to meet the performance requirements of Category C. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | TPL-003-0a R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4664 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4677 | Consider all contingencies applicable to Category D. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | TPL-004-1 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4686 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4692 | Address any planned upgrades needed to meet the performance requirements of Category C. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | TPL-003-0a R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4704 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 471 | Develop, maintain, and implement a set of plans for system restoration. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  | EOP-001-0 R3. | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4718 | Address any planned upgrades needed to meet the performance requirements of Category C. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | TPL-003-0a R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4727 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4742 | Consider all contingencies applicable to Category D. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | TPL-004-0 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4751 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4755 | Consider all contingencies applicable to Category D. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | TPL-004-1 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 476 | Staffing levels for the emergency. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  | EOP-001-0 R4. | 44000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4760 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4812 | Where applicable, these facilities shall be redundant and diversely routed. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 483 | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2007-06-18 |  | 2011-12-14 |  |  | EOP-001-0 R7. | 74000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4841 | Requesting emergency assistance from other Balancing Authorities. |  | BA | BA | [23 empty] | 2006-11-01 |  |  |  | 74000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4848 | The Reliability Coordinator shall use EEA 2 to announce the change of the priority oftransmission service of an Interchange Transaction on the system from Priority 6 toPriority 7. |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 104000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4858 | Requesting emergency assistance from other Balancing Authorities. |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4869 | The Reliability Coordinator shall use EEA 2 to announce the change of the priority oftransmission service of an Interchange Transaction on the system from Priority 6 toPriority 7. |  | RC | [11 empty] | RC | [12 empty] | 2007-01-01 |  |  |  | 94000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 489 | Develop, maintain, and implement a set of plans for system restoration. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  | EOP-001-1 R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4890 | The affected Transmission Operators shall give high priority to restoration of off-site power to nuclear stations. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-05-02 |  |  |  | 94000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4895 | Load is shed in neighboring areas, if required, to permit successful interconnected system restoration. |  | TOP | [18 empty] | TOP | [5 empty] | 2007-05-02 |  |  |  | 95400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4912 | Terminal equipment (e.g., switches, breakers, current transformers, etc) |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-08-01 |  |  |  | 11400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4918 | Ratings of jointly-owned and jointly-operated facilities shall be coordinated amongthe joint owners and joint operators resulting in a single set of Ratings. |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-08-01 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 494 | Staffing levels for the emergency. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  | EOP-001-1 R3. | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4944 | Reliability analysis services (IDC or other regional reliability tools). |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4950 | OASIS reservation accommodates all Interchange Transactions. |  | TSP | [20 empty] | TSP |  |  |  | 2007-01-01 |  |  |  | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4957 | Scheduling path (proper connectivity of adjacent Balancing Authorities). |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 4983 | Loss of generation. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 50 | Reserve held by other entities by agreement that is deliverable on Firm Transmission Service; |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2010-11-26 |  |  | BAL-002-WECC-1 R3. | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 501 | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  | BA, TOP | BA | [17 empty] | TOP | [5 empty] | 2011-05-23 |  |  | EOP-001-1 R6. | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5030 | System real and reactive reserves (actual versus required). |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5085 | Dynamics data shall be consistent with the reported steady-state (power flow) data supplied per Reliability Standard MOD-010-0_R1. |  | RRO | [14 empty] | RRO | [9 empty] | 2006-11-02 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 511 | Requesting emergency assistance from other Balancing Authorities. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  | EOP-002-2 R6. | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5113 | Event triggering requirements |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 12400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5118 | MW and/or MVAR, as appropriate. |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5119 | Data retention capabilities (e.g., length of time data is to be available for retrieval). |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5132 | Identification of the Regional Reliability Organization group responsible for the procedure and the process for Regional Reliability Organization approval of the procedure. |  | RRO | [14 empty] | RRO | [9 empty] | 2006-05-01 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5142 | Batteries. |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2006-05-01 |  |  |  | 11400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5145 | Schedule for system testing. |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2006-05-01 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5209 | Planned outages of transmission elements. |  | TOP | [18 empty] | TOP | [5 empty] | 2005-04-01 |  |  |  | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 522 | The Reliability Coordinator shall use EEA 2 to announce the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-05-12 |  |  | EOP-002-2 R9. | 94000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5273 | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. | CIP-003-3 R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5297 | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-003-4 R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 532 | Requesting emergency assistance from other Balancing Authorities. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-09-30 |  |  | EOP-002-2.1 R6. | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5344 | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-007-3a R6. | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5353 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-007-3a R8. | 84000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5387 | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-007-4a R6. | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5396 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-007-4a R8. | 84000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 543 | The Reliability Coordinator shall use EEA 2 to announce the change of the priority of transmission service of an Interchange Transaction on the system from Priority 6 to Priority 7. |  | RC | [11 empty] | RC | [10 empty] | 2009-05-13 |  | 2011-09-30 |  |  | EOP-002-2.1 R9. | 94000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 558 | If, in the judgment of the Regional Reliability Organization, after consultation with the Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load-Serving Entity in which a disturbance occurred, a final report is required, the affected Reliability Coordinator, Balancing Authority, Transmission Operator, Generator Operator, or Load-Serving Entity shall prepare this report within 60 days. As a minimum, the final report shall have a discussion of the events and its cause, the conclusions reached, and recommendations to prevent recurrence of this type of event. The report shall be subject to Regional Reliability Organization approval. |  | BA, GOP, LSE, RC, TOP | BA |  |  |  |  | GOP |  | LSE |  |  |  | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-12-31 |  |  | EOP-004-1 R3. | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5612 | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5621 | Allowed uses of Remedial Action Schemes. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5643 | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. |  | RC | [11 empty] | RC | [10 empty] | 2017-04-01 | [5 empty] | 23300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5644 | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5650 | Level of detail of system models used to determine SOLs. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5664 | System real and reactive reserves (actual versus required). |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 568 | The affected Transmission Operators shall give high priority to restoration of off-site power to nuclear stations. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | EOP-005-1 R11. | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5688 | If the Transmission Service Provider’s AFC calculation process involves a grouping of generators, the ATCID must identify how these generators participate in the group. |  | TSP | [20 empty] | TSP |  | 2017-04-01 | [5 empty] | 12400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5701 | Any limiting Element/Contingency combination within the Transmission model that has been requested to be included by any other Transmission Service Provider using the Flowgate Methodology or Area Interchange Methodology, where: |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 21400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5706 | Establish the TFC of each of the defined Flowgates as equal to: - For thermal limits, the System Operating Limit (SOL) of the Flowgate. - For voltage or stability limits, the flow that will respect the SOL of the Flowgate |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5714 | Contains modeling data and system topology for the Facilities within its Reliability Coordinator’s Area. Equivalent representation of radial lines and Facilities161kV or below is allowed. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5729 | The impact of any confirmed firm Point-to-Point Transmission Service expected to be scheduled, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, including roll-over rights for Firm Transmission Service contracts having a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. (Footnote: A percentage less than that used in the Interconnection-wide congestion management procedure may be utilized.) |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 573 | Load is shed in neighboring areas, if required, to permit successful interconnected system restoration. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  |  | 115400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5737 | The impact of any Grandfathered non-firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 74000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5756 | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5768 | Systems and facilities critical to system restoration, including blackstart generators and substations in the electrical path of transmission lines used for initial system restoration. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5792 | A dispute resolution mechanism. (Retirement approved by FERC effective January 21, 2014.) | [26 empty] | 2014-11-13 |  |  |  | 91400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5801 | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 93400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5805 | Communications and training: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  |  |  | 2014-11-13 |  |  |  | 94000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5809 | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 94400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5818 | Have established normal (pre-contingency) operating procedures in place. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5824 | Address any planned upgrades needed to meet the performance requirements of Category A. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5839 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5848 | Address any planned upgrades needed to meet the performance requirements of Category B of Table I. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5864 | Be conducted beyond the five-year horizon only as needed to address identified marginal conditions that may have longer lead-time solutions. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5873 | Address any planned upgrades needed to meet the performance requirements of Category C. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5889 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5895 | Consider all contingencies applicable to Category D. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5902 | Requirements to demonstrate that the inadvertent operation of a RAS shall meet the same performance requirement (TPL-001-0, TPL-002-0, and TPL-003-0) as that required of the contingency for which it was designed, and not exceed TPL-003-0. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5920 | Discussion of any coordination problems found between a RAS and other protection and control systems. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5938 | Batteries. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2017-04-01 |  | 2027-03-31 |  |  |  | 11400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5942 | Schedule for system testing. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-01-25 |  | 2027-03-31 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 595 | A requirement to review and update the Regional BCP at least every five years. |  | RRO | [14 empty] | RRO | [7 empty] | 2011-05-23 |  | 2011-05-23 |  |  | EOP-007-0 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5950 | Time delay from initiation to trip signal. | [26 empty] | 2014-11-13 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5958 | Breaker operating times. | [26 empty] | 2014-11-13 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 5994 | If the Protection System or RAS has a Dependability-Based Misoperation but has one or more FEPS or FERAS that operated correctly, the associated Element or transmission path may remain in service without removing from service the Protection System or RAS | [23 empty] | M2.4 Transmission Owners and Generation Owners shall have evidence that they repaired or replaced the Protection System or RAS that misoperated including documentation that describes the actions taken. | 2017-04-01 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf..4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. |  | 24000000 | WECC-US | [5 empty] | WECC-US
4. | 601 | The plan shall include procedures and responsibilities for maintaining basic voice communication capabilities with other areas. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | EOP-008-0 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6163 | System security management (CIP-007); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6172 | Incident response to a Cyber Security Incident. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2016-06-30 |  |  |  | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6176 | Incident handling procedures for Cyber Security Incidents. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.4. An example of evidence may include, but is not limited to, dated Cyber Security Incident response process(es) or procedure(s) that address incident handling (e.g., containment, eradication, recovery/incident resolution). | 2014-02-03 |  | 2020-12-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started. |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6192 | For each mitigation plan created or revised in Part 2.3, implement the plan within the timeframe specified in the plan, unless a revision to the plan or an extension to the timeframe specified in Part 2.3 is approved by the CIP Senior Manager or delegate. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6199 | Review a summarization or sampling of logged events as determined by the Responsible Entity at intervals no greater than 15 calendar days to identify undetected Cyber Security Incidents. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 44000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6203 | Change known default passwords, per Cyber Asset capability |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 54000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6222 | Any logical network accessible ports; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 11400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6226 | For a change that deviates from the existing baseline configuration: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6239 | Document the results of the assessments conducted according to Parts 3.1, 3.2, and 3.3 and the action plan to remediate or mitigate vulnerabilities identified in the assessments including the planned date of completing the action plan and the execution status of any remediation or mitigation action items. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 624 | Breaker duty and surge protection. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 21400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6243 | Where technically feasible, perform authentication when establishing Dial-up Connectivity with applicable Cyber Assets. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.4. An example of evidence may include, but is not limited to, a documented process that describes how the Responsible Entity is providing authenticated access through each dial-up connection. | 2014-02-03 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6251 | Monitor for unauthorized access through a physical access point into a Physical Security Perimeter. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 1.4 An example of evidence may include, but is not limited to, documentation of controls that monitor for unauthorized access through a physical access point into a Physical Security Perimeter. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6264 | One or more processes to verify the successful completion of the backup processes in Part 1.3 and to address any backup failures. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6280 | The visitor control program; | [23 empty] | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. |  |  | 2016-06-30 |  |  |  | 21400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6303 | Criteria or process for verifying that personnel risk assessments performed for contractors or service vendors are conducted according to Parts 3.1 through 3.3. | [23 empty] | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s criteria or process for verifying contractors or service vendors personnel risk assessments. |  |  | 2016-06-30 |  |  |  | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6311 | Verify at least once every 15 calendar months that access to the designated storage locations for BES Cyber System Information, whether physical or electronic, are correct and are those that the Responsible Entity determines are necessary for performing assigned work functions. | [23 empty] | An example of evidence may include, but is not limited to, the documentation of the review that includes all of the following:1. A dated listing of authorizations for BES Cyber System information;2. Any privileges associated with the authorizations; and 3. Dated evidence showing a verification of the authorizations and any privileges were confirmed correct and the minimum necessary for performing assigned work functions. |  |  | 2016-06-30 |  |  |  | 44000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6315 | For termination actions, revoke the individual’s non-shared user accounts (unless already revoked according to Parts 5.1 or 5.3) within 30 calendar days of the effective date of the termination action. | [23 empty] | An example of evidence may include, but is not limited to, workflow or sign-off form showing access removal for any individual BES Cyber Assets and software applications as determined necessary to completing the revocation of access and dated within thirty calendar days of the termination actions. |  |  | 2016-06-30 |  |  |  | 54000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6329 | Operating limitations. (Footnote: Such as temporary de-ratings of impaired equipment in accordance with good utility practice.) |  | GO | [22 empty] | 2013-01-01 |  | 2021-09-30 |  |  |  | 22400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6331 | The process by which the Rating of equipment that comprises a Facility is determined. |  | GO | [22 empty] | 2011-11-17 |  | 2021-09-30 |  |  |  | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6339 | Operating limitations. (Footnote: Such as temporary de-ratings of impaired equipment in accordance with good utility practice.) |  | TO | [22 empty] | 2013-01-01 |  | 2021-09-30 |  |  |  | 32400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6341 | The process by which the Rating of equipment that comprises a Facility is determined. |  | TO | [22 empty] | 2011-11-17 |  | 2021-09-30 |  |  |  | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 635 | Evidence that the assessment included steady-state, short-circuit, and dynamics studies as necessary to evaluate system performance in accordance with Reliability Standard TPL-001-0. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [14 empty] | 2007-06-18 |  | 2011-09-30 |  |  | FAC-002-0 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6386 | Each Transmission Owner shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party verifier and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. |  | TO | [22 empty] | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.Voltage Value of a Line Weight Value per Lineless than 200 kV (not applicable) (not applicable)200 kV to 299 kV 700300 kV to 499 kV 1300500 kV and above 04.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6397 | Provisions to evaluate evolving physical threats, and their corresponding security measures, to the Transmission station(s), Transmission substation(s), or primary control center(s). |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.Voltage Value of a Line Weight Value per Lineless than 200 kV (not applicable) (not applicable)200 kV to 299 kV 700300 kV to 499 kV 1300500 kV and above 04.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 54000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6404 | Each Transmission Owner and Transmission Operator shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party reviewer and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-02 |  |  |  | 4.1.1 Transmission Owner that owns a Transmission station or Transmission substation that meets any of the following criteria:4.1.1.1 Transmission Facilities operated at 500 kV or higher. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.4.1.1.2 Transmission Facilities that are operating between 200 kV and 499 kV at a single station or substation, where the station or substation is connected at 200 kV or higher voltages to three or more other Transmission stations or substations and has an "aggregate weighted value" exceeding 3000 according to the table below. The "aggregate weighted value" for a single station or substation is determined by summing the "weight value per line" shown in the table below for each incoming and each outgoing BES Transmission Line that is connected to another Transmission station or substation. For the purpose of this criterion, the collector bus for a generation plant is not considered a Transmission Facility, but is part of the generation interconnection Facility.Voltage Value of a Line Weight Value per Lineless than 200 kV (not applicable) (not applicable)200 kV to 299 kV 700300 kV to 499 kV 1300500 kV and above 04.1.1.3 Transmission Facilities at a single station or substation location that are identified by its Reliability Coordinator, Planning Coordinator, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies.4.1.1.4 Transmission Facilities identified as essential to meeting Nuclear Plant Interface Requirements. Exemption: Facilities in a “protected area,” as defined in 10 C.F.R. § 73.2, within the scope of a security plan approved or accepted by the Nuclear Regulatory Commission are not subject to this Standard; or, Facilities within the scope of a security plan approved or accepted by the Canadian Nuclear Safety Commission are not subject to this Standard. |  | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6427 | Model structure and data for the excitation control system, including the closed loop voltage regulator if a closed loop voltage regulator is installed or the model structure and data for the plant volt/var control function system, |  | GO | [22 empty] | 2018-07-01 |  |  |  | 4.2. Facilities:For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following:4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).4.2.2 Generation in the Western Interconnection with the following characteristics:4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.3 Generation in the ERCOT Interconnection with the following characteristics:4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.4 For all Interconnections:• A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. |  | 21400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6437 | Model structure and data for turbine/governor and load control or active power/frequency control, and |  | GO | [22 empty] | 2014-07-01 |  |  |  | 4.2. FacilitiesFor the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred to as an “applicable unit” that meet the following:4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics:4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).4.2.2 Generation in the Western Interconnection with the following characteristics:4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.3 Generation in the ERCOT Interconnection with the following characteristics:4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). |  | 21400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6446 | System operations |  | RC | [11 empty] | RC | [10 empty] | 2012-10-01 |  | 2019-06-30 |  |  |  | 11400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6455 | Protection and control |  | TOP | [18 empty] | TOP |  |  |  | 2012-10-01 |  | 2019-06-30 |  |  |  | 21400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 646 | Each Transmission Owner shall develop mitigation measures to achieve sufficient clearances for the protection of the transmission facilities when it identifies locations on the ROW where the Transmission Owner is restricted from attaining the clearances specified in Requirement 1.2.1. |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  | FAC-003-1 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6462 | Interchange scheduling and coordination |  | BA | BA | [21 empty] | 2012-10-01 |  | 2019-06-30 |  |  |  | 31400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6478 | An amount of capacity from a resource that is deployable within ten minutes. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | 1.4 Evidence of compliance with Requirement R1, Part 1.4 may include, but is not limited to, documentation that the reserves maintained to comply with Requirement R1, Part 1.4 are fully deployable within ten minutes. | 2014-01-28 |  | 2017-01-23 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity.4.2.1. The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group.4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | 14000000 | WECC-US | [5 empty] | WECC-US
4. | 6493 | Power source(s). |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2013-07-01 |  | 2019-03-31 |  |  |  | 12400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6496 | Operating Procedures, including decision authority, for use in determining when to implement the Operating Plan for backup functionality |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6528 | Provide its Planning Coordinator with an analysis demonstrating that no alternative load shedding solution is available that would allow the Distribution Provider or Transmission Owner to comply with UFLS Attachment C Table 2 or Attachment C Table 3. |  | DP, DP-UFLS, TO |  | DP | [20 empty] | 2016-01-01 |  | 2020-03-31 |  |  |  | 54000000 | NPCC-US |  | NPCC-US
4. | 653 | An outage shall be categorized as one of the following: |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  | FAC-003-1 R3. | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6540 | The location and amount of additional elements to be switched for voltage control that are coordinated with UFLS program tripping. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2013-04-29 |  | 2020-03-31 |  |  |  | 204000000 | NPCC-US |  | NPCC-US
4. | 6558 | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 44000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6570 | A description of how each of the following assumptions and criteria used in performing the assessment are addressed: |  | PCPA | [9 empty] | PA | [12 empty] | 2012-01-23 |  | 2020-12-14 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6594 | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 440000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6606 | The lowest frequency set point shall be no lower than 58.4 Hz. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2013-02-25 |  | 2017-12-31 |  |  |  | 24000000 | SERC-US |  |  |  | SERC-US
4. | 6626 | Real and reactive Load forecasts |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-01-01 | [5 empty] | 11400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6633 | For each of the studies described in Requirement R2, Parts 2.1.1 and 2.1.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in System response :-Real and reactive forecasted Load.-Expected transfers.-Expected in service dates of new or modified Transmission Facilities.-Generation additions, retirements, or other dispatch scenarios.-Controllable Loads and Demand Side Management.-Duration or timing of known Transmission outages. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 21400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6638 | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed annually and be supported by current or past studies as qualified in Requirement R2, Part2.6. The following studies are required: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6659 | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 27400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6670 | Those planning events in Table 1, that are expected to produce more severe System impacts on its portion of the BES, shall be identified and a list of those Contingencies to be evaluated for System performance in Requirement R3, Part 3.1 created. The rationale for those Contingencies selected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6684 | Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES, shall be identified, and a list created of those Contingencies to be evaluated in Requirement R4, Part 4.1. The rationale for those Contingencies selected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 44000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6694 | Current approved and projected Transmission uses. |  | PCPA | [9 empty] | PA | [12 empty] | 2013-04-01 |  | 2020-12-14 |  |  |  | 14400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6710 | Each Transmission Service Provider included in the Arranged Interchange, and |  | BA | BA | [21 empty] | 2014-06-30 |  | 2021-03-31 |  |  |  | 54000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6721 | Each Generator Operator within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  |  | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6727 | Each adjacent Transmission Operator asynchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  |  | 44000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6731 | Each Generator Operator that operates Facilities within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 54000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6745 | Each Transmission Owner shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party verifier and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. |  | TO | [22 empty] | 2015-10-01 |  | 2015-10-01 |  |  |  | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6753 | Provisions to evaluate evolving physical threats, and their corresponding security measures, to the Transmission station(s), Transmission substation(s), or primary control center(s). |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  |  | 54000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6757 | Each Transmission Owner and Transmission Operator shall implement procedures, such as the use of non-disclosure agreements, for protecting sensitive or confidential information made available to the unaffiliated third party reviewer and to protect or exempt sensitive or confidential information developed pursuant to this Reliability Standard from public disclosure. |  | TO, TOP | [17 empty] | TO | TOP |  |  |  | 2015-10-01 |  | 2015-10-01 |  |  |  | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6768 | Study assumptions, system performance, alternatives considered, and coordinated recommendations. While these studies may be performed independently, the results shall be evaluated and coordinated by the entities involved. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2014-11-06 |  | 2021-03-31 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6782 | Monthly and annual peak hour controllable and dispatchable Demand Side Management under the control or supervision of the System Operator in megawatts for the prior calendar year. Three values shall be reported for each hour: 1) the committed megawatts (the amount under control or supervision), 2) the dispatched megawatts (the amount, if any, activated for use by the System Operator), and 3) the realized megawatts (the amount of actual demand reduction). |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6783 | A request to provide any or all of the following forecast data, as necessary: |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2015-04-27 |  | 2016-09-30 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6787 | Annual forecast Net Energy for Load in gigawatthours for ten calendar years into the future. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 14400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6793 | How the controllable and dispatchable Demand Side Management forecast compares to actual controllable and dispatchable Demand Side Management for the prior calendar year and, if applicable, how the assumptions and methods for future forecasts were adjusted. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 15400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6801 | A schedule for submission of data at least once every 13 calendar months. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-07-01 |  |  |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. |  | 12400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6808 | Guidelines to resolve the unacceptable differences in performance identified under Part 1.3. |  | PCPA | [9 empty] | PA | [12 empty] | 2014-05-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both Planning Authority and Planning Coordinator. |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6812 | Exchange of information including planned and unplanned outage information to support its Operational Planning Analyses and Real-time Assessments. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-26 | [5 empty] | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6822 | Define the process to coordinate the resolution of identified outage conflicts with its Transmission Operators and Balancing Authorities, and other Reliability Coordinators. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-26 | [5 empty] | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6826 | The deadline by which the respondent is to provide the indicated data. |  | TOP | [18 empty] | TOP | [5 empty] | 2016-01-26 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6830 | The deadline by which the respondent is to provide the indicated data. |  | BA | BA | [23 empty] | 2016-01-26 |  |  |  | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6834 | The deadline by which the respondent is to provide the indicated data. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-26 |  | 2021-03-31 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6838 | The deadline by which the respondent is to provide the indicated data. |  | BA | BA | [21 empty] | 2016-01-26 |  | 2021-03-31 |  |  |  | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6855 | Redispatch of generation request; |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 12400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6866 | environmental constraints. |  | BA | BA | [21 empty] | 2017-04-01 | [5 empty] | 22340000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6867 | Public appeals for voluntary Load reductions; |  | BA | BA | [21 empty] | 2017-04-01 | [5 empty] | 22400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6907 | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 93400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6911 | Communications and training Administrative elements: |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2014-11-04 |  | 2021-03-31 |  |  |  | 94000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6916 | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 94400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6920 | One or more processes to verify the successful completion of the backup processes in Part 1.3 and to address any backup failures. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.4. An example of evidence may include, but is not limited to, logs, workflow or other documentation confirming that the backup process completed successfully and backup failures, if any, were addressed. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 694 | Operating limitations. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2012-12-31 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6941 | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 44000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6963 | Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct an evaluation each calendar year of the training program established in Requirement R1 to identify any needed changes to the training program and shall implement the changes identified. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  | M1.4 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall have available for inspection evidence (such as instructor observations, trainee feedback, supervisor feedback, course evaluations, learning assessments, or internal audit results) that it performed an evaluation of its training program each calendar year, as specified in Requirement R1 part 1.4. | 2014-06-19 | [5 empty] | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 6968 | Each Transmission Owner shall conduct an evaluation each calendar year of the training program established in Requirement R2 to identify any needed changes to the training program and shall implement the changes identified. |  | TO | [21 empty] | M2.4 Each Transmission Owner shall have available for inspection evidence (such as instructor observations, trainee feedback, supervisor feedback, course evaluations, learning assessments, or internal audit results) that it performed an evaluation of its training program each calendar year, as specified in Requirement R2 part 2.4. | 2014-06-19 | [5 empty] | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7046 | Cyber Security Incident response |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2017-04-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7050 | The deadline by which the respondent is to provide the indicated data. |  | RC | [11 empty] | RC | [10 empty] | 2017-01-01 |  | 2021-03-31 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7057 | Control of voltage, including the coordination of reactive resources. |  | RC | [11 empty] | RC | [12 empty] | 2016-01-26 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7068 | Voltage stability limits; and |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 11400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7074 | Planned outages; |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 12400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7086 | Planned outages; |  | TSP | [20 empty] | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 21400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7109 | Capacity and energy reserve requirements, including deliverability capability |  | BA | BA | [21 empty] | 2016-01-26 | [5 empty] | 44000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7132 | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2021-01-01 |  | 2019-06-30 |  | 4.2. Facilities:4.2.1 Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 714 | Starting with all facilities in service and following any of the multiple Contingencies identified in Reliability Standard TPL-003 the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading Outages or uncontrolled separation shall not occur. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-010-1 R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7181 | One or more BES Elements that are part of an Interconnection Reliability Operating Limit (IROL). |  | PCPA, RC | [9 empty] | PA |  | RC | [10 empty] | 2016-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 51400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7187 | Re-evaluate all BES Elements at least once every five calendar years in accordance with Parts 5.1 and 5.2, and notify owners in accordance with Part 5.3 to implement the re-evaluated list of BES Elements as per the Implementation Plan. |  | PCPA, RC | [9 empty] | PA |  | RC | [10 empty] | 2015-11-24 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 54000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7191 | Frequency of any one of the voltage(s) in Requirement R6, Part 6.1. |  | TO | [22 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7195 | Frequency of at least one of the voltages in Requirement R7, Part 7.1. |  | GO | [22 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 74000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7205 | FR and DDR data will be provided in electronic files that are formatted in conformance with C37.111, (IEEE Standard for Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 or later. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 721 | Allowed uses of Special Protection Systems or Remedial Action Plans. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-010-1 R3. | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7212 | The visitor control program; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7223 | Any logical network accessible ports; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 11400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7227 | For a change that deviates from the existing baseline configuration: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.4. An example of evidence may include, but is not limited to, a list of cyber security controls verified or tested along with the dated test results. | 2016-03-31 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7240 | Document the results of the assessments conducted according to Parts 3.1, 3.2, and 3.3 and the action plan to remediate or mitigate vulnerabilities identified in the assessments including the planned date of completing the action plan and the execution status of any remediation or mitigation action items. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.4. An example of evidence may include, but is not limited to, a document listing the results or the review or assessment, a list of action items, documented proposed dates of completion for the action plan, and records of the status of the action items (such as minutes of a status meeting, updates in a work order system, or a spreadsheet tracking the action items). | 2016-07-01 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7264 | Verify at least once every 15 calendar months that access to the designated storage locations for BES Cyber System Information, whether physical or electronic, are correct and are those that the Responsible Entity determines are necessary for performing assigned work functions. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.4. An example of evidence may include, but is not limited to, the documentation of the review that includes all of the following:1. A dated listing of authorizations for BES Cyber System information;2. Any privileges associated with the authorizations; and 3. Dated evidence showing a verification of the authorizations and any privileges were confirmed correct and the minimum necessary for performing assigned work functions. | 2017-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 44000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7268 | For termination actions, revoke the individual’s non-shared user accounts (unless already revoked according to Parts 5.1 or 5.3) within 30 calendar days of the effective date of the termination action. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.4 An example of evidence may include, but is not limited to, workflow or sign-off form showing access removal for any individual BES Cyber Assets and software applications as determined necessary to completing the revocation of access and dated within thirty calendar days of the termination actions. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 54000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7291 | For each mitigation plan created or revised in Part 2.3, implement the plan within the timeframe specified in the plan, unless a revision to the plan or an extension to the timeframe specified in Part 2.3 is approved by the CIP Senior Manager or delegate. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M2.4. An example of evidence may include, but is not limited to, records of implementation of mitigations. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7309 | Review a summarization or sampling of logged events as determined by the Responsible Entity at intervals no greater than 15 calendar days to identify undetected Cyber Security Incidents. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M4.4. Examples of evidence may include, but are not limited to, documentation describing the review, any findings from the review (if any), and dated documentation showing the review occurred. | 2016-07-15 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 44000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7313 | Change known default passwords, per Cyber Asset capability |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.4. Examples of evidence may include, but are not limited to:• Records of a procedure that passwords are changed when new devices are in production; or• Documentation in system manuals or other vendor documents showing default vendor passwords were generated pseudo-randomly and are thereby unique to the device. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 54000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7342 | Monitor for unauthorized access through a physical access point into a Physical Security Perimeter. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.4. An example of evidence may include, but is not limited to, documentation of controls that monitor for unauthorized access through a physical access point into a Physical Security Perimeter. | 2016-07-01 | [5 empty] | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7356 | Frequency. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 54000000 | NPCC-US |  | NPCC-US
4. | 7364 | Document additional triggers and deviations from the settings in 6.3.2 and 6.3.3 when local conditions dictate. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 64000000 | NPCC-US |  | NPCC-US
4. | 7404 | Major transmission interfaces. |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 72400000 | NPCC-US |  | NPCC-US
4. | 7414 | Oscillation of Frequency. |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 93400000 | NPCC-US |  | NPCC-US
4. | 7418 | Frequency. |  | RC | [11 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 104000000 | NPCC-US |  | NPCC-US
4. | 742 | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | FAC-010-2 R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7423 | Monthly verification of time synchronization (if the loss of time synchronization is not monitored to a 24/7 control center). |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 144000000 | NPCC-US |  | NPCC-US
4. | 7435 | Operational Status.Operational Status. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 174000000 | NPCC-US |  | NPCC-US
4. | 7475 | Each Generator Operator within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  |  | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7481 | System security management (CIP-007); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7492 | Each adjacent Transmission Operator asynchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  |  | 44000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7496 | Each Generator Operator that operates Facilities within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 54000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 750 | Allowed uses of Special Protection Systems or Remedial Action Plans. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | FAC-010-2 R3. | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7519 | Criteria or process for verifying that personnel risk assessments performed for contractors or service vendors are conducted according to Parts 3.1 through 3.3. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.4. An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s criteria or process for verifying contractors or service vendors personnel risk assessments. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7570 | Communicate with the other owner(s) of the electrically joined Facilities regarding revised Protection System settings resulting from unforeseen circumstances that arise during implementation or commissioning, Misoperation investigations, maintenance activities, or emergency replacements required as a result of Protection System component failure. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-04-01 |  |  |  | 4.1.3. Distribution Provider (that owns Protection Systems identified in the Facilities section 4.2 below)4.2. Facilities: Protection Systems installed to detect and isolate Faults on BES Elements. |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7588 | Monthly and annual peak hour controllable and dispatchable Demand Side Management under the control or supervision of the System Operator in megawatts for the prior calendar year. Three values shall be reported for each hour: 1) the committed megawatts (the amount under control or supervision), 2) the dispatched megawatts (the amount, if any, activated for use by the System Operator), and 3) the realized megawatts (the amount of actual demand reduction). |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7589 | A request to provide any or all of the following forecast data, as necessary: |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-02-18 |  | 2021-03-31 |  |  |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7593 | Annual forecast Net Energy for Load in gigawatthours for ten calendar years into the future. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” |  | 14400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7599 | How the controllable and dispatchable Demand Side Management forecast compares to actual controllable and dispatchable Demand Side Management for the prior calendar year and, if applicable, how the assumptions and methods for future forecasts were adjusted. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” |  | 15400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7642 | An encroachment due to vegetation growth into the MVCD that caused a vegetation-related Sustained Outage. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:4.1.1. Applicable Transmission Owners4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.4.1.2. Applicable Generator Owners4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.2.1. Each overhead transmission line operated at 200kV or higher.4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:4.3.1.1. Operated at 200kV or higher; or4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7646 | An encroachment due to vegetation growth into the line MVCD that caused a vegetation-related Sustained Outage. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:4.1.1. Applicable Transmission Owners4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.4.1.2. Applicable Generator Owners4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.2.1. Each overhead transmission line operated at 200kV or higher.4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:4.3.1.1. Operated at 200kV or higher; or4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7651 | Crew or contractor availability/Mutual assistance agreements |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:4.1.1. Applicable Transmission Owners4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.4.1.2. Applicable Generator Owners4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.2.1. Each overhead transmission line operated at 200kV or higher.4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:4.3.1.1. Operated at 200kV or higher; or4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 73000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7670 | For an ATC Path whose TTC varies due to simultaneous interaction with one or more other paths, develop a nomogram describing the interaction of the paths and the resulting TTC under specified conditions. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7697 | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 440000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7717 | Due to component failure, the AVR may be out of service up to 60 consecutive days for repair per incident. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2015-03-03 |  | 2018-09-05 |  |  |  | 14000000 | WECC-US | [5 empty] | WECC-US
4. | 772 | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-011-1 R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7754 | Except for limited impact RAS, the possible inadvertent operation of the RAS, resulting from any single RAS component malfunction satisfies all of the following: |  | PCPA | [9 empty] | PA | [12 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 41400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7758 | BES voltages shall be within post-Contingency voltage limits and post-Contingency voltage deviation limits as established by the Transmission Planner and the Planning Coordinator. |  | PCPA | [9 empty] | PA | [12 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 41440000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7767 | The RAS operation resulted in any unintended or adverse BES response. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 51400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7779 | Require its operating personnel that issue a written or oral single-party to multiple-party burst Operating Instruction to confirm or verify that the Operating Instruction was received by at least one receiver of the Operating Instruction. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2015-06-22 | [5 empty] | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 778 | Level of detail of system models used to determine SOLs. |  | RC | [11 empty] | RC | [10 empty] | 2008-05-29 |  | 2009-04-28 |  |  | FAC-011-1 R3. | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7795 | Each Generator Operator within its Transmission Operator Area. |  | TOP | [18 empty] | TOP |  |  |  | 2016-10-28 | [5 empty] | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7802 | Each adjacent Transmission Operator asynchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2016-10-28 | [5 empty] | 44000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7807 | Each Generator Operator that operates Facilities within its Balancing Authority Area. |  | BA | BA | [21 empty] | 2016-10-28 | [5 empty] | 54000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7831 | Unit is operating in the synchronous condenser mode (very near zero real power level). |  | GOP | [5 empty] | GOP | [16 empty] | 2015-04-01 |  | 2017-06-30 |  |  |  | 14000000 | WECC-US | [5 empty] | WECC-US
4. | 7878 | An amount of capacity from a resource that is deployable within ten minutes. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Part 1.4. Evidence of compliance with Requirement R1, Part 1.4 may include, but is not limited to, documentation that the reserves maintained to comply with Requirement R1, Part 1.4 are fully deployable within ten minutes. | 2017-01-24 |  | 2021-06-27 |  | 4.1.1. The Balancing Authority is the responsible entity unless the Balancing Authority is a member of a Reserve Sharing Group, in which case, the Reserve Sharing Group becomes the responsible entity.4.2.1.The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group.4.2.2. The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | 14000000 | WECC-US | [5 empty] | WECC-US
4. | 7892 | Power source(s). |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2019-04-01 | [5 empty] | 12400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7895 | Operating Procedures, including decision authority, for use in determining when to implement the Operating Plan for backup functionality. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7915 | Criteria for sharing information regarding restoration with neighboring Reliability Coordinators and with Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2018-03-26 | [5 empty] | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7935 | Identification of each Blackstart Resource and its characteristics including but not limited to the following: the name of the Blackstart Resource, location, megawatt and megavar capacity, and type of unit. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7961 | Synchronizing (re-energized sections of the System). |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 84000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 7980 | PSS washout time constant shall be no greater than 30 seconds. |  | GO | [22 empty] | 2017-04-28 |  | 2017-09-25 |  |  |  | 34000000 | WECC-US | [5 empty] | WECC-US
4. | 7992 | System security management (CIP-007); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8001 | Cyber Security Incident response; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 801 | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | FAC-011-2 R2. | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8026 | Obtain and utilize status, voltages, and flow data for Facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator; |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-17 |  | 2021-03-31 |  |  |  | 104000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 807 | Level of detail of system models used to determine SOLs. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | FAC-011-2 R3. | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8091 | Disclosure by vendors of known vulnerabilities related to the products or services provided to the Responsible Entity; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and4.1.2.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and4.2.1.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers4.2.2.1. All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-013-1:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the identification and categorization process required by CIP-002-5, or any subsequent version of that Reliability Standard. |  | 12400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8100 | Where technically feasible, perform authentication when establishing Dial-up Connectivity with applicable Cyber Assets. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a documented process that describes how the Responsible Entity is providing authenticated access through each dial-up connection. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-005-6:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8106 | Have one or more methods for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation of the methods used to determine active vendor remote access (including Interactive Remote Access and system-to-system remote access), such as: • Methods for accessing logged or monitoring information to determine active vendor remote access sessions;• Methods for monitoring activity (e.g. connection tables or rule hit counters in a firewall, or user activity monitoring) or open ports (e.g. netstat or related commands to display currently active ports) to determine active system to system remote access sessions; or• Methods that control vendor initiation of remote access such as vendors calling and requesting a second factor in order to initiate remote access. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-005-6:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8113 | Any logical network accessible ports; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 11400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8117 | For a change that deviates from the existing baseline configuration: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a list of cyber security controls verified or tested along with the dated test results. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8135 | Document the results of the assessments conducted according to Parts 3.1, 3.2, and 3.3 and the action plan to remediate or mitigate vulnerabilities identified in the assessments including the planned date of completing the action plan and the execution status of any remediation or mitigation action items. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a document listing the results or the review or assessment, a list of action items, documented proposed dates of completion for the action plan, and records of the status of the action items (such as minutes of a status meeting, updates in a work order system, or a spreadsheet tracking the action items). | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8144 | The lowest frequency set point shall be no lower than 58.4 Hz. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2017-10-16 | [5 empty] | 24000000 | SERC-US |  |  |  | SERC-US
4. | 8177 | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-3 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 44000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8212 | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-3 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 440000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 823 | Current and projected transmission uses |  | PCPA, RC | [9 empty] | PA |  | RC | [12 empty] | 2013-03-31 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8234 | Seasonal Load variations. |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 13140000 | RF-US |  |  | RF-US
4. | 8241 | Resource planned outage schedules, deratings, and retirements. |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 13240000 | RF-US |  |  | RF-US
4. | 8246 | Assistance from other interconnected systems including multi-area assessment considering Transmission limitations into the study area. |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 13400000 | RF-US |  |  | RF-US
4. | 8247 | Consider the following resource availability characteristics and document how and why they were included in the analysis or why they were not included: |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-16 | [5 empty] | 14000000 | RF-US |  |  | RF-US
4. | 8251 | Any other demand (Load) response programs not included in R1.3.1. |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 14400000 | RF-US |  |  | RF-US
4. | 8270 | PSS washout time constant shall be no greater than 30 seconds. |  | GO | [22 empty] | 2017-09-26 |  |  |  | 5. Facilities: This standard applies to synchronous generators, connected to the Bulk Electric System, that meet the definition of Commercial Operation. |  | 34000000 | WECC-US | [5 empty] | WECC-US
4. | 8343 | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2019-06-30 |  |  |  | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8350 | Be revised if situations beyond the control of the responsible entity determined in Requirement R1 prevent implementation of the CAP within the timetable for implementation provided in Part 7.3. The revised CAP shall document the following, and be updated at least once every 12 calendar months until implemented: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  |  | 74000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8362 | The supplemental GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2019-06-30 |  |  |  | 84000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8371 | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2019-06-30 |  |  |  | 104000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8400 | System operations |  | RC | [11 empty] | RC | [10 empty] | 2019-07-01 | [5 empty] | 11400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8410 | Protection and control |  | TOP | [18 empty] | TOP |  |  |  | 2019-07-01 | [5 empty] | 21400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8418 | Interchange scheduling and coordination |  | BA | BA | [21 empty] | 2019-07-01 | [5 empty] | 31400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8456 | Known commitments for Firm Transmission Service and Interchange. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  |  | 11400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 846 | The type of limitation represented by the IROL (e.g., voltage collapse, angular stability). |  | RC | [11 empty] | RC | [10 empty] | 2009-01-01 |  | 2009-04-28 |  |  |  | 51400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8463 | When known outage(s) of generation or Transmission Facility(ies) are planned in the Near-Term Planning Horizon, the impact of selected known outages on System performance shall be assessed. These known outage(s) shall be selected for assessment consistent with a documented outage coordination procedure or technical rationale by the Planning Coordinator or Transmission Planner. Known outage(s) shall not be excluded solely based upon outage duration. The assessment shall be performed for the P0 and P1 categories identified in Table 1 with the System peak or Off-Peak conditions that the System is expected to experience when the known outage(s) are planned. This assessment shall include, at a minimum known outages expected to produce more severe System impacts on the Planning Coordinator or Transmission Planner’s portion of the BES. Past or current studies may support the selection of known outage(s), if the study(s) has comparable post-Contingency System conditions and configuration such as those following P3 or P6 category events in Table 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  |  | 21400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8468 | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed annually and be supported by current or past studies as qualified in Requirement R2, Part2.6. The following studies are required: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-04-13 |  | 2020-06-10 |  |  |  | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8472 | When known outage(s) of generation or Transmission Facility(ies) are planned in the Near-Term Planning Horizon, the impact of selected known outages on System performance shall be assessed. These known outage(s) shall be selected for assessment consistent with a documented outage coordination procedure or technical rationale by the Planning Coordinator or Transmission Planner. Known outage(s) shall not be excluded solely based upon outage duration. The assessment shall be performed for the P1 categories identified in Table 1 with the System peak or Off-Peak conditions that the System is expected to experience when the known outage(s) are planned. This assessment shall include, at a minimum, those known outages expected to produce more severe System impacts on the Planning Coordinator or Transmission Planner’s portion of the BES. Past or current studies may support the selection of known outage(s), if the study(s) has comparable post-Contingency System conditions and configuration such as those following P3 or P6 category events in Table 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  |  | 24400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8480 | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  |  | 27400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 849 | The Transmission Planner shall provide its SOLs (including the subset of SOLs that are IROLs) to its Planning Authority, Reliability Coordinators, Transmission Operators, and Transmission Service Providers that work within its Transmission Planning Area and to adjacent Transmission Planners. |  | TP | [19 empty] | TP |  |  | 2008-02-08 |  | 2009-04-28 |  |  | FAC-014-1 R5. | 54000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8498 | Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES shall be identified, and a list of those Contingencies to be evaluated for System performance in Requirement R3, Part 3.1 created. The rationale for those Contingencies selected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-04-13 |  | 2020-06-10 |  |  |  | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8525 | Incident handling procedures for Cyber Security Incidents. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, dated Cyber Security Incident response process(es) or procedure(s) that address incident handling (e.g., containment, eradication, recovery/incident resolution). | 2019-06-20 |  |  |  | 4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Remedial Action Scheme where the Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-008-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002 identification and categorization processes. |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8568 | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2020-10-05 |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8573 | Be revised if situations beyond the control of the responsible entity determined in Requirement R1 prevent implementation of the CAP within the timetable for implementation provided in Part 7.3. The revised CAP shall document the following, and be updated at least once every 12 calendar months until implemented: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2020-10-05 |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 74000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8585 | The supplemental GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-01-01 |  | 2020-10-05 |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 84000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8601 | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  | 2020-10-05 |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 104000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 862 | The type of limitation represented by the IROL (e.g., voltage collapse, angular stability). |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 | [5 empty] | 51400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8636 | The Responsible Entity shall retain all logs specified in Requirement R6 for ninety calendar days. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 64000000 | MRO-MB | MRO-US
4. | 864 | The Transmission Planner shall provide its SOLs (including the subset of SOLs that are IROLs) to its Planning Authority, Reliability Coordinators, Transmission Operators, and Transmission Service Providers that work within its Transmission Planning Area and to adjacent Transmission Planners. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  |  |  |  | FAC-014-2 R5. | 53000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8646 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. | [30 empty] | 84000000 | MRO-MB | MRO-US
4. | 865 | The Transmission Planner shall provide its SOLs (including the subset of SOLs that are IROLs) to its Planning Authority, Reliability Coordinators, Transmission Operators, and Transmission Service Providers that work within its Transmission Planning Area and to adjacent Transmission Planners. |  | TP | [19 empty] | TP |  |  | 2009-04-29 |  |  |  |  | FAC-014-2 R5. | 54000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8661 | A method to determine Remedial Action Schemes included in analyses and assessments; | [24 empty] | 2020-01-01 |  | 2021-03-31 |  | ApplicabilityAs used in this WECC Regional Variance, Reliability Coordinator is specific to those Reliability Coordinators providing Reliability Coordinator service(s) to entities operating within the Western Interconnection, regardless of where the Reliability Coordinator may be located. |  | 740000 | WECC-US | [5 empty] | WECC-US
4. | 8675 | A method to determine Remedial Action Schemes included in analyses and assessments; |  | RC | [11 empty] | RC | [10 empty] | 2021-04-01 | [5 empty] | 740000 | WECC-US | [5 empty] | WECC-US
4. | 8684 | System security management (CIP-007); |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8694 | Cyber Security Incident response; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8728 | The process by which the Rating of equipment that comprises a Facility is determined. |  | GO | [24 empty] | 2021-02-04 |  |  |  | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8732 | Operating limitations. |  | GO | [24 empty] | 2021-02-04 |  |  |  | 22400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8738 | The process by which the Rating of equipment that comprises a Facility is determined. |  | TO | [24 empty] | 2021-02-04 |  |  |  | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8743 | Operating limitations. |  | TO | [24 empty] | 2021-02-04 |  |  |  | 32400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8775 | Obtain and utilize status, voltages, and flow data for Facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator; |  | TOP | [18 empty] | TOP |  |  |  | 2021-04-01 | [5 empty] | 104000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 8842 | An amount of capacity from a resource that is deployable within ten minutes. |  | BA, RSG | BA | [15 empty] | RSG |  |  |  |  | Part 1.4 Evidence of compliance with Requirement R1, Part 1.4 may include, but is not limited to, documentation that the reserves maintained to comply with Requirement R1, Part 1.4 are fully deployable within ten minutes. | 2021-06-28 |  |  |  | 4.1.2.1 The Reserve Sharing Group when comprised of a Source Balancing Authority becomes the source Reserve Sharing Group.4.1.2.2 The Reserve Sharing Group when comprised of a Sink Balancing Authority becomes the sink Reserve Sharing Group. |  | 14000000 | WECC-US | [5 empty] | WECC-US
4. | 8912 | Each Generator Owner in the ISO-NE Planning Coordinator area and in NYISO Planning Coordinator area shall arrange for compensatory load shedding, in accordance with Attachment B and as provided by a Distribution Provider or Transmission Owner, that is adequate to compensate for the loss of generator(s) due to early tripping that is within the UFLS island identified by the Planning Coordinator in Requirement R2. |  | GO | [22 empty] | 2020-02-18 |  |  |  | 4.1.3. Distribution Providers that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators4.1.4. Transmission Owners that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators |  | 134000000 | NPCC-US |  | NPCC-US
4. | 8998 | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 64000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 9005 | Be submitted to the Compliance Enforcement Authority (CEA) with a request for extension of time if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. The submitted CAP shall document the following: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 74000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 9025 | Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 104000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 9035 | Be submitted to the CEA with a request for extension of time if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. The submitted CAP shall document the following: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 114000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 9061 | Study assumptions, system performance, alternatives considered, and coordinated recommendations. While these studies may be performed independently, the results shall be evaluated and coordinated by the entities involved. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2021-04-01 |  |  |  | Applicable Generator Owner: Generator Owner with a fully executed Agreement to conduct a study on the reliability impact of interconnecting a third party Facility to the Generator Owner’s existing Facility that is used to interconnect to the Transmission system. |  | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 9070 | The deadline by which the respondent is to provide the indicated data. |  | RC | [11 empty] | RC | [10 empty] | 2021-04-01 | [5 empty] | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 9084 | Monthly and annual peak hour controllable and dispatchable Demand Side Management under the control or supervision of the System Operator in megawatts for the prior calendar year. Three values shall be reported for each hour: 1) the committed megawatts (the amount under control or supervision), 2) the dispatched megawatts (the amount, if any, activated for use by the System Operator), and 3) the realized megawatts (the amount of actual demand reduction). | [24 empty] | 2021-04-01 | [5 empty] | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 9085 | A request to provide any or all of the following forecast data, as necessary: |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 9089 | Annual forecast Net Energy for Load in gigawatthours for ten calendar years into the future. | [24 empty] | 2021-04-01 | [5 empty] | 14400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 9105 | Guidelines to resolve the unacceptable differences in performance identified under Part 1.3. |  | PCPA | [9 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 9128 | Provisions to address mitigating actions needed to avoid violating NPIRs and to address periods when responsible Transmission Entity loses the ability to assess the capability of the electric system to meet the NPIRs. These provisions shall include responsibility to notify the Nuclear Plant Generator Operator within a specified time frame. | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 93400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 9132 | Communications and training Administrative elements: |  | BA, DP, GO, GOP, PCPA, RC, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  |  |  | PA |  | RC | [5 empty] | TO | TOP | TP | TSP |  | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 94000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 9136 | Provisions for supplying information necessary to report to government agencies, as related to NPIRs. | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 94400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 9161 | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-4 — Attachment 1. |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 440000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 9182 | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-4 — Attachment 1. |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 44000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 9208 | The deadline by which the respondent is to provide the indicated data. |  | TOP | [18 empty] | TOP |  |  |  | 2021-04-01 | [5 empty] | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 9213 | The deadline by which the respondent is to provide the indicated data. |  | BA | BA | [21 empty] | 2021-04-01 | [5 empty] | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 9312 | For the Planning Assessment, the Near-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed annually and be supported by current or past studies as qualified in Requirement R2, Part2.6. The following studies are required: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 932 | Interchange duration. |  | IA | [6 empty] | IA | [15 empty] | 2007-06-18 |  | 2014-09-30 |  |  |  | 13400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 933 | Each Balancing Authority and Transmission Service Provider that received the Arranged Interchange information from the Interchange Authority for reliability assessment has provided approval. |  | IA | [6 empty] | IA | [15 empty] | 2007-06-18 |  | 2014-09-30 |  |  | INT-007-1 R1. | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 9336 | Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES shall be identified, and a list of those Contingencies to be evaluated for System performance in Requirement R3, Part 3.1 created. The rationale for those Contingencies selected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 9371 | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-5 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 440000 | WECC-US | [5 empty] | WECC-US
4. | 9454 | Where technically feasible, perform authentication when establishing Dial-up Connectivity with applicable Cyber Assets. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 9459 | Have one or more methods for determining active vendor remote access sessions (including Interactive Remote Access and system-to-system remote access). |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 24000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 9472 | For a change that deviates from the existing baseline configuration: |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 14000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | 9488 | Document the results of the assessments conducted according to Parts 3.1, 3.2, and 3.3 and the action plan to remediate or mitigate vulnerabilities identified in the assessments including the planned date of completing the action plan and the execution status of any remediation or mitigation action items. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 34000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-04-12-0000008 | The process by which the Rating of equipment that comprises a Facility is determined. |  | GO | [22 empty] | 2021-10-01 | [5 empty] | 22400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-04-12-0000018 | The process by which the Rating of equipment that comprises a Facility is determined. |  | GO | [22 empty] | 2021-10-01 | [5 empty] | 32400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-06-07-0000002 | What recourse a customer has if the response is deemed unsatisfactory. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 10400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-06-08-0000007 | Undervoltage inhibit setting shall be less than or equal to 85 percent of nominal voltage. |  | DP, TO |  | DP | [22 empty] | 2013-11-07 |  |  |  | 20400000 | SPPRE-US
4. | RP-2021-06-08-0000011 | Breaker operating time (nameplate) of each location |  | DP, TO |  | DP | [22 empty] | 2013-11-07 |  |  |  | 50400000 | SPPRE-US
4. | RP-2021-06-08-0000019 | Breaker operating time (nameplate) of each location |  | GO | [24 empty] | 2013-11-07 |  |  |  | 60400000 | SPPRE-US
4. | RP-2021-06-08-0000024 | Time delay from initiation to trip signal | [26 empty] | 2014-11-13 |  |  |  | 10400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-06-14-0000021 | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 20400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-06-14-0000024 | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 20400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-06-14-0000027 | Where external interactive access into the Electronic Security Perimeter has been enabled, the Responsible Entity shall implement strong procedural or technical controls at the access points to ensure authenticity of the accessing party, where technically feasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 20400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-06-15-0000001 | Where external interactive access into the Electronic Security Perimeter has beenenabled, the Responsible Entity shall implement strong procedural or technical controlsat the access points to ensure authenticity of the accessing party, where technicallyfeasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 20400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-06-15-0000003 | Where external interactive access into the Electronic Security Perimeter has beenenabled, the Responsible Entity shall implement strong procedural or technical controlsat the access points to ensure authenticity of the accessing party, where technicallyfeasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2011-02-01 |  |  |  | 20400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-06-15-0000006 | Where external interactive access into the Electronic Security Perimeter has beenenabled, the Responsible Entity shall implement strong procedural or technical controlsat the access points to ensure authenticity of the accessing party, where technicallyfeasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 20400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-06-15-0000027 | Where applicable, these facilities shall be redundant and diversely routed. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 10400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-06-16-0000010 | The process by which the Rating of equipment that comprises a Facility is determined. |  | GO | [24 empty] | 2011-05-24 |  |  |  | 20400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-06-16-0000020 | The process by which the Rating of equipment that comprises a Facility is determined. |  | TO | [24 empty] | 2011-05-24 |  |  |  | 30400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-06-16-0000024 | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 20400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-06-16-0000040 | Consider the following resource availability characteristics and document how and why they were included in the analysis or why they were not included: • Availability and deliverability of fuel. • Common mode outages that affect resource availability • Environmental or regulatory restrictions of resource availability. • Any other demand (Load) response programs not included in R1.3.1. • Sensitivity to resource outage rates. • Impacts of extreme weather/drought conditions that affect unit availability. • Modeling assumptions for emergency operation procedures used to make reserves available. • Market resources not committed to serving Load (uncommitted resources) within the Planning Coordinator area. |  | PCPA | [9 empty] | PA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  |  | 10400000 | RF-US |  |  | RF-US
4. | RP-2021-06-17-0000007 | Verify at least once every 15 calendarmonths that access to the designatedstorage locations for BES Cyber SystemInformation, whether physical orelectronic, are correct and are those thatthe Responsible Entity determines arenecessary for performing assigned workfunctions. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 40400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-06-17-0000009 | Where external interactive access into the Electronic Security Perimeter has beenenabled, the Responsible Entity shall implement strong procedural or technical controlsat the access points to ensure authenticity of the accessing party, where technicallyfeasible. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. |  | 20400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-06-17-0000011 | Where technically feasible, performauthentication when establishingDial-up Connectivity with applicableCyber Assets. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 10400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-06-18-0000018 | Where applicable, these facilities shall be redundant and diversely routed. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2009-05-13 |  | 2015-09-30 |  |  |  | 10400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-06-21-0000003 | The Transmission Operator and Balancing Authority shall arrange deliveries of electrical energy or fuel from remote systems through normal operating channels. |  | BA, TOP | BA | [17 empty] | TOP |  |  |  | 2013-07-01 |  | 2017-03-31 |  |  |  | 60400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-06-22-0000001 | To prepare for the next Contingency, system adjustments may be made, includingchanges to generation, uses of the transmission system, and the transmission systemtopology. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 20400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-06-22-0000002 | To prepare for the next Contingency, system adjustments may be made, includingchanges to generation, uses of the transmission system, and the transmission systemtopology. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 20400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-06-23-0000013 | Individual generator line interconnections. |  | TO | [22 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 20400000 | NPCC-US |  | NPCC-US
4. | RP-2021-06-24-0000026 | Time delay from initiation to trip signal. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  |  | 10400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-06-24-0000039 | Those planning events in Table 1 that are expected to produce more severeSystem impacts on its portion of the BES shall be identified, and a list of thoseContingencies to be evaluated for System performance in Requirement R3,Part 3.1 created. The rationale for those Contingencies selected for evaluationshall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-07-01 |  | 2020-06-10 |  |  |  | 30400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-06-24-0000051 | Those planning events in Table 1 that are expected to produce more severeSystem impacts on its portion of the BES, shall be identified, and a list createdof those Contingencies to be evaluated in Requirement R4, Part 4.1. Therationale for those Contingencies selected for evaluation shall be available assupporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-07-01 |  | 2020-06-10 |  |  |  | 40400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-06-24-0000131 | A periodicity for providing data. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 42200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-06-24-0000150 | A periodicity for providing data. |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 10400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-06-24-0000164 | A periodicity for providing data. |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 20400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-06-25-0000004 | Unit is operating in the synchronous condenser mode (very near zero real power level). |  | GOP | [5 empty] | GOP | [16 empty] | 2011-07-01 |  | 2015-03-31 |  |  |  | 10400000 | WECC-US | [5 empty] | WECC-US
4. | RP-2021-06-25-0000005 | Unit is operating in the synchronous condenser mode (very near zero real power level). |  | GOP | [5 empty] | GOP | [16 empty] | 2011-07-01 |  | 2015-03-31 |  |  |  | 10400000 | WECC-US | [5 empty] | WECC-US
4. | RP-2021-06-25-0000010 | Unit is operating in the synchronous condenser mode (very near zero real power level). |  | GOP | [5 empty] | GOP | [16 empty] | 2015-04-01 |  | 2017-06-30 |  |  |  | 10400000 | WECC-US | [5 empty] | WECC-US
4. | RP-2021-06-30-0000005 | Verify at least once every 15 calendar months that access to the designated storage locations for BES Cyber System Information, whether physical or electronic, are correct and are those that the Responsible Entity determines are necessary for performing assigned work functions. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 40400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-06-30-0000006 | Where technically feasible, perform authentication when establishing Dialup Connectivity with applicable Cyber Assets. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-005-6:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 10400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-06-30-0000007 | Where technically feasible, perform authentication when establishing Dialup Connectivity with applicable Cyber Assets. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 10400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-07-01-0000015 | To prepare for the next Contingency, system adjustments may be made, including changes to generation, uses of the transmission system, and the transmission system topology. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 23200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-07-09-0000010 | Overfrequency trip settings of individual generating units greater than 20 MVA (gross nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-5 — Attachment 1. |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2021-04-01 |  |  |  | UFLS entities shall mean all entities that are responsible for the ownership,operation, or control of UFLS equipment as required by the UFLS programestablished by the Planning Coordinators. Such entities may include one ormore of the following: 4.2.1 Transmission Owners4.2.2 Distribution Providers4.2.3 UFLS-Only Distribution Providers4.3. Transmission Owners that own Elements identified in the UFLS programestablished by the Planning Coordinators. |  | 40400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-07-09-0000052 | Those planning events in Table 1, that are expected to produce more severe System impacts on its portion of the BES, shall be identified and a list of those Contingencies to be evaluated for System performance in Requirement R3, Part 3.1 created. The rationale for those Contingencies selected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 30400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-07-09-0000056 | Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES, shall be identified, and a list created of those Contingencies to be evaluated in Requirement R4, Part 4.1. The rationale for those Contingencies selected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 40400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-07-12-0000029 | Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES shall be identified, and a list of those Contingencies to be evaluated for System performance in Requirement R3, Part 3.1 created. The rationale for those Contingencies selected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 30400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-07-12-0000043 | Those planning events in Table 1 that are expected to produce more severe System impacts on its portion of the BES, shall be identified, and a list created of those Contingencies to be evaluated in Requirement R4, Part 4.1. The rationale for those Contingencies selected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 40400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-07-13-0000004 | Obtain and utilize status, voltages, and flow data for Facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator; |  | BA, DP, GOP, TOP | BA | DP |  |  |  | GOP | [12 empty] | TOP | [9 empty] | 100400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-07-13-0000010 | Identify the minimum allowable System Voltage Limit; |  | RC | [11 empty] | RC | [16 empty] | 30400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-07-13-0000019 | Describe how stability limits are determined, considering levels of transfers, Load and generation dispatch, and System conditions including any changes to System topology such as Facility outages. |  | RC | [11 empty] | RC | [16 empty] | 40400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-07-13-0000038 | In determining the System’s response to any Contingency identified in Requirement R5, planned manual load shedding is acceptable only after all other available System adjustments have been made. |  | RC | [11 empty] | RC | [16 empty] | 60400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-07-13-0000065 | Each impacted Transmission Operator within its Reliability Coordinator Area, the information identified in Requirement R5 Parts 5.2.2 – 5.2.6 for each established stability limit and each established IROL, and any updates to that information within an agreed upon time frame necessary for inclusion in the Transmission Operator’s Operational Planning Analyses. |  | RC, TOP, TP | [11 empty] | RC | [6 empty] | TOP | TP | [8 empty] | 50400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-07-13-0000071 | The planning event Contingency(ies) associated with the identified instability requiring the Corrective Action Plan; |  | RC, TOP, TP | [11 empty] | RC | [6 empty] | TOP | TP | [8 empty] | 70400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-07-13-0000076 | An encroachment due to vegetation growth into the MVCD that caused a vegetation‐related Sustained Outage.Footnote: Multiple Sustained Outages on an individual line, if caused by the same vegetation, will be reported as one outage regardless of the actual number of outages within a 24‐hour period. |  | GO, TO |  |  |  |  | GO | [23 empty] | 10400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-07-13-0000082 | Crew or contractor availability/Mutual assistance agreements |  | GO, TO |  |  |  |  | GO | [23 empty] | 70400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-07-15-0000025 | Re-evaluate all BES Elements at least once every five calendar years in accordance with Parts 5.1 and 5.2, and notify owners in accordance with Part 5.3 to implement the re-evaluated list of BES Elements as per the Implementation Plan. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 50400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-07-15-0000029 | Frequency of any one of the voltage(s) in Requirement R6, Part 6.1. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 60400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-07-15-0000033 | Frequency of at least one of the voltages in Requirement R7, Part 7.1. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 70400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-07-15-0000043 | FR and DDR data will be provided in electronic files that are formatted in conformance with C37.111, (IEEE Standard for Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 or later. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 110400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-08-13-0000007 | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 20400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-08-13-0000012 | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  |  |  | 20400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-08-13-0000016 | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-003-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets shall only be required to comply with CIP-003-3 Requirement R2. |  | 20400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-08-13-0000020 | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 20400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4. | RP-2021-08-13-0000024 | The senior manager or delegate(s), shall authorize and document any exception from the requirements of the cyber security policy. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 20400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.1 | RP-2021-04-12-0000011 | The scope of equipment addressed shall include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | GO | [22 empty] | 2021-10-01 | [5 empty] | 24100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.1 | RP-2021-04-12-0000021 | The scope of equipment addressed shall include, but not be limited to, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | GO | [22 empty] | 2021-10-01 | [5 empty] | 34100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.1. | RP-2021-06-16-0000011 | The scope of equipment addressed shall include, but not be limited to, conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | GO | [24 empty] | 2011-05-24 |  |  |  | 24100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.1. | RP-2021-06-16-0000021 | The scope of equipment addressed shall include, but not be limited to, transmission conductors, transformers, relay protective devices, terminal equipment, and series and shunt compensation devices. |  | TO | [24 empty] | 2011-05-24 |  |  |  | 34100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.1. | RP-2021-06-23-0000026 | Transmission Owners or Generator Owners shall repair or replace any Protection System or RAS that misoperated with FEPS and FERAS within 20 business days of the date of the Misoperation identification, or |  | GO, TO, TOP |  |  |  |  | GO | [12 empty] | TO | TOP |  |  |  | 2011-10-01 |  | 2017-03-31 |  |  |  | 24100000 | WECC-US | [5 empty] | WECC-US
4.1. | RP-2021-06-24-0000052 | Each Planning Coordinator and Transmission Planner shall coordinatewith adjacent Planning Coordinators and Transmission Planners toensure that Contingencies on adjacent Systems which may impacttheir Systems are included in the Contingency list. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-07-01 |  | 2020-06-10 |  |  |  | 44100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.1. | RP-2021-06-30-0000025 | Prior to the change, determine required cyber security controls in CIP-005 and CIP-007 that could be impacted by the change; |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 14100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.1. | RP-2021-07-01-0000018 | The scope of equipment addressed shall include, but not be limited to,conductors, transformers, relay protective devices, terminal equipment, andseries and shunt compensation devices. |  | GO | [22 empty] | 2013-01-01 |  | 2021-09-30 |  |  |  | 24100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.1. | RP-2021-07-01-0000020 | The scope of equipment addressed shall include, but not be limited to,transmission conductors, transformers, relay protective devices, terminalequipment, and series and shunt compensation devices. |  | TO | [22 empty] | 2013-01-01 |  | 2021-09-30 |  |  |  | 34100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.1. | RP-2021-07-12-0000012 | System peak Load for one of the five years. System peak Load levels shall include a Load model which represents the expected dynamic behavior of Loads that could impact the study area, considering the behavior of induction motor Loads. An aggregate System Load model which represents the overall dynamic behavior of the Load is acceptable. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 24100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.1. | RP-2021-07-12-0000030 | The Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 34100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.1. | RP-2021-07-12-0000044 | Each Planning Coordinator and Transmission Planner shall coordinate with adjacent Planning Coordinators and Transmission Planners to ensure that Contingencies on adjacent Systems which may impact their Systems are included in the Contingency list. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 44100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.2 | RP-2021-04-12-0000012 | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | GO | [22 empty] | 2021-10-01 | [5 empty] | 24200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.2 | RP-2021-04-12-0000022 | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | GO | [22 empty] | 2021-10-01 | [5 empty] | 34200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.2. | RP-2021-06-16-0000012 | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | GO | [24 empty] | 2011-05-24 |  |  |  | 24200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.2. | RP-2021-06-16-0000022 | The scope of Ratings addressed shall include, as a minimum, both Normal and Emergency Ratings. |  | TO | [24 empty] | 2011-05-24 |  |  |  | 34200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.2. | RP-2021-06-23-0000027 | Transmission Owners or Generator Owners shall remove from service the associated Element or RAS. |  | GO, TO, TOP |  |  |  |  | GO | [12 empty] | TO | TOP |  |  |  | 2011-10-01 |  | 2017-03-31 |  |  |  | 24200000 | WECC-US | [5 empty] | WECC-US
4.2. | RP-2021-06-23-0000029 | Transmission Owners or Generator Owners shall remove from service the associated Element or RAS. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2017-04-01 |  | 2021-01-01 |  | 4.1. Transmission Owners of selected WECC major transmission path facilities and RAS listed in tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. 4.2. Generator Owners that own RAS listed in the Table titled “Major WECC Remedial Action Schemes (RAS)” provided at https://wecc.biz/Reliability/TableMajorRAS4-28-08.pdf..4.3. Transmission Operators that operate major transmission path facilities and RAS listed in Tables titled “Major WECC Transfer Paths in the Bulk Electric System” provided at https://www.wecc.biz/Reliability/TableMajorPaths4-28-08.pdf and “Major WECC Remedial Action Schemes (RAS)” provided at https://www.wecc.biz/Reliability/TableMajorRAS4-28-08.pdf. |  | 24200000 | WECC-US | [5 empty] | WECC-US
4.2. | RP-2021-06-30-0000026 | Following the change, verify that required cyber security controls determined in 1.4.1 are not adversely affected; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 14200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.2. | RP-2021-07-01-0000019 | The scope of Ratings addressed shall include, as a minimum, both Normaland Emergency Ratings. |  | GO | [22 empty] | 2013-01-01 |  | 2021-09-30 |  |  |  | 24200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.2. | RP-2021-07-01-0000021 | The scope of Ratings addressed shall include, as a minimum, both Normaland Emergency Ratings. |  | TO | [22 empty] | 2013-01-01 |  | 2021-09-30 |  |  |  | 34200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.2. | RP-2021-07-12-0000013 | System Off-Peak Load for one of the five years. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 24200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.3. | RP-2021-06-30-0000027 | Document the results of the verification. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 14300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.3. | RP-2021-07-12-0000014 | For each of the studies described in Requirement R2, Parts 2.4.1 and 2.4.2, sensitivity case(s) shall be utilized to demonstrate the impact of changes to the basic assumptions used in the model. To accomplish this, the sensitivity analysis in the Planning Assessment must vary one or more of the following conditions by a sufficient amount to stress the System within a range of credible conditions that demonstrate a measurable change in performance:  Load level, Load forecast, or dynamic Load model assumptions.  Expected transfers.  Expected in service dates of new or modified Transmission Facilities.  Reactive resource capability.  Generation additions, retirements, or other dispatch scenarios. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 24300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.3. | RP-2021-07-12-0000049 | Updated timetable for implementing the selected actions in Part 11.1 |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 114300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.3. | RP-2021-07-12-0000054 | Updated timetable for implementing the selected actions in Part 7.1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 74300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.4. | RP-2021-06-24-0000033 | When known outage(s) of generation or Transmission Facility(ies) areplanned in the Near-Term Planning Horizon, the impact of selectedknown outages on System performance shall be assessed. Theseknown outage(s) shall be selected for assessment consistent with adocumented outage coordination procedure or technical rationale bythe Planning Coordinator or Transmission Planner. Known outage(s)shall not be excluded solely based upon outage duration. Theassessment shall be performed for the P1 categories identified inTable 1 with the System peak or Off-Peak conditions that the Systemis expected to experience when the known outage(s) are planned.This assessment shall include, at a minimum, those known outagesexpected to produce more severe System impacts on the PlanningCoordinator or Transmission Planner’s portion of the BES. Past orcurrent studies may support the selection of known outage(s), if thestudy(s) has comparable post-Contingency System conditions andconfiguration such as those following P3 or P6 category events inTable 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-07-01 |  | 2020-06-10 |  |  |  | 24400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.4. | RP-2021-07-12-0000015 | When known outage(s) of generation or Transmission Facility(ies) are planned in the Near-Term Planning Horizon, the impact of selected known outages on System performance shall be assessed. These known outage(s) shall be selected for assessment consistent with a documented outage coordination procedure or technical rationale by the Planning Coordinator or Transmission Planner. Known outage(s) shall not be excluded solely based upon outage duration. The assessment shall be performed for the P1 categories identified in Table 1 with the System peak or Off-Peak conditions that the System is expected to experience when the known outage(s) are planned. This assessment shall include, at a minimum, those known outages expected to produce more severe System impacts on the Planning Coordinator or Transmission Planner’s portion of the BES. Past or current studies may support the selection of known outage(s), if the study(s) has comparable post-Contingency System conditions and configuration such as those following P3 or P6 category events in Table 1. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 24400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.5. | RP-2021-06-22-0000036 | Total and available peak hour forecast of controllable and dispatchableDemand Side Management (summer and winter), in megawatts, underthe control or supervision of the System Operator for ten calendar yearsinto the future. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 14500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.5. | RP-2021-06-24-0000034 | When an entity’s spare equipment strategy could result in theunavailability of major Transmission equipment that has a lead timeof one year or more (such as a transformer), the impact of thispossible unavailability on System performance shall be assessed.Based upon this assessment, an analysis shall be performed for theselected P1 and P2 category events identified in Table 1 for which theunavailability is expected to produce more severe System impacts onits portion of the BES. The analysis shall simulate the conditions thatthe System is expected to experience during the possibleunavailability of the long lead time equipment. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-07-01 |  | 2020-06-10 |  |  |  | 24500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.5. | RP-2021-07-07-0000027 | Total and available peak hour forecast of controllable and dispatchable Demand Side Management (summer and winter), in megawatts, under the control or supervision of the System Operator for ten calendar years into the future. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 14500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
4.5. | RP-2021-07-12-0000016 | When an entity’s spare equipment strategy could result in the unavailability of major Transmission equipment that has a lead time of one year or more (such as a transformer), the impact of this possible unavailability on System performance shall be assessed. Based upon this assessment, an analysis shall be performed for the selected P1 and P2 category events identified in Table 1 for which the unavailability is expected to produce more severe System impacts on its portion of the BES. The analysis shall simulate the conditions that the System is expected to experience during the possible unavailability of the long lead time equipment. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 24500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5 | 79780000024 | The limitations, if any, upon the amount of interruptible load that may be included. |  | RRO, RSG | [14 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  |  | 25000000 | NPCC-ON |  | NPCC-US
5 | 79780000251 | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 12500000 | NPCC-ON |  | NPCC-US
5 | 79780000304 | Cyber Assets used in the access control and monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003, Standard CIP-004 Requirement R3, Standard CIP-005 Requirements R2 and R3, Standard CIP-006 Requirements R2 and R3, Standard CIP-007, Requirements R1 and R3 through R9, Standard CIP-008, and Standard CIP-009. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780000311 | The required documentation shall, at least, identify and describe: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 25000000 | NPCC-ON |  | NPCC-US
5 | 79780000325 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  |  | 45000000 | NPCC-ON |  | NPCC-US
5 | 79780000335 | Procedures for reviewing access authorization requests and revocation of access authorization, in accordance with CIP-004 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780000362 | Procedures for reviewing access authorization requests and revocation of access authorization, in accordance with CIP-004 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780000416 | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 65000000 | NPCC-ON |  | NPCC-US
5 | 79780000432 | Process for ensuring that the Cyber Security Incident response plan is reviewed at least annually. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780000512 | Declaring an Energy Emergency through its Reliability Coordinator; and |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | 65000000 | NPCC-ON |  | NPCC-US
5 | 79780000533 | Declaring an Energy Emergency through its Reliability Coordinator; and |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-09-30 |  |  |  | 65000000 | NPCC-ON |  | NPCC-US
5 | 79780000569 | The affected Transmission Operators may resynchronize the isolated area(s) with the surrounding area(s) when the following conditions are met: |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  |  | 115000000 | NPCC-ON |  | NPCC-US
5 | 79780000602 | The plan shall include procedures and responsibilities for conducting periodic tests, at least annually, to ensure viability of the plan. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780000625 | System protection and coordination. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 21500000 | NPCC-ON |  | NPCC-US
5 | 79780000636 | Documentation that the assessment included study assumptions, system performance, alternatives considered, and jointly coordinated recommendations. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [14 empty] | 2007-06-18 |  | 2011-09-30 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780000647 | Each Transmission Owner shall establish and document a process for the immediate communication of vegetation conditions that present an imminent threat of a transmission line outage. This is so that action (temporary reduction in line rating, switching line out of service, etc.) may be taken until the threat is relieved. |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780000695 | Other assumptions. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2012-12-31 |  |  |  | 13500000 | NPCC-ON |  | NPCC-US
5 | 79780000715 | In determining the system’s response to any of the multiple Contingencies, identified in Reliability Standard TPL-003, in addition to the actions identified in R2.3.1 and R2.3.2, the following shall be acceptable: |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 25000000 | NPCC-ON |  | NPCC-US
5 | 79780000722 | Anticipated transmission system configuration, generation dispatch and Load level. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 35000000 | NPCC-ON |  | NPCC-US
5 | 79780000743 | Starting with all Facilities in service and following any of the multiple Contingencies identified in Reliability Standard TPL-003 the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 25000000 | NPCC-ON |  | NPCC-US
5 | 79780000751 | Anticipated transmission system configuration, generation dispatch and Load level. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 35000000 | NPCC-ON |  | NPCC-US
5 | 79780000779 | Allowed uses of Special Protection Systems or Remedial Action Plans. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 35000000 | NPCC-ON |  | NPCC-US
5 | 79780000808 | Allowed uses of Special Protection Systems or Remedial Action Plans. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 35000000 | NPCC-ON |  | NPCC-US
5 | 79780001001 | Capacity and energy adequacy conditions. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780001028 | Capacity and energy adequacy conditions. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780001055 | Capacity and energy adequacy conditions. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780001111 | Coordination of information exchange to support reliability assessments. |  | RC | [11 empty] | RC | [9 empty] | M1.1.5 Coordination of information exchange to support reliability assessments. | 2007-06-18 |  | 2017-03-31 |  |  |  | 11500000 | NPCC-ON |  | NPCC-US
5 | 79780001141 | A requirement that TTC and ATC values shall be determined and posted as follows: |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780001162 | A description of the allocation processes listed below that are applicable to the Transmission Service Provider: • Processes used to allocate transfer or Flowgate capability among multiple lines or sub-paths within a larger ATC Path or Flowgate. • Processes used to allocate transfer or Flowgate capabilities among multiple owners or users of an ATC Path or Flowgate. • Processes used to allocate transfer or Flowgate capabilities between Transmission Service Providers to address issues such as forward looking congestion management and seams coordination. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 35000000 | NPCC-ON |  | NPCC-US
5 | 79780001172 | Each Reliability Coordinator adjacent to the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 45000000 | NPCC-ON |  | NPCC-US
5 | 79780001202 | Describe the inclusion or exclusion rationale for generation resources of each Load-Serving Entity including those generation resources not directly connected to the Transmission Service Provider’s system but serving Load-Serving Entity loads connected to the Transmission Service Provider’s system. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780001266 | Allowances for parallel path (loop flow) impacts. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 13500000 | NPCC-ON |  | NPCC-US
5 | 79780001271 | Describe the formal process for the Regional Reliability Organization to grant any variances to individual Transmission Service Providers from the Regional TRM methodology. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780001298 | Transformer (voltage and phase-shifting): nominal voltages of windings, impedance, tap ratios (voltage and/or phase angle or tap step size), regulated bus and voltage set point, Normal and Emergency Ratings (consistent with methodologies defined and Ratings supplied per Reliability Standard FAC-004-0 and FAC-005-0.), and equipment status. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780001312 | Dynamics data shall be consistent with the reported steady-state (power flow) data supplied per Reliability Standard MOD-010 Requirement 1. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780001360 | Information to be verified and reported: |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780001371 | Information to be reported: |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780001383 | The following information on how source and sink for transmission service is accounted for in ATC calculations including: |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2013-09-30 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780001431 | Uses Load forecast by Balancing Authority. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 11500000 | NPCC-ON |  | NPCC-US
5 | 79780001445 | The Transmission Operator shall identify when the TTC for the ATC Path being studied has an adverse impact on the TTC value of any existing path. Do this by modeling the flow on the path being studied at its proposed new TTC level simultaneous with the flow on the existing path at its TTC level while at the same time honoring the reliability criteria outlined in R2.1. The Transmission Operator shall include the resolution of this adverse impact in its study report for the ATC Path. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 25000000 | NPCC-ON |  | NPCC-US
5 | 79780001482 | At a minimum, establish the TFC once per calendar year. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 25000000 | NPCC-ON |  | NPCC-US
5 | 79780001490 | Contains modeling data and system topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination Areas. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 35000000 | NPCC-ON |  | NPCC-US
5 | 79780001505 | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 65000000 | NPCC-ON |  | NPCC-US
5 | 79780001513 | The impact of non-firm Network Integration Transmission Service serving Load within the Transmission Service Provider’s area (i.e., secondary service), to include load growth, and losses not otherwise included in Transmission Reliability Margin or Capacity Benefit Margin. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 75000000 | NPCC-ON |  | NPCC-US
5 | 79780001547 | At a minimum, establish the TFC once per calendar year. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 25000000 | NPCC-ON |  | NPCC-US
5 | 79780001555 | Contains modeling data and system topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination Areas. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 35000000 | NPCC-ON |  | NPCC-US
5 | 79780001570 | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 65000000 | NPCC-ON |  | NPCC-US
5 | 79780001578 | The impact of non-firm Network Integration Transmission Service serving Load within the Transmission Service Provider’s area (i.e., secondary service), to include load growth, and losses not otherwise included in Transmission Reliability Margin or Capacity Benefit Margin. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 75000000 | NPCC-ON |  | NPCC-US
5 | 79780001609 | Provision to consider nuclear plant coping times required by the NPLRs and their relation to the coordination of grid and nuclear plant restoration following a nuclear plant loss of Off-site Power. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 93500000 | NPCC-ON |  | NPCC-US
5 | 79780001617 | Provisions for personnel training, as related to NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 94500000 | NPCC-ON |  | NPCC-US
5 | 79780001674 | Megawatts and megavars. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 21350000 | NPCC-ON |  | NPCC-US
5 | 79780001694 | Naming of data files in conformance with the IEEE C37.232 Recommended Practice for Naming Time Sequence Data Files2. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 45000000 | NPCC-ON |  | NPCC-US
5 | 79780001740 | Tie tripping schemes. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  |  | 12500000 | NPCC-ON |  | NPCC-US
5 | 79780001776 | Schedule for system maintenance. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2021-03-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780001784 | Requirements to demonstrate the proposed SPS will coordinate with other protection and control systems and applicable Regional Reliability Organization Emergency procedures. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780001802 | Provide corrective action plans for non-compliant SPSs. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  |  | 35000000 | NPCC-ON |  | NPCC-US
5 | 79780001821 | Schedule for system maintenance. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780001833 | Date last tested. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2022-06-30 |  |  |  | 35000000 | NPCC-ON |  | NPCC-US
5 | 79780001847 | Breaker operating times. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780001855 | Any other schemes that are part of or impact the UVLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UFLS and Special Protection Systems. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780001862 | For any Misoperation, a Corrective Action Plan to avoid future Misoperations of a similar nature. |  | DP, LSE, TOP |  | DP | [5 empty] | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780001878 | Set transmission line relays on weak source systems so they do not operate at or below 170% of the maximum end-of-line three-phase fault magnitude (expressed in amperes). |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780001973 | Development of IROLs and SOLs. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-01-21 |  |  |  | 65000000 | NPCC-ON |  | NPCC-US
5 | 79780002041 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 13500000 | NPCC-ON |  | NPCC-US
5 | 79780002062 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 13500000 | NPCC-ON |  | NPCC-US
5 | 79780002086 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13500000 | NPCC-ON |  | NPCC-US
5 | 79780002092 | Consider all contingencies applicable to Category B. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780002111 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 13500000 | NPCC-ON |  | NPCC-US
5 | 79780002117 | Consider all contingencies applicable to Category B. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780002136 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13500000 | NPCC-ON |  | NPCC-US
5 | 79780002142 | Consider all contingencies applicable to Category C. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780002161 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 13500000 | NPCC-ON |  | NPCC-US
5 | 79780002167 | Consider all contingencies applicable to Category C. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780002183 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  |  | 13500000 | NPCC-ON |  | NPCC-US
5 | 79780002204 | Reliability impacts of new or proposed environmental rules and regulations. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  |  | 35000000 | NPCC-ON |  | NPCC-US
5 | 79780002211 | Transmission system and supporting information (thermal, voltage, and Stability Limits, contingency analyses, system restoration, system modeling and data requirements, and protection systems.) |  | RRO | [14 empty] | RRO | [9 empty] | 2009-04-15 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780002351 | Transmission system and supporting information (thermal, voltage, and Stability Limits, contingency analyses, system restoration, system modeling and data requirements, and protection systems.) |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780002361 | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 12500000 | NPCC-ON |  | NPCC-US
5 | 79780002415 | Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003-2; Standard CIP-004-2 Requirement R3; Standard CIP-005-2 Requirements R2 and R3; Standard CIP-006-2 Requirement R3; Standard CIP-007-2 Requirements R1 and R3 through R9; Standard CIP-008-2; and Standard CIP-009-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780002422 | The required documentation shall, at least, identify and describe: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 25000000 | NPCC-ON |  | NPCC-US
5 | 79780002436 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 45000000 | NPCC-ON |  | NPCC-US
5 | 79780002446 | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-2 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780002494 | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  |  | 65000000 | NPCC-ON |  | NPCC-US
5 | 79780002510 | Process for ensuring that the Cyber Security Incident response plan is reviewed at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780002546 | Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. . |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 93500000 | NPCC-ON |  | NPCC-US
5 | 79780002554 | Provisions for personnel training, as related to NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 94500000 | NPCC-ON |  | NPCC-US
5 | 79780002577 | Identification of Cranking Paths and initial switching requirements between each Blackstart Resource and the unit(s) to be started. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780002622 | Criteria and conditions for reestablishing interconnections with other Transmission Operators within its Reliability Coordinator Area, with Transmission Operators in other Reliability Coordinator Areas, and with other Reliability Coordinators. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780002672 | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  |  | 65000000 | NPCC-ON |  | NPCC-US
5 | 79780002696 | Starting with all Facilities in service and following any of the multiple Contingencies identified in Reliability Standard TPL-003 the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 25000000 | NPCC-ON |  | NPCC-US
5 | 79780002706 | Anticipated transmission system configuration, generation dispatch and Load level. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 35000000 | NPCC-ON |  | NPCC-US
5 | 79780002720 | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | 12500000 | NPCC-ON |  | NPCC-US
5 | 79780002774 | Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirement R3; Standard CIP-007-3 Requirements R1 and R3 through R9; Standard CIP-008-3; and Standard CIP-009-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780002781 | The required documentation shall, at least, identify and describe: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  |  | 25000000 | NPCC-ON |  | NPCC-US
5 | 79780002795 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  |  | 45000000 | NPCC-ON |  | NPCC-US
5 | 79780002805 | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-3 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780002855 | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. |  | 65000000 | NPCC-ON |  | NPCC-US
5 | 79780002871 | Process for ensuring that the Cyber Security Incident response plan is reviewed at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780002891 | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-2 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780002912 | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-2 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780002930 | Procedures for reviewing access authorization requests and revocation of access authorization, in accordance with CIP-004 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780002964 | Procedures for reviewing access authorization requests and revocation of access authorization, in accordance with CIP-004 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780002985 | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-3 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780003013 | A description of the allocation processes listed below that are applicable to the Transmission Service Provider: • Processes used to allocate transfer or Flowgate capability among multiple lines or sub-paths within a larger ATC Path or Flowgate. • Processes used to allocate transfer or Flowgate capabilities among multiple owners or users of an ATC Path or Flowgate. • Processes used to allocate transfer or Flowgate capabilities between Transmission Service Providers to address issues such as forward looking congestion management and seams coordination. |  | TSP | [20 empty] | TSP |  | 2010-09-16 | [5 empty] | 35000000 | NPCC-ON |  | NPCC-US
5 | 79780003024 | Each Reliability Coordinator adjacent to the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-09-16 | [5 empty] | 45000000 | NPCC-ON |  | NPCC-US
5 | 79780003048 | Uses Load forecast by Balancing Authority. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 11500000 | NPCC-ON |  | NPCC-US
5 | 79780003063 | The Transmission Operator shall identify when the TTC for the ATC Path being studied has an adverse impact on the TTC value of any existing path. Do this by modeling the flow on the path being studied at its proposed new TTC level simultaneous with the flow on the existing path at its TTC level while at the same time honoring the reliability criteria outlined in R2.1. The Transmission Operator shall include the resolution of this adverse impact in its study report for the ATC Path. |  | TOP | [18 empty] | TOP |  |  |  | 2010-09-16 |  | 2017-03-31 |  |  |  | 25000000 | NPCC-ON |  | NPCC-US
5 | 79780003161 | Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirement R3; Standard CIP-007-3 Requirements R1 and R3 through R9; Standard CIP-008-3; and Standard CIP-009-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780003167 | The required documentation shall, at least, identify and describe: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | 25000000 | NPCC-ON |  | NPCC-US
5 | 79780003179 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | 45000000 | NPCC-ON |  | NPCC-US
5 | 79780003190 | The limitations, if any, upon the amount of interruptible load that may be included. |  | RRO, RSG | [14 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  |  | 25000000 | NPCC-ON |  | NPCC-US
5 | 79780003263 | Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003-4; Standard CIP-004-4 Requirement R3; Standard CIP-005-4 Requirements R2 and R3; Standard CIP-006-4 Requirement R3; Standard CIP-007-4 Requirements R1 and R3 through R9; Standard CIP-008-4; and Standard CIP-009-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780003270 | The required documentation shall, at least, identify and describe: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 25000000 | NPCC-ON |  | NPCC-US
5 | 79780003284 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 45000000 | NPCC-ON |  | NPCC-US
5 | 79780003294 | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-4 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780003344 | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 65000000 | NPCC-ON |  | NPCC-US
5 | 79780003360 | Process for ensuring that the Cyber Security Incident response plan is reviewed at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780003380 | Declaring an Energy Emergency through its Reliability Coordinator; and |  | BA | BA | [21 empty] | 2011-01-10 |  | 2012-09-12 |  |  |  | 65000000 | NPCC-ON |  | NPCC-US
5 | 79780003412 | Documentation that the assessment included study assumptions, system performance, alternatives considered, and jointly coordinated recommendations. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [14 empty] | 2011-01-10 |  | 2015-12-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780003426 | Capacity and energy adequacy conditions. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780003460 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13500000 | NPCC-ON |  | NPCC-US
5 | 79780003484 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 13500000 | NPCC-ON |  | NPCC-US
5 | 79780003490 | Consider all contingencies applicable to Category B. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780003509 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13500000 | NPCC-ON |  | NPCC-US
5 | 79780003515 | Consider all contingencies applicable to Category B. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780003534 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13500000 | NPCC-ON |  | NPCC-US
5 | 79780003540 | Consider all contingencies applicable to Category C. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780003556 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13500000 | NPCC-ON |  | NPCC-US
5 | 79780003625 | Cyber Assets used in the access control and monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003, Standard CIP-004 Requirement R3, Standard CIP-005 Requirements R2 and R3, Standard CIP-006 Requirements R2 and R3, Standard CIP-007, Requirements R1 and R3 through R9, Standard CIP-008, and Standard CIP-009. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780003631 | The required documentation shall, at least, identify and describe: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 25000000 | NPCC-ON |  | NPCC-US
5 | 79780003643 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 45000000 | NPCC-ON |  | NPCC-US
5 | 79780003656 | Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003-2; Standard CIP-004-2 Requirement R3; Standard CIP-005-2 Requirements R2 and R3; Standard CIP-006-2 Requirement R3; Standard CIP-007-2 Requirements R1 and R3 through R9; Standard CIP-008-2; and Standard CIP-009-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780003662 | The required documentation shall, at least, identify and describe: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  |  | 25000000 | NPCC-ON |  | NPCC-US
5 | 79780003674 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  |  | 45000000 | NPCC-ON |  | NPCC-US
5 | 79780003806 | Capacity and energy adequacy conditions. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780003900 | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-2 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780003919 | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-3 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780003965 | The following information on how source and sink for transmission service is accounted for in ATC calculations including: |  | TSP | [20 empty] | TSP |  | 2013-09-27 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780003982 | Unit commitment and dispatch order, to include all designated network resources and other resources that are committed or have the legal obligation to run, (within or out of economic dispatch) as they are expected to run. |  | TOP | [18 empty] | TOP |  |  |  | 2013-10-01 |  |  |  | 4. Applicability:&lt;br/&gt;4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. &lt;br/&gt;4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 31500000 | NPCC-ON |  | NPCC-US
5 | 79780004040 | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-3 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780004058 | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-4 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780004182 | Capacity and energy adequacy conditions. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780004201 | Declaring an Energy Emergency through its Reliability Coordinator; and |  | BA | BA | [21 empty] | 2012-09-13 |  | 2017-03-31 |  |  |  | 65000000 | NPCC-ON |  | NPCC-US
5 | 79780004236 | Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. . |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 93500000 | NPCC-ON |  | NPCC-US
5 | 79780004243 | Provisions for personnel training, as related to NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 94500000 | NPCC-ON |  | NPCC-US
5 | 79780004338 | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 12500000 | NPCC-ON |  | NPCC-US
5 | 79780004445 | The limitations, if any, upon the amount of interruptible load that may be included. |  | RRO, RSG | [14 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  |  | 25000000 | NPCC-ON |  | NPCC-US
5 | 79780004566 | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 12500000 | NPCC-ON |  | NPCC-US
5 | 79780004590 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13500000 | NPCC-ON |  | NPCC-US
5 | 79780004629 | Consider all contingencies applicable to Category B. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780004634 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13500000 | NPCC-ON |  | NPCC-US
5 | 79780004654 | Consider all contingencies applicable to Category C. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780004659 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13500000 | NPCC-ON |  | NPCC-US
5 | 79780004680 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13500000 | NPCC-ON |  | NPCC-US
5 | 79780004694 | Consider all contingencies applicable to Category C. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780004699 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13500000 | NPCC-ON |  | NPCC-US
5 | 79780004715 | Consider all contingencies applicable to Category C. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780004732 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13500000 | NPCC-ON |  | NPCC-US
5 | 79780004745 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13500000 | NPCC-ON |  | NPCC-US
5 | 79780004766 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13500000 | NPCC-ON |  | NPCC-US
5 | 79780004842 |  |  | BA | BA | [23 empty] | 2006-11-01 |  |  |  | 75000000 | NPCC-ON |  | NPCC-US
5 | 79780004859 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 65000000 | NPCC-ON |  | NPCC-US
5 | 79780004891 |  |  | TOP | [18 empty] | TOP | [5 empty] | 2007-05-02 |  |  |  | 95000000 | NPCC-ON |  | NPCC-US
5 | 79780004913 |  |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-08-01 |  |  |  | 11500000 | NPCC-ON |  | NPCC-US
5 | 79780004919 |  |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-08-01 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780004945 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780004951 |  |  | TSP | [20 empty] | TSP |  |  |  | 2007-01-01 |  |  |  | 25000000 | NPCC-ON |  | NPCC-US
5 | 79780004984 |  |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780005031 |  |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780005120 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780005133 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2006-05-01 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780005146 |  |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2006-05-01 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780005210 |  |  | TOP | [18 empty] | TOP | [5 empty] | 2005-04-01 |  |  |  | 65000000 | NPCC-ON |  | NPCC-US
5 | 79780005343 | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 65000000 | NPCC-ON |  | NPCC-US
5 | 79780005386 | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  |  | 65000000 | NPCC-ON |  | NPCC-US
5 | 79780005613 | Starting with all Facilities in service and following any of the multiple Contingencies identified in Reliability Standard TPL-003 the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 25000000 | NPCC-ON |  | NPCC-US
5 | 79780005622 | Anticipated transmission system configuration, generation dispatch and Load level. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 35000000 | NPCC-ON |  | NPCC-US
5 | 79780005651 | Allowed uses of Remedial Action Schemes. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 35000000 | NPCC-ON |  | NPCC-US
5 | 79780005665 | Capacity and energy adequacy conditions. |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780005707 | At a minimum, establish the TFC once per calendar year. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 25000000 | NPCC-ON |  | NPCC-US
5 | 79780005715 | Contains modeling data and system topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination Areas. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 35000000 | NPCC-ON |  | NPCC-US
5 | 79780005730 | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 65000000 | NPCC-ON |  | NPCC-US
5 | 79780005738 | The impact of non-firm Network Integration Transmission Service serving Load within the Transmission Service Provider’s area (i.e., secondary service), to include load growth, and losses not otherwise included in Transmission Reliability Margin or Capacity Benefit Margin. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 75000000 | NPCC-ON |  | NPCC-US
5 | 79780005757 | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12500000 | NPCC-ON |  | NPCC-US
5 | 79780005769 | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12500000 | NPCC-ON |  | NPCC-US
5 | 79780005802 | Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 93500000 | NPCC-ON |  | NPCC-US
5 | 79780005810 | Provisions for personnel training, as related to NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 94500000 | NPCC-ON |  | NPCC-US
5 | 79780005819 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13500000 | NPCC-ON |  | NPCC-US
5 | 79780005840 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13500000 | NPCC-ON |  | NPCC-US
5 | 79780005849 | Consider all contingencies applicable to Category B. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780005865 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13500000 | NPCC-ON |  | NPCC-US
5 | 79780005874 | Consider all contingencies applicable to Category C. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780005890 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13500000 | NPCC-ON |  | NPCC-US
5 | 79780005903 | Requirements to demonstrate the proposed RAS will coordinate with other protection and control systems and applicable Regional Reliability Organization Emergency procedures. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780005921 | Provide corrective action plans for non-compliant RAS. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 35000000 | NPCC-ON |  | NPCC-US
5 | 79780005943 | Schedule for system maintenance. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-01-25 |  | 2021-03-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780005951 | Breaker operating times. | [26 empty] | 2014-11-13 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780005959 | Any other schemes that are part of or impact the UVLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UFLS and Remedial Action Schemes. | [26 empty] | 2014-11-13 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780006035 | Uses Load forecast by Balancing Authority. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 11500000 | NPCC-ON |  | NPCC-US
5 | 79780006164 | Incident reporting and response planning (CIP-008); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780006204 | For password-only authentication for interactive user access, either technically or procedurally enforce the following password parameters: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 55000000 | NPCC-ON |  | NPCC-US
5 | 79780006223 | Any security patches applied. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 11500000 | NPCC-ON |  | NPCC-US
5 | 79780006230 | Where technically feasible, for each change that deviates from the existing baseline configuration: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780006244 | Have one or more methods for detecting known or suspected malicious communications for both inbound and outbound communications. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.5. An example of evidence may include, but is not limited to, documentation that malicious communications detection methods (e.g. intrusion detection system, application layer firewall, etc.) are implemented. | 2014-02-03 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780006252 | Issue an alarm or alert in response to detected unauthorized access through a physical access point into a Physical Security Perimeter to the personnel identified in the BES Cyber Security Incident response plan within 15 minutes of detection. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 1.5 An example of evidence may include, but is not limited to, language in the physical security plan that describes the issuance of an alarm or alert in response to unauthorized access through a physical access control into a Physical Security Perimeter and additional evidence that the alarm or alert was issued and communicated as identified in the BES Cyber Security Incident Response Plan, such as manual or electronic alarm or alert logs, cell phone or pager logs, or other evidence that documents that the alarm or alert was generated and communicated. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780006265 | One or more processes to preserve data, per Cyber Asset capability, for determining the cause of a Cyber Security Incident that triggers activation of the recovery plan(s). Data preservation should not impede or restrict recovery. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780006281 | The visitor control program; | [23 empty] | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. |  |  | 2016-06-30 |  |  |  | 21500000 | NPCC-ON |  | NPCC-US
5 | 79780006304 | Process to ensure that individuals with authorized electronic or authorized unescorted physical access have had a personnel risk assessment completed according to Parts 3.1 to 3.4 within the last seven years. | [23 empty] | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process for ensuring that individuals with authorized electronic or authorized unescorted physical access have had a personnel risk assessment completed within the last seven years. |  |  | 2016-06-30 |  |  |  | 35000000 | NPCC-ON |  | NPCC-US
5 | 79780006316 | For termination actions, revoke the individual’s non-shared user accounts (unless already revoked according to Parts 5.1 or 5.3) within 30 calendar days of the effective date of the termination action. | [23 empty] | Examples of evidence may include, but are not limited to:&lt;br/&gt;• Workflow or sign-off form showing password reset within 30 calendar days of the termination; &lt;br/&gt;• Workflow or sign-off form showing password reset within 30 calendar days of the reassignments or transfers; or&lt;br/&gt;• Documentation of the extenuating operating circumstance and workflow or sign-off form showing password reset within 10 calendar days following the end of the operating circumstance. |  |  | 2016-06-30 |  |  |  | 55000000 | NPCC-ON |  | NPCC-US
5 | 79780006428 | Compensation settings (such as droop, line drop, differential compensation), if used, and |  | GO | [22 empty] | 2018-07-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following:&lt;br/&gt;4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: &lt;br/&gt;4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).&lt;br/&gt;4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.2 Generation in the Western Interconnection with the following characteristics:&lt;br/&gt;4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).&lt;br/&gt;4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.3 Generation in the ERCOT Interconnection with the following characteristics:&lt;br/&gt;4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).&lt;br/&gt;4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.4 For all Interconnections:&lt;br/&gt;• A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. |  | 21500000 | NPCC-ON |  | NPCC-US
5 | 79780006438 | Representation of the real power response effects of outer loop controls such as operator set point controls, and load control but excluding AGC control) that would override the governor response (including blocked or nonfunctioning governors or modes of operation that limit Frequency Response), if applicable. |  | GO | [22 empty] | 2018-07-01 |  |  |  | 4.2. Facilities&lt;br/&gt;For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred to as an “applicable unit” that meet the following:&lt;br/&gt;4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics:&lt;br/&gt;4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).&lt;br/&gt;4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.2 Generation in the Western Interconnection with the following characteristics:&lt;br/&gt;4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).&lt;br/&gt;4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.3 Generation in the ERCOT Interconnection with the following characteristics:&lt;br/&gt;4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).&lt;br/&gt;4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). |  | 21500000 | NPCC-ON |  | NPCC-US
5 | 79780006447 | Protection and control |  | RC | [11 empty] | RC | [10 empty] | 2012-10-01 |  | 2019-06-30 |  |  |  | 11500000 | NPCC-ON |  | NPCC-US
5 | 79780006456 | Voltage and reactive |  | TOP | [18 empty] | TOP |  |  |  | 2012-10-01 |  | 2019-06-30 |  |  |  | 21500000 | NPCC-ON |  | NPCC-US
5 | 79780006494 | &lt;p&gt;Physical and cyber security.&lt;/p&gt; |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2013-07-01 |  | 2019-03-31 |  |  |  | 12500000 | NPCC-ON |  | NPCC-US
5 | 79780006497 | A transition period between the loss of primary control center functionality and the time to fully implement the backup functionality that is less than or equal to two hours. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780006541 | A list of all UFLS relay inhibit functions along with the corresponding settings and locations of these relays. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2013-04-29 |  | 2020-03-31 |  |  |  | 205000000 | NPCC-ON |  | NPCC-US
5 | 79780006559 | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 45000000 | NPCC-ON |  | NPCC-US
5 | 79780006571 | A description of how simulations of transfers are performed through the adjustment of generation, Load or both. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-01-23 |  | 2020-12-14 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780006595 | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 450000 | NPCC-ON |  | NPCC-US
5 | 79780006627 | Known commitments for Firm Transmission Service and Interchange |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-01-01 | [5 empty] | 11500000 | NPCC-ON |  | NPCC-US
5 | 79780006634 | When an entity’s spare equipment strategy could result in the unavailability of major Transmission equipment that has a lead time of one year or more (such as a transformer), the impact of this possible unavailability on System performance shall be studied. The studies shall be performed for the P0, P1, and P2 categories identified in Table 1 with the conditions that the System is expected to experience during the possible unavailability of the long lead time equipment. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 21500000 | NPCC-ON |  | NPCC-US
5 | 79780006651 | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed to address the impact of proposed material generation additions or changes in that timeframe and be supported by current or past studies as qualified in Requirement R2, Part2.6 and shall include documentation to support the technical rationale for determining material changes. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 25000000 | NPCC-ON |  | NPCC-US
5 | 79780006672 | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R3, Part 3.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 35000000 | NPCC-ON |  | NPCC-US
5 | 79780006686 | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R4, Part 4.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences of the event(s) shall be conducted. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 45000000 | NPCC-ON |  | NPCC-US
5 | 79780006695 | Parallel path (loop flow) adjustments. |  | PCPA | [9 empty] | PA | [12 empty] | 2013-04-01 |  | 2020-12-14 |  |  |  | 14500000 | NPCC-ON |  | NPCC-US
5 | 79780006711 | Each Purchasing Selling Entity included in the Arranged Interchange. |  | BA | BA | [21 empty] | 2014-06-30 |  | 2021-03-31 |  |  |  | 55000000 | NPCC-ON |  | NPCC-US
5 | 79780006722 | Each adjacent Transmission Operator synchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  |  | 35000000 | NPCC-ON |  | NPCC-US
5 | 79780006732 | Each Adjacent Balancing Authority. |  | BA | BA | [21 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 55000000 | NPCC-ON |  | NPCC-US
5 | 79780006788 | Total and available peak hour forecast of controllable and dispatchable Demand Side Management (summer and winter), in megawatts, under the control or supervision of the System Operator for ten calendar years into the future. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 14500000 | NPCC-ON |  | NPCC-US
5 | 79780006789 | A request to provide any or all of the following summary explanations, as necessary,: |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2015-04-27 |  | 2016-09-30 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780006794 | How the peak Demand forecast compares to actual Demand for the prior calendar year with due regard to any relevant weather-related variations (e.g., temperature, humidity, or wind speed) and, if applicable, how the assumptions and methods for future forecasts were adjusted. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 15500000 | NPCC-ON |  | NPCC-US
5 | 79780006813 | Provisions for periodic communications to support reliable operations. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-26 | [5 empty] | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780006856 | Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 12500000 | NPCC-ON |  | NPCC-US
5 | 79780006868 | Requests to government agencies to implement their programs to achieve necessary energy reductions; |  | BA | BA | [21 empty] | 2017-04-01 | [5 empty] | 22500000 | NPCC-ON |  | NPCC-US
5 | 79780006908 | Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 93500000 | NPCC-ON |  | NPCC-US
5 | 79780006917 | Provisions for personnel training, as related to NPIRs |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 94500000 | NPCC-ON |  | NPCC-US
5 | 79780006921 | One or more processes to preserve data, per Cyber Asset capability, for determining the cause of a Cyber Security Incident that triggers activation of the recovery plan(s). Data preservation should not impede or restrict recovery. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.5. An example of evidence may include, but is not limited to, procedures to preserve data, such as preserving a corrupted drive or making a data mirror of the system before proceeding with recovery. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780006942 | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 45000000 | NPCC-ON |  | NPCC-US
5 | 79780007058 | Coordination of information exchange to support reliability assessments. |  | RC | [11 empty] | RC | [12 empty] | 2016-01-26 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780007069 | Other System Operating Limits (SOLs). |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 11500000 | NPCC-ON |  | NPCC-US
5 | 79780007075 | Parallel path (loop flow) adjustments; |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 12500000 | NPCC-ON |  | NPCC-US
5 | 79780007087 | Parallel path (loop flow) adjustments; |  | TSP | [20 empty] | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 21500000 | NPCC-ON |  | NPCC-US
5 | 79780007182 | Any one BES Element within a major voltage sensitive area as defined by an area with an in-service undervoltage load shedding (UVLS) program. |  | PCPA, RC | [9 empty] | PA |  | RC | [10 empty] | 2016-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 51500000 | NPCC-ON |  | NPCC-US
5 | 79780007206 | Data files will be named in conformance with C37.232, IEEE Standard for Common Format for Naming Time Sequence Data Files (COMNAME), revision C37.232-2011 or later. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: &lt;br/&gt;4.1.1 Eastern Interconnection – Planning Coordinator&lt;br/&gt;4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator&lt;br/&gt;4.1.3 Western Interconnection – Reliability Coordinator&lt;br/&gt;4.1.4 Quebec Interconnection – Planning Coordinator or Reliability&lt;br/&gt; Coordinator |  | 115000000 | NPCC-ON |  | NPCC-US
5 | 79780007213 | Handling of BES Cyber System Information and its storage; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21500000 | NPCC-ON |  | NPCC-US
5 | 79780007224 | Any security patches applied. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 11500000 | NPCC-ON |  | NPCC-US
5 | 79780007231 | Where technically feasible, for each change that deviates from the existing baseline configuration: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.5. An example of evidence may include, but is not limited to, a list of cyber security controls tested along with successful test results and a list of differences between the production and test environments with descriptions of how any differences were accounted for, including of the date of the test. | 2016-03-31 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780007269 | For termination actions, change passwords for shared account(s) known to the user within 30 calendar days of the termination action. For reassignments or transfers, change passwords for shared account(s) known to the user within 30 calendar days following the date that the Responsible Entity determines that the individual no longer requires retention of that access. If the Responsible Entity determines and documents that extenuating operating circumstances require a longer time period, change the password(s) within 10 calendar days following the end of the operating circumstances.&lt;br/&gt;&lt;br/&gt;If the Responsible Entity determines and documents that extenuating operating circumstances require a longer time period, change the password(s) within 10 calendar days following the end of the operating circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.5 Examples of evidence may include, but are not limited to:&lt;br/&gt;• Workflow or sign-off form showing password reset within 30 calendar days of the termination; &lt;br/&gt;• Workflow or sign-off form showing password reset within 30 calendar days of the reassignments or transfers; or&lt;br/&gt;• Documentation of the extenuating operating circumstance and workflow or sign-off form showing password reset within 10 calendar days following the end of the operating circumstance. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 55000000 | NPCC-ON |  | NPCC-US
5 | 79780007314 | For password-only authentication for interactive user access, either technically or procedurally enforce the following password parameters: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.5. Examples of evidence may include, but are not limited to:&lt;br/&gt;• System-generated reports or screen-shots of the system-enforced password parameters, including length and complexity; or &lt;br/&gt;• Attestations that include a reference to the documented procedures that were followed. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 55000000 | NPCC-ON |  | NPCC-US
5 | 79780007343 | Issue an alarm or alert in response to detected unauthorized access through a physical access point into a Physical Security Perimeter to the personnel identified in the BES Cyber Security Incident response plan within 15 minutes of detection. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.5. An example of evidence may include, but is not limited to, language in the physical security plan that describes the issuance of an alarm or alert in response to unauthorized access through a physical access control into a Physical Security Perimeter and additional evidence that the alarm or alert was issued and communicated as identified in the BES Cyber Security Incident Response Plan, such as manual or electronic alarm or alert logs, cell phone or pager logs, or other evidence that documents that the alarm or alert was generated and communicated. | 2016-07-01 | [5 empty] | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780007357 | Real and reactive power. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 55000000 | NPCC-ON |  | NPCC-US
5 | 79780007405 | Major transmission junctions. |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 72500000 | NPCC-ON |  | NPCC-US
5 | 79780007419 | Real and reactive power. |  | RC | [11 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 105000000 | NPCC-ON |  | NPCC-US
5 | 79780007424 | Monthly verification of active analog quantities. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 145000000 | NPCC-ON |  | NPCC-US
5 | 79780007436 | Date last tested. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 175000000 | NPCC-ON |  | NPCC-US
5 | 79780007476 | Each adjacent Transmission Operator synchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  |  | 35000000 | NPCC-ON |  | NPCC-US
5 | 79780007482 | Incident reporting and response planning (CIP-008); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11500000 | NPCC-ON |  | NPCC-US
5 | 79780007497 | Each Adjacent Balancing Authority. |  | BA | BA | [21 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 55000000 | NPCC-ON |  | NPCC-US
5 | 79780007520 | Process to ensure that individuals with unescorted physical access have had a personnel risk assessment completed according to Parts 3.1 to 3.4 within the last seven years. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.5. An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process for ensuring that individuals with authorized electronic or authorized unescorted physical access have had a personnel risk assessment completed within the last seven years. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 35000000 | NPCC-ON |  | NPCC-US
5 | 79780007594 | &lt;p&gt;Total and available peak hour forecast of controllable and dispatchable Demand Side Management (summer and winter), in megawatts, under the control or supervision of the System Operator for ten calendar years into the future.&lt;/p&gt; |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | &lt;p&gt;This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.”&lt;/p&gt; |  | 14500000 | NPCC-ON |  | NPCC-US
5 | 79780007595 | A request to provide any or all of the following summary explanations, as necessary,: |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-02-18 |  | 2021-03-31 |  |  |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780007600 | &lt;p&gt;How the peak Demand forecast compares to actual Demand for the prior calendar year with due regard to any relevant weather-related variations (e.g., temperature, humidity, or wind speed) and, if applicable, how the assumptions and methods for future forecasts were adjusted.&lt;/p&gt; |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | &lt;p&gt;This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.”&lt;/p&gt; |  | 15500000 | NPCC-ON |  | NPCC-US
5 | 79780007653 | Identified unanticipated high priority work |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:&lt;br/&gt;4.1.1. Applicable Transmission Owners&lt;br/&gt;4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.&lt;br/&gt;4.1.2. Applicable Generator Owners&lt;br/&gt;4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. &lt;br/&gt;4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.2.1. Each overhead transmission line operated at 200kV or higher.&lt;br/&gt;4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.&lt;br/&gt;4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.&lt;br/&gt;4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. &lt;br/&gt;4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:&lt;br/&gt;4.3.1.1. Operated at 200kV or higher; or&lt;br/&gt;4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or&lt;br/&gt;4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 75000000 | NPCC-ON |  | NPCC-US
5 | 79780007671 | The Transmission Operator shall identify when the TTC for the ATC Path being studied has an adverse impact on the TTC value of any existing path. Do this by modeling the flow on the path being studied at its proposed new TTC level simultaneous with the flow on the existing path at its TTC level while at the same time honoring the reliability criteria outlined in R2.1. The Transmission Operator shall include the resolution of this adverse impact in its study report for the ATC Path. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 25000000 | NPCC-ON |  | NPCC-US
5 | 79780007698 | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 450000 | NPCC-ON |  | NPCC-US
5 | 79780007760 | Except for limited impact RAS, a single component failure in the RAS, when the RAS is intended to operate does not prevent the BES from meeting the same performance requirements (defined in Reliability Standard TPL-001-4 or its successor) as those required for the events and conditions for which the RAS is designed. |  | PCPA | [9 empty] | PA | [12 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 41500000 | NPCC-ON |  | NPCC-US
5 | 79780007780 | Specify the instances that require time identification when issuing an oral or written Operating Instruction and the format for that time identification. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2015-06-22 | [5 empty] | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780007796 | Each adjacent Transmission Operator synchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2016-10-28 | [5 empty] | 35000000 | NPCC-ON |  | NPCC-US
5 | 79780007808 | Each Adjacent Balancing Authority. |  | BA | BA | [21 empty] | 2016-10-28 | [5 empty] | 55000000 | NPCC-ON |  | NPCC-US
5 | 79780007893 | Physical and cyber security. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2019-04-01 | [5 empty] | 12500000 | NPCC-ON |  | NPCC-US
5 | 79780007896 | A transition period between the loss of primary control center functionality and the time to fully implement the backup functionality that is less than or equal to two hours. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780007916 | Identification of the Reliability Coordinator as the primary contact for disseminating information regarding restoration to neighboring Reliability Coordinators, and to Transmission Operators, and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2018-03-26 | [5 empty] | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780007936 | Identification of Cranking Paths and initial switching requirements between each Blackstart Resource and the unit(s) to be started. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780007962 | Transition of Demand and resource balance within its area to the Balancing Authority. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 85000000 | NPCC-ON |  | NPCC-US
5 | 79780007993 | Incident reporting and response planning (CIP-008); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11500000 | NPCC-ON |  | NPCC-US
5 | 79780008002 | Transient Cyber Assets and Removable Media malicious code risk mitigation; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12500000 | NPCC-ON |  | NPCC-US
5 | 79780008027 | Obtain and utilize the status of Remedial Action Schemes outside its Transmission Operator Area identified as necessary by the Transmission Operator; and |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-17 |  | 2021-03-31 |  |  |  | 105000000 | NPCC-ON |  | NPCC-US
5 | 79780008092 | Verification of software integrity and authenticity of all software and patches provided by the vendor for use in the BES Cyber System; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and&lt;br/&gt;4.1.2.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and&lt;br/&gt;4.2.1.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers&lt;br/&gt;4.2.2.1. All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-013-1:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the identification and categorization process required by CIP-002-5, or any subsequent version of that Reliability Standard. |  | 12500000 | NPCC-ON |  | NPCC-US
5 | 79780008101 | Have one or more methods for detecting known or suspected malicious communications for both inbound and outbound communications. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation that malicious communications detection methods (e.g. intrusion detection system, application layer firewall, etc.) are implemented. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-005-6:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780008107 | Have one or more method(s) to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation of the methods(s) used to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access), such as:&lt;br/&gt;• Methods to disable vendor remote access at the applicable Electronic Access Point for system-to-system remote access; or&lt;br/&gt;• Methods to disable vendor Interactive Remote Access at the applicable Intermediate System. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-005-6:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 25000000 | NPCC-ON |  | NPCC-US
5 | 79780008114 | Any security patches applied. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 11500000 | NPCC-ON |  | NPCC-US
5 | 79780008121 | Where technically feasible, for each change that deviates from the existing baseline configuration: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a list of cyber security controls tested along with successful test results and a list of differences between the production and test environments with descriptions of how any differences were accounted for, including of the date of the test. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780008178 | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-3 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 45000000 | NPCC-ON |  | NPCC-US
5 | 79780008354 | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  |  | 75000000 | NPCC-ON |  | NPCC-US
5 | 79780008401 | Protection and control |  | RC | [11 empty] | RC | [10 empty] | 2019-07-01 | [5 empty] | 11500000 | NPCC-ON |  | NPCC-US
5 | 79780008411 | Voltage and reactive |  | TOP | [18 empty] | TOP |  |  |  | 2019-07-01 | [5 empty] | 21500000 | NPCC-ON |  | NPCC-US
5 | 79780008457 | Resources (supply or demand side) required for Load. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP | [8 empty] | 11500000 | NPCC-ON |  | NPCC-US
5 | 79780008464 | When an entity’s spare equipment strategy could result in the unavailability of major Transmission equipment that has a lead time of one year or more (such as a transformer), the impact of this possible unavailability on System performance shall be assessed. Based upon this assessment, an analysis shall be performed for the P0, P1, and P2 categories identified in Table 1 with the conditions that the System is expected to experience during the possible unavailability of the long lead time equipment. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP | [8 empty] | 21500000 | NPCC-ON |  | NPCC-US
5 | 79780008473 | When an entity’s spare equipment strategy could result in the unavailability of major Transmission equipment that has a lead time of one year or more (such as a transformer), the impact of this possible unavailability on System performance shall be assessed. Based upon this assessment, an analysis shall be performed for the selected P1 and P2 category events identified in Table 1 for which the unavailability is expected to produce more severe System impacts on its portion of the BES. The analysis shall simulate the conditions that the System is expected to experience during the possible unavailability of the long lead time equipment. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP | [8 empty] | 24500000 | NPCC-ON |  | NPCC-US
5 | 79780008474 | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed to address the impact of proposed material generation additions or changes in that timeframe and be supported by current or past studies as qualified in Requirement R2, Part2.6 and shall include documentation to support the technical rationale for determining material changes. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-04-13 |  | 2020-06-10 |  |  |  | 25000000 | NPCC-ON |  | NPCC-US
5 | 79780008499 | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R3, Part 3.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-04-13 |  | 2020-06-10 |  |  |  | 35000000 | NPCC-ON |  | NPCC-US
5 | 79780008574 | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2020-10-05 |  | 4.2. Facilities:&lt;br/&gt;4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 75000000 | NPCC-ON |  | NPCC-US
5 | 79780008685 | Incident reporting and response planning (CIP-008); | [28 empty] | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service &lt;br/&gt;&lt;br/&gt;equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11500000 | NPCC-ON |  | NPCC-US
5 | 79780008695 | Transient Cyber Assets and Removable Media malicious code risk mitigation; and | [28 empty] | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service &lt;br/&gt;&lt;br/&gt;equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12500000 | NPCC-ON |  | NPCC-US
5 | 79780008776 | Obtain and utilize the status of Remedial Action Schemes outside its Transmission Operator Area identified as necessary by the Transmission Operator; and |  | TOP | [18 empty] | TOP |  |  |  | 2021-04-01 | [5 empty] | 105000000 | NPCC-ON |  | NPCC-US
5 | 79780009008 | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 75000000 | NPCC-ON |  | NPCC-US
5 | 79780009039 | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 115000000 | NPCC-ON |  | NPCC-US
5 | 79780009090 | Total and available peak hour forecast of controllable and dispatchable Demand Side Management (summer and winter), in megawatts, under the control or supervision of the System Operator for ten calendar years into the future. | [24 empty] | 2021-04-01 | [5 empty] | 14500000 | NPCC-ON |  | NPCC-US
5 | 79780009091 | A request to provide any or all of the following summary explanations, as necessary,: |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780009129 | Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 93500000 | NPCC-ON |  | NPCC-US
5 | 79780009137 | Provisions for personnel training, as related to NPIRs | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 94500000 | NPCC-ON |  | NPCC-US
5 | 79780009183 | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-4 — Attachment 1. |  | PCPA | [9 empty] | PA | [16 empty] | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 45000000 | NPCC-ON |  | NPCC-US
5 | 79780009318 | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed to address the impact of proposed material generation additions or changes in that timeframe and be supported by current or past studies as qualified in Requirement R2, Part2.6 and shall include documentation to support the technical rationale for determining material changes. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 25000000 | NPCC-ON |  | NPCC-US
5 | 79780009338 | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R3, Part 3.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 35000000 | NPCC-ON |  | NPCC-US
5 | 79780009455 | Have one or more methods for detecting known or suspected malicious communications for both inbound and outbound communications. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 15000000 | NPCC-ON |  | NPCC-US
5 | 79780009460 | Have one or more method(s) to disable active vendor remote access including Interactive Remote Access and system-to-system remote access). |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 25000000 | NPCC-ON |  | NPCC-US
5 | 79780009476 | Where technically feasible, for each change that deviates from the existing baseline configuration: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 15000000 | NPCC-ON |  | NPCC-US
5. | 1001 | Capacity and energy adequacy conditions. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  | IRO-005-1 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1028 | Capacity and energy adequacy conditions. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  | IRO-005-2 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1055 | Capacity and energy adequacy conditions. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  | IRO-005-3a R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1111 | Coordination of information exchange to support reliability assessments. |  | RC | [11 empty] | RC | [9 empty] | M1.1.5 Coordination of information exchange to support reliability assessments. | 2007-06-18 |  | 2017-03-31 |  |  |  | 11500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1141 | A requirement that TTC and ATC values shall be determined and posted as follows: |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-001-0 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1162 | A description of the allocation processes listed below that are applicable to the Transmission Service Provider: • Processes used to allocate transfer or Flowgate capability among multiple lines or sub-paths within a larger ATC Path or Flowgate. • Processes used to allocate transfer or Flowgate capabilities among multiple owners or users of an ATC Path or Flowgate. • Processes used to allocate transfer or Flowgate capabilities between Transmission Service Providers to address issues such as forward looking congestion management and seams coordination. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-001-1 R3. | 35000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1172 | Each Reliability Coordinator adjacent to the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-001-1 R4. | 45000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1202 | Describe the inclusion or exclusion rationale for generation resources of each Load-Serving Entity including those generation resources not directly connected to the Transmission Service Provider’s system but serving Load-Serving Entity loads connected to the Transmission Service Provider’s system. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-004-0 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1266 | Allowances for parallel path (loop flow) impacts. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 13500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1271 | Describe the formal process for the Regional Reliability Organization to grant any variances to individual Transmission Service Providers from the Regional TRM methodology. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-008-0 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1298 | Transformer (voltage and phase-shifting): nominal voltages of windings, impedance, tap ratios (voltage and/or phase angle or tap step size), regulated bus and voltage set point, Normal and Emergency Ratings (consistent with methodologies defined and Ratings supplied per Reliability Standard FAC-004-0 and FAC-005-0.), and equipment status. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | MOD-011-0 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1312 | Dynamics data shall be consistent with the reported steady-state (power flow) data supplied per Reliability Standard MOD-010 Requirement 1. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | MOD-013-1 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1360 | Information to be verified and reported: |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | MOD-024-1 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1371 | Information to be reported: |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | MOD-025-1 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1383 | The following information on how source and sink for transmission service is accounted for in ATC calculations including: |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2013-09-30 |  |  | MOD-028-1 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1431 | Uses Load forecast by Balancing Authority. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 11500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1445 | The Transmission Operator shall identify when the TTC for the ATC Path being studied has an adverse impact on the TTC value of any existing path. Do this by modeling the flow on the path being studied at its proposed new TTC level simultaneous with the flow on the existing path at its TTC level while at the same time honoring the reliability criteria outlined in R2.1. The Transmission Operator shall include the resolution of this adverse impact in its study report for the ATC Path. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-029-1 R2. | 25000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1482 | At a minimum, establish the TFC once per calendar year. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | MOD-030-1 R2. | 25000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1490 | Contains modeling data and system topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination Areas. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | MOD-030-1 R3. | 35000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1505 | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | MOD-030-1 R6. | 65000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1513 | The impact of non-firm Network Integration Transmission Service serving Load within the Transmission Service Provider’s area (i.e., secondary service), to include load growth, and losses not otherwise included in Transmission Reliability Margin or Capacity Benefit Margin. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | MOD-030-1 R7. | 75000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1547 | At a minimum, establish the TFC once per calendar year. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R2. | 25000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1555 | Contains modeling data and system topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination Areas. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R3. | 35000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1570 | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R6. | 65000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1578 | The impact of non-firm Network Integration Transmission Service serving Load within the Transmission Service Provider’s area (i.e., secondary service), to include load growth, and losses not otherwise included in Transmission Reliability Margin or Capacity Benefit Margin. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R7. | 75000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1609 | Provision to consider nuclear plant coping times required by the NPLRs and their relation to the coordination of grid and nuclear plant restoration following a nuclear plant loss of Off-site Power. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 93500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1617 | Provisions for personnel training, as related to NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 94500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1674 | Megawatts and megavars. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 21350000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1694 | Naming of data files in conformance with the IEEE C37.232 Recommended Practice for Naming Time Sequence Data Files2. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | PRC-002-1 R4. | 45000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1740 | Tie tripping schemes. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  |  | 12500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1776 | Schedule for system maintenance. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2027-03-31 |  |  | PRC-011-0 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1784 | Requirements to demonstrate the proposed SPS will coordinate with other protection and control systems and applicable Regional Reliability Organization Emergency procedures. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  | PRC-012-0 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1802 | Provide corrective action plans for non-compliant SPSs. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  | PRC-014-0 R3. | 35000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1821 | Schedule for system maintenance. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2007-06-18 |  | 2017-03-31 |  |  | PRC-017-0 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1833 | Date last tested. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2022-06-30 |  |  | PRC-018-1 R3. | 35000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1847 | Breaker operating times. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  | PRC-020-1 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1855 | Any other schemes that are part of or impact the UVLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UFLS and Special Protection Systems. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2017-03-31 |  |  | PRC-021-1 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1862 | For any Misoperation, a Corrective Action Plan to avoid future Misoperations of a similar nature. |  | DP, LSE, TOP |  | DP | [5 empty] | LSE | [10 empty] | TOP |  |  |  | 2007-06-18 |  | 2017-03-31 |  |  | PRC-022-1 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1878 | Set transmission line relays on weak source systems so they do not operate at or below 170% of the maximum end-of-line three-phase fault magnitude (expressed in amperes). |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  | PRC-023-1 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 1973 | Development of IROLs and SOLs. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-01-21 |  |  | TOP-004-1 R6. | 65000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2041 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 13500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2062 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 13500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2086 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2092 | Consider all contingencies applicable to Category B. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | TPL-002-0 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2111 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 13500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2117 | Consider all contingencies applicable to Category B. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  | TPL-002-0a R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2136 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2142 | Consider all contingencies applicable to Category C. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  | TPL-003-0 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2161 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 13500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2167 | Consider all contingencies applicable to Category C. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  | TPL-003-0a R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2183 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  |  | 13500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2204 | Reliability impacts of new or proposed environmental rules and regulations. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | TPL-005-0 R3. | 35000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2211 | Transmission system and supporting information (thermal, voltage, and Stability Limits, contingency analyses, system restoration, system modeling and data requirements, and protection systems.) |  | RRO | [14 empty] | RRO | [9 empty] | 2009-04-15 |  |  | TPL-006-0 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2312 | Due to a component failure, the AVR may be out of service up to one year provided the Generator Operator or Transmission Operator submits documentation identifying the need for time to obtain replacement parts and if required to schedule an outage. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-06-27 |  | 2015-03-31 |  |  | VAR-002-WECC-1 R1. | 15000000 | WECC-US | [5 empty] | WECC-US
5. | 2326 | Unit is generating less power than its design limit for effective PSS operation. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-06-27 |  | 2015-03-31 |  |  | VAR-501-WECC-1 R1. | 15000000 | WECC-US | [5 empty] | WECC-US
5. | 2351 | Transmission system and supporting information (thermal, voltage, and Stability Limits, contingency analyses, system restoration, system modeling and data requirements, and protection systems.) |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | TPL-006-0.1 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2361 | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 12500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 24 | The limitations, if any, upon the amount of interruptible load that may be included. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  | BAL-002-0 R2. | 25000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2415 | Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003-2; Standard CIP-004-2 Requirement R3; Standard CIP-005-2 Requirements R2 and R3; Standard CIP-006-2 Requirement R3; Standard CIP-007-2 Requirements R1 and R3 through R9; Standard CIP-008-2; and Standard CIP-009-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-005-2 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2422 | The required documentation shall, at least, identify and describe: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-005-2 R2. | 25000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2436 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-005-2 R4. | 45000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2446 | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-2 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  | CIP-006-2 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2494 | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-03-31 |  |  | CIP-007-2 R6. | 65000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 251 | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 12500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2510 | Process for ensuring that the Cyber Security Incident response plan is reviewed at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-008-2 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2546 | Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. . |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 93500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2554 | Provisions for personnel training, as related to NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 94500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2577 | Identification of Cranking Paths and initial switching requirements between each Blackstart Resource and the unit(s) to be started. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | EOP-005-2 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2622 | Criteria and conditions for reestablishing interconnections with other Transmission Operators within its Reliability Coordinator Area, with Transmission Operators in other Reliability Coordinator Areas, and with other Reliability Coordinators. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  | EOP-006-2 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2672 | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-18 |  | 2010-09-30 |  |  | CIP-007-2a R6. | 65000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2696 | Starting with all Facilities in service and following any of the multiple Contingencies identified in Reliability Standard TPL-003 the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | FAC-010-2.1 R2. | 25000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2706 | Anticipated transmission system configuration, generation dispatch and Load level. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | FAC-010-2.1 R3. | 35000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2720 | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | 12500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2774 | Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirement R3; Standard CIP-007-3 Requirements R1 and R3 through R9; Standard CIP-008-3; and Standard CIP-009-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | CIP-005-3 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2781 | The required documentation shall, at least, identify and describe: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | CIP-005-3 R2. | 25000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2795 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | CIP-005-3 R4. | 45000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2805 | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-3 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  | CIP-006-3 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2855 | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  | 4.2. The following are exempt from Standard CIP-007-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that they have no Critical Cyber Assets. | CIP-007-3a R6. | 65000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2871 | Process for ensuring that the Cyber Security Incident response plan is reviewed at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | CIP-008-3 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2891 | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-2 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  | CIP-006-2b R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2912 | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-2 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | CIP-006-2c R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2930 | Procedures for reviewing access authorization requests and revocation of access authorization, in accordance with CIP-004 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1b R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2964 | Procedures for reviewing access authorization requests and revocation of access authorization, in accordance with CIP-004 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | CIP-006-1c R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 2985 | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-3 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  | CIP-006-3c R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3013 | A description of the allocation processes listed below that are applicable to the Transmission Service Provider: • Processes used to allocate transfer or Flowgate capability among multiple lines or sub-paths within a larger ATC Path or Flowgate. • Processes used to allocate transfer or Flowgate capabilities among multiple owners or users of an ATC Path or Flowgate. • Processes used to allocate transfer or Flowgate capabilities between Transmission Service Providers to address issues such as forward looking congestion management and seams coordination. |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  |  |  |  | MOD-001-1a R3. | 35000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3024 | Each Reliability Coordinator adjacent to the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  |  |  |  | MOD-001-1a R4. | 45000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 304 | Cyber Assets used in the access control and monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003, Standard CIP-004 Requirement R3, Standard CIP-005 Requirements R2 and R3, Standard CIP-006 Requirements R2 and R3, Standard CIP-007, Requirements R1 and R3 through R9, Standard CIP-008, and Standard CIP-009. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-005-1 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3048 | Uses Load forecast by Balancing Authority. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 11500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3063 | The Transmission Operator shall identify when the TTC for the ATC Path being studied has an adverse impact on the TTC value of any existing path. Do this by modeling the flow on the path being studied at its proposed new TTC level simultaneous with the flow on the existing path at its TTC level while at the same time honoring the reliability criteria outlined in R2.1. The Transmission Operator shall include the resolution of this adverse impact in its study report for the ATC Path. |  | TOP | [18 empty] | TOP |  |  |  | 2010-09-16 |  | 2017-03-31 |  |  | MOD-029-1a R2. | 25000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 311 | The required documentation shall, at least, identify and describe: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-005-1 R2. | 25000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3161 | Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirement R3; Standard CIP-007-3 Requirements R1 and R3 through R9; Standard CIP-008-3; and Standard CIP-009-3. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. | CIP-005-3a R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3167 | The required documentation shall, at least, identify and describe: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. | CIP-005-3a R2. | 25000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3179 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. | CIP-005-3a R4. | 45000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3190 | The limitations, if any, upon the amount of interruptible load that may be included. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  | BAL-002-1 R2. | 25000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 325 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | CIP-005-1 R4. | 45000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3263 | Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003-4; Standard CIP-004-4 Requirement R3; Standard CIP-005-4 Requirements R2 and R3; Standard CIP-006-4 Requirement R3; Standard CIP-007-4 Requirements R1 and R3 through R9; Standard CIP-008-4; and Standard CIP-009-4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-005-4a R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3270 | The required documentation shall, at least, identify and describe: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-005-4a R2. | 25000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3284 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-005-4a R4. | 45000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3294 | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-4 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-006-4c R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3344 | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-007-4a R6. | 65000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 335 | Procedures for reviewing access authorization requests and revocation of access authorization, in accordance with CIP-004 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2009-02-02 |  | 2010-03-31 |  |  | CIP-006-1 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3360 | Process for ensuring that the Cyber Security Incident response plan is reviewed at least annually. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-008-4 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3380 | Declaring an Energy Emergency through its Reliability Coordinator; and |  | BA | BA | [21 empty] | 2011-01-10 |  | 2012-09-12 |  |  | EOP-002-3 R6. | 65000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3412 | Documentation that the assessment included study assumptions, system performance, alternatives considered, and jointly coordinated recommendations. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [14 empty] | 2011-01-10 |  | 2015-12-31 |  |  | FAC-002-1 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3426 | Capacity and energy adequacy conditions. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  | IRO-005-2a R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3460 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3484 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 13500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3490 | Consider all contingencies applicable to Category B. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  | TPL-002-0b R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3509 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3515 | Consider all contingencies applicable to Category B. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | TPL-002-1b R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3534 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3540 | Consider all contingencies applicable to Category C. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2012-07-06 |  | 2012-07-06 |  |  | TPL-003-1a R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3556 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 362 | Procedures for reviewing access authorization requests and revocation of access authorization, in accordance with CIP-004 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1a R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3625 | Cyber Assets used in the access control and monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003, Standard CIP-004 Requirement R3, Standard CIP-005 Requirements R2 and R3, Standard CIP-006 Requirements R2 and R3, Standard CIP-007, Requirements R1 and R3 through R9, Standard CIP-008, and Standard CIP-009. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | CIP-005-1a R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3631 | The required documentation shall, at least, identify and describe: |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | CIP-005-1a R2. | 25000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3643 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | CIP-005-1a R4. | 45000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3656 | Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter(s) shall be afforded the protective measures as a specified in Standard CIP-003-2; Standard CIP-004-2 Requirement R3; Standard CIP-005-2 Requirements R2 and R3; Standard CIP-006-2 Requirement R3; Standard CIP-007-2 Requirements R1 and R3 through R9; Standard CIP-008-2; and Standard CIP-009-2. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | CIP-005-2a R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3662 | The required documentation shall, at least, identify and describe: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | CIP-005-2a R2. | 25000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3674 | Documentation of the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | CIP-005-2a R4. | 45000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3806 | Capacity and energy adequacy conditions. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  | IRO-005-3 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3900 | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-2 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | CIP-006-2a R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3919 | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-3 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  | CIP-006-3a R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3965 | The following information on how source and sink for transmission service is accounted for in ATC calculations including: |  | TSP | [20 empty] | TSP |  | 2013-09-27 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. | MOD-028-2 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 3982 | Unit commitment and dispatch order, to include all designated network resources and other resources that are committed or have the legal obligation to run, (within or out of economic dispatch) as they are expected to run. |  | TOP | [18 empty] | TOP |  |  |  | 2013-10-01 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 31500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4040 | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-3 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-006-3d R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4058 | Review of access authorization requests and revocation of access authorization, in accordance with CIP-004-4 Requirement R4. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-006-4d R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 416 | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-007-1 R6. | 65000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4182 | Capacity and energy adequacy conditions. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  | IRO-005-3.1a R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4201 | Declaring an Energy Emergency through its Reliability Coordinator; and |  | BA | BA | [21 empty] | 2012-09-13 |  | 2017-03-31 |  |  | EOP-002-3.1 R6. | 65000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4236 | Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. . |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 93500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4243 | Provisions for personnel training, as related to NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 94500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 432 | Process for ensuring that the Cyber Security Incident response plan is reviewed at least annually. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-008-1 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4338 | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 12500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4445 | The limitations, if any, upon the amount of interruptible load that may be included. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  | BAL-002-1a R2. | 25000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4566 | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 12500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4590 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4629 | Consider all contingencies applicable to Category B. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | TPL-002-0b R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4634 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4654 | Consider all contingencies applicable to Category C. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  | TPL-003-0a R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4659 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4680 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4694 | Consider all contingencies applicable to Category C. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  | TPL-003-0a R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4699 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4715 | Consider all contingencies applicable to Category C. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  | TPL-003-0a R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4732 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4745 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4766 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4842 | Declaring an Energy Emergency through its Reliability Coordinator; and |  | BA | BA | [23 empty] | 2006-11-01 |  |  |  | 75000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4859 | Declaring an Energy Emergency through its Reliability Coordinator; and |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 65000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4891 | The affected Transmission Operators may resynchronize the isolated area(s) with the surrounding area(s) when the following conditions are met: |  | TOP | [18 empty] | TOP | [5 empty] | 2007-05-02 |  |  |  | 95000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4913 | VAR compensators. |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-08-01 |  |  |  | 11500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4919 | The documentation shall identify the assumptions used to determine each of theequipment and Facility Ratings, including references to industry Rating practices andstandards (e.g., ANSI, IEEE, etc.). Seasonal Ratings and variations in assumptionsshall be included. |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-08-01 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4945 | Transmission Operators and Reliability Coordinators who may receive the information through Reliability analysis services. |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4951 | Connectivity of adjacent Transmission Service Providers. |  | TSP | [20 empty] | TSP |  |  |  | 2007-01-01 |  |  |  | 25000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 4984 | Loss of Load. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP | [5 empty] | 2007-01-01 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5031 | Capacity and energy adequacy conditions. |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 51 | An amount of off-line generation which can be synchronized and generating; or |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2010-11-26 |  |  | BAL-002-WECC-1 R3. | 35000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 512 | Declaring an Energy Emergency through its Reliability Coordinator; and |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  | EOP-002-2 R6. | 65000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5120 | Regional coverage requirements (e.g., by voltage, geographic area, electric area or subarea). |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5133 | Regional Reliability Organization definition of misoperations. |  | RRO | [14 empty] | RRO | [9 empty] | 2006-05-01 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5146 | Schedule for system maintenance. |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2006-05-01 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5210 | Development of IROLs and SOLs. |  | TOP | [18 empty] | TOP | [5 empty] | 2005-04-01 |  |  |  | 65000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 533 | Declaring an Energy Emergency through its Reliability Coordinator; and |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-09-30 |  |  | EOP-002-2.1 R6. | 65000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5343 | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  | CIP-007-3a R6. | 65000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5386 | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-02-03 |  |  | CIP-007-4a R6. | 65000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5613 | Starting with all Facilities in service and following any of the multiple Contingencies identified in Reliability Standard TPL-003 the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 25000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5622 | Anticipated transmission system configuration, generation dispatch and Load level. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 35000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5651 | Allowed uses of Remedial Action Schemes. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 35000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5665 | Capacity and energy adequacy conditions. |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 569 | The affected Transmission Operators may resynchronize the isolated area(s) with the surrounding area(s) when the following conditions are met: |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | EOP-005-1 R11. | 115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5707 | At a minimum, establish the TFC once per calendar year. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 25000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5715 | Contains modeling data and system topology (or equivalent representation) for immediately adjacent and beyond Reliability Coordination Areas. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 35000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5730 | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow for the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 65000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5738 | The impact of non-firm Network Integration Transmission Service serving Load within the Transmission Service Provider’s area (i.e., secondary service), to include load growth, and losses not otherwise included in Transmission Reliability Margin or Capacity Benefit Margin. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 75000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5757 | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5769 | Systems and facilities critical to automatic load shedding under a common control system capable of shedding 300 MW or more. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5802 | Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 93500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5810 | Provisions for personnel training, as related to NPIRs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 94500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5819 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5840 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5849 | Consider all contingencies applicable to Category B. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5865 | Have all projected firm transfers modeled. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5874 | Consider all contingencies applicable to Category C. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-25 |  | 2015-12-31 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5890 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5903 | Requirements to demonstrate the proposed RAS will coordinate with other protection and control systems and applicable Regional Reliability Organization Emergency procedures. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5921 | Provide corrective action plans for non-compliant RAS. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 35000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5943 | Schedule for system maintenance. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-01-25 |  | 2027-03-31 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5951 | Breaker operating times. | [26 empty] | 2014-11-13 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 5959 | Any other schemes that are part of or impact the UVLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UFLS and Remedial Action Schemes. | [26 empty] | 2014-11-13 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 602 | The plan shall include procedures and responsibilities for conducting periodic tests, at least annually, to ensure viability of the plan. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | EOP-008-0 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6035 | Uses Load forecast by Balancing Authority. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 11500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6164 | Incident reporting and response planning (CIP-008); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6204 | For password-only authentication for interactive user access, either technically or procedurally enforce the following password parameters: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 55000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6223 | Any security patches applied. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 11500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6230 | Where technically feasible, for each change that deviates from the existing baseline configuration: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6244 | Have one or more methods for detecting known or suspected malicious communications for both inbound and outbound communications. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.5. An example of evidence may include, but is not limited to, documentation that malicious communications detection methods (e.g. intrusion detection system, application layer firewall, etc.) are implemented. | 2014-02-03 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-005-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 625 | System protection and coordination. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 21500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6252 | Issue an alarm or alert in response to detected unauthorized access through a physical access point into a Physical Security Perimeter to the personnel identified in the BES Cyber Security Incident response plan within 15 minutes of detection. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 1.5 An example of evidence may include, but is not limited to, language in the physical security plan that describes the issuance of an alarm or alert in response to unauthorized access through a physical access control into a Physical Security Perimeter and additional evidence that the alarm or alert was issued and communicated as identified in the BES Cyber Security Incident Response Plan, such as manual or electronic alarm or alert logs, cell phone or pager logs, or other evidence that documents that the alarm or alert was generated and communicated. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6265 | One or more processes to preserve data, per Cyber Asset capability, for determining the cause of a Cyber Security Incident that triggers activation of the recovery plan(s). Data preservation should not impede or restrict recovery. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6281 | The visitor control program; | [23 empty] | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. |  |  | 2016-06-30 |  |  |  | 21500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6304 | Process to ensure that individuals with authorized electronic or authorized unescorted physical access have had a personnel risk assessment completed according to Parts 3.1 to 3.4 within the last seven years. | [23 empty] | An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process for ensuring that individuals with authorized electronic or authorized unescorted physical access have had a personnel risk assessment completed within the last seven years. |  |  | 2016-06-30 |  |  |  | 35000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6316 | For termination actions, change passwords for shared account(s) known to the user within 30 calendar days of the termination action. For reassignments or transfers, change passwords for shared account(s) known to the user within 30 calendar days following the date that the Responsible Entity determines that the individual no longer requires retention of that access.If the Responsible Entity determines and documents that extenuating operating circumstances require a longer time period, change the password(s) within 10 calendar days following the end of the operating circumstances. | [23 empty] | Examples of evidence may include, but are not limited to:• Workflow or sign-off form showing password reset within 30 calendar days of the termination; • Workflow or sign-off form showing password reset within 30 calendar days of the reassignments or transfers; or• Documentation of the extenuating operating circumstance and workflow or sign-off form showing password reset within 10 calendar days following the end of the operating circumstance. |  |  | 2016-06-30 |  |  |  | 55000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 636 | Documentation that the assessment included study assumptions, system performance, alternatives considered, and jointly coordinated recommendations. |  | DP, GO, LSE, TO |  | DP |  |  | GO |  |  | LSE | [14 empty] | 2007-06-18 |  | 2011-09-30 |  |  | FAC-002-0 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6428 | Compensation settings (such as droop, line drop, differential compensation), if used, and |  | GO | [22 empty] | 2018-07-01 |  |  |  | 4.2. Facilities:For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following:4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).4.2.2 Generation in the Western Interconnection with the following characteristics:4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.3 Generation in the ERCOT Interconnection with the following characteristics:4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.4 For all Interconnections:• A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. |  | 21500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6438 | Representation of the real power response effects of outer loop controls such as operator set point controls, and load control but excluding AGC control) that would override the governor response (including blocked or nonfunctioning governors or modes of operation that limit Frequency Response), if applicable. |  | GO | [22 empty] | 2018-07-01 |  |  |  | 4.2. FacilitiesFor the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred to as an “applicable unit” that meet the following:4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics:4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).4.2.2 Generation in the Western Interconnection with the following characteristics:4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.3 Generation in the ERCOT Interconnection with the following characteristics:4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating). |  | 21500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6447 | Protection and control |  | RC | [11 empty] | RC | [10 empty] | 2012-10-01 |  | 2019-06-30 |  |  |  | 11500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6456 | Voltage and reactive |  | TOP | [18 empty] | TOP |  |  |  | 2012-10-01 |  | 2019-06-30 |  |  |  | 21500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 647 | Each Transmission Owner shall establish and document a process for the immediate communication of vegetation conditions that present an imminent threat of a transmission line outage. This is so that action (temporary reduction in line rating, switching line out of service, etc.) may be taken until the threat is relieved. |  | TO | [22 empty] | 2007-06-18 |  | 2014-06-30 |  |  | FAC-003-1 R1. | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6494 | Physical and cyber security. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2013-07-01 |  | 2019-03-31 |  |  |  | 12500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6497 | A transition period between the loss of primary control center functionality and the time to fully implement the backup functionality that is less than or equal to two hours. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6541 | A list of all UFLS relay inhibit functions along with the corresponding settings and locations of these relays. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2013-04-29 |  | 2020-03-31 |  |  |  | 205000000 | NPCC-US |  | NPCC-US
5. | 6559 | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 45000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6571 | A description of how simulations of transfers are performed through the adjustment of generation, Load or both. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-01-23 |  | 2020-12-14 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6595 | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 450000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6607 | The difference between frequency set points shall be at least 0.2 Hz but no greater than 0.5 Hz. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2013-02-25 |  | 2017-12-31 |  |  |  | 25000000 | SERC-US |  |  |  | SERC-US
5. | 6627 | Known commitments for Firm Transmission Service and Interchange |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-01-01 | [5 empty] | 11500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6634 | When an entity’s spare equipment strategy could result in the unavailability of major Transmission equipment that has a lead time of one year or more (such as a transformer), the impact of this possible unavailability on System performance shall be studied. The studies shall be performed for the P0, P1, and P2 categories identified in Table 1 with the conditions that the System is expected to experience during the possible unavailability of the long lead time equipment. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 | [5 empty] | 21500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6651 | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed to address the impact of proposed material generation additions or changes in that timeframe and be supported by current or past studies as qualified in Requirement R2, Part2.6 and shall include documentation to support the technical rationale for determining material changes. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 25000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6672 | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R3, Part 3.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 35000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6686 | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R4, Part 4.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences of the event(s) shall be conducted. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 45000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6695 | Parallel path (loop flow) adjustments. |  | PCPA | [9 empty] | PA | [12 empty] | 2013-04-01 |  | 2020-12-14 |  |  |  | 14500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6711 | Each Purchasing Selling Entity included in the Arranged Interchange. |  | BA | BA | [21 empty] | 2014-06-30 |  | 2021-03-31 |  |  |  | 55000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6722 | Each adjacent Transmission Operator synchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  |  | 35000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6732 | Each Adjacent Balancing Authority. |  | BA | BA | [21 empty] | 2015-06-22 |  | 2015-11-12 |  |  |  | 55000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6788 | Total and available peak hour forecast of controllable and dispatchable Demand Side Management (summer and winter), in megawatts, under the control or supervision of the System Operator for ten calendar years into the future. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 14500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6789 | A request to provide any or all of the following summary explanations, as necessary,: |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2015-04-27 |  | 2016-09-30 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6794 | How the peak Demand forecast compares to actual Demand for the prior calendar year with due regard to any relevant weather-related variations (e.g., temperature, humidity, or wind speed) and, if applicable, how the assumptions and methods for future forecasts were adjusted. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-07-01 |  | 2016-09-30 |  |  |  | 15500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6813 | Provisions for periodic communications to support reliable operations. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-26 | [5 empty] | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6856 | Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 12500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6868 | Requests to government agencies to implement their programs to achieve necessary energy reductions; |  | BA | BA | [21 empty] | 2017-04-01 | [5 empty] | 22500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6908 | Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 93500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6917 | Provisions for personnel training, as related to NPIRs |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 94500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6921 | One or more processes to preserve data, per Cyber Asset capability, for determining the cause of a Cyber Security Incident that triggers activation of the recovery plan(s). Data preservation should not impede or restrict recovery. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.5. An example of evidence may include, but is not limited to, procedures to preserve data, such as preserving a corrupted drive or making a data mirror of the system before proceeding with recovery. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-009-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 6942 | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 45000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 695 | Other assumptions. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2012-12-31 |  |  |  | 13500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7058 | Coordination of information exchange to support reliability assessments. |  | RC | [11 empty] | RC | [12 empty] | 2016-01-26 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7069 | Other System Operating Limits (SOLs). |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 11500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7075 | Parallel path (loop flow) adjustments; |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 12500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7087 | Parallel path (loop flow) adjustments; |  | TSP | [20 empty] | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 21500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 715 | In determining the system’s response to any of the multiple Contingencies, identified in Reliability Standard TPL-003, in addition to the actions identified in R2.3.1 and R2.3.2, the following shall be acceptable: |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-010-1 R2. | 25000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7182 | Any one BES Element within a major voltage sensitive area as defined by an area with an in-service undervoltage load shedding (UVLS) program. |  | PCPA, RC | [9 empty] | PA |  | RC | [10 empty] | 2016-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 51500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7206 | Data files will be named in conformance with C37.232, IEEE Standard for Common Format for Naming Time Sequence Data Files (COMNAME), revision C37.232-2011 or later. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2022-07-01 |  |  |  | 4.1 The Responsible Entity is: 4.1.1 Eastern Interconnection – Planning Coordinator4.1.2 ERCOT Interconnection – Planning Coordinator or Reliability Coordinator4.1.3 Western Interconnection – Reliability Coordinator4.1.4 Quebec Interconnection – Planning Coordinator or Reliability Coordinator |  | 115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7213 | Handling of BES Cyber System Information and its storage; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 722 | Anticipated transmission system configuration, generation dispatch and Load level. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-010-1 R3. | 35000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7224 | Any security patches applied. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 11500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7231 | Where technically feasible, for each change that deviates from the existing baseline configuration: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.5. An example of evidence may include, but is not limited to, a list of cyber security controls tested along with successful test results and a list of differences between the production and test environments with descriptions of how any differences were accounted for, including of the date of the test. | 2016-03-31 |  | 2020-09-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7269 | For termination actions, change passwords for shared account(s) known to the user within 30 calendar days of the termination action. For reassignments or transfers, change passwords for shared account(s) known to the user within 30 calendar days following the date that the Responsible Entity determines that the individual no longer requires retention of that access. If the Responsible Entity determines and documents that extenuating operating circumstances require a longer time period, change the password(s) within 10 calendar days following the end of the operating circumstances.If the Responsible Entity determines and documents that extenuating operating circumstances require a longer time period, change the password(s) within 10 calendar days following the end of the operating circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.5 Examples of evidence may include, but are not limited to:• Workflow or sign-off form showing password reset within 30 calendar days of the termination; • Workflow or sign-off form showing password reset within 30 calendar days of the reassignments or transfers; or• Documentation of the extenuating operating circumstance and workflow or sign-off form showing password reset within 10 calendar days following the end of the operating circumstance. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 55000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7314 | For password-only authentication for interactive user access, either technically or procedurally enforce the following password parameters: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.5. Examples of evidence may include, but are not limited to:• System-generated reports or screen-shots of the system-enforced password parameters, including length and complexity; or • Attestations that include a reference to the documented procedures that were followed. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 55000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7343 | Issue an alarm or alert in response to detected unauthorized access through a physical access point into a Physical Security Perimeter to the personnel identified in the BES Cyber Security Incident response plan within 15 minutes of detection. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.5. An example of evidence may include, but is not limited to, language in the physical security plan that describes the issuance of an alarm or alert in response to unauthorized access through a physical access control into a Physical Security Perimeter and additional evidence that the alarm or alert was issued and communicated as identified in the BES Cyber Security Incident Response Plan, such as manual or electronic alarm or alert logs, cell phone or pager logs, or other evidence that documents that the alarm or alert was generated and communicated. | 2016-07-01 | [5 empty] | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7357 | Real and reactive power. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 55000000 | NPCC-US |  | NPCC-US
5. | 7405 | Major transmission junctions. |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 72500000 | NPCC-US |  | NPCC-US
5. | 7419 | Real and reactive power. |  | RC | [11 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 105000000 | NPCC-US |  | NPCC-US
5. | 7424 | Monthly verification of active analog quantities. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 145000000 | NPCC-US |  | NPCC-US
5. | 743 | Starting with all Facilities in service and following any of the multiple Contingencies identified in Reliability Standard TPL-003 the system shall demonstrate transient, dynamic and voltage stability; all Facilities shall be operating within their Facility Ratings and within their thermal, voltage and stability limits; and Cascading or uncontrolled separation shall not occur. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | FAC-010-2 R2. | 25000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7436 | Date last tested. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 175000000 | NPCC-US |  | NPCC-US
5. | 7476 | Each adjacent Transmission Operator synchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  |  | 35000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7482 | Incident reporting and response planning (CIP-008); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7497 | Each Adjacent Balancing Authority. |  | BA | BA | [21 empty] | 2015-11-13 |  | 2017-09-30 |  |  |  | 55000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 751 | Anticipated transmission system configuration, generation dispatch and Load level. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | FAC-010-2 R3. | 35000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7520 | Process to ensure that individuals with unescorted physical access have had a personnel risk assessment completed according to Parts 3.1 to 3.4 within the last seven years. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M3.5. An example of evidence may include, but is not limited to, documentation of the Responsible Entity’s process for ensuring that individuals with authorized electronic or authorized unescorted physical access have had a personnel risk assessment completed within the last seven years. | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 35000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7594 | Total and available peak hour forecast of controllable and dispatchable Demand Side Management (summer and winter), in megawatts, under the control or supervision of the System Operator for ten calendar years into the future. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” |  | 14500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7595 | A request to provide any or all of the following summary explanations, as necessary,: |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-02-18 |  | 2021-03-31 |  |  |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7600 | How the peak Demand forecast compares to actual Demand for the prior calendar year with due regard to any relevant weather-related variations (e.g., temperature, humidity, or wind speed) and, if applicable, how the assumptions and methods for future forecasts were adjusted. |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2016-10-01 |  | 2021-03-31 |  | This proposed standard combines “Planning Authority” with “Planning Coordinator” in the list of applicable functional entities. The NERC Functional Model lists “Planning Coordinator” while the registration criteria list “Planning Authority,” and they are not yet synchronized. Until that occurs, the proposed standard applies to both “Planning Authority” and “Planning Coordinator.” |  | 15500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7652 | Identified unanticipated high priority work |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:4.1.1. Applicable Transmission Owners4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.4.1.2. Applicable Generator Owners4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.2.1. Each overhead transmission line operated at 200kV or higher.4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:4.3.1.1. Operated at 200kV or higher; or4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 74000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7671 | The Transmission Operator shall identify when the TTC for the ATC Path being studied has an adverse impact on the TTC value of any existing path. Do this by modeling the flow on the path being studied at its proposed new TTC level simultaneous with the flow on the existing path at its TTC level while at the same time honoring the reliability criteria outlined in R2.1. The Transmission Operator shall include the resolution of this adverse impact in its study report for the ATC Path. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 25000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7698 | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 450000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7718 | Due to a component failure, the AVR may be out of service up to one year provided the Generator Operator or Transmission Operator submits documentation identifying the need for time to obtain replacement parts and if required to schedule an outage. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2015-03-03 |  | 2018-09-05 |  |  |  | 15000000 | WECC-US | [5 empty] | WECC-US
5. | 7759 | Transient voltage responses shall be within acceptable limits as established by the Transmission Planner and the Planning Coordinator. |  | PCPA | [9 empty] | PA | [12 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 41450000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7760 | Except for limited impact RAS, a single component failure in the RAS, when the RAS is intended to operate does not prevent the BES from meeting the same performance requirements (defined in Reliability Standard TPL-001-4 or its successor) as those required for the events and conditions for which the RAS is designed. |  | PCPA | [9 empty] | PA | [12 empty] | 2021-01-01 |  |  |  | 4.1.3. RAS-entity – the Transmission Owner, Generator Owner, or Distribution Provider that owns all or part of a RAS |  | 41500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7780 | Specify the instances that require time identification when issuing an oral or written Operating Instruction and the format for that time identification. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2015-06-22 | [5 empty] | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 779 | Allowed uses of Special Protection Systems or Remedial Action Plans. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-011-1 R3. | 35000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7796 | Each adjacent Transmission Operator synchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2016-10-28 | [5 empty] | 35000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7808 | Each Adjacent Balancing Authority. |  | BA | BA | [21 empty] | 2016-10-28 | [5 empty] | 55000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7832 | Unit is generating less power than its design limit for effective PSS operation. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-04-01 |  | 2017-06-30 |  |  |  | 15000000 | WECC-US | [5 empty] | WECC-US
5. | 7893 | Physical and cyber security. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2019-04-01 | [5 empty] | 12500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7896 | A transition period between the loss of primary control center functionality and the time to fully implement the backup functionality that is less than or equal to two hours. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7916 | Identification of the Reliability Coordinator as the primary contact for disseminating information regarding restoration to neighboring Reliability Coordinators, and to Transmission Operators, and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2018-03-26 | [5 empty] | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7936 | Identification of Cranking Paths and initial switching requirements between each Blackstart Resource and the unit(s) to be started. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7962 | Transition of Demand and resource balance within its area to the Balancing Authority. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 85000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 7981 | Units that have an excitation system or PSS that is incapable of meeting the tuning requirements of Requirement R3 are exempt from Requirement R3 until the voltage regulator is either replaced or retrofitted such that the PSS becomes capable of meeting the tuning requirements. |  | GO | [22 empty] | 2017-04-28 |  | 2017-09-25 |  |  |  | 35000000 | WECC-US | [5 empty] | WECC-US
5. | 7993 | Incident reporting and response planning (CIP-008); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 8002 | Transient Cyber Assets and Removable Media malicious code risk mitigation; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 8027 | Obtain and utilize the status of Remedial Action Schemes outside its Transmission Operator Area identified as necessary by the Transmission Operator; and |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-17 |  | 2021-03-31 |  |  |  | 105000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 808 | Allowed uses of Special Protection Systems or Remedial Action Plans. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | FAC-011-2 R3. | 35000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 8092 | Verification of software integrity and authenticity of all software and patches provided by the vendor for use in the BES Cyber System; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and4.1.2.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and4.2.1.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers4.2.2.1. All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-013-1:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the identification and categorization process required by CIP-002-5, or any subsequent version of that Reliability Standard. |  | 12500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 8101 | Have one or more methods for detecting known or suspected malicious communications for both inbound and outbound communications. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, documentation that malicious communications detection methods (e.g. intrusion detection system, application layer firewall, etc.) are implemented. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-005-6:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 8107 | Have one or more method(s) to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access). |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | Examples of evidence may include, but are not limited to, documentation of the methods(s) used to disable active vendor remote access (including Interactive Remote Access and system-to-system remote access), such as:• Methods to disable vendor remote access at the applicable Electronic Access Point for system-to-system remote access; or• Methods to disable vendor Interactive Remote Access at the applicable Intermediate System. | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-005-6:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 25000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 8114 | Any security patches applied. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 11500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 8121 | Where technically feasible, for each change that deviates from the existing baseline configuration: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to, a list of cyber security controls tested along with successful test results and a list of differences between the production and test environments with descriptions of how any differences were accounted for, including of the date of the test. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 8145 | The difference between frequency set points shall be at least 0.2 Hz but no greater than 0.5 Hz. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2017-10-16 | [5 empty] | 25000000 | SERC-US |  |  |  | SERC-US
5. | 8178 | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-3 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 45000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 8213 | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-3 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 450000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 8235 | Daily demand modeling assumptions (firm, interruptible). |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 13150000 | RF-US |  |  | RF-US
5. | 8242 | Modeling assumptions of intermittent and energy limited resource such as wind and cogeneration. |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 13250000 | RF-US |  |  | RF-US
5. | 8252 | Sensitivity to resource outage rates. |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 14500000 | RF-US |  |  | RF-US
5. | 8256 | Consider Transmission maintenance outage schedules and document how and why they were included in the Resource Adequacy analysis or why they were not included |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-16 | [5 empty] | 15000000 | RF-US |  |  | RF-US
5. | 8271 | Units that have an excitation system or PSS that is incapable of meeting the tuning requirements of Requirement R3 are exempt from Requirement R3 until the voltage regulator is either replaced or retrofitted such that the PSS becomes capable of meeting the tuning requirements. |  | GO | [22 empty] | 2017-09-26 |  |  |  | 5. Facilities: This standard applies to synchronous generators, connected to the Bulk Electric System, that meet the definition of Commercial Operation. |  | 35000000 | WECC-US | [5 empty] | WECC-US
5. | 8354 | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2019-06-30 |  |  |  | 75000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 8401 | Protection and control |  | RC | [11 empty] | RC | [10 empty] | 2019-07-01 | [5 empty] | 11500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 8411 | Voltage and reactive |  | TOP | [18 empty] | TOP |  |  |  | 2019-07-01 | [5 empty] | 21500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 8457 | Resources (supply or demand side) required for Load. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  |  | 11500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 8464 | When an entity’s spare equipment strategy could result in the unavailability of major Transmission equipment that has a lead time of one year or more (such as a transformer), the impact of this possible unavailability on System performance shall be assessed. Based upon this assessment, an analysis shall be performed for the P0, P1, and P2 categories identified in Table 1 with the conditions that the System is expected to experience during the possible unavailability of the long lead time equipment. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  |  | 21500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 8473 | When an entity’s spare equipment strategy could result in the unavailability of major Transmission equipment that has a lead time of one year or more (such as a transformer), the impact of this possible unavailability on System performance shall be assessed. Based upon this assessment, an analysis shall be performed for the selected P1 and P2 category events identified in Table 1 for which the unavailability is expected to produce more severe System impacts on its portion of the BES. The analysis shall simulate the conditions that the System is expected to experience during the possible unavailability of the long lead time equipment. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2020-06-10 |  |  |  | 24500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 8474 | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed to address the impact of proposed material generation additions or changes in that timeframe and be supported by current or past studies as qualified in Requirement R2, Part2.6 and shall include documentation to support the technical rationale for determining material changes. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-04-13 |  | 2020-06-10 |  |  |  | 25000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 8499 | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R3, Part 3.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-04-13 |  | 2020-06-10 |  |  |  | 35000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 8574 | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  | 2020-10-05 |  | 4.2. Facilities:4.2.1. Facilities that include power transformer(s) with a high side, wye-grounded winding with terminal voltage greater than 200 kV. |  | 75000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 8637 | The Responsible Entity shall review logs of system events related to cyber security and maintain records documenting review of logs. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP | [7 empty] | 65000000 | MRO-MB | MRO-US
5. | 8662 | A method to determine forecast data included in analyses and assessments; and | [24 empty] | 2020-01-01 |  | 2021-03-31 |  | ApplicabilityAs used in this WECC Regional Variance, Reliability Coordinator is specific to those Reliability Coordinators providing Reliability Coordinator service(s) to entities operating within the Western Interconnection, regardless of where the Reliability Coordinator may be located. |  | 750000 | WECC-US | [5 empty] | WECC-US
5. | 8676 | A method to determine forecast data included in analyses and assessments; and |  | RC | [11 empty] | RC | [10 empty] | 2021-04-01 | [5 empty] | 750000 | WECC-US | [5 empty] | WECC-US
5. | 8685 | Incident reporting and response planning (CIP-008); |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 8695 | Transient Cyber Assets and Removable Media malicious code risk mitigation; and | [28 empty] | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 8776 | Obtain and utilize the status of Remedial Action Schemes outside its Transmission Operator Area identified as necessary by the Transmission Operator; and |  | TOP | [18 empty] | TOP |  |  |  | 2021-04-01 | [5 empty] | 105000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 9008 | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 75000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 9039 | Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2024-01-01 |  |  |  | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 115000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 9090 | Total and available peak hour forecast of controllable and dispatchable Demand Side Management (summer and winter), in megawatts, under the control or supervision of the System Operator for ten calendar years into the future. | [24 empty] | 2021-04-01 | [5 empty] | 14500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 9091 | A request to provide any or all of the following summary explanations, as necessary,: |  | BA, PCPA | BA | [8 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 9129 | Provision for considering, within the restoration process, the requirements and urgency of a nuclear plant that has lost all off-site and on-site AC power. | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 93500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 9137 | Provisions for personnel training, as related to NPIRs | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 94500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 9162 | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-4 — Attachment 1. |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 450000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 9183 | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-4 — Attachment 1. |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 45000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 9318 | For the Planning Assessment, the Long-Term Transmission Planning Horizon portion of the Stability analysis shall be assessed to address the impact of proposed material generation additions or changes in that timeframe and be supported by current or past studies as qualified in Requirement R2, Part2.6 and shall include documentation to support the technical rationale for determining material changes. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 25000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 9338 | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R3, Part 3.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 35000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 9372 | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-5 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 450000 | WECC-US | [5 empty] | WECC-US
5. | 9455 | Have one or more methods for detecting known or suspected malicious communications for both inbound and outbound communications. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 9460 | Have one or more method(s) to disable active vendor remote access including Interactive Remote Access and system-to-system remote access). |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 25000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | 9476 | Where technically feasible, for each change that deviates from the existing baseline configuration: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 15000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | RP-2021-06-08-0000012 | Percentage and/or MW of bus load to be shed at the location |  | DP, TO |  | DP | [22 empty] | 2013-11-07 |  |  |  | 50500000 | SPPRE-US
5. | RP-2021-06-08-0000020 | MW of generation shed at each location |  | GO | [24 empty] | 2013-11-07 |  |  |  | 60500000 | SPPRE-US
5. | RP-2021-06-16-0000041 | Consider Transmission maintenance outage schedules and document how and why they were included in the Resource Adequacy analysis or why they were not included |  | PCPA | [9 empty] | PA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  |  | 10500000 | RF-US |  |  | RF-US
5. | RP-2021-06-18-0000010 | Where technically feasible, for eachchange that deviates from the existingbaseline configuration: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP | [5 empty] | 2016-06-30 |  |  |  | 10500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | RP-2021-06-18-0000011 | Where technically feasible, for eachchange that deviates from the existingbaseline configuration: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2020-06-30 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-010-2: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 10500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | RP-2021-06-22-0000013 | Transformer (voltage and phase-shifting): nominal voltages of windings, impedance,tap ratios (voltage and/or phase angle or tap step size), regulated bus and voltage setpoint, Normal and Emergency Ratings (consistent with methodologies defined andRatings supplied per Reliability Standard FAC-008-1 and FAC-009-1), and equipmentstatus. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 10500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | RP-2021-06-23-0000014 | Dynamic VAR Devices. |  | TO | [22 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 20500000 | NPCC-US |  | NPCC-US
5. | RP-2021-06-24-0000040 | Those extreme events in Table 1 that are expected to produce more severeSystem impacts shall be identified and a list created of those events to beevaluated in Requirement R3, Part 3.2. The rationale for those Contingenciesselected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-07-01 |  | 2020-06-10 |  |  |  | 30500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | RP-2021-06-24-0000053 | Those extreme events in Table 1 that are expected to produce more severeSystem impacts shall be identified and a list created of those events to beevaluated in Requirement R4, Part 4.2. The rationale for those Contingenciesselected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-07-01 |  | 2020-06-10 |  |  |  | 40500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | RP-2021-06-24-0000132 | The deadline by which the respondent is to provide the indicated data. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 42300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | RP-2021-06-24-0000151 | The deadline by which the respondent is to provide the indicated data. |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 10500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | RP-2021-06-24-0000165 | The deadline by which the respondent is to provide the indicated data. | [30 empty] | 20500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | RP-2021-06-24-0000166 | The deadline by which the respondent is to provide the indicated data. |  | BA, DP, GO, GOP, TO, TOP | BA | DP |  |  | GO | GOP | [11 empty] | TO | TOP | [9 empty] | 20500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | RP-2021-06-25-0000006 | Unit is generating less power than its design limit for effective PSS operation. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-07-01 |  | 2015-03-31 |  |  |  | 10500000 | WECC-US | [5 empty] | WECC-US
5. | RP-2021-06-25-0000011 | Unit is generating less power than its design limit for effective PSS operation. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-04-01 |  | 2017-06-30 |  |  |  | 10500000 | WECC-US | [5 empty] | WECC-US
5. | RP-2021-06-25-0000013 | Units that have an excitation system or PSS that is incapable of meeting the tuning requirements of Requirement R3 are exempt from Requirement R3 until the voltage regulator is either replaced or retrofitted such that the PSS becomes capable of meeting the tuning requirements. |  | GO | [22 empty] | 2017-07-01 |  | 2017-09-25 |  |  |  | 30500000 | WECC-US | [5 empty] | WECC-US
5. | RP-2021-06-30-0000017 | Where technically feasible, for each change that deviates from the existing baseline configuration: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 10500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | RP-2021-06-30-0000028 | Where technically feasible, for each change that deviates from the existing baseline configuration: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 10500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | RP-2021-07-01-0000002 | Transition of Demand and resource balance within its area to the Balancing Authority. |  | TOP | [18 empty] | TOP |  |  |  | 2019-04-01 | [5 empty] | 80500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | RP-2021-07-07-0000016 | The Transmission Operator shall identify when the TTC for the ATC Path being studied has an adverse impact on the TTC value of any existing path. Do this by modeling the flow on the path being studied at its proposed new TTC level simultaneous with the flow on the existing path at its TTC level while at the same time honoring the reliability criteria outlined in R2.1. The Transmission Operator shall include the resolution of this adverse impact in its study report for the ATC Path. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 20500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | RP-2021-07-09-0000011 | Overfrequency trip settings of generating plants/facilities greater than 75 MVA (gross aggregate nameplate rating) directly connected to the BES that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-5 — Attachment 1. |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2021-04-01 |  |  |  | UFLS entities shall mean all entities that are responsible for the ownership,operation, or control of UFLS equipment as required by the UFLS programestablished by the Planning Coordinators. Such entities may include one ormore of the following: 4.2.1 Transmission Owners4.2.2 Distribution Providers4.2.3 UFLS-Only Distribution Providers4.3. Transmission Owners that own Elements identified in the UFLS programestablished by the Planning Coordinators. |  | 40500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | RP-2021-07-09-0000053 | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R3, Part 3.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences and adverse impacts of the event(s) shall be conducted. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 30500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | RP-2021-07-09-0000057 | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R4, Part 4.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. If the analysis concludes there is Cascading caused by the occurrence of extreme events, an evaluation of possible actions designed to reduce the likelihood or mitigate the consequences of the event(s) shall be conducted. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 40500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | RP-2021-07-12-0000031 | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R3, Part 3.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 30500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | RP-2021-07-12-0000045 | Those extreme events in Table 1 that are expected to produce more severe System impacts shall be identified and a list created of those events to be evaluated in Requirement R4, Part 4.2. The rationale for those Contingencies selected for evaluation shall be available as supporting information. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 40500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | RP-2021-07-12-0000062 | Units that have an excitation system or PSS that is incapable of meeting the tuning requirements of Requirement R3 are exempt from Requirement R3 until the voltage regulator is either replaced or retrofitted such that the PSS becomes capable of meeting the tuning requirements. |  | GO | [22 empty] | 2017-09-26 |  |  | Requirement R3 has an effective date of July 1, 2017 for first-time service after regulatory approval; R3 has an effective date of July 1, 2022 for units placed in service prior to final regulatory approval. | 5. Facilities: This standard applies to synchronous generators, connected to the Bulk Electric System, that meet the definition of Commercial Operation. |  | 30500000 | WECC-US | [5 empty] | WECC-US
5. | RP-2021-07-13-0000005 | Obtain and utilize the status of Remedial Action Schemes outside its Transmission Operator Area identified as necessary by the Transmission Operator; and |  | BA, DP, GOP, TOP | BA | DP |  |  |  | GOP | [12 empty] | TOP | [9 empty] | 100500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | RP-2021-07-13-0000011 | Define the method for determining common System Voltage Limits between the Reliability Coordinator and its Transmission Operators, between adjacent Transmission Operators, and between adjacent Reliability Coordinators within an Interconnection. |  | RC | [11 empty] | RC | [16 empty] | 30500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | RP-2021-07-13-0000020 | Describe the level of detail that is required for the study model(s), including the portion modeled of the Reliability Coordinator Area, and the critical modeling details from other Reliability Coordinator Areas, necessary to determine different types of stability limits. |  | RC | [11 empty] | RC | [16 empty] | 40500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | RP-2021-07-13-0000066 | Each requesting Transmission Operator within its Reliability Coordinator Area, requested SOL information for its Reliability Coordinator Area, on a mutually agreed upon schedule. |  | RC, TOP, TP | [11 empty] | RC | [6 empty] | TOP | TP | [8 empty] | 50500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | RP-2021-07-13-0000072 | The System conditions and Facilities associated with the identified instability requiring the Corrective Action Plan. |  | RC, TOP, TP | [11 empty] | RC | [6 empty] | TOP | TP | [8 empty] | 70500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | RP-2021-07-13-0000083 | Identified unanticipated high priority work |  | GO, TO |  |  |  |  | GO | [23 empty] | 70500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5. | RP-2021-07-15-0000044 | Data files will be named in conformance with C37.232, IEEE Standard for Common Format for Naming Time Sequence Data Files (COMNAME), revision C37.232-2011 or later. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [16 empty] | 110500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5.1. | 79780009009 | If a recipient of the CAP provides documented comments on the CAP, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 75100000 | NPCC-ON |  | NPCC-US
5.1. | 79780009040 | If a recipient of the CAP provides documented comments on the CAP, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 115100000 | NPCC-ON |  | NPCC-US
5.1. | 79780009092 | The assumptions and methods used in the development of aggregated Peak Demand and Net Energy for Load forecasts. | [24 empty] | 2021-04-01 | [5 empty] | 15100000 | NPCC-ON |  | NPCC-US
5.1. | 9009 | If a recipient of the CAP provides documented comments on the CAP, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 75100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5.1. | 9040 | If a recipient of the CAP provides documented comments on the CAP, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | [28 empty] | 4.1. Functional Entities: 4.1.1. Planning Coordinator with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.2. Transmission Planner with a planning area that includes a Facility or Facilities specified in 4.2; 4.1.3. Transmission Owner who owns a Facility or Facilities specified in 4.2; and 4.1.4. Generator Owner who owns a Facility or Facilities specified in 4.2. 4.2. Facilities: 4.2.1. Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV. |  | 115100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5.1. | 9092 | The assumptions and methods used in the development of aggregated Peak Demand and Net Energy for Load forecasts. | [24 empty] | 2021-04-01 | [5 empty] | 15100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5.1. | RP-2021-06-22-0000015 | Verified maximum gross and net Reactive Power capability (both laggingand leading) at Seasonal Real Power generating capabilities as reported inaccordance with Reliability Standard MOD-024 Requirement 1.5.1. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 15100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5.1. | RP-2021-06-30-0000029 | Prior to implementing any change in the production environment, test the changes in a test environment or test the changes in a production environment where the test is performed in a manner that minimizes adverse effects, that models the baseline configuration to ensure that required cyber security controls in CIP-005 and CIP-007 are not adversely affected; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 15100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5.2. | 79780009093 | The Demand and energy effects of controllable and dispatchable Demand Side Management under the control or supervision of the System Operator. | [24 empty] | 2021-04-01 | [5 empty] | 15200000 | NPCC-ON |  | NPCC-US
5.2. | 9093 | The Demand and energy effects of controllable and dispatchable Demand Side Management under the control or supervision of the System Operator. | [24 empty] | 2021-04-01 | [5 empty] | 15200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5.2. | RP-2021-06-22-0000016 | Verified Reactive Power limitations, such as generator terminal voltagelimitations, shorted rotor turns, etc. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 15200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5.2. | RP-2021-06-30-0000030 | Document the results of the testing and, if a test environment was used, the differences between the test environment and the production environment, including a description of the measures used to account for any differences in operation between the test and production environments. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 15200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5.3. | 79780009094 | How Demand Side Management is addressed in the forecasts of its Peak Demand and annual Net Energy for Load. | [24 empty] | 2021-04-01 | [5 empty] | 15300000 | NPCC-ON |  | NPCC-US
5.3. | 9094 | How Demand Side Management is addressed in the forecasts of its Peak Demand and annual Net Energy for Load. | [24 empty] | 2021-04-01 | [5 empty] | 15300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5.3. | RP-2021-06-22-0000017 | Verified Reactive Power of auxiliary loads. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 15300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5.3. | RP-2021-07-07-0000001 | The source/sink or POR/POD identification and mapping to the model. |  | TSP | [20 empty] | TSP |  | 2013-10-01 |  |  |  | 4. Applicability:4.1. Each Transmission Operator that uses the Area Interchange Methodology to calculate Total Transfer Capabilities (TTCs) for ATC Paths. 4.2. Each Transmission Service Provider that uses the Area Interchange Methodology to calculate Available Transfer Capabilities (ATCs) for ATC Paths. |  | 15300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5.4. | 79780009095 | How the controllable and dispatchable Demand Side Management forecast compares to actual controllable and dispatchable Demand Side Management for the prior calendar year and, if applicable, how the assumptions and methods for future forecasts were adjusted. | [24 empty] | 2021-04-01 | [5 empty] | 15400000 | NPCC-ON |  | NPCC-US
5.4. | 9095 | How the controllable and dispatchable Demand Side Management forecast compares to actual controllable and dispatchable Demand Side Management for the prior calendar year and, if applicable, how the assumptions and methods for future forecasts were adjusted. | [24 empty] | 2021-04-01 | [5 empty] | 15400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
5.5. | 79780009096 | How the peak Demand forecast compares to actual Demand for the prior calendar year with due regard to any relevant weather-related variations (e.g., temperature, humidity, or wind speed) and, if applicable, how the assumptions and methods for future forecasts were adjusted. | [24 empty] | 2021-04-01 | [5 empty] | 15500000 | NPCC-ON |  | NPCC-US
5.5. | 9096 | How the peak Demand forecast compares to actual Demand for the prior calendar year with due regard to any relevant weather-related variations (e.g., temperature, humidity, or wind speed) and, if applicable, how the assumptions and methods for future forecasts were adjusted. | [24 empty] | 2021-04-01 | [5 empty] | 15500000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6 | 79780000025 | The same portion of resource capacity (e.g., reserves from jointly owned generation) shall not be counted more than once as Contingency Reserve by multiple Balancing Authorities. |  | RRO, RSG | [14 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  |  | 26000000 | NPCC-ON |  | NPCC-US
6 | 79780000252 | Special Protection Systems that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 12600000 | NPCC-ON |  | NPCC-US
6 | 79780000305 | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780000316 | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 26000000 | NPCC-ON |  | NPCC-US
6 | 79780000336 | Procedures for escorted access within the physical security perimeter of personnel not authorized for unescorted access. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780000363 | Procedures for escorted access within the physical security perimeter of personnel not authorized for unescorted access. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780000433 | Process for ensuring the Cyber Security Incident response plan is tested at least annually. A test of the incident response plan can range from a paper drill, to a full operational exercise, to the response to an actual incident. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780000513 | Reducing load, through procedures such as public appeals, voltage reductions, curtailing interruptible loads and firm loads. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  |  | 66000000 | NPCC-ON |  | NPCC-US
6 | 79780000534 | Reducing load, through procedures such as public appeals, voltage reductions, curtailing interruptible loads and firm loads. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-09-30 |  |  |  | 66000000 | NPCC-ON |  | NPCC-US
6 | 79780000603 | The plan shall include procedures and responsibilities for providing annual training to ensure that operating personnel are able to implement the contingency plans. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780000626 | Metering and telecommunications. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 21600000 | NPCC-ON |  | NPCC-US
6 | 79780000723 | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-05-29 |  | 2009-04-28 |  |  |  | 36000000 | NPCC-ON |  | NPCC-US
6 | 79780000744 | In determining the system’s response to any of the multiple Contingencies, identified in Reliability Standard TPL-003, in addition to the actions identified in R2.3.1 and R2.3.2, the following shall be acceptable: |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 26000000 | NPCC-ON |  | NPCC-US
6 | 79780000752 | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  |  | 36000000 | NPCC-ON |  | NPCC-US
6 | 79780000780 | Anticipated transmission system configuration, generation dispatch and Load level. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 36000000 | NPCC-ON |  | NPCC-US
6 | 79780000809 | Anticipated transmission system configuration, generation dispatch and Load level |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 36000000 | NPCC-ON |  | NPCC-US
6 | 79780001002 | Current ACE for all its Balancing Authorities. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780001029 | Current ACE for all its Balancing Authorities. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780001056 | Current ACE for all its Balancing Authorities. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780001112 | Authority to act to prevent and mitigate instances of causing Adverse Reliability Impacts to other Reliability Coordinator Areas. |  | RC | [11 empty] | RC | [9 empty] | M1.1.6 Authority to act to prevent and mitigate instances of causing Adverse&lt;br/&gt;Reliability Impacts to other Reliability Coordinator Areas. | 2007-06-18 |  | 2017-03-31 |  |  |  | 11600000 | NPCC-ON |  | NPCC-US
6 | 79780001145 | Indication of the treatment and level of customer demands, including interruptible demands. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780001163 | A description of how generation and transmission outages are considered in transfer or Flowgate capability calculations, including: |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 36000000 | NPCC-ON |  | NPCC-US
6 | 79780001173 | Each Transmission Service Provider whose area is adjacent to the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 46000000 | NPCC-ON |  | NPCC-US
6 | 79780001203 | Describe the inclusion or exclusion rationale for generation connected to the Transmission Service Provider’s system but not obligated to serve Native/Network Load connected to the Transmission Service Provider’s system. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780001267 | Allowances for simultaneous path interactions. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 13600000 | NPCC-ON |  | NPCC-US
6 | 79780001299 | Reactive Compensation (shunt and series capacitors and reactors): nominal Ratings, impedance, percent compensation, connection point, and controller device. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780001432 | Uses Transmission Facility additions and retirements. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 11600000 | NPCC-ON |  | NPCC-US
6 | 79780001446 | Where multiple ownership of Transmission rights exists on an ATC Path, allocate TTC of that ATC Path in accordance with the contractual agreement made by the multiple owners of that ATC Path. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 26000000 | NPCC-ON |  | NPCC-US
6 | 79780001484 | Provide the Transmission Service Provider with the TFCs within seven calendar days of their establishment. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  |  | 26000000 | NPCC-ON |  | NPCC-US
6 | 79780001506 | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 66000000 | NPCC-ON |  | NPCC-US
6 | 79780001514 | The impact of any non-firm Network Integration Transmission Service (secondary service) with a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 76000000 | NPCC-ON |  | NPCC-US
6 | 79780001549 | Provide the Transmission Service Provider with the TFCs within seven calendar days of their establishment. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 26000000 | NPCC-ON |  | NPCC-US
6 | 79780001571 | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 66000000 | NPCC-ON |  | NPCC-US
6 | 79780001579 | The impact of any non-firm Network Integration Transmission Service (secondary service) with a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 76000000 | NPCC-ON |  | NPCC-US
6 | 79780001610 | Coordination of physical and cyber security protection of the Bulk Electric System at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 93600000 | NPCC-ON |  | NPCC-US
6 | 79780001695 | Data content requirements and guidelines. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 46000000 | NPCC-ON |  | NPCC-US
6 | 79780001741 | Islanding schemes. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  |  | 12600000 | NPCC-ON |  | NPCC-US
6 | 79780001777 | Date last tested/maintained. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2021-03-31 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780001785 | Regional Reliability Organization definition of misoperation. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780001822 | Date last tested/maintained. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2007-06-18 |  | 2017-03-31 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780001834 | Monitored elements, such as transmission circuit, bus section, etc. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2022-06-30 |  |  |  | 36000000 | NPCC-ON |  | NPCC-US
6 | 79780001848 | Any other schemes that are part of or impact the UVLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UFLS and Special Protection Systems. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780001879 | Set transmission line relays applied on transmission lines connected to generation stations remote to load so they do not operate at or below 230% of the aggregated generation nameplate capability. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780001974 | Responding to IROL and SOL violations. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-01-21 |  |  |  | 66000000 | NPCC-ON |  | NPCC-US
6 | 79780002042 | Be performed for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 13600000 | NPCC-ON |  | NPCC-US
6 | 79780002063 | Be performed for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 13600000 | NPCC-ON |  | NPCC-US
6 | 79780002087 | Be performed and evaluated for selected demand levels over the range of forecast system Demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13600000 | NPCC-ON |  | NPCC-US
6 | 79780002112 | Be performed and evaluated for selected demand levels over the range of forecast system Demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 13600000 | NPCC-ON |  | NPCC-US
6 | 79780002137 | Be performed and evaluated for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13600000 | NPCC-ON |  | NPCC-US
6 | 79780002162 | Be performed and evaluated for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 13600000 | NPCC-ON |  | NPCC-US
6 | 79780002184 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  |  | 13600000 | NPCC-ON |  | NPCC-US
6 | 79780002205 | Reliability impacts of new or proposed legislation that affects, has affected, or has the potential to affect the Adequacy of the interconnected Bulk Electric Systems in North America. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  |  | 36000000 | NPCC-ON |  | NPCC-US
6 | 79780002212 | System operations and supporting information (extreme weather impacts, Interchange Transactions, and Congestion impacts on the reliability of the interconnected Bulk Electric Systems.) |  | RRO | [14 empty] | RRO | [9 empty] | 2009-04-15 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780002352 | System operations and supporting information (extreme weather impacts, Interchange Transactions, and Congestion impacts on the reliability of the interconnected Bulk Electric Systems.) |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780002362 | Special Protection Systems that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 12600000 | NPCC-ON |  | NPCC-US
6 | 79780002416 | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780002427 | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 26000000 | NPCC-ON |  | NPCC-US
6 | 79780002447 | Continuous escorted access within the Physical Security Perimeter of personnel not authorized for unescorted access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780002511 | Process for ensuring the Cyber Security Incident response plan is tested at least annually. A test of the Cyber Security Incident response plan can range from a paper drill, to a full operational exercise, to the response to an actual incident. Testing the Cyber Security Incident response plan does not require removing a component or system from service during the test. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780002547 | Coordination of physical and cyber security protection of the Bulk Electric System at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 93600000 | NPCC-ON |  | NPCC-US
6 | 79780002578 | Identification of acceptable operating voltage and frequency limits during restoration. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780002623 | Reporting requirements for the entities within the Reliability Coordinator Area during a restoration event. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780002697 | In determining the system’s response to any of the multiple Contingencies, identified in Reliability Standard TPL-003, in addition to the actions identified in R2.3.1 and R2.3.2, the following shall be acceptable: |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 26000000 | NPCC-ON |  | NPCC-US
6 | 79780002707 | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  |  | 36000000 | NPCC-ON |  | NPCC-US
6 | 79780002721 | Special Protection Systems that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | 12600000 | NPCC-ON |  | NPCC-US
6 | 79780002775 | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780002786 | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  |  | 26000000 | NPCC-ON |  | NPCC-US
6 | 79780002806 | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780002872 | Process for ensuring the Cyber Security Incident response plan is tested at least annually. A test of the Cyber Security Incident response plan can range from a paper drill, to a full operational exercise, to the response to an actual incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780002889 | Continuous escorted access within the Physical Security Perimeter of personnel not authorized for unescorted access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780002910 | Continuous escorted access within the Physical Security Perimeter of personnel not authorized for unescorted access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780002933 | Procedures for escorted access within the physical security perimeter of personnel not authorized for unescorted access. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780002963 | Procedures for escorted access within the physical security perimeter of personnel not authorized for unescorted access. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780002988 | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780003016 | A description of how generation and transmission outages are considered in transfer or Flowgate capability calculations, including: |  | TSP | [20 empty] | TSP |  | 2010-09-16 | [5 empty] | 36000000 | NPCC-ON |  | NPCC-US
6 | 79780003026 | Each Transmission Service Provider whose area is adjacent to the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-09-16 | [5 empty] | 46000000 | NPCC-ON |  | NPCC-US
6 | 79780003047 | Uses Transmission Facility additions and retirements. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 11600000 | NPCC-ON |  | NPCC-US
6 | 79780003067 | Where multiple ownership of Transmission rights exists on an ATC Path, allocate TTC of that ATC Path in accordance with the contractual agreement made by the multiple owners of that ATC Path. |  | TOP | [18 empty] | TOP |  |  |  | 2010-09-16 |  | 2017-03-31 |  |  |  | 26000000 | NPCC-ON |  | NPCC-US
6 | 79780003159 | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780003166 | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:&lt;br/&gt;4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian&lt;br/&gt;Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication&lt;br/&gt;links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify that&lt;br/&gt;they have no Critical Cyber Assets. |  | 26000000 | NPCC-ON |  | NPCC-US
6 | 79780003191 | The same portion of resource capacity (e.g. reserves from jointly owned generation) shall not be counted more than once as Contingency Reserve by multiple Balancing Authorities. |  | RRO, RSG | [14 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  |  | 26000000 | NPCC-ON |  | NPCC-US
6 | 79780003264 | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780003275 | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 26000000 | NPCC-ON |  | NPCC-US
6 | 79780003295 | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780003361 | Process for ensuring the Cyber Security Incident response plan is tested at least annually. A test of the Cyber Security Incident response plan can range from a paper drill, to a full operational exercise, to the response to an actual incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780003381 | Reducing load, through procedures such as public appeals, voltage reductions, curtailing interruptible loads and firm loads. |  | BA | BA | [21 empty] | 2011-01-10 |  | 2012-09-12 |  |  |  | 66000000 | NPCC-ON |  | NPCC-US
6 | 79780003427 | Current ACE for all its Balancing Authorities. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780003461 | Be performed for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13600000 | NPCC-ON |  | NPCC-US
6 | 79780003485 | Be performed and evaluated for selected demand levels over the range of forecast system Demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 13600000 | NPCC-ON |  | NPCC-US
6 | 79780003510 | Be performed and evaluated for selected demand levels over the range of forecast system Demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13600000 | NPCC-ON |  | NPCC-US
6 | 79780003535 | Be performed and evaluated for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13600000 | NPCC-ON |  | NPCC-US
6 | 79780003557 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13600000 | NPCC-ON |  | NPCC-US
6 | 79780003623 | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780003630 | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  |  | 26000000 | NPCC-ON |  | NPCC-US
6 | 79780003654 | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780003661 | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  |  | 26000000 | NPCC-ON |  | NPCC-US
6 | 79780003805 | Current ACE for all its Balancing Authorities. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780003898 | Continuous escorted access within the Physical Security Perimeter of personnel not authorized for unescorted access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780003922 | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780004039 | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780004061 | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780004181 | Current ACE for all its Balancing Authorities. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780004200 | Reducing load, through procedures such as public appeals, voltage reductions, curtailing interruptible loads and firm loads. |  | BA | BA | [21 empty] | 2012-09-13 |  | 2017-03-31 |  |  |  | 66000000 | NPCC-ON |  | NPCC-US
6 | 79780004237 | Coordination of physical and cyber security protection of the Bulk Electric System at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 93600000 | NPCC-ON |  | NPCC-US
6 | 79780004340 | Special Protection Systems that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 12600000 | NPCC-ON |  | NPCC-US
6 | 79780004446 | The same portion of resource capacity (e.g. reserves from jointly owned generation) shall not be counted more than once as Contingency Reserve by multiple Balancing Authorities. |  | RRO, RSG | [14 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  |  | 26000000 | NPCC-ON |  | NPCC-US
6 | 79780004563 | Special Protection Systems that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 12600000 | NPCC-ON |  | NPCC-US
6 | 79780004587 | Be performed for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13600000 | NPCC-ON |  | NPCC-US
6 | 79780004633 | Be performed and evaluated for selected demand levels over the range of forecast system Demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13600000 | NPCC-ON |  | NPCC-US
6 | 79780004658 | Be performed and evaluated for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13600000 | NPCC-ON |  | NPCC-US
6 | 79780004681 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13600000 | NPCC-ON |  | NPCC-US
6 | 79780004698 | Be performed and evaluated for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13600000 | NPCC-ON |  | NPCC-US
6 | 79780004733 | Be performed and evaluated for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13600000 | NPCC-ON |  | NPCC-US
6 | 79780004746 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13600000 | NPCC-ON |  | NPCC-US
6 | 79780004765 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13600000 | NPCC-ON |  | NPCC-US
6 | 79780004843 |  |  | BA | BA | [23 empty] | 2006-11-01 |  |  |  | 76000000 | NPCC-ON |  | NPCC-US
6 | 79780004860 |  |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 66000000 | NPCC-ON |  | NPCC-US
6 | 79780004914 |  |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-08-01 |  |  |  | 11600000 | NPCC-ON |  | NPCC-US
6 | 79780004952 |  |  | TSP | [20 empty] | TSP |  |  |  | 2007-01-01 |  |  |  | 26000000 | NPCC-ON |  | NPCC-US
6 | 79780005032 |  |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780005121 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780005147 |  |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2006-05-01 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780005211 |  |  | TOP | [18 empty] | TOP | [5 empty] | 2005-04-01 |  |  |  | 66000000 | NPCC-ON |  | NPCC-US
6 | 79780005614 | In determining the system’s response to any of the multiple Contingencies, identified in Reliability Standard TPL-003, in addition to the actions identified in R2.3.1 and R2.3.2, the following shall be acceptable: |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 26000000 | NPCC-ON |  | NPCC-US
6 | 79780005623 | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 36000000 | NPCC-ON |  | NPCC-US
6 | 79780005652 | Anticipated transmission system configuration, generation dispatch and Load level |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 36000000 | NPCC-ON |  | NPCC-US
6 | 79780005666 | Current ACE for all its Balancing Authorities. |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780005709 | Provide the Transmission Service Provider with the TFCs within seven calendar days of their establishment. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 26000000 | NPCC-ON |  | NPCC-US
6 | 79780005731 | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. (Footnote: A percentage less than that used in the Interconnection-wide congestion management procedure may be utilized.) |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 66000000 | NPCC-ON |  | NPCC-US
6 | 79780005739 | The impact of any non-firm Network Integration Transmission Service (secondary service) with a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 76000000 | NPCC-ON |  | NPCC-US
6 | 79780005758 | Remedial Action Schemes that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12600000 | NPCC-ON |  | NPCC-US
6 | 79780005770 | Remedial Action Schemes that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12600000 | NPCC-ON |  | NPCC-US
6 | 79780005803 | Coordination of physical and cyber security protection of the Bulk Electric System at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 93600000 | NPCC-ON |  | NPCC-US
6 | 79780005820 | Be performed for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13600000 | NPCC-ON |  | NPCC-US
6 | 79780005841 | Be performed and evaluated for selected demand levels over the range of forecast system Demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13600000 | NPCC-ON |  | NPCC-US
6 | 79780005866 | Be performed and evaluated for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13600000 | NPCC-ON |  | NPCC-US
6 | 79780005891 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13600000 | NPCC-ON |  | NPCC-US
6 | 79780005904 | Regional Reliability Organization definition of misoperation. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780005944 | Date last tested/maintained. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-01-25 |  | 2021-03-31 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780005952 | Any other schemes that are part of or impact the UVLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UFLS and Remedial Action Schemes. | [26 empty] | 2014-11-13 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780006036 | Uses Transmission Facility additions and retirements. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 11600000 | NPCC-ON |  | NPCC-US
6 | 79780006165 | Recovery plans for BES Cyber Systems (CIP-009); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780006205 | Where technically feasible, for password-only authentication for interactive user access, either technically or procedurally enforce password changes or an obligation to change the password at least once every 15 calendar months. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 56000000 | NPCC-ON |  | NPCC-US
6 | 79780006253 | Monitor each Physical Access Control System for unauthorized physical access to a Physical Access Control System. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 1.6 An example of evidence may include, but is not limited to, documentation of controls that monitor for unauthorized physical access to a PACS. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780006282 | Identification of a Cyber Security Incident and initial notifications in accordance with the entity’s incident response plan; | [23 empty] | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. |  |  | 2016-06-30 |  |  |  | 21600000 | NPCC-ON |  | NPCC-US
6 | 79780006429 | Model structure and data for power system stabilizer, if so equipped. |  | GO | [22 empty] | 2018-07-01 |  |  |  | 4.2. Facilities:&lt;br/&gt;For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following:&lt;br/&gt;4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: &lt;br/&gt;4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).&lt;br/&gt;4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.2 Generation in the Western Interconnection with the following characteristics:&lt;br/&gt;4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).&lt;br/&gt;4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.3 Generation in the ERCOT Interconnection with the following characteristics:&lt;br/&gt;4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).&lt;br/&gt;4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).&lt;br/&gt;4.2.4 For all Interconnections:&lt;br/&gt;• A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. |  | 21600000 | NPCC-ON |  | NPCC-US
6 | 79780006448 | Voltage and reactive |  | RC | [11 empty] | RC | [10 empty] | 2012-10-01 |  | 2019-06-30 |  |  |  | 11600000 | NPCC-ON |  | NPCC-US
6 | 79780006498 | An Operating Process describing the actions to be taken during the transition period between the loss of primary control center functionality and the time to fully implement backup functionality elements identified in Requirement R1, Part 1.2. The Operating Process shall include at a minimum: |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780006560 | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 46000000 | NPCC-ON |  | NPCC-US
6 | 79780006596 | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 460000 | NPCC-ON |  | NPCC-US
6 | 79780006628 | Resources (supply or demand side) required for Load |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-01-01 | [5 empty] | 11600000 | NPCC-ON |  | NPCC-US
6 | 79780006652 | Past studies may be used to support the Planning Assessment if they meet the following requirements: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 26000000 | NPCC-ON |  | NPCC-US
6 | 79780006696 | Contingencies |  | PCPA | [9 empty] | PA | [12 empty] | 2013-04-01 |  | 2020-12-14 |  |  |  | 14600000 | NPCC-ON |  | NPCC-US
6 | 79780006723 | Each adjacent Transmission Operator asynchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  |  | 36000000 | NPCC-ON |  | NPCC-US
6 | 79780006857 | Reliability impacts of extreme weather conditions. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 12600000 | NPCC-ON |  | NPCC-US
6 | 79780006869 | Reduction of internal utility energy use; |  | BA | BA | [21 empty] | 2017-04-01 | [5 empty] | 22600000 | NPCC-ON |  | NPCC-US
6 | 79780006909 | Coordination of physical and cyber security protection at the nuclear plant interface to ensure each asset is covered under at least one entity’s pla |  | BA, DP, GO, GOP, LSE, PCPA, RSG, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA | [6 empty] | RSG | TO | TOP | TP | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 93600000 | NPCC-ON |  | NPCC-US
6 | 79780006943 | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 46000000 | NPCC-ON |  | NPCC-US
6 | 79780007059 | Authority to act to prevent and mitigate system conditions which could cause Adverse Reliability Impacts to other Reliability Coordinator Areas. |  | RC | [11 empty] | RC | [12 empty] | 2016-01-26 |  |  |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780007076 | Load forecast; and |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 12600000 | NPCC-ON |  | NPCC-US
6 | 79780007088 | Load forecast; and |  | TSP | [20 empty] | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 21600000 | NPCC-ON |  | NPCC-US
6 | 79780007214 | Identification of a Cyber Security Incident and initial notifications in accordance with the entity’s incident response plan; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21600000 | NPCC-ON |  | NPCC-US
6 | 79780007315 | Where technically feasible, for password-only authentication for interactive user access, either technically or procedurally enforce password changes or an obligation to change the password at least once every 15 calendar months. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.6. Examples of evidence may include, but are not limited to:&lt;br/&gt;• System-generated reports or screen-shots of the system-enforced periodicity of changing passwords; or&lt;br/&gt;• Attestations that include a reference to the documented procedures that were followed. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 56000000 | NPCC-ON |  | NPCC-US
6 | 79780007344 | Monitor each Physical Access Control System for unauthorized physical access to a Physical Access Control System. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.6. An example of evidence may include, but is not limited to, documentation of controls that monitor for unauthorized physical access to a PACS. | 2016-07-01 | [5 empty] | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780007406 | Elements associated with Interconnection Reliability Operating Limits (IROLs). |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 72600000 | NPCC-ON |  | NPCC-US
6 | 79780007425 | Verification of DDR and DFR settings in the software every six (6) years. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 146000000 | NPCC-ON |  | NPCC-US
6 | 79780007437 | Monitored Elements. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 176000000 | NPCC-ON |  | NPCC-US
6 | 79780007477 | Each adjacent Transmission Operator asynchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  |  | 36000000 | NPCC-ON |  | NPCC-US
6 | 79780007483 | Recovery plans for BES Cyber Systems (CIP-009); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11600000 | NPCC-ON |  | NPCC-US
6 | 79780007654 | Weather conditions/Accessibility |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:&lt;br/&gt;4.1.1. Applicable Transmission Owners&lt;br/&gt;4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.&lt;br/&gt;4.1.2. Applicable Generator Owners&lt;br/&gt;4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. &lt;br/&gt;4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.2.1. Each overhead transmission line operated at 200kV or higher.&lt;br/&gt;4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.&lt;br/&gt;4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.&lt;br/&gt;4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. &lt;br/&gt;4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:&lt;br/&gt;4.3.1.1. Operated at 200kV or higher; or&lt;br/&gt;4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or&lt;br/&gt;4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 76000000 | NPCC-ON |  | NPCC-US
6 | 79780007672 | Where multiple ownership of Transmission rights exists on an ATC Path, allocate TTC of that ATC Path in accordance with the contractual agreement made by the multiple owners of that ATC Path. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 26000000 | NPCC-ON |  | NPCC-US
6 | 79780007699 | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 460000 | NPCC-ON |  | NPCC-US
6 | 79780007781 | Specify the nomenclature for Transmission interface Elements and Transmission interface Facilities when issuing an oral or written Operating Instruction. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2015-06-22 | [5 empty] | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780007797 | Each adjacent Transmission Operator asynchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2016-10-28 | [5 empty] | 36000000 | NPCC-ON |  | NPCC-US
6 | 79780007897 | An Operating Process describing the actions to be taken during the transition period between the loss of primary control center functionality and the time to fully implement backup functionality elements identified in Requirement R1, Part 1.2. The Operating Process shall include: |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780007917 | Criteria for transferring operations and authority back to the Balancing Authority. |  | RC | [11 empty] | RC | [10 empty] | 2019-04-01 | [5 empty] | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780007918 | Criteria for transferring operations and authority back to the Balancing Authority. |  | RC | [11 empty] | RC | [10 empty] | 2018-03-26 | [5 empty] | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780007937 | Identification of acceptable operating voltage and frequency limits during restoration. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780007994 | Recovery plans for BES Cyber Systems (CIP-009); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11600000 | NPCC-ON |  | NPCC-US
6 | 79780008003 | Declaring and responding to CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12600000 | NPCC-ON |  | NPCC-US
6 | 79780008028 | Obtain and utilize status, voltages, and flow data for non-BES facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-17 |  | 2021-03-31 |  |  |  | 106000000 | NPCC-ON |  | NPCC-US
6 | 79780008093 | Coordination of controls for (i) vendor-initiated Interactive Remote Access, and (ii) system-to-system remote access with a vendor(s). |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and&lt;br/&gt;4.1.2.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and&lt;br/&gt;4.2.1.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers&lt;br/&gt;4.2.2.1. All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-013-1:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the identification and categorization process required by CIP-002-5, or any subsequent version of that Reliability Standard. |  | 12600000 | NPCC-ON |  | NPCC-US
6 | 79780008124 | Prior to a change that deviates from the existing baseline configuration associated with baseline items in Parts 1.1.1, 1.1.2, and 1.1.5, and when the method to do so is available to the Responsible Entity from the software source: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to a change request record that demonstrates the verification of identity of the software source and integrity of the software was performed prior to the baseline change or a process which documents the mechanisms in place that would automatically ensure the identity of the software source and integrity of the software. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 16000000 | NPCC-ON |  | NPCC-US
6 | 79780008179 | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-3 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 46000000 | NPCC-ON |  | NPCC-US
6 | 79780008402 | Voltage and reactive |  | RC | [11 empty] | RC | [10 empty] | 2019-07-01 | [5 empty] | 11600000 | NPCC-ON |  | NPCC-US
6 | 79780008475 | Past studies may be used to support the Planning Assessment if they meet the following requirements: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-04-13 |  | 2020-06-10 |  |  |  | 26000000 | NPCC-ON |  | NPCC-US
6 | 79780008686 | Recovery plans for BES Cyber Systems (CIP-009); | [28 empty] | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service &lt;br/&gt;&lt;br/&gt;equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11600000 | NPCC-ON |  | NPCC-US
6 | 79780008696 | Declaring and responding to CIP Exceptional Circumstances. | [28 empty] | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service &lt;br/&gt;&lt;br/&gt;equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12600000 | NPCC-ON |  | NPCC-US
6 | 79780008777 | Obtain and utilize status, voltages, and flow data for non-BES facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator. |  | TOP | [18 empty] | TOP |  |  |  | 2021-04-01 | [5 empty] | 106000000 | NPCC-ON |  | NPCC-US
6 | 79780009130 | Coordination of physical and cyber security protection at the nuclear plant interface to ensure each asset is covered under at least one entity’s pla | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 93600000 | NPCC-ON |  | NPCC-US
6 | 79780009184 | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-4 — Attachment 1. |  | PCPA | [9 empty] | PA | [16 empty] | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 46000000 | NPCC-ON |  | NPCC-US
6 | 79780009319 | Past studies may be used to support the Planning Assessment if they meet the following requirements:&lt;br/&gt;2.6.1. For steady state, short circuit, or Stability analysis: the study shall be five calendar years old or less, unless a technical rationale can be provided to demonstrate that the results of an older study are still valid. &lt;br/&gt;2.6.2. For steady state, short circuit, or Stability analysis: no material changes have occurred to the System represented in the study. Documentation to support the technical rationale for determining material changes shall be included. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 26000000 | NPCC-ON |  | NPCC-US
6 | 79780009479 | Prior to a change that deviates from the existing baseline configuration associated with baseline items in Parts 1.1.1, 1.1.2, and 1.1.5, and when the method to do so is available to the Responsible Entity from the software source: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP | [9 empty] | 16000000 | NPCC-ON |  | NPCC-US
6. | 1002 | Current ACE for all its Balancing Authorities. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  | IRO-005-1 R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 1029 | Current ACE for all its Balancing Authorities. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  | IRO-005-2 R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 1056 | Current ACE for all its Balancing Authorities. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  | IRO-005-3a R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 1112 | Authority to act to prevent and mitigate instances of causing Adverse Reliability Impacts to other Reliability Coordinator Areas. |  | RC | [11 empty] | RC | [9 empty] | M1.1.6 Authority to act to prevent and mitigate instances of causing AdverseReliability Impacts to other Reliability Coordinator Areas. | 2007-06-18 |  | 2017-03-31 |  |  |  | 11600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 1145 | Indication of the treatment and level of customer demands, including interruptible demands. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-001-0 R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 1163 | A description of how generation and transmission outages are considered in transfer or Flowgate capability calculations, including: |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-001-1 R3. | 36000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 1173 | Each Transmission Service Provider whose area is adjacent to the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-001-1 R4. | 46000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 1203 | Describe the inclusion or exclusion rationale for generation connected to the Transmission Service Provider’s system but not obligated to serve Native/Network Load connected to the Transmission Service Provider’s system. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-004-0 R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 1267 | Allowances for simultaneous path interactions. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 13600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 1299 | Reactive Compensation (shunt and series capacitors and reactors): nominal Ratings, impedance, percent compensation, connection point, and controller device. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | MOD-011-0 R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 1432 | Uses Transmission Facility additions and retirements. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 11600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 1446 | Where multiple ownership of Transmission rights exists on an ATC Path, allocate TTC of that ATC Path in accordance with the contractual agreement made by the multiple owners of that ATC Path. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-029-1 R2. | 26000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 1484 | Provide the Transmission Service Provider with the TFCs within seven calendar days of their establishment. |  | TOP | [18 empty] | TOP | [5 empty] | 2009-11-24 |  |  | MOD-030-1 R2. | 26000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 1506 | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | MOD-030-1 R6. | 66000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 1514 | The impact of any non-firm Network Integration Transmission Service (secondary service) with a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | MOD-030-1 R7. | 76000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 1549 | Provide the Transmission Service Provider with the TFCs within seven calendar days of their establishment. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R2. | 26000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 1571 | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R6. | 66000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 1579 | The impact of any non-firm Network Integration Transmission Service (secondary service) with a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R7. | 76000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 1610 | Coordination of physical and cyber security protection of the Bulk Electric System at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 93600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 1695 | Data content requirements and guidelines. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | PRC-002-1 R4. | 46000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 1741 | Islanding schemes. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  |  | 12600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 1777 | Date last tested/maintained. |  | DP, TO |  | DP | [20 empty] | 2007-06-18 |  | 2027-03-31 |  |  | PRC-011-0 R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 1785 | Regional Reliability Organization definition of misoperation. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  | PRC-012-0 R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 1822 | Date last tested/maintained. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2007-06-18 |  | 2017-03-31 |  |  | PRC-017-0 R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 1834 | Monitored elements, such as transmission circuit, bus section, etc. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2022-06-30 |  |  | PRC-018-1 R3. | 36000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 1848 | Any other schemes that are part of or impact the UVLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UFLS and Special Protection Systems. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  | PRC-020-1 R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 1879 | Set transmission line relays applied on transmission lines connected to generation stations remote to load so they do not operate at or below 230% of the aggregated generation nameplate capability. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  | PRC-023-1 R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 1974 | Responding to IROL and SOL violations. |  | TOP | [18 empty] | TOP |  |  |  | 2007-06-18 |  | 2009-01-21 |  |  | TOP-004-1 R6. | 66000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2042 | Be performed for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 13600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2063 | Be performed for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 13600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2087 | Be performed and evaluated for selected demand levels over the range of forecast system Demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2112 | Be performed and evaluated for selected demand levels over the range of forecast system Demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 13600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2137 | Be performed and evaluated for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2162 | Be performed and evaluated for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 13600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2184 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  |  | 13600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2205 | Reliability impacts of new or proposed legislation that affects, has affected, or has the potential to affect the Adequacy of the interconnected Bulk Electric Systems in North America. |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | TPL-005-0 R3. | 36000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2212 | System operations and supporting information (extreme weather impacts, Interchange Transactions, and Congestion impacts on the reliability of the interconnected Bulk Electric Systems.) |  | RRO | [14 empty] | RRO | [9 empty] | 2009-04-15 |  |  | TPL-006-0 R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2313 | Due to a component failure, the AVR may be out of service up to 24 months provided the Generator Operator or Transmission Operator submits documentation identifying the need for time for excitation system replacement (replace the AVR, limiters, and controls but not necessarily the power source and power bridge) and to schedule an outage. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-06-27 |  | 2015-03-31 |  |  | VAR-002-WECC-1 R1. | 16000000 | WECC-US | [5 empty] | WECC-US
6. | 2327 | Unit is passing through a range of output that is a known “rough zone” (range in which a hydro unit is experiencing excessive vibration). |  | GOP | [5 empty] | GOP | [16 empty] | 2011-06-27 |  | 2015-03-31 |  |  | VAR-501-WECC-1 R1. | 16000000 | WECC-US | [5 empty] | WECC-US
6. | 2352 | System operations and supporting information (extreme weather impacts, Interchange Transactions, and Congestion impacts on the reliability of the interconnected Bulk Electric Systems.) |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | TPL-006-0.1 R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2362 | Special Protection Systems that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 12600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2416 | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-005-2 R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2427 | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-005-2 R2. | 26000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2447 | Continuous escorted access within the Physical Security Perimeter of personnel not authorized for unescorted access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  | CIP-006-2 R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 25 | The same portion of resource capacity (e.g., reserves from jointly owned generation) shall not be counted more than once as Contingency Reserve by multiple Balancing Authorities. |  | RRO, RSG | [14 empty] | RRO |  | RSG | [5 empty] | 2007-06-18 |  | 2012-03-31 |  |  | BAL-002-0 R2. | 26000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2511 | Process for ensuring the Cyber Security Incident response plan is tested at least annually. A test of the Cyber Security Incident response plan can range from a paper drill, to a full operational exercise, to the response to an actual incident. Testing the Cyber Security Incident response plan does not require removing a component or system from service during the test. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-09-30 |  |  | CIP-008-2 R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 252 | Special Protection Systems that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 12600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2547 | Coordination of physical and cyber security protection of the Bulk Electric System at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 93600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2578 | Identification of acceptable operating voltage and frequency limits during restoration. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | EOP-005-2 R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2623 | Reporting requirements for the entities within the Reliability Coordinator Area during a restoration event. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  | EOP-006-2 R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2697 | In determining the system’s response to any of the multiple Contingencies, identified in Reliability Standard TPL-003, in addition to the actions identified in R2.3.1 and R2.3.2, the following shall be acceptable: |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | FAC-010-2.1 R2. | 26000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2707 | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. |  | PCPA | [9 empty] | PA | [12 empty] | 2010-04-19 |  | 2017-03-31 |  |  | FAC-010-2.1 R3. | 36000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2721 | Special Protection Systems that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | 12600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2775 | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | CIP-005-3 R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2786 | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2011-02-01 |  |  | CIP-005-3 R2. | 26000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2806 | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  | CIP-006-3 R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2872 | Process for ensuring the Cyber Security Incident response plan is tested at least annually. A test of the Cyber Security Incident response plan can range from a paper drill, to a full operational exercise, to the response to an actual incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2016-06-30 |  |  | CIP-008-3 R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2889 | Continuous escorted access within the Physical Security Perimeter of personnel not authorized for unescorted access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  | CIP-006-2b R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2910 | Continuous escorted access within the Physical Security Perimeter of personnel not authorized for unescorted access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | CIP-006-2c R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2933 | Procedures for escorted access within the physical security perimeter of personnel not authorized for unescorted access. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1b R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2963 | Procedures for escorted access within the physical security perimeter of personnel not authorized for unescorted access. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | CIP-006-1c R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 2988 | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  | CIP-006-3c R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 3016 | A description of how generation and transmission outages are considered in transfer or Flowgate capability calculations, including: |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  |  |  |  | MOD-001-1a R3. | 36000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 3026 | Each Transmission Service Provider whose area is adjacent to the Transmission Service Provider’s area. |  | TSP | [20 empty] | TSP |  | 2010-09-16 |  |  |  |  | MOD-001-1a R4. | 46000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 3047 | Uses Transmission Facility additions and retirements. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 11600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 305 | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-005-1 R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 3067 | Where multiple ownership of Transmission rights exists on an ATC Path, allocate TTC of that ATC Path in accordance with the contractual agreement made by the multiple owners of that ATC Path. |  | TOP | [18 empty] | TOP |  |  |  | 2010-09-16 |  | 2017-03-31 |  |  | MOD-029-1a R2. | 26000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 3159 | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. | CIP-005-3a R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 316 | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-005-1 R2. | 26000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 3166 | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. (Retirement approved by FERC effective January 21, 2014.) |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2016-06-30 |  | The following are exempt from Standard CIP-005-3:4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the CanadianNuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communicationlinks between discrete Electronic Security Perimeters.4.2.3 Responsible Entities that, in compliance with Standard CIP-002-3, identify thatthey have no Critical Cyber Assets. | CIP-005-3a R2. | 26000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 3191 | The same portion of resource capacity (e.g. reserves from jointly owned generation) shall not be counted more than once as Contingency Reserve by multiple Balancing Authorities. |  | RRO, RSG | [14 empty] | RRO |  | RSG | [5 empty] | 2011-01-10 |  | 2017-12-31 |  |  | BAL-002-1 R2. | 26000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 3264 | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-005-4a R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 3275 | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-005-4a R2. | 26000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 3295 | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-006-4c R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 336 | Procedures for escorted access within the physical security perimeter of personnel not authorized for unescorted access. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-006-1 R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 3361 | Process for ensuring the Cyber Security Incident response plan is tested at least annually. A test of the Cyber Security Incident response plan can range from a paper drill, to a full operational exercise, to the response to an actual incident. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-008-4 R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 3381 | Reducing load, through procedures such as public appeals, voltage reductions, curtailing interruptible loads and firm loads. |  | BA | BA | [21 empty] | 2011-01-10 |  | 2012-09-12 |  |  | EOP-002-3 R6. | 66000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 3427 | Current ACE for all its Balancing Authorities. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  | IRO-005-2a R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 3461 | Be performed for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 3485 | Be performed and evaluated for selected demand levels over the range of forecast system Demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 13600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 3510 | Be performed and evaluated for selected demand levels over the range of forecast system Demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 3535 | Be performed and evaluated for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 3557 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 3623 | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | CIP-005-1a R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 363 | Procedures for escorted access within the physical security perimeter of personnel not authorized for unescorted access. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1a R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 3630 | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2011-02-01 |  |  | CIP-005-1a R2. | 26000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 3654 | The Responsible Entity shall maintain documentation of Electronic Security Perimeter(s), all interconnected Critical and non-critical Cyber Assets within the Electronic Security Perimeter(s), all electronic access points to the Electronic Security Perimeter(s) and the Cyber Assets deployed for the access control and monitoring of these access points. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | CIP-005-2a R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 3661 | Appropriate Use Banner — Where technically feasible, electronic access control devices shall display an appropriate use banner on the user screen upon all interactive access attempts. The Responsible Entity shall maintain a document identifying the content of the banner. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-02-02 |  | 2011-02-01 |  |  | CIP-005-2a R2. | 26000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 3805 | Current ACE for all its Balancing Authorities. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  | IRO-005-3 R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 3898 | Continuous escorted access within the Physical Security Perimeter of personnel not authorized for unescorted access. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | CIP-006-2a R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 3922 | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  | CIP-006-3a R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 4039 | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-006-3d R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 4061 | A visitor control program for visitors (personnel without authorized unescorted access to a Physical Security Perimeter), containing at a minimum the following: |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-006-4d R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 4181 | Current ACE for all its Balancing Authorities. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  | IRO-005-3.1a R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 4200 | Reducing load, through procedures such as public appeals, voltage reductions, curtailing interruptible loads and firm loads. |  | BA | BA | [21 empty] | 2012-09-13 |  | 2017-03-31 |  |  | EOP-002-3.1 R6. | 66000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 4237 | Coordination of physical and cyber security protection of the Bulk Electric System at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 93600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 433 | Process for ensuring the Cyber Security Incident response plan is tested at least annually. A test of the incident response plan can range from a paper drill, to a full operational exercise, to the response to an actual incident. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-008-1 R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 4340 | Special Protection Systems that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 12600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 4446 | The same portion of resource capacity (e.g. reserves from jointly owned generation) shall not be counted more than once as Contingency Reserve by multiple Balancing Authorities. |  | RRO, RSG | [14 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  | BAL-002-1a R2. | 26000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 4563 | Special Protection Systems that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 12600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 4587 | Be performed for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 4633 | Be performed and evaluated for selected demand levels over the range of forecast system Demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 4658 | Be performed and evaluated for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 4681 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 4698 | Be performed and evaluated for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 4733 | Be performed and evaluated for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 4746 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 4765 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 4843 | Reducing load, through procedures such as public appeals, voltage reductions,curtailing interruptible loads and firm loads. |  | BA | BA | [23 empty] | 2006-11-01 |  |  |  | 76000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 4860 | Reducing load, through procedures such as public appeals, voltage reductions,curtailing interruptible loads and firm loads. |  | BA | BA | [23 empty] | 2007-01-01 |  |  |  | 66000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 4914 | High voltage direct current converters. |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-08-01 |  |  |  | 11600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 4952 | Loss accounting. |  | TSP | [20 empty] | TSP |  |  |  | 2007-01-01 |  |  |  | 26000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 5032 | Current ACE for all its Balancing Authorities. |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 5121 | Installation requirements: |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 513 | Reducing load, through procedures such as public appeals, voltage reductions, curtailing interruptible loads and firm loads. |  | BA | BA | [21 empty] | 2007-06-18 |  | 2009-05-12 |  |  | EOP-002-2 R6. | 66000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 5147 | Date last tested/maintained. |  | DP, GO, TO |  | DP |  |  | GO | [19 empty] | 2006-05-01 |  |  |  | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 52 | Load, other than Interruptible Load, once the Reliability Coordinator has declared a capacity or energy emergency. |  | BA, RSG | BA | [15 empty] | RSG | [7 empty] | 2010-11-26 |  |  | BAL-002-WECC-1 R3. | 36000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 5211 | Responding to IROL and SOL violations. |  | TOP | [18 empty] | TOP | [5 empty] | 2005-04-01 |  |  |  | 66000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 534 | Reducing load, through procedures such as public appeals, voltage reductions, curtailing interruptible loads and firm loads. |  | BA | BA | [21 empty] | 2009-05-13 |  | 2011-09-30 |  |  | EOP-002-2.1 R6. | 66000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 5614 | In determining the system’s response to any of the multiple Contingencies, identified in Reliability Standard TPL-003, in addition to the actions identified in R2.3.1 and R2.3.2, the following shall be acceptable: |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 26000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 5623 | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 36000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 5652 | Anticipated transmission system configuration, generation dispatch and Load level |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 36000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 5666 | Current ACE for all its Balancing Authorities. |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  |  | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 5709 | Provide the Transmission Service Provider with the TFCs within seven calendar days of their establishment. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 26000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 5731 | The impact of any Grandfathered firm obligations expected to be scheduled or expected to flow that have a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. (Footnote: A percentage less than that used in the Interconnection-wide congestion management procedure may be utilized.) |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 66000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 5739 | The impact of any non-firm Network Integration Transmission Service (secondary service) with a distribution factor equal to or greater than the percentage used to curtail in the Interconnection-wide congestion management procedure used by the Transmission Service Provider, filtered to reduce or eliminate duplicate impacts from transactions using Transmission service from multiple Transmission Service Providers, for all adjacent Transmission Service Providers and any other Transmission Service Providers with which coordination agreements have been executed. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 76000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 5758 | Remedial Action Schemes that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 5770 | Remedial Action Schemes that support the reliable operation of the Bulk Electric System. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 5803 | Coordination of physical and cyber security protection of the Bulk Electric System at the nuclear plant interface to ensure each asset is covered under at least one entity’s plan. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 93600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 5820 | Be performed for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 5841 | Be performed and evaluated for selected demand levels over the range of forecast system Demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 5866 | Be performed and evaluated for selected demand levels over the range of forecast system demands. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 5891 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 5904 | Regional Reliability Organization definition of misoperation. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 5944 | Date last tested/maintained. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2016-01-25 |  | 2027-03-31 |  |  |  | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 5952 | Any other schemes that are part of or impact the UVLS programs such as related generation protection, islanding schemes, automatic load restoration schemes, UFLS and Remedial Action Schemes. | [26 empty] | 2014-11-13 |  |  |  | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 603 | The plan shall include procedures and responsibilities for providing annual training to ensure that operating personnel are able to implement the contingency plans. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | EOP-008-0 R1. | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 6036 | Uses Transmission Facility additions and retirements. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 11600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 6165 | Recovery plans for BES Cyber Systems (CIP-009); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 6205 | Where technically feasible, for password-only authentication for interactive user access, either technically or procedurally enforce password changes or an obligation to change the password at least once every 15 calendar months. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 56000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 6253 | Monitor each Physical Access Control System for unauthorized physical access to a Physical Access Control System. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 1.6 An example of evidence may include, but is not limited to, documentation of controls that monitor for unauthorized physical access to a PACS. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 626 | Metering and telecommunications. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 21600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 6429 | Model structure and data for power system stabilizer, if so equipped. |  | GO | [22 empty] | 2018-07-01 |  |  |  | 4.2. Facilities:For the purpose of the requirements contained herein, Facilities that are directly connected to the Bulk Electric System (BES) will be collectively referred as an “applicable unit” that meet the following:4.2.1 Generation in the Eastern or Quebec Interconnections with the following characteristics: 4.2.1.1 Individual generating unit greater than 100 MVA (gross nameplate rating).4.2.1.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 100 MVA (gross aggregate nameplate rating).4.2.2 Generation in the Western Interconnection with the following characteristics:4.2.2.1 Individual generating unit greater than 75 MVA (gross nameplate rating).4.2.2.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.3 Generation in the ERCOT Interconnection with the following characteristics:4.2.3.1 Individual generating unit greater than 50 MVA (gross nameplate rating).4.2.3.2 Individual generating plant consisting of multiple generating units that are directly connected at a common BES bus with total generation greater than 75 MVA (gross aggregate nameplate rating).4.2.4 For all Interconnections:• A technically justified unit that meets NERC registry criteria but is not otherwise included in the above Applicability sections 4.2.1, 4.2.2, or 4.2.3 and is requested by the Transmission Planner. |  | 21600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 6448 | Voltage and reactive |  | RC | [11 empty] | RC | [10 empty] | 2012-10-01 |  | 2019-06-30 |  |  |  | 11600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 6498 | An Operating Process describing the actions to be taken during the transition period between the loss of primary control center functionality and the time to fully implement backup functionality elements identified in Requirement R1, Part 1.2. The Operating Process shall include at a minimum: |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2011-06-27 |  | 2019-03-31 |  |  |  | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 6560 | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 46000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 6596 | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-1 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 460000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 6608 | Time delay (from frequency reaching the set point to the trip signal) shall be at least six cycles. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2013-02-25 |  | 2017-12-31 |  |  |  | 26000000 | SERC-US |  |  |  | SERC-US
6. | 6628 | Resources (supply or demand side) required for Load |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2015-01-01 | [5 empty] | 11600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 6652 | Past studies may be used to support the Planning Assessment if they meet the following requirements: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 26000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 6696 | Contingencies |  | PCPA | [9 empty] | PA | [12 empty] | 2013-04-01 |  | 2020-12-14 |  |  |  | 14600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 6723 | Each adjacent Transmission Operator asynchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2015-06-22 |  | 2015-11-12 |  |  |  | 36000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 6857 | Reliability impacts of extreme weather conditions. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 12600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 6869 | Reduction of internal utility energy use; |  | BA | BA | [21 empty] | 2017-04-01 | [5 empty] | 22600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 6909 | Coordination of physical and cyber security protection at the nuclear plant interface to ensure each asset is covered under at least one entity’s pla |  | BA, DP, GO, GOP, LSE, PCPA, RSG, TO, TOP, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA | [6 empty] | RSG | TO | TOP | TP | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 93600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 6943 | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 46000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 7059 | Authority to act to prevent and mitigate system conditions which could cause Adverse Reliability Impacts to other Reliability Coordinator Areas. |  | RC | [11 empty] | RC | [12 empty] | 2016-01-26 |  |  |  | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 7076 | Load forecast; and |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 12600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 7088 | Load forecast; and |  | TSP | [20 empty] | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 21600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 7214 | Identification of a Cyber Security Incident and initial notifications in accordance with the entity’s incident response plan; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 723 | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. |  | PCPA | [9 empty] | PA | [12 empty] | 2008-05-29 |  | 2009-04-28 |  |  | FAC-010-1 R3. | 36000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 7315 | Where technically feasible, for password-only authentication for interactive user access, either technically or procedurally enforce password changes or an obligation to change the password at least once every 15 calendar months. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.6. Examples of evidence may include, but are not limited to:• System-generated reports or screen-shots of the system-enforced periodicity of changing passwords; or• Attestations that include a reference to the documented procedures that were followed. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 56000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 7344 | Monitor each Physical Access Control System for unauthorized physical access to a Physical Access Control System. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.6. An example of evidence may include, but is not limited to, documentation of controls that monitor for unauthorized physical access to a PACS. | 2016-07-01 | [5 empty] | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 7406 | Elements associated with Interconnection Reliability Operating Limits (IROLs). |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 72600000 | NPCC-US |  | NPCC-US
6. | 7425 | Verification of DDR and DFR settings in the software every six (6) years. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 146000000 | NPCC-US |  | NPCC-US
6. | 7437 | Monitored Elements. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 176000000 | NPCC-US |  | NPCC-US
6. | 744 | In determining the system’s response to any of the multiple Contingencies, identified in Reliability Standard TPL-003, in addition to the actions identified in R2.3.1 and R2.3.2, the following shall be acceptable: |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | FAC-010-2 R2. | 26000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 7477 | Each adjacent Transmission Operator asynchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2015-11-13 |  | 2017-09-30 |  |  |  | 36000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 7483 | Recovery plans for BES Cyber Systems (CIP-009); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 752 | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. |  | PCPA | [9 empty] | PA | [12 empty] | 2009-04-29 |  | 2010-04-18 |  |  | FAC-010-2 R3. | 36000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 7653 | Weather conditions/Accessibility |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:4.1.1. Applicable Transmission Owners4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.4.1.2. Applicable Generator Owners4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.2.1. Each overhead transmission line operated at 200kV or higher.4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:4.3.1.1. Operated at 200kV or higher; or4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 75000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 7654 | Weather conditions/Accessibility |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:4.1.1. Applicable Transmission Owners4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.4.1.2. Applicable Generator Owners4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.2.1. Each overhead transmission line operated at 200kV or higher.4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:4.3.1.1. Operated at 200kV or higher; or4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 76000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 7672 | Where multiple ownership of Transmission rights exists on an ATC Path, allocate TTC of that ATC Path in accordance with the contractual agreement made by the multiple owners of that ATC Path. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 26000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 7699 | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-2 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 460000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 7719 | Due to a component failure, the AVR may be out of service up to 24 months provided the Generator Operator or Transmission Operator submits documentation identifying the need for time for excitation system replacement (replace the AVR, limiters, and controls but not necessarily the power source and power bridge) and to schedule an outage. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2015-03-03 |  | 2018-09-05 |  |  |  | 16000000 | WECC-US | [5 empty] | WECC-US
6. | 7781 | Specify the nomenclature for Transmission interface Elements and Transmission interface Facilities when issuing an oral or written Operating Instruction. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2015-06-22 | [5 empty] | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 7797 | Each adjacent Transmission Operator asynchronously connected. |  | TOP | [18 empty] | TOP |  |  |  | 2016-10-28 | [5 empty] | 36000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 780 | Anticipated transmission system configuration, generation dispatch and Load level. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-011-1 R3. | 36000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 7833 | Unit is passing through a range of output that is a known “rough zone” (range in which a hydro unit is experiencing excessive vibration). |  | GOP | [5 empty] | GOP | [16 empty] | 2015-04-01 |  | 2017-06-30 |  |  |  | 16000000 | WECC-US | [5 empty] | WECC-US
6. | 7897 | An Operating Process describing the actions to be taken during the transition period between the loss of primary control center functionality and the time to fully implement backup functionality elements identified in Requirement R1, Part 1.2. The Operating Process shall include: |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 7917 | Criteria for transferring operations and authority back to the Balancing Authority. |  | RC | [11 empty] | RC | [10 empty] | 2019-04-01 | [5 empty] | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 7918 | Criteria for transferring operations and authority back to the Balancing Authority. |  | RC | [11 empty] | RC | [10 empty] | 2018-03-26 | [5 empty] | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 7937 | Identification of acceptable operating voltage and frequency limits during restoration. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 7994 | Recovery plans for BES Cyber Systems (CIP-009); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 8003 | Declaring and responding to CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 8028 | Obtain and utilize status, voltages, and flow data for non-BES facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-17 |  | 2021-03-31 |  |  |  | 106000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 809 | Anticipated transmission system configuration, generation dispatch and Load level |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | FAC-011-2 R3. | 36000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 8093 | Coordination of controls for (i) vendor-initiated Interactive Remote Access, and (ii) system-to-system remote access with a vendor(s). |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and4.1.2.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. Is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and4.2.1.1.2. Performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers4.2.2.1. All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-013-1:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the identification and categorization process required by CIP-002-5, or any subsequent version of that Reliability Standard. |  | 12600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 8124 | Prior to a change that deviates from the existing baseline configuration associated with baseline items in Parts 1.1.1, 1.1.2, and 1.1.5, and when the method to do so is available to the Responsible Entity from the software source: |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | An example of evidence may include, but is not limited to a change request record that demonstrates the verification of identity of the software source and integrity of the software was performed prior to the baseline change or a process which documents the mechanisms in place that would automatically ensure the identity of the software source and integrity of the software. | 2018-12-26 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 8146 | Time delay (from frequency reaching the set point to the trip signal) shall be at least six cycles. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2017-10-16 | [5 empty] | 26000000 | SERC-US |  |  |  | SERC-US
6. | 8179 | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-3 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 46000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 8214 | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-3 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 460000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 8236 | Contractual arrangements concerning curtailable/Interruptible Demand. |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 13160000 | RF-US |  |  | RF-US
6. | 8243 | Criteria for including planned resource additions in the analysis |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 13260000 | RF-US |  |  | RF-US
6. | 8253 | Impacts of extreme weather/drought conditions that affect unit availability. |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 14600000 | RF-US |  |  | RF-US
6. | 8257 | Document that capacity resources are appropriately accounted for in its Resource Adequacy analysis |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-16 | [5 empty] | 16000000 | RF-US |  |  | RF-US
6. | 8402 | Voltage and reactive |  | RC | [11 empty] | RC | [10 empty] | 2019-07-01 | [5 empty] | 11600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 8475 | Past studies may be used to support the Planning Assessment if they meet the following requirements: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-04-13 |  | 2020-06-10 |  |  |  | 26000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 8663 | A method for the validation and periodic review of the Reliability Coordinator’s operational model for steady state and dynamic/oscillatory system response. | [24 empty] | 2020-01-01 |  | 2021-03-31 |  | ApplicabilityAs used in this WECC Regional Variance, Reliability Coordinator is specific to those Reliability Coordinators providing Reliability Coordinator service(s) to entities operating within the Western Interconnection, regardless of where the Reliability Coordinator may be located. |  | 760000 | WECC-US | [5 empty] | WECC-US
6. | 8677 | A method for the validation and periodic review of the Reliability Coordinator’s operational model for steady state and dynamic/oscillatory system response. |  | RC | [11 empty] | RC | [10 empty] | 2021-04-01 | [5 empty] | 760000 | WECC-US | [5 empty] | WECC-US
6. | 8686 | Recovery plans for BES Cyber Systems (CIP-009); |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 8696 | Declaring and responding to CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 12600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 8777 | Obtain and utilize status, voltages, and flow data for non-BES facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator. |  | TOP | [18 empty] | TOP |  |  |  | 2021-04-01 | [5 empty] | 106000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 9130 | Coordination of physical and cyber security protection at the nuclear plant interface to ensure each asset is covered under at least one entity’s pla | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 93600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 9163 | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-4 — Attachment 1. |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 460000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 9184 | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-4 — Attachment 1. |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 46000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 9319 | Past studies may be used to support the Planning Assessment if they meet the following requirements:2.6.1. For steady state, short circuit, or Stability analysis: the study shall be five calendar years old or less, unless a technical rationale can be provided to demonstrate that the results of an older study are still valid. 2.6.2. For steady state, short circuit, or Stability analysis: no material changes have occurred to the System represented in the study. Documentation to support the technical rationale for determining material changes shall be included. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 26000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | 9373 | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-5 — Attachment 1. |  | PCPA | [9 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 460000 | WECC-US | [5 empty] | WECC-US
6. | 9479 | Prior to a change that deviates from the existing baseline configuration associated with baseline items in Parts 1.1.1, 1.1.2, and 1.1.5, and when the method to do so is available to the Responsible Entity from the software source: |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 16000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | RP-2021-06-08-0000013 | Total amount of load shed by each trip frequency and the total forecasted peak Load |  | DP, TO |  | DP | [22 empty] | 2013-11-07 |  |  |  | 50600000 | SPPRE-US
6. | RP-2021-06-16-0000042 | Document that capacity resources are appropriately accounted for in its Resource Adequacy analysis |  | PCPA | [9 empty] | PA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  |  | 10600000 | RF-US |  |  | RF-US
6. | RP-2021-06-22-0000028 | Where multiple ownership of Transmission rights exists on an ATC Path,allocate TTC of that ATC Path in accordance with the contractual agreementmade by the multiple owners of that ATC Path. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 20600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | RP-2021-06-23-0000015 | HVDC terminals. |  | TO | [22 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 20600000 | NPCC-US |  | NPCC-US
6. | RP-2021-06-23-0000019 | Verification of DDR and DFR settings in the software every six (6) years. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 140600000 | NPCC-US |  | NPCC-US
6. | RP-2021-06-24-0000018 | Time delay (from frequency reaching the set point to the trip signal) shall be atleast six cycles. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2014-04-01 |  | 2017-12-31 |  |  |  | 20600000 | SERC-US |  |  |  | SERC-US
6. | RP-2021-06-25-0000007 | Unit is passing through a range of output that is a known “rough zone” (range in which a hydro unit is experiencing excessive vibration). |  | GOP | [5 empty] | GOP | [16 empty] | 2011-07-01 |  | 2015-03-31 |  |  |  | 10600000 | WECC-US | [5 empty] | WECC-US
6. | RP-2021-06-25-0000012 | Unit is passing through a range of output that is a known “rough zone” (range in which a hydro unit is experiencing excessive vibration). |  | GOP | [5 empty] | GOP | [16 empty] | 2015-04-01 |  | 2017-06-30 |  |  |  | 10600000 | WECC-US | [5 empty] | WECC-US
6. | RP-2021-06-30-0000012 | Where technically feasible, for password-only authentication for interactive user access, either technically or procedurally enforce password changes or an obligation to change the password at least once every 15 calendar months. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 50600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | RP-2021-07-07-0000017 | Where multiple ownership of Transmission rights exists on an ATC Path, allocate TTC of that ATC Path in accordance with the contractual agreement made by the multiple owners of that ATC Path. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 20600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | RP-2021-07-09-0000012 | Overfrequency trip settings of any facility consisting of one or more units connected to the BES at a common bus with total generation above 75 MVA (gross nameplate rating) that trip below the Generator Overfrequency Trip Modeling curve in PRC-006-5 — Attachment 1. |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2021-04-01 |  |  |  | UFLS entities shall mean all entities that are responsible for the ownership,operation, or control of UFLS equipment as required by the UFLS programestablished by the Planning Coordinators. Such entities may include one ormore of the following: 4.2.1 Transmission Owners4.2.2 Distribution Providers4.2.3 UFLS-Only Distribution Providers4.3. Transmission Owners that own Elements identified in the UFLS programestablished by the Planning Coordinators. |  | 40600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | RP-2021-07-09-0000032 | Time delay (from frequency reaching the set point to the trip signal) shall be at leastsix cycles. |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 20600000 | SERC-US |  |  |  | SERC-US
6. | RP-2021-07-13-0000006 | Obtain and utilize status, voltages, and flow data for non-BES facilities outside its Transmission Operator Area identified as necessary by the Transmission Operator. |  | BA, DP, GOP, TOP | BA | DP |  |  |  | GOP | [12 empty] | TOP | [9 empty] | 100600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | RP-2021-07-13-0000021 | Describe the allowed uses of Remedial Action Schemes and other automatic post-Contingency mitigation actions in establishing stability limits used in operations. |  | RC | [11 empty] | RC | [16 empty] | 40600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | RP-2021-07-13-0000067 | Each impacted Generator Owner or Transmission Owner, within its Reliability Coordinator Area, with a list of their Facilities that have been identified as critical to the derivation of an IROL and its associated critical contingencies at least once every twelve calendar months. |  | RC, TOP, TP | [11 empty] | RC | [6 empty] | TOP | TP | [8 empty] | 50600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | RP-2021-07-13-0000084 | Weather conditions/Accessibility |  | GO, TO |  |  |  |  | GO | [23 empty] | 70600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | RP-2021-08-09-0000001 | The same portion of resource capacity (e.g. reserves from jointly owned generation) shall not be counted more than once as Contingency Reserve by multiple Balancing Authorities. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [5 empty] | 2012-04-01 |  | 2017-12-31 |  |  |  | 20600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6. | RP-2021-08-09-0000002 | The same portion of resource capacity (e.g. reserves from jointly owned generation) shall not be counted more than once as Contingency Reserve by multiple Balancing Authorities. |  | BA, RRO, RSG | BA | [13 empty] | RRO |  | RSG | [7 empty] | 2017-02-17 |  |  |  | 20600000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6.1. | RP-2021-06-24-0000035 | For steady state, short circuit, or Stability analysis: the study shall befive calendar years old or less, unless a technical rationale can beprovided to demonstrate that the results of an older study are stillvalid. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-07-01 |  | 2020-06-10 |  |  |  | 26100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6.1. | RP-2021-06-30-0000018 | Verify the identity of the software source; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 16100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6.1. | RP-2021-06-30-0000031 | Verify the identity of the software source; and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 16100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6.1. | RP-2021-07-01-0000016 | Planned or controlled interruption of electric supply to customers (load shedding), the planned removal from service of certain generators, and/or the curtailment of contracted Firm (non-recallable reserved) electric power Transfers. |  | PCPA | [9 empty] | PA | [12 empty] | 2016-01-25 | [5 empty] | 26100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6.1. | RP-2021-07-12-0000017 | For steady state, short circuit, or Stability analysis: the study shall be five calendar years old or less, unless a technical rationale can be provided to demonstrate that the results of an older study are still valid. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 26100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6.2. | RP-2021-06-24-0000036 | For steady state, short circuit, or Stability analysis: no materialchanges have occurred to the System represented in the study.Documentation to support the technical rationale for determiningmaterial changes shall be included. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2023-07-01 |  | 2020-06-10 |  |  |  | 26200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6.2. | RP-2021-06-30-0000019 | Verify the integrity of the software obtained from the software source. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-07-01 |  | 2022-09-30 |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-010-3:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters.4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 16200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6.2. | RP-2021-06-30-0000032 | Verify the integrity of the software obtained from the software source. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2022-10-01 | [5 empty] | 16200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
6.2. | RP-2021-07-12-0000018 | For steady state, short circuit, or Stability analysis: no material changes have occurred to the System represented in the study. Documentation to support the technical rationale for determining material changes shall be included. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 26200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7 | 79780000253 | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 12700000 | NPCC-ON |  | NPCC-US
7 | 79780000337 | Process for updating the physical security plan within ninety calendar days of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the physical security perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780000364 | Process for updating the physical security plan within ninety calendar days of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the physical security perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780000604 | The plan shall be reviewed and updated annually. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780000627 | Grounding and safety issues. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 21700000 | NPCC-ON |  | NPCC-US
7 | 79780000781 | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  |  | 37000000 | NPCC-ON |  | NPCC-US
7 | 79780000810 | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  |  | 37000000 | NPCC-ON |  | NPCC-US
7 | 79780001003 | Current local or Transmission Loading Relief procedures in effect. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780001030 | Current local or Transmission Loading Relief procedures in effect. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780001057 | Current local or Transmission Loading Relief procedures in effect. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780001146 | A specification of how system conditions, limiting facilities, contingencies, transmission reservations, energy schedules, and other data needed by Transmission Service Providers for the calculation of TTC and ATC values are shared and used within the Regional Reliability Organization and with neighboring interconnected electric systems, including adjacent systems, subregions, and Regional Reliability Organizations. In addition, specify how this information is to be used to determine TTC and ATC values. If some data is not used, provide an explanation. |  | RRO, TSP | [14 empty] | RRO | [5 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780001204 | Describe the formal process and rationale for the Regional Reliability Organization to grant any variances to individual Transmission Service Providers from the Regional Reliability Organization’s CBM methodology. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780001268 | Variations in generation dispatch. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 13700000 | NPCC-ON |  | NPCC-US
7 | 79780001300 | Interchange Schedules: Existing and future Interchange Schedules and/or assumptions. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780001433 | Uses Generation Facility additions and retirements. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 11700000 | NPCC-ON |  | NPCC-US
7 | 79780001447 | For ATC Paths whose path rating, adjusted for seasonal variance, was established, known and used in operation since January 1, 1994, and no action has been taken to have the path rated using a different method, set the TTC at that previously established amount. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 27000000 | NPCC-ON |  | NPCC-US
7 | 79780001507 | The impact of other firm services determined by the Transmission Service Provider. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 67000000 | NPCC-ON |  | NPCC-US
7 | 79780001515 | The impact of other non-firm services determined by the Transmission Service Provider. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  |  | 77000000 | NPCC-ON |  | NPCC-US
7 | 79780001572 | The impact of other firm services determined by the Transmission Service Provider. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 67000000 | NPCC-ON |  | NPCC-US
7 | 79780001580 | The impact of other non-firm services determined by the Transmission Service Provider. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  |  | 77000000 | NPCC-ON |  | NPCC-US
7 | 79780001611 | Coordination of the NPIRs with transmission system Special Protection Systems and underfrequency and undervoltage load shedding programs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 93700000 | NPCC-ON |  | NPCC-US
7 | 79780001742 | Automatic load restoration schemes. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  |  | 12700000 | NPCC-ON |  | NPCC-US
7 | 79780001786 | Requirements for analysis and documentation of corrective action plans for all SPS misoperations. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780001835 | Monitored devices, such as circuit breaker, disconnect status, alarms, etc. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2022-06-30 |  |  |  | 37000000 | NPCC-ON |  | NPCC-US
7 | 79780001880 | Set transmission line relays applied at the load center terminal, remote from generation stations, so they do not operate at or below 115% of the maximum current flow from the load to the generation source under any system configuration. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780002043 | Demonstrate that system performance meets Table 1 for Category A (no contingencies). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 13700000 | NPCC-ON |  | NPCC-US
7 | 79780002064 | Demonstrate that system performance meets Table 1 for Category A (no contingencies). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 13700000 | NPCC-ON |  | NPCC-US
7 | 79780002088 | Demonstrate that system performance meets Category B contingencies. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13700000 | NPCC-ON |  | NPCC-US
7 | 79780002113 | Demonstrate that system performance meets Category B contingencies. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 13700000 | NPCC-ON |  | NPCC-US
7 | 79780002138 | Demonstrate that System performance meets Table 1 for Category C contingencies. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13700000 | NPCC-ON |  | NPCC-US
7 | 79780002163 | Demonstrate that System performance meets Table 1 for Category C contingencies. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 13700000 | NPCC-ON |  | NPCC-US
7 | 79780002185 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  |  | 13700000 | NPCC-ON |  | NPCC-US
7 | 79780002213 | Environmental and regulatory issues and impacts (air and water quality issues, and impacts of existing, new, and proposed regulations and legislation.) |  | RRO | [14 empty] | RRO | [9 empty] | 2009-04-15 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780002353 | Environmental and regulatory issues and impacts (air and water quality issues, and impacts of existing, new, and proposed regulations and legislation.) |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780002363 | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 12700000 | NPCC-ON |  | NPCC-US
7 | 79780002448 | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780002548 | Coordination of the NPIRs with transmission system Special Protection Systems and underfrequency and undervoltage load shedding programs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 93700000 | NPCC-ON |  | NPCC-US
7 | 79780002579 | Operating Processes to reestablish connections within the Transmission Operator’s System for areas that have been restored and are prepared for reconnection. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780002624 | Criteria for sharing information regarding restoration with neighboring Reliability Coordinators and with Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780002722 | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | 12700000 | NPCC-ON |  | NPCC-US
7 | 79780002809 | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780002896 | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780002917 | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780002937 | Process for updating the physical security plan within ninety calendar days of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the physical security perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780002962 | Process for updating the physical security plan within ninety calendar days of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the physical security perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780002986 | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780003050 | Uses Generation Facility additions and retirements. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 11700000 | NPCC-ON |  | NPCC-US
7 | 79780003065 | For ATC Paths whose path rating, adjusted for seasonal variance, was established, known and used in operation since January 1, 1994, and no action has been taken to have the path rated using a different method, set the TTC at that previously established amount. |  | TOP | [18 empty] | TOP |  |  |  | 2010-09-16 |  | 2017-03-31 |  |  |  | 27000000 | NPCC-ON |  | NPCC-US
7 | 79780003298 | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780003428 | Current local or Transmission Loading Relief procedures in effect. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780003462 | Demonstrate that system performance meets Table 1 for Category A (no contingencies). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13700000 | NPCC-ON |  | NPCC-US
7 | 79780003486 | Demonstrate that system performance meets Category B contingencies. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 13700000 | NPCC-ON |  | NPCC-US
7 | 79780003511 | Demonstrate that system performance meets Category B contingencies. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13700000 | NPCC-ON |  | NPCC-US
7 | 79780003536 | Demonstrate that System performance meets Table 1 for Category C contingencies. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13700000 | NPCC-ON |  | NPCC-US
7 | 79780003558 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13700000 | NPCC-ON |  | NPCC-US
7 | 79780003804 | Current local or Transmission Loading Relief procedures in effect. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780003905 | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780003920 | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780004041 | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780004059 | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780004180 | Current local or Transmission Loading Relief procedures in effect. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780004238 | Coordination of the NPIRs with transmission system Special Protection Systems and underfrequency and undervoltage load shedding programs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 93700000 | NPCC-ON |  | NPCC-US
7 | 79780004339 | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 12700000 | NPCC-ON |  | NPCC-US
7 | 79780004562 | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 12700000 | NPCC-ON |  | NPCC-US
7 | 79780004593 | Demonstrate that system performance meets Table 1 for Category A (no contingencies). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13700000 | NPCC-ON |  | NPCC-US
7 | 79780004630 | Demonstrate that system performance meets Category B contingencies. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13700000 | NPCC-ON |  | NPCC-US
7 | 79780004655 | Demonstrate that System performance meets Table 1 for Category C contingencies. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13700000 | NPCC-ON |  | NPCC-US
7 | 79780004684 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13700000 | NPCC-ON |  | NPCC-US
7 | 79780004695 | Demonstrate that System performance meets Table 1 for Category C contingencies. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13700000 | NPCC-ON |  | NPCC-US
7 | 79780004731 | Demonstrate that System performance meets Table 1 for Category C contingencies. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13700000 | NPCC-ON |  | NPCC-US
7 | 79780004749 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13700000 | NPCC-ON |  | NPCC-US
7 | 79780004758 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13700000 | NPCC-ON |  | NPCC-US
7 | 79780004915 |  |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-08-01 |  |  |  | 11700000 | NPCC-ON |  | NPCC-US
7 | 79780005033 |  |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780005125 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780005653 | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 37000000 | NPCC-ON |  | NPCC-US
7 | 79780005667 | Current local or Transmission Loading Relief procedures in effect. |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780005732 | The impact of other firm services determined by the Transmission Service Provider. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 67000000 | NPCC-ON |  | NPCC-US
7 | 79780005740 | The impact of other non-firm services determined by the Transmission Service Provider. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 77000000 | NPCC-ON |  | NPCC-US
7 | 79780005759 | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12700000 | NPCC-ON |  | NPCC-US
7 | 79780005771 | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. |  | BA, GO, GOP, IA, LSE, RC, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | [5 empty] | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12700000 | NPCC-ON |  | NPCC-US
7 | 79780005804 | Coordination of the NPIRs with transmission system Remedial Action Schemes and underfrequency and undervoltage load shedding programs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 93700000 | NPCC-ON |  | NPCC-US
7 | 79780005821 | Demonstrate that system performance meets Table 1 for Category A (no contingencies). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13700000 | NPCC-ON |  | NPCC-US
7 | 79780005842 | Demonstrate that system performance meets Category B contingencies. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13700000 | NPCC-ON |  | NPCC-US
7 | 79780005867 | Demonstrate that System performance meets Table 1 for Category C contingencies. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13700000 | NPCC-ON |  | NPCC-US
7 | 79780005892 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13700000 | NPCC-ON |  | NPCC-US
7 | 79780005905 | Requirements for analysis and documentation of corrective action plans for all RAS misoperations. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780006037 | Uses Generation Facility additions and retirements. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 11700000 | NPCC-ON |  | NPCC-US
7 | 79780006166 | Configuration change management and vulnerability assessments (CIP-010); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780006206 | Where technically feasible, either:&lt;br/&gt;• Limit the number of unsuccessful authentication attempts; or&lt;br/&gt;• Generate alerts after a threshold of unsuccessful authentication attempts. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 57000000 | NPCC-ON |  | NPCC-US
7 | 79780006254 | Issue an alarm or alert in response to detected unauthorized physical access to a Physical Access Control System to the personnel identified in the BES Cyber Security Incident response plan within 15 minutes of the detection. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 1.7 An example of evidence may include, but is not limited to, language in the physical security plan that describes the issuance of an alarm or alert in response to unauthorized physical access to Physical Access Control Systems and additional evidence that the alarm or alerts was issued and communicated as identified in the BES Cyber Security Incident Response Plan, such as alarm or alert logs, cell phone or pager logs, or other evidence that the alarm or alert was generated and communicated. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780006283 | Recovery plans for BES Cyber Systems; | [23 empty] | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. |  |  | 2016-06-30 |  |  |  | 21700000 | NPCC-ON |  | NPCC-US
7 | 79780006449 | Interchange scheduling and coordination |  | RC | [11 empty] | RC | [10 empty] | 2012-10-01 |  | 2019-06-30 |  |  |  | 11700000 | NPCC-ON |  | NPCC-US
7 | 79780006561 | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 47000000 | NPCC-ON |  | NPCC-US
7 | 79780006597 | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 470000 | NPCC-ON |  | NPCC-US
7 | 79780006655 | For planning events shown in Table 1, when the analysis indicates an inability of the System to meet the performance requirements in Table 1, the Planning Assessment shall include Corrective Action Plan(s) addressing how the performance requirements will be met. Revisions to the Corrective Action Plan(s) are allowed in subsequent Planning Assessments but the planned System shall continue to meet the performance requirements in Table 1. Corrective Action Plan(s) do not need to be developed solely to meet the performance requirements for a single sensitivity case analyzed in accordance with Requirements R2, Parts 2.1.4 and 2.4.3. The Corrective Action Plan(s) shall: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 27000000 | NPCC-ON |  | NPCC-US
7 | 79780006697 | Monitored Facilities. |  | PCPA | [9 empty] | PA | [12 empty] | 2013-04-01 |  | 2020-12-14 |  |  |  | 14700000 | NPCC-ON |  | NPCC-US
7 | 79780006870 | Use of Interruptible Load, curtailable Load and demand response; |  | BA | BA | [21 empty] | 2017-04-01 | [5 empty] | 22700000 | NPCC-ON |  | NPCC-US
7 | 79780006910 | Coordination of the NPIRs with transmission system Remedial Action Schemes and any programs that reduce or shed load based on underfrequency or undervoltage. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO |  | TP | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 93700000 | NPCC-ON |  | NPCC-US
7 | 79780006944 | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessmen |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 47000000 | NPCC-ON |  | NPCC-US
7 | 79780007060 | Weekly conference calls |  | RC | [11 empty] | RC | [12 empty] | 2016-01-26 |  |  |  | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780007077 | Generator dispatch, including, but not limited to, additions and retirements. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 12700000 | NPCC-ON |  | NPCC-US
7 | 79780007089 | Generator dispatch, including, but not limited to, additions and retirements. |  | TSP | [20 empty] | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.&lt;br/&gt;4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 21700000 | NPCC-ON |  | NPCC-US
7 | 79780007215 | Recovery plans for BES Cyber Systems; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21700000 | NPCC-ON |  | NPCC-US
7 | 79780007318 | Where technically feasible, either:&lt;br/&gt;• Limit the number of unsuccessful authentication attempts; or&lt;br/&gt;• Generate alerts after a threshold of unsuccessful authentication attempts. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.7. Examples of evidence may include, but are not limited to:&lt;br/&gt;• Documentation of the account-lockout parameters; or &lt;br/&gt;• Rules in the alerting configuration showing how the system notified individuals after a determined number of unsuccessful login attempts. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1 Balancing Authority&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 57000000 | NPCC-ON |  | NPCC-US
7 | 79780007345 | Issue an alarm or alert in response to detected unauthorized physical access to a Physical Access Control System to the personnel identified in the BES Cyber Security Incident response plan within 15 minutes of the detection. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.7. An example of evidence may include, but is not limited to, language in the physical security plan that describes the issuance of an alarm or alert in response to unauthorized physical access to Physical Access Control Systems and additional evidence that the alarm or alerts was issued and communicated as identified in the BES Cyber Security Incident Response Plan, such as alarm or alert logs, cell phone or pager logs, or other evidence that the alarm or alert was generated and communicated. | 2016-07-01 | [5 empty] | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780007407 | Major EHV interconnections between operating areas. |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 72700000 | NPCC-ON |  | NPCC-US
7 | 79780007426 | A requirement to return failed units to service within 90 days. If a DME device will be out of service for greater than 90 days the owner shall keep a record of efforts aimed at restoring the DME to service. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 147000000 | NPCC-ON |  | NPCC-US
7 | 79780007438 | All identified channels. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 177000000 | NPCC-ON |  | NPCC-US
7 | 79780007484 | Configuration change management and vulnerability assessments (CIP-010); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11700000 | NPCC-ON |  | NPCC-US
7 | 79780007655 | Permitting delays |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:&lt;br/&gt;4.1.1. Applicable Transmission Owners&lt;br/&gt;4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.&lt;br/&gt;4.1.2. Applicable Generator Owners&lt;br/&gt;4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. &lt;br/&gt;4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.2.1. Each overhead transmission line operated at 200kV or higher.&lt;br/&gt;4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.&lt;br/&gt;4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.&lt;br/&gt;4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. &lt;br/&gt;4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:&lt;br/&gt;4.3.1.1. Operated at 200kV or higher; or&lt;br/&gt;4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or&lt;br/&gt;4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 77000000 | NPCC-ON |  | NPCC-US
7 | 79780007673 | For ATC Paths whose path rating, adjusted for seasonal variance, was established, known and used in operation since January 1, 1994, and no action has been taken to have the path rated using a different method, set the TTC at that previously established amount. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 27000000 | NPCC-ON |  | NPCC-US
7 | 79780007700 | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | PCPA | [9 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 470000 | NPCC-ON |  | NPCC-US
7 | 79780007938 | Operating Processes to reestablish connections within the Transmission Operator’s System for areas that have been restored and are prepared for reconnection. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 17000000 | NPCC-ON |  | NPCC-US
7 | 79780007995 | Configuration change management and vulnerability assessments (CIP-010); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11700000 | NPCC-ON |  | NPCC-US
7 | 79780008180 | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 47000000 | NPCC-ON |  | NPCC-US
7 | 79780008403 | Interchange scheduling and coordination |  | RC | [11 empty] | RC | [10 empty] | 2019-07-01 | [5 empty] | 11700000 | NPCC-ON |  | NPCC-US
7 | 79780008476 | For planning events shown in Table 1, when the analysis indicates an inability of the System to meet the performance requirements in Table 1, the Planning Assessment shall include Corrective Action Plan(s) addressing how the performance requirements will be met. Revisions to the Corrective Action Plan(s) are allowed in subsequent Planning Assessments, but the planned System shall continue to meet the performance requirements in Table 1. Corrective Action Plan(s) do not need to be developed solely to meet the performance requirements for a single sensitivity case analyzed in accordance with Requirements R2, Parts 2.1.4 and 2.4.3. The Corrective Action Plan(s) shall: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2025-07-01 |  | 2020-06-10 |  |  |  | 27000000 | NPCC-ON |  | NPCC-US
7 | 79780008687 | Configuration change management and vulnerability assessments (CIP-010); | [28 empty] | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service &lt;br/&gt;&lt;br/&gt;equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11700000 | NPCC-ON |  | NPCC-US
7 | 79780009131 | Coordination of the NPIRs with transmission system Remedial Action Schemes and any programs that reduce or shed load based on underfrequency or undervoltage. | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 93700000 | NPCC-ON |  | NPCC-US
7 | 79780009185 | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | PCPA | [9 empty] | PA | [16 empty] | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 47000000 | NPCC-ON |  | NPCC-US
7 | 79780009320 | For planning events shown in Table 1, when the analysis indicates an inability of the System to meet the performance requirements in Table 1, the Planning Assessment shall include Corrective Action Plan(s) addressing how the performance requirements will be met. Revisions to the Corrective Action Plan(s) are allowed in subsequent Planning Assessments, but the planned System shall continue to meet the performance requirements in Table 1. Corrective Action Plan(s) do not need to be developed solely to meet the performance requirements for a single sensitivity case analyzed in accordance with Requirements R2, Parts 2.1.3 and 2.4.3. The Corrective Action Plan(s) shall: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2025-07-01 | [5 empty] | 27000000 | NPCC-ON |  | NPCC-US
7 | RP-2021-06-15-0000019 | Update of the physical security plan within thirty calendar days of the completion ofany physical security system redesign or reconfiguration, including, but not limitedto, addition or removal of access points through the Physical Security Perimeter,physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2014-10-01 |  | 2014-02-03 |  |  |  | 10700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 1003 | Current local or Transmission Loading Relief procedures in effect. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  | IRO-005-1 R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 1030 | Current local or Transmission Loading Relief procedures in effect. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  | IRO-005-2 R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 1057 | Current local or Transmission Loading Relief procedures in effect. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  | IRO-005-3a R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 1146 | A specification of how system conditions, limiting facilities, contingencies, transmission reservations, energy schedules, and other data needed by Transmission Service Providers for the calculation of TTC and ATC values are shared and used within the Regional Reliability Organization and with neighboring interconnected electric systems, including adjacent systems, subregions, and Regional Reliability Organizations. In addition, specify how this information is to be used to determine TTC and ATC values. If some data is not used, provide an explanation. |  | RRO, TSP | [14 empty] | RRO | [5 empty] | TSP |  |  |  | 2009-11-24 |  |  | MOD-001-0 R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 1204 | Describe the formal process and rationale for the Regional Reliability Organization to grant any variances to individual Transmission Service Providers from the Regional Reliability Organization’s CBM methodology. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-004-0 R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 1268 | Variations in generation dispatch. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 13700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 1300 | Interchange Schedules: Existing and future Interchange Schedules and/or assumptions. |  | RRO | [14 empty] | RRO | [9 empty] | 2016-06-30 |  |  | MOD-011-0 R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 1433 | Uses Generation Facility additions and retirements. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 11700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 1447 | For ATC Paths whose path rating, adjusted for seasonal variance, was established, known and used in operation since January 1, 1994, and no action has been taken to have the path rated using a different method, set the TTC at that previously established amount. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-029-1 R2. | 27000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 1507 | The impact of other firm services determined by the Transmission Service Provider. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | MOD-030-1 R6. | 67000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 1515 | The impact of other non-firm services determined by the Transmission Service Provider. |  | TSP | [20 empty] | TSP |  |  |  | 2009-11-24 |  |  | MOD-030-1 R7. | 77000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 1572 | The impact of other firm services determined by the Transmission Service Provider. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R6. | 67000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 1580 | The impact of other non-firm services determined by the Transmission Service Provider. |  | TSP | [20 empty] | TSP |  | 2010-02-08 |  | 2017-03-31 |  |  | MOD-030-2 R7. | 77000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 1611 | Coordination of the NPIRs with transmission system Special Protection Systems and underfrequency and undervoltage load shedding programs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-03-31 |  |  |  | 93700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 1742 | Automatic load restoration schemes. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  |  | 12700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 1786 | Requirements for analysis and documentation of corrective action plans for all SPS misoperations. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  | PRC-012-0 R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 1835 | Monitored devices, such as circuit breaker, disconnect status, alarms, etc. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2022-06-30 |  |  | PRC-018-1 R3. | 37000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 1880 | Set transmission line relays applied at the load center terminal, remote from generation stations, so they do not operate at or below 115% of the maximum current flow from the load to the generation source under any system configuration. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  | PRC-023-1 R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 2043 | Demonstrate that system performance meets Table 1 for Category A (no contingencies). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 13700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 2064 | Demonstrate that system performance meets Table 1 for Category A (no contingencies). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 13700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 2088 | Demonstrate that system performance meets Category B contingencies. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 2113 | Demonstrate that system performance meets Category B contingencies. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 13700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 2138 | Demonstrate that System performance meets Table 1 for Category C contingencies. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 2163 | Demonstrate that System performance meets Table 1 for Category C contingencies. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 13700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 2185 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  |  | 13700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 2213 | Environmental and regulatory issues and impacts (air and water quality issues, and impacts of existing, new, and proposed regulations and legislation.) |  | RRO | [14 empty] | RRO | [9 empty] | 2009-04-15 |  |  | TPL-006-0 R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 2314 | The synchronous generator or synchronous condenser has not achieved Commercial Operation. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-06-27 |  | 2015-03-31 |  |  | VAR-002-WECC-1 R1. | 17000000 | WECC-US | [5 empty] | WECC-US
7. | 2328 | The generator AVR is not in service. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-06-27 |  | 2015-03-31 |  |  | VAR-501-WECC-1 R1. | 17000000 | WECC-US | [5 empty] | WECC-US
7. | 2353 | Environmental and regulatory issues and impacts (air and water quality issues, and impacts of existing, new, and proposed regulations and legislation.) |  | RRO | [14 empty] | RRO | [9 empty] | 2014-12-31 |  |  | TPL-006-0.1 R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 2363 | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-09-30 |  |  |  | 12700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 2448 | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  | CIP-006-2 R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 253 | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. |  | BA, GO, GOP, IA, LSE, NERC, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 12700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 2548 | Coordination of the NPIRs with transmission system Special Protection Systems and underfrequency and undervoltage load shedding programs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2013-03-31 |  |  |  | 93700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 2579 | Operating Processes to reestablish connections within the Transmission Operator’s System for areas that have been restored and are prepared for reconnection. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | EOP-005-2 R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 2624 | Criteria for sharing information regarding restoration with neighboring Reliability Coordinators and with Transmission Operators and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  | EOP-006-2 R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 2722 | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2016-06-30 |  | 4.2.1 Facilities regulated by the U.S. Nuclear Regulatory Commission or the Canadian Nuclear Safety Commission.4.2.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. |  | 12700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 2809 | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  | CIP-006-3 R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 2896 | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  | CIP-006-2b R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 2917 | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | CIP-006-2c R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 2937 | Process for updating the physical security plan within ninety calendar days of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the physical security perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1b R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 2962 | Process for updating the physical security plan within ninety calendar days of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the physical security perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | CIP-006-1c R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 2986 | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  | CIP-006-3c R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 3050 | Uses Generation Facility additions and retirements. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 11700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 3065 | For ATC Paths whose path rating, adjusted for seasonal variance, was established, known and used in operation since January 1, 1994, and no action has been taken to have the path rated using a different method, set the TTC at that previously established amount. |  | TOP | [18 empty] | TOP |  |  |  | 2010-09-16 |  | 2017-03-31 |  |  | MOD-029-1a R2. | 27000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 3298 | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-006-4c R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 337 | Process for updating the physical security plan within ninety calendar days of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the physical security perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-006-1 R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 3428 | Current local or Transmission Loading Relief procedures in effect. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  | IRO-005-2a R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 3462 | Demonstrate that system performance meets Table 1 for Category A (no contingencies). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 3486 | Demonstrate that system performance meets Category B contingencies. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 13700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 3511 | Demonstrate that system performance meets Category B contingencies. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 3536 | Demonstrate that System performance meets Table 1 for Category C contingencies. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 3558 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 364 | Process for updating the physical security plan within ninety calendar days of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the physical security perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1a R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 3804 | Current local or Transmission Loading Relief procedures in effect. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  | IRO-005-3 R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 3905 | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | CIP-006-2a R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 3920 | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  | CIP-006-3a R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 4041 | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-006-3d R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 4059 | Update of the physical security plan within thirty calendar days of the completion of any physical security system redesign or reconfiguration, including, but not limited to, addition or removal of access points through the Physical Security Perimeter, physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-006-4d R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 4180 | Current local or Transmission Loading Relief procedures in effect. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  | IRO-005-3.1a R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 4238 | Coordination of the NPIRs with transmission system Special Protection Systems and underfrequency and undervoltage load shedding programs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  | 2013-04-01 |  | 2015-12-31 |  |  |  | 93700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 4339 | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 12700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 4562 | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2016-06-30 |  |  |  | 12700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 4593 | Demonstrate that system performance meets Table 1 for Category A (no contingencies). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 4630 | Demonstrate that system performance meets Category B contingencies. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 4655 | Demonstrate that System performance meets Table 1 for Category C contingencies. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 4684 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 4695 | Demonstrate that System performance meets Table 1 for Category C contingencies. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 4731 | Demonstrate that System performance meets Table 1 for Category C contingencies. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 4749 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 4758 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 4915 | Any other device listed as a Limiting Element |  | GO, TO |  |  |  |  | GO | [19 empty] | 2006-08-01 |  |  |  | 11700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 5033 | Current local or Transmission Loading Relief procedures in effect. |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 5125 | Responsibility for maintenance and testing. |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 5653 | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. |  | RC | [11 empty] | RC | [10 empty] | 2016-01-25 | [5 empty] | 37000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 5667 | Current local or Transmission Loading Relief procedures in effect. |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  |  | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 5732 | The impact of other firm services determined by the Transmission Service Provider. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 67000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 5740 | The impact of other non-firm services determined by the Transmission Service Provider. |  | TSP | [20 empty] | TSP |  | 2016-01-25 | [5 empty] | 77000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 5759 | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 5771 | Any additional assets that support the reliable operation of the Bulk Electric System that the Responsible Entity deems appropriate to include in its assessment. |  | BA, GO, GOP, IA, LSE, NERC, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE | NERC |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 12700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 5804 | Coordination of the NPIRs with transmission system Remedial Action Schemes and underfrequency and undervoltage load shedding programs. |  | BA, DP, GO, GOP, LSE, PCPA, RC, RP, TO, TOP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC |  | RP |  |  |  | TO | TOP |  | TSP |  |  |  | 2014-11-13 |  |  |  | 93700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 5821 | Demonstrate that system performance meets Table 1 for Category A (no contingencies). |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 5842 | Demonstrate that system performance meets Category B contingencies. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 5867 | Demonstrate that System performance meets Table 1 for Category C contingencies. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 5892 | Include the effects of existing and planned protection systems, including any backup or redundant systems. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 5905 | Requirements for analysis and documentation of corrective action plans for all RAS misoperations. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 6037 | Uses Generation Facility additions and retirements. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 11700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 604 | The plan shall be reviewed and updated annually. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | EOP-008-0 R1. | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 6166 | Configuration change management and vulnerability assessments (CIP-010); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 6206 | Where technically feasible, either:• Limit the number of unsuccessful authentication attempts; or• Generate alerts after a threshold of unsuccessful authentication attempts. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 57000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 6254 | Issue an alarm or alert in response to detected unauthorized physical access to a Physical Access Control System to the personnel identified in the BES Cyber Security Incident response plan within 15 minutes of the detection. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 1.7 An example of evidence may include, but is not limited to, language in the physical security plan that describes the issuance of an alarm or alert in response to unauthorized physical access to Physical Access Control Systems and additional evidence that the alarm or alerts was issued and communicated as identified in the BES Cyber Security Incident Response Plan, such as alarm or alert logs, cell phone or pager logs, or other evidence that the alarm or alert was generated and communicated. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 627 | Grounding and safety issues. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 21700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 6449 | Interchange scheduling and coordination |  | RC | [11 empty] | RC | [10 empty] | 2012-10-01 |  | 2019-06-30 |  |  |  | 11700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 6561 | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 47000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 6597 | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | PCPA | [9 empty] | PA | [12 empty] | 2012-07-10 |  | 2015-09-30 |  |  |  | 470000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 6655 | For planning events shown in Table 1, when the analysis indicates an inability of the System to meet the performance requirements in Table 1, the Planning Assessment shall include Corrective Action Plan(s) addressing how the performance requirements will be met. Revisions to the Corrective Action Plan(s) are allowed in subsequent Planning Assessments but the planned System shall continue to meet the performance requirements in Table 1. Corrective Action Plan(s) do not need to be developed solely to meet the performance requirements for a single sensitivity case analyzed in accordance with Requirements R2, Parts 2.1.4 and 2.4.3. The Corrective Action Plan(s) shall: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 27000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 6697 | Monitored Facilities. |  | PCPA | [9 empty] | PA | [12 empty] | 2013-04-01 |  | 2020-12-14 |  |  |  | 14700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 6870 | Use of Interruptible Load, curtailable Load and demand response; |  | BA | BA | [21 empty] | 2017-04-01 | [5 empty] | 22700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 6910 | Coordination of the NPIRs with transmission system Remedial Action Schemes and any programs that reduce or shed load based on underfrequency or undervoltage. |  | BA, DP, GO, GOP, LSE, PCPA, RC, TO, TP, TSP | BA | DP |  |  | GO | GOP |  | LSE |  | PA |  | RC | [5 empty] | TO |  | TP | TSP |  | 2016-01-01 |  | 2021-03-31 |  |  |  | 93700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 6944 | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessmen |  | DP-UFLS, PCPA |  | DP | [7 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 47000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 7060 | Weekly conference calls |  | RC | [11 empty] | RC | [12 empty] | 2016-01-26 |  |  |  | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 7077 | Generator dispatch, including, but not limited to, additions and retirements. |  | TOP, TSP | [18 empty] | TOP |  | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 12700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 7089 | Generator dispatch, including, but not limited to, additions and retirements. |  | TSP | [20 empty] | TSP |  |  | X | 2019-05-09 |  | 4.2. Exemptions: The following is exempt from MOD-001-2.4.2.1 Functional Entities operating within the Electric Reliability Council of Texas (ERCOT) |  | 21700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 7215 | Recovery plans for BES Cyber Systems; |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 7318 | Where technically feasible, either:• Limit the number of unsuccessful authentication attempts; or• Generate alerts after a threshold of unsuccessful authentication attempts. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M5.7. Examples of evidence may include, but are not limited to:• Documentation of the account-lockout parameters; or • Rules in the alerting configuration showing how the system notified individuals after a determined number of unsuccessful login attempts. | 2016-03-31 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 57000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 7345 | Issue an alarm or alert in response to detected unauthorized physical access to a Physical Access Control System to the personnel identified in the BES Cyber Security Incident response plan within 15 minutes of the detection. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.7. An example of evidence may include, but is not limited to, language in the physical security plan that describes the issuance of an alarm or alert in response to unauthorized physical access to Physical Access Control Systems and additional evidence that the alarm or alerts was issued and communicated as identified in the BES Cyber Security Incident Response Plan, such as alarm or alert logs, cell phone or pager logs, or other evidence that the alarm or alert was generated and communicated. | 2016-07-01 | [5 empty] | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 7407 | Major EHV interconnections between operating areas. |  | RC | [11 empty] | RC | [10 empty] | 2013-10-20 |  | 2016-07-01 |  |  |  | 72700000 | NPCC-US |  | NPCC-US
7. | 7426 | A requirement to return failed units to service within 90 days. If a DME device will be out of service for greater than 90 days the owner shall keep a record of efforts aimed at restoring the DME to service. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 147000000 | NPCC-US |  | NPCC-US
7. | 7438 | All identified channels. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 177000000 | NPCC-US |  | NPCC-US
7. | 7484 | Configuration change management and vulnerability assessments (CIP-010); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 7655 | Permitting delays |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:4.1.1. Applicable Transmission Owners4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.4.1.2. Applicable Generator Owners4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.2.1. Each overhead transmission line operated at 200kV or higher.4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:4.3.1.1. Operated at 200kV or higher; or4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 77000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 7673 | For ATC Paths whose path rating, adjusted for seasonal variance, was established, known and used in operation since January 1, 1994, and no action has been taken to have the path rated using a different method, set the TTC at that previously established amount. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 27000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 7700 | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | PCPA | [9 empty] | PA | [12 empty] | 2015-03-04 |  | 2017-09-30 |  |  |  | 470000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 7720 | The synchronous generator or synchronous condenser has not achieved Commercial Operation. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2015-03-03 |  | 2018-09-05 |  |  |  | 17000000 | WECC-US | [5 empty] | WECC-US
7. | 781 | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. |  | RC | [11 empty] | RC | [10 empty] | 2008-02-08 |  | 2009-04-28 |  |  | FAC-011-1 R3. | 37000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 7834 | The generator AVR is not in service. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-04-01 |  | 2017-06-30 |  |  |  | 17000000 | WECC-US | [5 empty] | WECC-US
7. | 7938 | Operating Processes to reestablish connections within the Transmission Operator’s System for areas that have been restored and are prepared for reconnection. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 17000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 7995 | Configuration change management and vulnerability assessments (CIP-010); |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 810 | Criteria for determining when violating a SOL qualifies as an Interconnection Reliability Operating Limit (IROL) and criteria for developing any associated IROL Tv. |  | RC | [11 empty] | RC | [10 empty] | 2009-04-29 |  | 2017-03-31 |  |  | FAC-011-2 R3. | 37000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 8180 | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 47000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 8215 | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-01 |  | 2021-03-31 |  |  |  | 470000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 8254 | Modeling assumptions for emergency operation procedures used to make reserves available. |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 14700000 | RF-US |  |  | RF-US
7. | 8258 | Document that all Load in the Planning Coordinator area is accounted for in its Resource Adequacy analysis |  | PCPA | [9 empty] | PA | [12 empty] | 2017-10-16 | [5 empty] | 17000000 | RF-US |  |  | RF-US
7. | 8403 | Interchange scheduling and coordination |  | RC | [11 empty] | RC | [10 empty] | 2019-07-01 | [5 empty] | 11700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 8476 | For planning events shown in Table 1, when the analysis indicates an inability of the System to meet the performance requirements in Table 1, the Planning Assessment shall include Corrective Action Plan(s) addressing how the performance requirements will be met. Revisions to the Corrective Action Plan(s) are allowed in subsequent Planning Assessments, but the planned System shall continue to meet the performance requirements in Table 1. Corrective Action Plan(s) do not need to be developed solely to meet the performance requirements for a single sensitivity case analyzed in accordance with Requirements R2, Parts 2.1.4 and 2.4.3. The Corrective Action Plan(s) shall: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2025-07-01 |  | 2020-06-10 |  |  |  | 27000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 8687 | Configuration change management and vulnerability assessments (CIP-010); |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 9131 | Coordination of the NPIRs with transmission system Remedial Action Schemes and any programs that reduce or shed load based on underfrequency or undervoltage. | [24 empty] | 2021-04-01 |  |  |  | 4.1. Functional Entities: 4.1.1 Nuclear Plant Generator Operators. 4.2. Transmission Entities shall mean all entities that are responsible for providing services related to Nuclear Plant Interface Requirements (NPIRs). Such entities may include one or more of the following: |  | 93700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 9164 | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 470000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 9185 | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | PCPA | [9 empty] | PA | [14 empty] | 2021-03-31 |  | Transmission Owners that own Elements identified in the UFLS program established by the Planning Coordinators. UFLS entities shall mean all entities that are responsible for the ownership, operation, or control of UFLS equipment as required by the UFLS program established by the Planning Coordinators. Such entities may include one or more of the following: |  | 47000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 9320 | For planning events shown in Table 1, when the analysis indicates an inability of the System to meet the performance requirements in Table 1, the Planning Assessment shall include Corrective Action Plan(s) addressing how the performance requirements will be met. Revisions to the Corrective Action Plan(s) are allowed in subsequent Planning Assessments, but the planned System shall continue to meet the performance requirements in Table 1. Corrective Action Plan(s) do not need to be developed solely to meet the performance requirements for a single sensitivity case analyzed in accordance with Requirements R2, Parts 2.1.3 and 2.4.3. The Corrective Action Plan(s) shall: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2025-07-01 | [5 empty] | 27000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | 9374 | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | PCPA | [9 empty] | PA | [12 empty] | 2021-04-01 | [5 empty] | 470000 | WECC-US | [5 empty] | WECC-US
7. | RP-2021-06-08-0000014 | Tie tripping schemes and the frequency and time delay at which they operate |  | DP, TO |  | DP | [22 empty] | 2013-11-07 |  |  |  | 50700000 | SPPRE-US
7. | RP-2021-06-15-0000012 | Update of the physical security plan within thirty calendar days of the completion ofany physical security system redesign or reconfiguration, including, but not limitedto, addition or removal of access points through the Physical Security Perimeter,physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-04-01 |  | 2010-07-14 |  |  |  | 10700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | RP-2021-06-15-0000013 | Update of the physical security plan within thirty calendar days of the completion ofany physical security system redesign or reconfiguration, including, but not limitedto, addition or removal of access points through the Physical Security Perimeter,physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  |  | 10700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | RP-2021-06-15-0000014 | Update of the physical security plan within thirty calendar days of the completion ofany physical security system redesign or reconfiguration, including, but not limitedto, addition or removal of access points through the Physical Security Perimeter,physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  |  | 10700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | RP-2021-06-15-0000015 | Update of the physical security plan within thirty calendar days of the completion ofany physical security system redesign or reconfiguration, including, but not limitedto, addition or removal of access points through the Physical Security Perimeter,physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-09-30 |  |  |  | 10700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | RP-2021-06-15-0000016 | Update of the physical security plan within thirty calendar days of the completion ofany physical security system redesign or reconfiguration, including, but not limitedto, addition or removal of access points through the Physical Security Perimeter,physical access controls, monitoring controls, or logging controls |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-09-30 |  |  |  | 10700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | RP-2021-06-15-0000017 | Update of the physical security plan within thirty calendar days of the completion ofany physical security system redesign or reconfiguration, including, but not limitedto, addition or removal of access points through the Physical Security Perimeter,physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-10-01 |  | 2011-05-18 |  |  |  | 10700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | RP-2021-06-15-0000018 | Update of the physical security plan within thirty calendar days of the completion ofany physical security system redesign or reconfiguration, including, but not limitedto, addition or removal of access points through the Physical Security Perimeter,physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 10700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | RP-2021-06-15-0000020 | Update of the physical security plan within thirty calendar days of the completion ofany physical security system redesign or reconfiguration, including, but not limitedto, addition or removal of access points through the Physical Security Perimeter,physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 10700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | RP-2021-06-16-0000043 | Document that all Load in the Planning Coordinator area is accounted for in its Resource Adequacy analysis |  | PCPA | [9 empty] | PA | [12 empty] | 2011-05-23 |  | 2017-12-31 |  |  |  | 10700000 | RF-US |  |  | RF-US
7. | RP-2021-06-17-0000013 | Update of the physical security plan within thirty calendar days of the completion ofany physical security system redesign or reconfiguration, including, but not limitedto, addition or removal of access points through the Physical Security Perimeter,physical access controls, monitoring controls, or logging controls. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  |  | 10700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | RP-2021-06-22-0000007 | Weekly conference calls |  | RC | [11 empty] | RC | [12 empty] | 2016-01-26 |  |  |  | 10700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | RP-2021-06-25-0000002 | The synchronous generator or synchronous condenser has not achieved Commercial Operation. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2015-04-01 |  | 2018-09-05 |  |  |  | 10700000 | WECC-US | [5 empty] | WECC-US
7. | RP-2021-06-30-0000013 | Where technically feasible, either: Limit the number of unsuccessful authentication attempts; or Generate alerts after a threshold of unsuccessful authentication attempts. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1 Balancing Authority4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-007-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 50700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | RP-2021-07-09-0000013 | Any automatic Load restoration that impacts frequency stabilization and operates within the duration of the simulations run for the assessment. |  | DP, DP-UFLS, PCPA, TO |  | DP | [7 empty] | PA | [12 empty] | 2021-04-01 |  |  |  | UFLS entities shall mean all entities that are responsible for the ownership,operation, or control of UFLS equipment as required by the UFLS programestablished by the Planning Coordinators. Such entities may include one ormore of the following: 4.2.1 Transmission Owners4.2.2 Distribution Providers4.2.3 UFLS-Only Distribution Providers4.3. Transmission Owners that own Elements identified in the UFLS programestablished by the Planning Coordinators. |  | 40700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | RP-2021-07-13-0000022 | State that the use of underfrequency load shedding (UFLS) programs and Undervoltage Load Shedding (UVLS) Programs are not allowed in the establishment of stability limits. |  | RC | [11 empty] | RC | [16 empty] | 40700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7. | RP-2021-07-14-0000001 | Permitting delays |  | GO, TO |  |  |  |  | GO | [23 empty] | 70700000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7.1. | RP-2021-07-12-0000019 | List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include:  Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment.  Installation, modification, or removal of Protection Systems or Remedial Action Schemes.  Installation or modification of automatic generation tripping as a response to a single or multiple Contingency to mitigate Stability performance violations.  Installation or modification of manual and automatic generation runback/tripping as a response to a single or multiple Contingency to mitigate steady state performance violations.  Use of Operating Procedures specifying how long they will be needed as part of the Corrective Action Plan.  Use of rate applications, DSM, new technologies, or other initiatives. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 27100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7.2. | RP-2021-07-12-0000020 | Include actions to resolve performance deficiencies identified in multiple sensitivity studies or provide a rationale for why actions were not necessary. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 27200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7.3. | RP-2021-07-12-0000021 | If situations arise that are beyond the control of the Transmission Planner or Planning Coordinator that prevent the implementation of a Corrective Action Plan in the required timeframe, then the Transmission Planner or Planning Coordinator is permitted to utilize Non-Consequential Load Loss and curtailment of Firm Transmission Service to correct the situation that would normally not be permitted in Table 1, provided that the Transmission Planner or Planning Coordinator documents that they are taking actions to resolve the situation. The Transmission Planner or Planning Coordinator shall document the situation causing the problem, alternatives evaluated, and the use of Non-Consequential Load Loss or curtailment of Firm Transmission Service. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 27300000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
7.4. | RP-2021-07-12-0000022 | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 27400000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8 | 79780000338 | Cyber Assets used in the access control and monitoring of the Physical Security Perimeter(s) shall be afforded the protective measures specified in Standard CIP-003, Standard CIP-004 Requirement R3, Standard CIP-005 Requirements R2 and R3, Standard CIP-006 Requirement R2 and R3, Standard CIP-007, Standard CIP-008 and Standard CIP-009. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780000365 | Cyber Assets used in the access control and monitoring of the Physical Security Perimeter(s) shall be afforded the protective measures specified in Standard CIP-003, Standard CIP-004 Requirement R3, Standard CIP-005 Requirements R2 and R3, Standard CIP-006 Requirement R2 and R3, Standard CIP-007, Standard CIP-008 and Standard CIP-009. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780000605 | Interim provisions must be included if it is expected to take more than one hour to implement the contingency plan for loss of primary control facility. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780000628 | Insulation and insulation coordination. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 21800000 | NPCC-ON |  | NPCC-US
8 | 79780001004 | Planned generation dispatches. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780001031 | Planned generation dispatches. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780001058 | Planned generation dispatches. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780001147 | A description of how the assumptions for and the calculations of TTC and ATC values change over different time (such as hourly, daily, and monthly) horizons. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780001205 | Specify the relationship of CBM to the generation reliability requirement and the allocation of the CBM values to the appropriate transmission facilities. The sum of the CBM values allocated to all interfaces shall not exceed that portion of the generation reliability requirement that is to be provided by outside resources. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780001269 | Short-term System Operator response (Operating Reserve actions not exceeding a 59-minute window). |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 13800000 | NPCC-ON |  | NPCC-US
8 | 79780001434 | Uses Special Protection System (SPS) models where currently existing or projected for implementation within the studied time horizon. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 11800000 | NPCC-ON |  | NPCC-US
8 | 79780001448 | Create a study report that describes the steps above that were undertaken (R2.1 - R2.7), including the contingencies and assumptions used, when determining the TTC and the results of the study. Where three phase fault damping is used to determine stability limits, that report shall also identify the percent used and include justification for use unless specified otherwise in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  |  | 28000000 | NPCC-ON |  | NPCC-US
8 | 79780001743 | Any other schemes that are part of or impact the UFLS programs. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  |  | 12800000 | NPCC-ON |  | NPCC-US
8 | 79780001787 | Identification of the Regional Reliability Organization group responsible for the Regional Reliability Organization’s review procedure and the process for Regional Reliability Organization approval of the procedure. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780001836 | Monitored electrical quantities, such as voltage, current, etc. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2022-06-30 |  |  |  | 38000000 | NPCC-ON |  | NPCC-US
8 | 79780001881 | Set transmission line relays applied on the bulk system-end of transmission lines that serve load remote to the system so they do not operate at or below 115% of the maximum current flow from the system to the load under any system configuration. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780002044 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 13800000 | NPCC-ON |  | NPCC-US
8 | 79780002065 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 13800000 | NPCC-ON |  | NPCC-US
8 | 79780002089 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13800000 | NPCC-ON |  | NPCC-US
8 | 79780002114 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 13800000 | NPCC-ON |  | NPCC-US
8 | 79780002139 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13800000 | NPCC-ON |  | NPCC-US
8 | 79780002164 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 13800000 | NPCC-ON |  | NPCC-US
8 | 79780002186 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  |  | 13800000 | NPCC-ON |  | NPCC-US
8 | 79780002449 | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780002580 | Operating Processes to restore Loads required to restore the System, such as station service for substations, units to be restarted or stabilized, the Load needed to stabilize generation and frequency, and provide voltage control. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780002625 | Identification of the Reliability Coordinator as the primary contact for disseminating information regarding restoration to neighboring Reliability Coordinators, and to Transmission Operators, and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780002810 | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780002890 | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780002911 | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780002931 | Cyber Assets used in the access control and monitoring of the Physical Security Perimeter(s) shall be afforded the protective measures specified in Standard CIP-003, Standard CIP-004 Requirement R3, Standard CIP-005 Requirements R2 and R3, Standard CIP-006 Requirement R2 and R3, Standard CIP-007, Standard CIP-008 and Standard CIP-009. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780002960 | Cyber Assets used in the access control and monitoring of the Physical Security Perimeter(s) shall be afforded the protective measures specified in Standard CIP-003, Standard CIP-004 Requirement R3, Standard CIP-005 Requirements R2 and R3, Standard CIP-006 Requirement R2 and R3, Standard CIP-007, Standard CIP-008 and Standard CIP-009. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780002987 | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780003051 | Uses Special Protection System (SPS) models where currently existing or projected for implementation within the studied time horizon. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 11800000 | NPCC-ON |  | NPCC-US
8 | 79780003064 | Create a study report that describes the steps above that were undertaken (R2.1 - R2.7), including the contingencies and assumptions used, when determining the TTC and the results of the study. Where three phase fault damping is used to determine stability limits, that report shall also identify the percent used and include justification for use unless specified otherwise in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2010-09-16 |  | 2017-03-31 |  |  |  | 28000000 | NPCC-ON |  | NPCC-US
8 | 79780003299 | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780003429 | Planned generation dispatches. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780003463 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13800000 | NPCC-ON |  | NPCC-US
8 | 79780003487 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 13800000 | NPCC-ON |  | NPCC-US
8 | 79780003512 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13800000 | NPCC-ON |  | NPCC-US
8 | 79780003537 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13800000 | NPCC-ON |  | NPCC-US
8 | 79780003559 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13800000 | NPCC-ON |  | NPCC-US
8 | 79780003803 | Planned generation dispatches. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780003899 | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780003921 | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780004038 | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780004060 | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780004179 | Planned generation dispatches. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780004592 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13800000 | NPCC-ON |  | NPCC-US
8 | 79780004635 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13800000 | NPCC-ON |  | NPCC-US
8 | 79780004660 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13800000 | NPCC-ON |  | NPCC-US
8 | 79780004683 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13800000 | NPCC-ON |  | NPCC-US
8 | 79780004700 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13800000 | NPCC-ON |  | NPCC-US
8 | 79780004730 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13800000 | NPCC-ON |  | NPCC-US
8 | 79780004748 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13800000 | NPCC-ON |  | NPCC-US
8 | 79780004759 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13800000 | NPCC-ON |  | NPCC-US
8 | 79780005034 |  |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780005126 |  |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780005668 | Planned generation dispatches. |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780005822 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13800000 | NPCC-ON |  | NPCC-US
8 | 79780005843 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13800000 | NPCC-ON |  | NPCC-US
8 | 79780005868 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13800000 | NPCC-ON |  | NPCC-US
8 | 79780005893 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13800000 | NPCC-ON |  | NPCC-US
8 | 79780005906 | Identification of the Regional Reliability Organization group responsible for the Regional Reliability Organization’s review procedure and the process for Regional Reliability Organization approval of the procedure. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780006038 | Uses Remedial Action Scheme (RAS) models where currently existing or projected for implementation within the studied time horizon. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 11800000 | NPCC-ON |  | NPCC-US
8 | 79780006167 | Information protection (CIP-011); and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780006255 | Log (through automated means or by personnel who control entry) entry of each individual with authorized unescorted physical access into each Physical Security Perimeter, with information to identify the individual and date and time of entry. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 1.8 An example of evidence may include, but is not limited to, language in the physical security plan that describes logging and recording of physical entry into each Physical Security Perimeter and additional evidence to demonstrate that this logging has been implemented, such as logs of physical access into Physical Security Perimeters that show the individual and the date and time of entry into Physical Security Perimeter. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780006284 | Response to Cyber Security Incidents; and | [23 empty] | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. |  |  | 2016-06-30 |  |  |  | 21800000 | NPCC-ON |  | NPCC-US
8 | 79780006450 | Interconnection reliability operations and coordination |  | RC | [11 empty] | RC | [10 empty] | 2012-10-01 |  | 2019-06-30 |  |  |  | 11800000 | NPCC-ON |  | NPCC-US
8 | 79780006660 | For short circuit analysis, if the short circuit current interrupting duty on circuit breakers determined in Requirement R2, Part 2.3 exceeds their Equipment Rating, the Planning Assessment shall include a Corrective Action Plan to address the Equipment Rating violations. The Corrective Action Plan shall: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 28000000 | NPCC-ON |  | NPCC-US
8 | 79780006871 | Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and |  | BA | BA | [21 empty] | 2017-04-01 | [5 empty] | 22800000 | NPCC-ON |  | NPCC-US
8 | 79780007216 | Response to Cyber Security Incidents; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21800000 | NPCC-ON |  | NPCC-US
8 | 79780007346 | Log (through automated means or by personnel who control entry) entry of each individual with authorized unescorted physical access into each Physical Security Perimeter, with information to identify the individual and date and time of entry. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.8. An example of evidence may include, but is not limited to, language in the physical security plan that describes logging and recording of physical entry into each Physical Security Perimeter and additional evidence to demonstrate that this logging has been implemented, such as logs of physical access into Physical Security Perimeters that show the individual and the date and time of entry into Physical Security Perimeter. | 2016-07-01 | [5 empty] | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780007439 | Monitored electrical quantities. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 178000000 | NPCC-ON |  | NPCC-US
8 | 79780007485 | Information protection (CIP-011); and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11800000 | NPCC-ON |  | NPCC-US
8 | 79780007656 | Land ownership changes/Change in land use by the landowner |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:&lt;br/&gt;4.1.1. Applicable Transmission Owners&lt;br/&gt;4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.&lt;br/&gt;4.1.2. Applicable Generator Owners&lt;br/&gt;4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. &lt;br/&gt;4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.2.1. Each overhead transmission line operated at 200kV or higher.&lt;br/&gt;4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.&lt;br/&gt;4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.&lt;br/&gt;4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. &lt;br/&gt;4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:&lt;br/&gt;4.3.1.1. Operated at 200kV or higher; or&lt;br/&gt;4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or&lt;br/&gt;4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 78000000 | NPCC-ON |  | NPCC-US
8 | 79780007674 | Create a study report that describes the steps above that were undertaken (R2.1 – R2.7), including the contingencies and assumptions used, when determining the TTC and the results of the study. Where three phase fault damping is used to determine stability limits, that report shall also identify the percent used and include justification for use unless specified otherwise in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 28000000 | NPCC-ON |  | NPCC-US
8 | 79780007939 | Operating Processes to restore Loads required to restore the System, such as station service for substations, units to be restarted or stabilized, the Load needed to stabilize generation and frequency, and provide voltage control. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 18000000 | NPCC-ON |  | NPCC-US
8 | 79780007996 | Information protection (CIP-011); and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11800000 | NPCC-ON |  | NPCC-US
8 | 79780008404 | Interconnection reliability operations and coordination |  | RC | [11 empty] | RC | [10 empty] | 2019-07-01 | [5 empty] | 11800000 | NPCC-ON |  | NPCC-US
8 | 79780008481 | For short circuit analysis, if the short circuit current interrupting duty on circuit breakers determined in Requirement R2, Part 2.3 exceeds their Equipment Rating, the Planning Assessment shall include a Corrective Action Plan to address the Equipment Rating violations. The Corrective Action Plan shall: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-04-13 |  | 2020-06-10 |  |  |  | 28000000 | NPCC-ON |  | NPCC-US
8 | 79780008688 | Information protection (CIP-011); and | [28 empty] | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service &lt;br/&gt;&lt;br/&gt;equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11800000 | NPCC-ON |  | NPCC-US
8 | 79780009325 | For short circuit analysis, if the short circuit current interrupting duty on circuit breakers determined in Requirement R2, Part 2.3 exceeds their Equipment Rating, the Planning Assessment shall include a Corrective Action Plan to address the Equipment Rating violations. The Corrective Action Plan shall: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 28000000 | NPCC-ON |  | NPCC-US
8. | 1004 | Planned generation dispatches. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  | IRO-005-1 R1. | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 1031 | Planned generation dispatches. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  | IRO-005-2 R1. | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 1058 | Planned generation dispatches. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  | IRO-005-3a R1. | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 1147 | A description of how the assumptions for and the calculations of TTC and ATC values change over different time (such as hourly, daily, and monthly) horizons. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-001-0 R1. | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 1205 | Specify the relationship of CBM to the generation reliability requirement and the allocation of the CBM values to the appropriate transmission facilities. The sum of the CBM values allocated to all interfaces shall not exceed that portion of the generation reliability requirement that is to be provided by outside resources. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-004-0 R1. | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 1269 | Short-term System Operator response (Operating Reserve actions not exceeding a 59-minute window). |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 13800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 1434 | Uses Special Protection System (SPS) models where currently existing or projected for implementation within the studied time horizon. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 11800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 1448 | Create a study report that describes the steps above that were undertaken (R2.1 - R2.7), including the contingencies and assumptions used, when determining the TTC and the results of the study. Where three phase fault damping is used to determine stability limits, that report shall also identify the percent used and include justification for use unless specified otherwise in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2010-02-08 |  | 2010-09-16 |  |  | MOD-029-1 R2. | 28000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 1743 | Any other schemes that are part of or impact the UFLS programs. |  | RRO | [14 empty] | RRO | [9 empty] | 2013-09-30 |  |  |  | 12800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 1787 | Identification of the Regional Reliability Organization group responsible for the Regional Reliability Organization’s review procedure and the process for Regional Reliability Organization approval of the procedure. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  | PRC-012-0 R1. | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 1836 | Monitored electrical quantities, such as voltage, current, etc. |  | GO, TO |  |  |  |  | GO | [17 empty] | 2007-06-18 |  | 2022-06-30 |  |  | PRC-018-1 R3. | 38000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 1881 | Set transmission line relays applied on the bulk system-end of transmission lines that serve load remote to the system so they do not operate at or below 115% of the maximum current flow from the system to the load under any system configuration. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  | PRC-023-1 R1. | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 2044 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 13800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 2065 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 13800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 2089 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 2114 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 13800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 2139 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 2164 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 13800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 2186 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  |  | 13800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 2315 | The Transmission Operator directs the Generator Operator to operate the synchronous generator, and the AVR is unavailable for service. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-06-27 |  | 2015-03-31 |  |  | VAR-002-WECC-1 R1. | 18000000 | WECC-US | [5 empty] | WECC-US
8. | 2329 | Due to component failure, the PSS may be out of service up to 60 consecutive days for repair per incident. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-06-27 |  | 2015-03-31 |  |  | VAR-501-WECC-1 R1. | 18000000 | WECC-US | [5 empty] | WECC-US
8. | 2449 | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2009-09-30 |  | 2010-07-14 |  |  | CIP-006-2 R1. | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 2580 | Operating Processes to restore Loads required to restore the System, such as station service for substations, units to be restarted or stabilized, the Load needed to stabilize generation and frequency, and provide voltage control. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | EOP-005-2 R1. | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 2625 | Identification of the Reliability Coordinator as the primary contact for disseminating information regarding restoration to neighboring Reliability Coordinators, and to Transmission Operators, and Balancing Authorities within its Reliability Coordinator Area. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  | EOP-006-2 R1. | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 2810 | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-03-31 |  | 2010-09-30 |  |  | CIP-006-3 R1. | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 2890 | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2010-07-14 |  |  | CIP-006-2b R1. | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 2911 | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | CIP-006-2c R1. | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 2931 | Cyber Assets used in the access control and monitoring of the Physical Security Perimeter(s) shall be afforded the protective measures specified in Standard CIP-003, Standard CIP-004 Requirement R3, Standard CIP-005 Requirements R2 and R3, Standard CIP-006 Requirement R2 and R3, Standard CIP-007, Standard CIP-008 and Standard CIP-009. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1b R1. | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 2960 | Cyber Assets used in the access control and monitoring of the Physical Security Perimeter(s) shall be afforded the protective measures specified in Standard CIP-003, Standard CIP-004 Requirement R3, Standard CIP-005 Requirements R2 and R3, Standard CIP-006 Requirement R2 and R3, Standard CIP-007, Standard CIP-008 and Standard CIP-009. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | CIP-006-1c R1. | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 2987 | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2011-05-19 |  | 2016-06-30 |  |  | CIP-006-3c R1. | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 3051 | Uses Special Protection System (SPS) models where currently existing or projected for implementation within the studied time horizon. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 11800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 3064 | Create a study report that describes the steps above that were undertaken (R2.1 - R2.7), including the contingencies and assumptions used, when determining the TTC and the results of the study. Where three phase fault damping is used to determine stability limits, that report shall also identify the percent used and include justification for use unless specified otherwise in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2010-09-16 |  | 2017-03-31 |  |  | MOD-029-1a R2. | 28000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 3299 | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2012-06-25 |  | 2014-02-03 |  |  | CIP-006-4c R1. | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 338 | Cyber Assets used in the access control and monitoring of the Physical Security Perimeter(s) shall be afforded the protective measures specified in Standard CIP-003, Standard CIP-004 Requirement R3, Standard CIP-005 Requirements R2 and R3, Standard CIP-006 Requirement R2 and R3, Standard CIP-007, Standard CIP-008 and Standard CIP-009. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-006-1 R1. | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 3429 | Planned generation dispatches. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  | IRO-005-2a R1. | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 3463 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 3487 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 13800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 3512 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 3537 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 3559 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 365 | Cyber Assets used in the access control and monitoring of the Physical Security Perimeter(s) shall be afforded the protective measures specified in Standard CIP-003, Standard CIP-004 Requirement R3, Standard CIP-005 Requirements R2 and R3, Standard CIP-006 Requirement R2 and R3, Standard CIP-007, Standard CIP-008 and Standard CIP-009. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1a R1. | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 3803 | Planned generation dispatches. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  | IRO-005-3 R1. | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 3899 | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2010-09-30 |  |  | CIP-006-2a R1. | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 3921 | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  | 2010-07-15 |  | 2011-05-18 |  |  | CIP-006-3a R1. | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 4038 | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-006-3d R1. | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 4060 | Annual review of the physical security plan. |  | BA, GO, GOP, IA, LSE, RC, RE, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC | RE |  |  |  |  | TO | TOP |  | TSP |  |  |  | 2013-03-21 |  |  | CIP-006-4d R1. | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 4179 | Planned generation dispatches. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  | IRO-005-3.1a R1. | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 4592 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 4635 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 4660 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 4683 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 4700 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 4730 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 4748 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 4759 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 5034 | Planned generation dispatches. |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 5126 | Requirements for periodic (at least every five years) updating, review, and approval of the Regional requirements. |  | RRO | [14 empty] | RRO | [9 empty] | 2007-01-01 |  |  |  | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 5668 | Planned generation dispatches. |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  |  | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 5822 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 5843 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 5868 | Include existing and planned facilities. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 5893 | Include the effects of existing and planned control devices. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 5906 | Identification of the Regional Reliability Organization group responsible for the Regional Reliability Organization’s review procedure and the process for Regional Reliability Organization approval of the procedure. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 6038 | Uses Remedial Action Scheme (RAS) models where currently existing or projected for implementation within the studied time horizon. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 11800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 605 | Interim provisions must be included if it is expected to take more than one hour to implement the contingency plan for loss of primary control facility. |  | BA, RC, TOP | BA | [10 empty] | RC | [6 empty] | TOP |  |  |  | 2007-06-18 |  | 2013-06-30 |  |  | EOP-008-0 R1. | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 6167 | Information protection (CIP-011); and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 6255 | Log (through automated means or by personnel who control entry) entry of each individual with authorized unescorted physical access into each Physical Security Perimeter, with information to identify the individual and date and time of entry. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 1.8 An example of evidence may include, but is not limited to, language in the physical security plan that describes logging and recording of physical entry into each Physical Security Perimeter and additional evidence to demonstrate that this logging has been implemented, such as logs of physical access into Physical Security Perimeters that show the individual and the date and time of entry into Physical Security Perimeter. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 628 | Insulation and insulation coordination. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 21800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 6450 | Interconnection reliability operations and coordination |  | RC | [11 empty] | RC | [10 empty] | 2012-10-01 |  | 2019-06-30 |  |  |  | 11800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 6660 | For short circuit analysis, if the short circuit current interrupting duty on circuit breakers determined in Requirement R2, Part 2.3 exceeds their Equipment Rating, the Planning Assessment shall include a Corrective Action Plan to address the Equipment Rating violations. The Corrective Action Plan shall: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2016-01-01 |  | 2023-06-30 |  |  |  | 28000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 6871 | Provisions for operator-controlled manual Load shedding that minimizes the overlap with automatic Load shedding and are capable of being implemented in a timeframe adequate for mitigating the Emergency; and |  | BA | BA | [21 empty] | 2017-04-01 | [5 empty] | 22800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 7216 | Response to Cyber Security Incidents; and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 7346 | Log (through automated means or by personnel who control entry) entry of each individual with authorized unescorted physical access into each Physical Security Perimeter, with information to identify the individual and date and time of entry. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.8. An example of evidence may include, but is not limited to, language in the physical security plan that describes logging and recording of physical entry into each Physical Security Perimeter and additional evidence to demonstrate that this logging has been implemented, such as logs of physical access into Physical Security Perimeters that show the individual and the date and time of entry into Physical Security Perimeter. | 2016-07-01 | [5 empty] | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 7439 | Monitored electrical quantities. |  | GO, RC, TO |  |  |  |  | GO | [6 empty] | RC | [10 empty] | 2011-10-20 |  | 2016-07-01 |  |  |  | 178000000 | NPCC-US |  | NPCC-US
8. | 7485 | Information protection (CIP-011); and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 7656 | Land ownership changes/Change in land use by the landowner |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:4.1.1. Applicable Transmission Owners4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.4.1.2. Applicable Generator Owners4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.2.1. Each overhead transmission line operated at 200kV or higher.4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:4.3.1.1. Operated at 200kV or higher; or4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 78000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 7674 | Create a study report that describes the steps above that were undertaken (R2.1 – R2.7), including the contingencies and assumptions used, when determining the TTC and the results of the study. Where three phase fault damping is used to determine stability limits, that report shall also identify the percent used and include justification for use unless specified otherwise in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2016-01-25 | [5 empty] | 28000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 7721 | The Transmission Operator directs the Generator Operator to operate the synchronous generator, and the AVR is unavailable for service. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2015-03-03 |  | 2018-09-05 |  |  |  | 18000000 | WECC-US | [5 empty] | WECC-US
8. | 7835 | Due to component failure, the PSS may be out of service up to 60 consecutive days for repair per incident. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-04-01 |  | 2017-06-30 |  |  |  | 18000000 | WECC-US | [5 empty] | WECC-US
8. | 7939 | Operating Processes to restore Loads required to restore the System, such as station service for substations, units to be restarted or stabilized, the Load needed to stabilize generation and frequency, and provide voltage control. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 18000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 7996 | Information protection (CIP-011); and |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 8255 | Market resources not committed to serving Load (uncommitted resources) within the Planning Coordinator area. |  | PCPA | [9 empty] | PA | [12 empty] | 2018-01-01 | [5 empty] | 14800000 | RF-US |  |  | RF-US
8. | 8404 | Interconnection reliability operations and coordination |  | RC | [11 empty] | RC | [10 empty] | 2019-07-01 | [5 empty] | 11800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 8481 | For short circuit analysis, if the short circuit current interrupting duty on circuit breakers determined in Requirement R2, Part 2.3 exceeds their Equipment Rating, the Planning Assessment shall include a Corrective Action Plan to address the Equipment Rating violations. The Corrective Action Plan shall: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-04-13 |  | 2020-06-10 |  |  |  | 28000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 8688 | Information protection (CIP-011); and |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | 9325 | For short circuit analysis, if the short circuit current interrupting duty on circuit breakers determined in Requirement R2, Part 2.3 exceeds their Equipment Rating, the Planning Assessment shall include a Corrective Action Plan to address the Equipment Rating violations. The Corrective Action Plan shall: |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 28000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8. | RP-2021-06-08-0000015 | Islanding schemes and the frequency and time delay at which they operate |  | DP, TO |  | DP | [22 empty] | 2013-11-07 |  |  |  | 50800000 | SPPRE-US
8. | RP-2021-06-24-0000077 | The Transmission Operator directs the Generator Operator to operate thesynchronous generator, and the AVR is unavailable for service. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-07-01 |  | 2015-03-31 |  |  |  | 10800000 | WECC-US | [5 empty] | WECC-US
8. | RP-2021-06-25-0000003 | The Transmission Operator directs the Generator Operator to operate the synchronous generator, and the AVR is unavailable for service. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2015-04-01 |  | 2018-09-05 |  |  |  | 10800000 | WECC-US | [5 empty] | WECC-US
8. | RP-2021-07-14-0000002 | Land ownership changes/Change in land use by the landowner |  | GO, TO |  |  |  |  | GO | [23 empty] | 70800000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8.1. | RP-2021-07-12-0000023 | List System deficiencies and the associated actions needed to achieve required System performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 28100000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
8.2. | RP-2021-07-12-0000024 | Be reviewed in subsequent annual Planning Assessments for continued validity and implementation status of identified System Facilities and Operating Procedures. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2020-06-10 | [5 empty] | 28200000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9 | 79780000339 | Process for ensuring that the physical security plan is reviewed at least annually. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  |  | 19000000 | NPCC-ON |  | NPCC-US
9 | 79780000366 | Process for ensuring that the physical security plan is reviewed at least annually. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 19000000 | NPCC-ON |  | NPCC-US
9 | 79780000629 | Voltage, Reactive Power, and power factor control. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 21900000 | NPCC-ON |  | NPCC-US
9 | 79780001005 | Planned transmission or generation outages. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  |  | 19000000 | NPCC-ON |  | NPCC-US
9 | 79780001032 | Planned transmission or generation outages. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  |  | 19000000 | NPCC-ON |  | NPCC-US
9 | 79780001059 | Planned transmission or generation outages. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  |  | 19000000 | NPCC-ON |  | NPCC-US
9 | 79780001148 | A description of the Regional Reliability Organization’s practice on the netting of transmission reservations for purposes of TTC and ATC determination. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 19000000 | NPCC-ON |  | NPCC-US
9 | 79780001206 | Describe the inclusion or exclusion rationale for the loads of each Load-Serving Entity, including interruptible demands and buy-through contracts (type of service contract that offers the customer the option to be interrupted or to accept a higher rate for service under certain conditions). |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  |  | 19000000 | NPCC-ON |  | NPCC-US
9 | 79780001435 | Models series compensation for each line at the expected operating level unless specified otherwise in the ATCID. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 11900000 | NPCC-ON |  | NPCC-US
9 | 79780001788 | Determination, as appropriate, of maintenance and testing requirements. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  |  | 19000000 | NPCC-ON |  | NPCC-US
9 | 79780001882 | Set transmission line relays applied on the load-end of transmission lines that serve load remote to the bulk system so they do not operate at or below 115% of the maximum current flow from the load to the system under any system configuration. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  |  | 19000000 | NPCC-ON |  | NPCC-US
9 | 79780002045 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 13900000 | NPCC-ON |  | NPCC-US
9 | 79780002066 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 13900000 | NPCC-ON |  | NPCC-US
9 | 79780002090 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13900000 | NPCC-ON |  | NPCC-US
9 | 79780002115 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 13900000 | NPCC-ON |  | NPCC-US
9 | 79780002140 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13900000 | NPCC-ON |  | NPCC-US
9 | 79780002165 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 13900000 | NPCC-ON |  | NPCC-US
9 | 79780002187 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  |  | 13900000 | NPCC-ON |  | NPCC-US
9 | 79780002581 | Operating Processes for transferring authority back to the Balancing Authority in accordance with the Reliability Coordinator’s criteria. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  |  | 19000000 | NPCC-ON |  | NPCC-US
9 | 79780002626 | Criteria for transferring operations and authority back to the Balancing Authority. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  |  | 19000000 | NPCC-ON |  | NPCC-US
9 | 79780002932 | Process for ensuring that the physical security plan is reviewed at least annually. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  |  | 19000000 | NPCC-ON |  | NPCC-US
9 | 79780002966 | Process for ensuring that the physical security plan is reviewed at least annually. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  |  | 19000000 | NPCC-ON |  | NPCC-US
9 | 79780003049 | Models series compensation for each line at the expected operating level unless specified otherwise in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 11900000 | NPCC-ON |  | NPCC-US
9 | 79780003430 | Planned transmission or generation outages. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  |  | 19000000 | NPCC-ON |  | NPCC-US
9 | 79780003464 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  | M1. The Planning Authority and Transmission Planner shall have a valid assessment and corrective&lt;br/&gt;plans as specified in Reliability Standard TPL-002-1_R1 and TPL-002-1_R2. |  |  | 2012-07-06 |  |  |  | 13900000 | NPCC-ON |  | NPCC-US
9 | 79780003488 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 13900000 | NPCC-ON |  | NPCC-US
9 | 79780003513 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13900000 | NPCC-ON |  | NPCC-US
9 | 79780003538 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13900000 | NPCC-ON |  | NPCC-US
9 | 79780003560 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13900000 | NPCC-ON |  | NPCC-US
9 | 79780003802 | Planned transmission or generation outages. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  |  | 19000000 | NPCC-ON |  | NPCC-US
9 | 79780004178 | Planned transmission or generation outages. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  |  | 19000000 | NPCC-ON |  | NPCC-US
9 | 79780004595 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13900000 | NPCC-ON |  | NPCC-US
9 | 79780004638 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13900000 | NPCC-ON |  | NPCC-US
9 | 79780004663 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13900000 | NPCC-ON |  | NPCC-US
9 | 79780004685 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13900000 | NPCC-ON |  | NPCC-US
9 | 79780004703 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13900000 | NPCC-ON |  | NPCC-US
9 | 79780004722 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13900000 | NPCC-ON |  | NPCC-US
9 | 79780004750 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13900000 | NPCC-ON |  | NPCC-US
9 | 79780004761 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13900000 | NPCC-ON |  | NPCC-US
9 | 79780005035 |  |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 19000000 | NPCC-ON |  | NPCC-US
9 | 79780005669 | Planned transmission or generation outages. |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  |  | 19000000 | NPCC-ON |  | NPCC-US
9 | 79780005823 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13900000 | NPCC-ON |  | NPCC-US
9 | 79780005844 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13900000 | NPCC-ON |  | NPCC-US
9 | 79780005869 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13900000 | NPCC-ON |  | NPCC-US
9 | 79780005894 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13900000 | NPCC-ON |  | NPCC-US
9 | 79780005907 | Determination, as appropriate, of maintenance and testing requirements. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 19000000 | NPCC-ON |  | NPCC-US
9 | 79780006039 | Models series compensation for each line at the expected operating level unless specified otherwise in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 11900000 | NPCC-ON |  | NPCC-US
9 | 79780006168 | Declaring and responding to CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 19000000 | NPCC-ON |  | NPCC-US
9 | 79780006256 | Retain physical access logs of entry of individuals with authorized unescorted physical access into each Physical Security Perimeter for at least ninety calendar days. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 1.9 An example of evidence may include, but is not limited to, dated documentation such as logs of physical access into Physical Security Perimeters that show the date and time of entry into Physical Security Perimeter. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 19000000 | NPCC-ON |  | NPCC-US
9 | 79780006285 | Cyber security risks associated with a BES Cyber System’s electronic interconnectivity and interoperability with other Cyber Assets. | [23 empty] | Examples of evidence may include, but are not limited to, training material such as power point presentations, instructor notes, student notes, handouts, or other training materials. |  |  | 2016-06-30 |  |  |  | 21900000 | NPCC-ON |  | NPCC-US
9 | 79780006872 | Reliability impacts of extreme weather conditions. |  | BA | BA | [21 empty] | 2017-04-01 | [5 empty] | 22900000 | NPCC-ON |  | NPCC-US
9 | 79780007217 | Cyber security risks associated with a BES Cyber System’s electronic interconnectivity and interoperability with other Cyber Assets, including Transient Cyber Assets, and with Removable Media. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.1. Balancing Authority&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: &lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. &lt;br/&gt; The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.&lt;br/&gt;4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21900000 | NPCC-ON |  | NPCC-US
9 | 79780007347 | Retain physical access logs of entry of individuals with authorized unescorted physical access into each Physical Security Perimeter for at least ninety calendar days. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.9. An example of evidence may include, but is not limited to, dated documentation such as logs of physical access into Physical Security Perimeters that show the date and time of entry into Physical Security Perimeter. | 2016-07-01 | [5 empty] | 19000000 | NPCC-ON |  | NPCC-US
9 | 79780007486 | Declaring and responding to CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: &lt;br/&gt;4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: &lt;br/&gt;4.2.1.1 Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: &lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: &lt;br/&gt;4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. &lt;br/&gt;4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11900000 | NPCC-ON |  | NPCC-US
9 | 79780007657 | Emerging technologies |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:&lt;br/&gt;4.1.1. Applicable Transmission Owners&lt;br/&gt;4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.&lt;br/&gt;4.1.2. Applicable Generator Owners&lt;br/&gt;4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. &lt;br/&gt;4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.2.1. Each overhead transmission line operated at 200kV or higher.&lt;br/&gt;4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.&lt;br/&gt;4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.&lt;br/&gt;4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. &lt;br/&gt;4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:&lt;br/&gt;4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:&lt;br/&gt;4.3.1.1. Operated at 200kV or higher; or&lt;br/&gt;4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or&lt;br/&gt;4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 79000000 | NPCC-ON |  | NPCC-US
9 | 79780007940 | Operating Processes for transferring operations back to the Balancing Authority in accordance with its Reliability Coordinator’s criteria. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 19000000 | NPCC-ON |  | NPCC-US
9 | 79780007997 | Declaring and responding to CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.&lt;br/&gt;4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.&lt;br/&gt;4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). &lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11900000 | NPCC-ON |  | NPCC-US
9 | 79780008689 | Declaring and responding to CIP Exceptional Circumstances. | [28 empty] | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:&lt;br/&gt;4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:&lt;br/&gt;4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service &lt;br/&gt;&lt;br/&gt;equipment owned by the Distribution Provider for the protection or restoration of the BES:&lt;br/&gt;4.2.1.1. Each UFLS or UVLS System that:&lt;br/&gt;4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and &lt;br/&gt;4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.&lt;br/&gt;4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.&lt;br/&gt;4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.&lt;br/&gt;4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:&lt;br/&gt;All BES Facilities.&lt;br/&gt;4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:&lt;br/&gt;4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.&lt;br/&gt;4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).&lt;br/&gt;4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.&lt;br/&gt;4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11900000 | NPCC-ON |  | NPCC-US
9. | 1005 | Planned transmission or generation outages. |  | RC | [11 empty] | RC | [10 empty] | 2007-06-18 |  | 2009-01-21 |  |  | IRO-005-1 R1. | 19000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 1032 | Planned transmission or generation outages. |  | RC | [11 empty] | RC | [10 empty] | 2009-01-22 |  | 2011-05-25 |  |  | IRO-005-2 R1. | 19000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 1059 | Planned transmission or generation outages. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2012-09-12 |  |  | IRO-005-3a R1. | 19000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 1148 | A description of the Regional Reliability Organization’s practice on the netting of transmission reservations for purposes of TTC and ATC determination. |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-001-0 R1. | 19000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 1206 | Describe the inclusion or exclusion rationale for the loads of each Load-Serving Entity, including interruptible demands and buy-through contracts (type of service contract that offers the customer the option to be interrupted or to accept a higher rate for service under certain conditions). |  | RRO | [14 empty] | RRO | [9 empty] | 2009-11-24 |  |  | MOD-004-0 R1. | 19000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 1435 | Models series compensation for each line at the expected operating level unless specified otherwise in the ATCID. |  | TOP | [18 empty] | TOP | [5 empty] | 2010-09-16 |  |  |  | 11900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 1788 | Determination, as appropriate, of maintenance and testing requirements. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2017-03-31 |  |  | PRC-012-0 R1. | 19000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 1882 | Set transmission line relays applied on the load-end of transmission lines that serve load remote to the bulk system so they do not operate at or below 115% of the maximum current flow from the load to the system under any system configuration. |  | DP, GO, TO |  | DP |  |  | GO | [17 empty] | 2010-07-01 |  | 2012-06-30 |  |  | PRC-023-1 R1. | 19000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 2045 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2009-05-12 |  |  |  | 13900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 2066 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2009-05-13 |  | 2015-12-31 |  |  |  | 13900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 2090 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 2115 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2011-10-23 |  |  |  | 13900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 2140 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2010-04-22 |  |  |  | 13900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 2165 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2010-04-23 |  | 2013-06-19 |  |  |  | 13900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 2187 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2007-06-18 |  | 2013-06-19 |  |  |  | 13900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 2316 | The Reliability Coordinator directs Transmission Operator to operate the synchronous condenser, and the AVR is unavailable for service. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2011-06-27 |  | 2015-03-31 |  |  | VAR-002-WECC-1 R1. | 19000000 | WECC-US | [5 empty] | WECC-US
9. | 2330 | Due to a component failure, the PSS may be out of service up to one year provided the Generator Operator submits documentation identifying the need for time to obtain replacement parts and if required to schedule an outage. |  | GOP | [5 empty] | GOP | [16 empty] | 2011-06-27 |  | 2015-03-31 |  |  | VAR-501-WECC-1 R1. | 19000000 | WECC-US | [5 empty] | WECC-US
9. | 2581 | Operating Processes for transferring authority back to the Balancing Authority in accordance with the Reliability Coordinator’s criteria. |  | TOP | [18 empty] | TOP |  |  |  | 2011-05-23 |  | 2019-03-31 |  |  | EOP-005-2 R1. | 19000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 2626 | Criteria for transferring operations and authority back to the Balancing Authority. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2019-03-31 |  |  | EOP-006-2 R1. | 19000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 2932 | Process for ensuring that the physical security plan is reviewed at least annually. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1b R1. | 19000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 2966 | Process for ensuring that the physical security plan is reviewed at least annually. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2010-04-20 |  |  | CIP-006-1c R1. | 19000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 3049 | Models series compensation for each line at the expected operating level unless specified otherwise in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2011-04-01 |  | 2017-03-31 |  |  |  | 11900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 339 | Process for ensuring that the physical security plan is reviewed at least annually. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  | 2008-07-01 |  | 2010-03-31 |  |  | CIP-006-1 R1. | 19000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 3430 | Planned transmission or generation outages. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-26 |  | 2011-09-30 |  |  | IRO-005-2a R1. | 19000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 3464 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  | M1. The Planning Authority and Transmission Planner shall have a valid assessment and correctiveplans as specified in Reliability Standard TPL-002-1_R1 and TPL-002-1_R2. |  |  | 2012-07-06 |  |  |  | 13900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 3488 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2011-10-24 |  | 2015-12-31 |  |  |  | 13900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 3513 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 3538 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 3560 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2012-07-06 |  |  |  | 13900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 366 | Process for ensuring that the physical security plan is reviewed at least annually. |  | BA, GO, GOP, IA, LSE, RC, RRO, TO, TOP, TSP | BA |  |  |  | GO | GOP | IA | LSE |  |  |  | RC |  |  | RRO |  |  | TO | TOP |  | TSP |  |  |  | 2009-12-22 |  |  | CIP-006-1a R1. | 19000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 3802 | Planned transmission or generation outages. |  | RC | [11 empty] | RC | [10 empty] | 2011-05-23 |  | 2011-05-25 |  |  | IRO-005-3 R1. | 19000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 4178 | Planned transmission or generation outages. |  | RC | [11 empty] | RC | [10 empty] | 2012-09-13 |  | 2017-03-31 |  |  | IRO-005-3.1a R1. | 19000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 4595 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 4638 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 4663 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 4685 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2014-12-31 |  |  |  | 13900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 4703 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 4722 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 4750 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  | 2013-06-20 |  | 2015-12-31 |  |  |  | 13900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 4761 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2013-12-23 |  |  |  | 13900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 5035 | Planned transmission or generation outages. |  | RC | [11 empty] | RC | [12 empty] | 2006-11-01 |  |  |  | 19000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 5669 | Planned transmission or generation outages. |  | RC | [11 empty] | RC | [12 empty] | 2014-11-13 |  |  |  | 19000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 5823 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 5844 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet system performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 5869 | Include Reactive Power resources to ensure that adequate reactive resources are available to meet System performance. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 5894 | Include the planned (including maintenance) outage of any bulk electric equipment (including protection systems or their components) at those demand levels for which planned (including maintenance) outages are performed. |  | PCPA, TP | [9 empty] | PA | [9 empty] | TP |  |  |  |  | 2015-12-31 |  |  |  | 13900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 5907 | Determination, as appropriate, of maintenance and testing requirements. |  | RRO | [14 empty] | RRO | [8 empty] | X | 2020-12-31 |  |  |  | 19000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 6039 | Models series compensation for each line at the expected operating level unless specified otherwise in the ATCID. |  | TOP | [18 empty] | TOP |  |  |  | 2017-04-01 | [5 empty] | 11900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 6168 | Declaring and responding to CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2014-02-03 |  | 2016-06-30 |  |  |  | 19000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 6256 | Retain physical access logs of entry of individuals with authorized unescorted physical access into each Physical Security Perimeter for at least ninety calendar days. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | 1.9 An example of evidence may include, but is not limited to, dated documentation such as logs of physical access into Physical Security Perimeters that show the date and time of entry into Physical Security Perimeter. | 2014-02-03 |  | 2016-06-30 |  | 4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each Special Protection System or Remedial Action Scheme where the Special Protection System or Remedial Action Scheme is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-006-5: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters. 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5 Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5 identification and categorization processes. |  | 19000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 629 | Voltage, Reactive Power, and power factor control. |  | TO | [22 empty] | 2007-06-18 |  | 2013-11-24 |  |  |  | 21900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 6872 | Reliability impacts of extreme weather conditions. |  | BA | BA | [21 empty] | 2017-04-01 | [5 empty] | 22900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 7217 | Cyber security risks associated with a BES Cyber System’s electronic interconnectivity and interoperability with other Cyber Assets, including Transient Cyber Assets, and with Removable Media. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  |  |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.1. Balancing Authority4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-004-6: 4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above.4.2.3.5. Responsible Entities that identify that they have no BES Cyber Systems categorized as high impact or medium impact according to the CIP-002-5.1 identification and categorization processes. |  | 21900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 7347 | Retain physical access logs of entry of individuals with authorized unescorted physical access into each Physical Security Perimeter for at least ninety calendar days. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  | M1.9. An example of evidence may include, but is not limited to, dated documentation such as logs of physical access into Physical Security Perimeters that show the date and time of entry into Physical Security Perimeter. | 2016-07-01 | [5 empty] | 19000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 7486 | Declaring and responding to CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2016-07-01 |  | 2019-12-31 |  | 1.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2 Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES: 4.1.2.1 Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2 Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1 Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES: 4.2.1.1 Each UFLS or UVLS System that:4.2.1.1.1 is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2 performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2 Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3 Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4 Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2 Responsible Entities listed in 4.1 other than Distribution Providers: All BES Facilities.4.2.3 Exemptions: The following are exempt from Standard CIP-003-6: 4.2.3.1 Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission. 4.2.3.2 Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3 The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4 For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 7657 | Emerging technologies |  | GO, TO |  |  |  |  | GO | [17 empty] | 2016-04-26 |  |  |  | 4.1. Functional Entities:4.1.1. Applicable Transmission Owners4.1.1.1. Transmission Owners that own Transmission Facilities defined in 4.2.4.1.2. Applicable Generator Owners4.1.2.1. Generator Owners that own generation Facilities defined in 4.3. 4.2. Transmission Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.2.1. Each overhead transmission line operated at 200kV or higher.4.2.2. Each overhead transmission line operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator.4.2.3. Each overhead transmission line operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC.4.2.4. Each overhead transmission line identified above (4.2.1. through 4.2.3.) located outside the fenced area of the switchyard, station or substation and any portion of the span of the transmission line that is crossing the substation fence. 4.3. Generation Facilities: Defined below (referred to as “applicable lines”), including but not limited to those that cross lands owned by federal , state, provincial, public, private, or tribal entities:4.3.1. Overhead transmission lines that (1) extend greater than one mile or 1.609 kilometers beyond the fenced area of the generating station switchyard to the point of interconnection with a Transmission Owner’s Facility or (2) do not have a clear line of sight from the generating station switchyard fence to the point of interconnection with a Transmission Owner’s Facility and are:4.3.1.1. Operated at 200kV or higher; or4.3.1.2. Operated below 200kV identified as an element of an IROL under NERC Standard FAC-014 by the Planning Coordinator; or4.3.1.3. Operated below 200 kV identified as an element of a Major WECC Transfer Path in the Bulk Electric System by WECC. |  | 79000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 7722 | The Reliability Coordinator directs Transmission Operator to operate the synchronous condenser, and the AVR is unavailable for service. |  | GOP, TOP | [5 empty] | GOP | [12 empty] | TOP |  |  |  | 2015-03-03 |  | 2018-09-05 |  |  |  | 19000000 | WECC-US | [5 empty] | WECC-US
9. | 7836 | Due to a component failure, the PSS may be out of service up to one year provided the Generator Operator submits documentation identifying the need for time to obtain replacement parts and if required to schedule an outage. |  | GOP | [5 empty] | GOP | [16 empty] | 2015-04-01 |  | 2017-06-30 |  |  |  | 19000000 | WECC-US | [5 empty] | WECC-US
9. | 7940 | Operating Processes for transferring operations back to the Balancing Authority in accordance with its Reliability Coordinator’s criteria. |  | TOP | [18 empty] | TOP |  |  |  | 2018-03-26 | [5 empty] | 19000000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 7997 | Declaring and responding to CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, IA, RC, TO, TOP | BA | DP |  |  | GO | GOP | IA |  |  |  |  | RC | [5 empty] | TO | TOP |  |  |  | 2020-01-01 |  | 2020-03-31 |  | 4.1. Functional Entities: For the purpose of the requirements contained herein, the following list of functional entities will be collectively referred to as “Responsible Entities.” For requirements in this standard where a specific functional entity or subset of functional entities are the applicable entity or entities, the functional entity or entities are specified explicitly.4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Special Protection System (SPS) or Remedial Action Scheme (RAS) where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2. Facilities: For the purpose of the requirements contained herein, the following Facilities, systems, and equipment owned by each Responsible Entity in Section 4.1 above are those to which these requirements are applicable. For requirements in this standard where a specific type of Facilities, system, or equipment or subset of Facilities, systems, and equipment are applicable, these are specified explicitly.4.2.1. Distribution Provider: One or more of the following Facilities, systems and equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each SPS or RAS where the SPS or RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-7:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs). 4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | 8689 | Declaring and responding to CIP Exceptional Circumstances. |  | BA, DP, GO, GOP, RC, TO, TOP | BA | DP |  |  | GO | GOP | [5 empty] | RC | [5 empty] | TO | TOP |  |  |  | 2020-04-01 |  |  |  | 4.1.2. Distribution Provider that owns one or more of the following Facilities, systems, and equipment for the protection or restoration of the BES:4.1.2.1. Each underfrequency Load shedding (UFLS) or undervoltage Load shedding (UVLS) system that:4.1.2.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.1.2.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.1.2.2. Each Remedial Action Scheme (RAS) where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.1.2.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service equipment owned by the Distribution Provider for the protection or restoration of the BES:4.2.1.1. Each UFLS or UVLS System that:4.2.1.1.1. is part of a Load shedding program that is subject to one or more requirements in a NERC or Regional Reliability Standard; and 4.2.1.1.2. performs automatic Load shedding under a common control system owned by the Responsible Entity, without human operator initiation, of 300 MW or more.4.2.1.2. Each RAS where the RAS is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.3. Each Protection System (excluding UFLS and UVLS) that applies to Transmission where the Protection System is subject to one or more requirements in a NERC or Regional Reliability Standard.4.2.1.4. Each Cranking Path and group of Elements meeting the initial switching requirements from a Blackstart Resource up to and including the first interconnection point of the starting station service of the next generation unit(s) to be started.4.2.2. Responsible Entities listed in 4.1 other than Distribution Providers:All BES Facilities.4.2.3. Exemptions: The following are exempt from Standard CIP-003-8:4.2.3.1. Cyber Assets at Facilities regulated by the Canadian Nuclear Safety Commission.4.2.3.2. Cyber Assets associated with communication networks and data communication links between discrete Electronic Security Perimeters (ESPs).4.2.3.3. The systems, structures, and components that are regulated by the Nuclear Regulatory Commission under a cyber security plan pursuant to 10 C.F.R. Section 73.54.4.2.3.4. For Distribution Providers, the systems and equipment that are not included in section 4.2.1 above. |  | 11900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US
9. | RP-2021-07-14-0000003 | Emerging technologies |  | GO, TO |  |  |  |  | GO | [23 empty] | 70900000 | MRO-US, NPCC-US, RF-US, SERC-US, TXRE-US, WECC-US | MRO-US | NPCC-US | RF-US | SERC-US | TXRE-US | WECC-US