## Data Entry
Balancing Authority | BA_1 |  | NERC FRS FORM 1 | [7 empty] | Enter Addition Data in columns O, P, and Q ==> |  | Information |  | Select Reason(s) for adjustment
Date/Time |  | BA | BA | Point "A" Information |  | Point "B" Information |  | SEFRD | Exclude for |  | Enter Data in Green Highlighted Cells |  | Point "A" | Point "B"
(Central Prevailing) | DelFreq | Time | DelFreq | NAI | Adjustment | NAI | Adjustment | (MW/0.1Hz) | data error * | 0.8 | Send copy to: | Chris.Scheetz@nerc.net | Load | Load | Reason(s)
2008-12-20 12:12 | -0.057761 | 12:12 | -0.057761 | -116.9972 | 0 | -93.7505 | 0 | -40.2466 | N | 23.2467 |  |  | 2869.1148 | 2861.1832 |  | -0.057761 | 23.2467 | Dynamic schedules for joint-owned units (DS)
2008-12-27 14:18 | -0.066093 | 14:18 | -0.066093 | -138.4941 | 0 | -110.7924 | 0 | -41.9129 | N | 27.7016 |  |  | 2553.6094 | 2576.9186 |  | -0.066093 | 27.7016 | Nonconforming load (NL)
2009-01-05 09:26 | -0.04024 | 9:26 | -0.04024 | -99.1958 | 0 | -88.5325 | 0 | -26.4992 | N | 10.6632 |  |  | 2838.7101 | 2857.8081 |  | -0.04024 | 10.6632 | Pumped hydro (PH)
2009-01-27 00:39 | -0.052525 | 0:39 | -0.052525 | -94.4203 | 0 | -13.7594 | 0 | -153.5669 | N | 80.6609 | 2010 | Bias Calculation Form Year | 2524.6843 | 2522.2965 |  | -0.052525 | 80.6609 | Ramping units (RU)
2009-02-01 18:59 | -0.070905 | 18:59 | -0.070905 | 62.2889 | 0 | 35.3913 | 0 | 37.9346 | N | -26.8976 | Eastern | Interconnection | 2628.5782 | 2642.9118 |  | -0.070905 | -26.8976 | Xfred Frequency Response (TFR)
2009-02-19 04:59 | -0.051907 | 4:59 | -0.051907 | 10.1628 | 0 | 20.1183 | 0 | -19.1795 | N | 9.9554 | BA_1 | Balancing Authority | 2295.6685 | 2283.7382 |  | -0.051907 | 9.9554 | Contingent BA adjustment for loss of units (CBA)
2009-03-24 21:27 | -0.058048 | 21:27 | -0.058048 | -164.4543 | 0 | -161.0872 | 0 | -5.8004 | N | 3.367 |  | Contact Name | 2438.2312 | 2465.2617 |  | -0.058048 | 3.367 | DS & NL
2009-03-26 03:51 | -0.075572 | 3:51 | -0.075572 | -167.5841 | 0 | -131.2497 | 0 | -48.0789 | N | 36.3344 |  | Contact Phone # | 2198.7744 | 2193.6265 |  | -0.075572 | 36.3344 | DS & PH
2009-04-01 17:05 | -0.05638 | 17:05 | -0.05638 | -185.2358 | 0 | -184.7476 | 0 | -0.866 | N | 0.48825 |  | Contact e-mail | 2447.8687 | 2436.4141 |  | -0.05638 | 0.48825 | DS & RU
2009-04-02 17:09 | -0.057333 | 17:09 | -0.057333 | -124.8163 | 0 | -122.0583 | 0 | -4.8106 | N | 2.758 | 3241 | Current Year's Actual Peak | 2273.1077 | 2269.4618 |  | -0.057333 | 2.758 | DS & TFR
2009-05-03 10:05 | -0.051761 | 10:05 | -0.051761 | -19.8886 | 0 | -6.2452 | 0 | -26.3585 | N | 13.6434 | 3882 | Internal Generating Capacity | 2010.725 | 2012.6499 |  | -0.051761 | 13.6434 | DS & CBA
2009-05-21 16:36 | -0.049999 | 16:36 | -0.049999 | -2.3187 | 0 | 8.7821 | 0 | -22.2018 | N | 11.1007 | 3242 | Next Year's Projected Peak | 2154.862 | 2155.396 |  | -0.049999 | 11.1007 | DS & NL & PH
2009-06-21 16:50 | -0.052 | 16:50 | -0.052 | 7.8209 | 0 | -12.0859 | 0 | 38.2824 | N | -19.9068 |  |  | 2104.4578 | 2103.3636 |  | -0.052 | -19.9068 | DS & NL & RU
2009-06-25 13:52 | -0.056 | 13:52 | -0.056 | 33.3936 | 0 | 45.7191 | 0 | -22.0099 | N | 12.3255 |  |  | 2505.8354 | 2505.2111 |  | -0.056 | 12.3255 | JOU DS & NL & TFR
2009-07-06 13:36 | -0.058498 | 13:36 | -0.058498 | 30.9075 | 0 | 31.6577 | 0 | -1.2824 | N | 0.75019 | 2009 | Current year | 2382.0347 | 2383.3364 |  | -0.058498 | 0.75019 | DS & NL & CBA
2009-07-26 14:06 | -0.0485 | 14:06 | -0.0485 | -51.5962 | 0 | -49.3661 | 0 | -4.5981 | N | 2.2301 | -15.8 | 2009 Frequency Response Obligation (FRO) | 2180.7638 | 2178.8078 |  | -0.0485 | 2.2301 | DS & NL & PH & RU
2009-08-04 19:48 | -0.045 | 19:48 | -0.045 | 0.22308 | 0 | 9.7009 | 0 | -21.0619 | N | 9.4779 |  |  | 2035.807 | 2035.5427 |  | -0.045 | 9.4779 | DS & NL & PH & TFR
2009-08-15 16:07 | -0.037502 | 16:07 | -0.037502 | 22.0437 | 0 | 22.399 | 0 | -0.94743 | N | 0.35531 | Summary Statistics |  | 2103.3326 | 2100.3692 |  | -0.037502 | 0.35531 | DS & NL & PH & CBA
2009-09-12 13:30 | -0.047501 | 13:30 | -0.047501 | -49.2669 | 0 | -47.0962 | 0 | -4.5698 | N | 2.1707 | -24.4587 | Average Frequency Response (MW/0.1Hz) | 2101.7279 | 2098.1863 |  | -0.047501 | 2.1707 | DS & NL & PH & RU & TFR
2009-09-29 11:16 | -0.0555 | 11:16 | -0.0555 | -13.3053 | 0 | 16.0767 | 0 | -52.9406 | N | 29.3821 |  |  | 2144.0105 | 2106.1429 |  | -0.0555 | 29.3821 | DS & NL & PH & RU & CBA
2009-10-19 09:46 | -0.047 | 9:46 | -0.047 | -103.5872 | 0 | -98.9858 | 0 | -9.7902 | N | 4.6014 | -33.7706 | Regression Estimate of Frequency Response (MW/0.1Hz) | 2376.8797 | 2372.8042 |  | -0.047 | 4.6014 | DS & NL & PH & RU & TFR & CBA
2009-10-26 14:54 | -0.06 | 14:54 | -0.06 | -4.1106 | 0 | -2.5171 | 0 | -2.6559 | N | 1.5935 |  |  | 2319.6964 | 2322.4229 |  | -0.06 | 1.5935 | NL & PH
| -0.06 | 21:40 | -0.06 | -154.4944 | 0 | -102.1235 | 0 | -87.2848 | N | 52.3709 |  |  | 2442.348 | 2488.226 |  | -0.06 | 52.3709 | NL & RU
2009-11-03 19:42 | -0.051 | 19:42 | -0.051 | -1.7817 | 0 | 32.1662 | 0 | -66.5645 | N | 33.9479 |  |  | 2550.655 | 2549.1314 |  | -0.051 | 33.9479 | NL & TFR
[5 empty] | 0 |  | 0 |  | N | [6 empty] | -0.1 | 100 | NL & CBA
[5 empty] | 0 |  | 0 |  | N | [8 empty] | NL & PH & RU
[5 empty] | 0 |  | 0 |  | N |  |  | Next Year's | [5 empty] | NL & PH & TFR
[5 empty] | 0 |  | 0 |  | N |  | -15.8 | 2010 Frequency Response Obligation (FRO) | [5 empty] | NL & PH & BAA
[5 empty] | 0 |  | 0 |  | N |  | -28.496 | 2010 Frequency Bias Setting - (minimum of FRM, next year's FRO, or 0.8% of Projected Peak [Load + Gen]/2) | [5 empty] | NL & PH & RU & TFR
[5 empty] | 0 |  | 0 |  | N | [7 empty] | N | NL & PH & RU & CBA
[5 empty] | 0 |  | 0 |  | N |  | -20.1207 | 2009 FRM - Median Frequency Response (MW/0.1Hz) |  |  |  |  | Y | NL & PH & RU & TFR & CBA
[5 empty] | 0 |  | 0 |  | N | [8 empty] | PH & RU
[5 empty] | 0 |  | 0 |  | N | [8 empty] | PH & TFR
[5 empty] | 0 |  | 0 |  | N | [8 empty] | PH & CBA
[5 empty] | 0 |  | 0 |  | N | [8 empty] | PH & RU & TFR
[5 empty] | 0 |  | 0 |  | N | [8 empty] | PH & RU & CBA
PH & RU & TFR & CBA
|  |  |  | Modified Heading for Single BA Interconnection | [13 empty] | RU & TFR
A | B | C | D | E | F | G | H | I | J | K | [7 empty] | RU & CBA
RU & TFR & CBA
A: Date/Time; Modified Heading for Single BA Interconnection E: Contingency; Modified Heading for Single BA Interconnection F: Point A; Modified Heading for Single BA Interconnection H: Point B; Modified Heading for Single BA Interconnection I: SEFRD | [7 empty] | TFR & CBA
(Central Prevailing) | DelFreq |  |  | MW | Adjustment |  | Adjustment | (MW/0.1Hz)
2008-12-15 15:18 | -0.1 |  |  | 600 |  |  |  | -600

## Adjustments
Balancing Authority | BA_1 | JOU Dynamic Schedules |  | Non conforming Load |  | Pumped Hydro |  | Ramping Units |  | Transferred Frequency Response | Contingent BA Adjustment |  | Net Total Adjustments
Date/Time |  | Point A | Point B | Point A | Point B | Point A | Point B | Point A | Point B | Point B | Point A | Point B
(Central Prevailing) | DelFreq | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment (MW/0.1Hz) | Adjustment | Adjustment
2008-12-20 12:12 | -0.057761 | [11 empty] | 0
2008-12-27 14:18 | -0.066093 | [11 empty] | 0
2009-01-05 09:26 | -0.04024 | [11 empty] | 0
2009-01-27 00:39 | -0.052525 | [11 empty] | 0
2009-02-01 18:59 | -0.070905 | [11 empty] | 0
2009-02-19 04:59 | -0.051907 | [11 empty] | 0
2009-03-24 21:27 | -0.058048 | [11 empty] | 0
2009-03-26 03:51 | -0.075572 | [11 empty] | 0
2009-04-01 17:05 | -0.05638 | [11 empty] | 0
2009-04-02 17:09 | -0.057333 | [11 empty] | 0
2009-05-03 10:05 | -0.051761 | [11 empty] | 0
2009-05-21 16:36 | -0.049999 | [11 empty] | 0
2009-06-21 16:50 | -0.052 | [11 empty] | 0
2009-06-25 13:52 | -0.056 | [11 empty] | 0
2009-07-06 13:36 | -0.058498 | [11 empty] | 0
2009-07-26 14:06 | -0.0485 | [11 empty] | 0
2009-08-04 19:48 | -0.045 | [11 empty] | 0
2009-08-15 16:07 | -0.037502 | [11 empty] | 0
2009-09-12 13:30 | -0.047501 | [11 empty] | 0
2009-09-29 11:16 | -0.0555 | [11 empty] | 0
2009-10-19 09:46 | -0.047 | [11 empty] | 0
2009-10-26 14:54 | -0.06 | [11 empty] | 0
| -0.06 | [11 empty] | 0
2009-11-03 19:42 | -0.051 | [11 empty] | 0
Sign Convention for data entry |  | Imports: MWs are - Exports: MWs are + |  | Loads in MW as - |  | Load MW as - Generation MW as + |  | Enter Gen MW as + |  | The transactional amount in MW/0.1 Hz Receiver enters - Deliverer enters + (The calculation will convert MW/0.1Hz to MW for the observed frequency deviation) | Generation MW as + (If load occurs due to gen loss, enter MW as - at point B)
Notes:
1) | Balancing Authorities making adjustments must retain evidence to verify: - Adjustment values are determined from scan-cycle data using Point A and Point B averaging periods. Scan-cycle data must be available if adjustments are made. - Adjustment values must be rounded to the nearest MW. - Adjustments are necessary to improve accuracy of calculations compared to using Net Actual Interchange (contingency size for single BA interconnections) solely. Said differently, unless an adjustment compensates for significant known error, it should not be made. However, as noted in the next item, once a decision to include an adjustment for one or more of the six types is made for one event, the entity must calculate adjustments for that (those) type(s) for all events. - Adjustments are included consistently for all events (e.g. if adjustments for nonconforming load are made for one event, the load must be included for all events, etc.).
2) | Dynamic Schedules: - Values use schedule sign convention. - Adjustments should include only dynamic schedules accounting for joint-owned units. Other dynamic schedules should be ignored.
3) | Nonconforming Loads: - Values must be entered as negative numbers.
4) | Pumped Hydro: - Values for pumping must be entered as negative values. - Values for generating must be entered as positive values.
5) | Rampling Units: - Values are entered as positive values.
6) | Transferred Frequency Response: - This value is the amount agreed upon between the entities expressed in MW/0.1 Hz. The spreadsheet will adjust this amount for the frequency deviation experienced. (e.g. if an entity agrees to provide 20 MW/0.1 Hz to another entity and a frequency event with a deviation of 50 mHz occurs, the delivering entity should enter +20 in the adjustment column and the receiving entity should enter - 20. The spreadsheet will adjust the SEFRD for each entity by the 10 for this event.) - Values for the entity receiving the response must be entered as a negative number. - Values for the entity delivering the response must be entered as a positive number. - Values between entities must sum to zero.
7) | Contingent Balancing Authority Adjustment: - Value for Point A is the pre-contingency generation from the contingent unit(s). - Value for Point B is usually 0 MW, but may be the load that remains on the system that was "netted" out by the now offline generation.

## Variable Bias Supplemental Info
Month | Minimum FBS* for month | Maximum FBS* for month | Time weighted ** average FBS* for month
January |  |  | -10
Feburary |  |  | -7
March |  |  | -12
April |  |  | -8
May |  |  | -27
June |  |  | -8.7
July |  |  | -8
August |  |  | -8
September |  |  | -8.2
October |  |  | -8
November |  |  | -8
December |  |  | -12
|  |  | -10.4107 | Average Annual Bias
* Frequency Bias Setting (FBS)
** Based on the one minute values used in BAL 001