## Instructions
The DMSDT developed this Excel Workbook is designed to assist Transmission Owners in using the Median Method
for determining monitoring bus locations for Fault Recording and Sequence of Events Recording on their individual systems.
Instructions for use: |  | 2013-08-14 | Version 3
For Transmission Owners Only:
1 | Organize your short circuit data in the format shown on the Data Input worksheet
2 | Your short circuit data should use three phase short circuit with your selected pre-fault voltage
3 | Your short circuit data should be ordered from highest three phase short circuit MVA value to lowest three phase short circuit MVA value for all buses greater than 100 kV
4 | Your short circuit data should either eliminate or commonly identify non-real buses, zero buses, pseudo buses, or buses which are used for modeling purposes only, by using a common designation for all these type buses that can be eliminated from the Median calculation. It is most common to identify these non-real buses with the number "0" in the bus coded number field.
5 | The Data Input Worksheet is designed to have you copy your properly formatted and sorted three phase MVA short circuit data into rows starting at column A row 6 of the worksheet.
6 | Data Input, Col. F, is the most important column, it must have the three phase MVA short circuit data values, sorted from highest MVA to lowest MVA. The MVA values in column F, as sorted from highest to lowest MVA, should include all voltage levels greater than or equal to 100 kV.
7 | Once you input all of your short circuit data into the Data Input worksheet starting at Column A Row 6, the values in cells B2, B3 and B4 should all be equal. These values should equal the number of rows of short circuit data that you have input. Copy Cell B2 using Cntrl C, then Paste Value, Special value only, back into Cell B2. This should be the total number of rows contained in the data set.
8 | If you have zero numbered buses, or pseudo buses, commonly identified by say a number 0 in the bus coded number column, then you need to determine the number of zero numbered buses that are included in this data set.
9 | For you to be able to determine this zero bus coded number, you need to select your entire data set, including the header row, from column / row A5 to G___(last row of data). As an example, if your data contains 100 rows, then your highlighted area for sorting and filtering should be A5 to G105. Then using the sort filter command, turn on Filter
10 | Once the Filter is on, go to the bus coded number column, pull down the Filter and select only the zero bus coded number rows. The values in cells B3, and B4 should now be equal and indicate the number of zero numbered buses in your data set.
11 | We want to store the zero numbered bus rows (number) into cell B4 as a value. To do this, select Cell B4, hit Cntrl C, then hit paste special, value only. This now repalces the formula in Cell B4 with the value of zero buses in the data set.
12 | Now we wish to eliminate the zero bus rows from the rest of our data processing, so in the bus coded number column, we want to filter out the zero bus rows, so we reverse the pull down selection by selecting all rows, except the zero bus coded numbered rows. Leave this Filter in place for the rest of the Median method process.
13 | If Cell B4 contains the number zero, then Cell F2 should now contain the 6th value down from the highest short circuit MVA value, and Cell G2 should contain 20% of the Cell F2 value. If Cell F2's value is greater than 1500 MVA this is the new lowest MVA value to be used to determine the number of Median selected buses. If the value in F2 is less than 1500 MVA, then we will use 1500 MVA as the lowest value to select the number of Median buses.
14 | If Cell B4 contains a value greater than zero, then Cell F2 needs to be replaced with the MVA value contained in the 11th row, column F of the filtered data set. If the value in F2 is less than 1500 MVA then we will use 1500 MVA as the lowest value to select the number of Median buses.
15 | With the Filter still applied to our data set, and zero buses deselected, we will need to use the F2 value to apply as the value used for the MVA column pull down.
16 | Using Column F, MVA value pull down, use the Number Filter function, greater than or equal to the F2 value. With this Filter F2 number value applied, now Cntrl C Cell C2, and replace C2 with paste special, value only. This now is the number of buses selected by the Median method.
17 | You are Finished!!! The number in Cell C2 indicates the number of Median method selected buses, D2 contains the number of total FR and SOER locations, E2 shows the number of FR / SOER for the Top 10% buses and F2 shows the number of FR / SOER for the Distributed 10% buses.
Notes: | Example 1 (Ex 1 without zero buses) is an additional worksheet shown for a system that does not contains any zero buses. All zero bus entries have been eliminated from the data set.
Notes: | Example 2 (Ex 2 with zero buses) is an additional worksheet shown for a system that contains zero buses. Note for a system that contains zero buses, you must observe the row 11, column F MVA value, and place it into Cell F2. In example 2, this MVA value is equal to 5685 MVA, based on the data set provided.

## Data Input
Transmission Owner Name | Total Bus Count | Total DFR bus count | Top 10% Bus Count | 10% Distributed Bus Count | Median MVA (6th Bus from Top) | New Lowest Median Calc. MVA (20% of Median Value)
Base Values | 0 | 1 | 1 | 0 | 0 | 1500
Median Method | 0 | 1 | 1 | 0 |  | 1500
Zero Busses | 0 | 0 | 0 | 0
Bus Coded Number | NCR-ID Number | Region | Bus kV (L-L) | Bus 3 Phase Fault--Current (amps) | Bus 3 Phase Fault MVA

## Ex 1 without zero buses
Transmission Owner Name | Total Bus Count | Total DFR bus count | Top 10% Bus Count | 10% Distributed Bus Count | Median MVA (6th Bus from Top) | New Lowest Median Calc. MVA (20% of Median Value)
Base Values | 96 | 20 | 10 | 10 | 5685.0827 | 1500
Median Method | 64 | 13 | 7 | 6 |  | 1500
Zero Busses | 0 | 0 | 0 | 0
Bus Coded Number | NCR-ID Number | Region | Bus kV (L-L) | Bus 3 Phase Fault--Current (amps) | Bus 3 Phase Fault MVA
19 | NCR ID# | FRCC | 230 | 31119.8 | 12397.2472
319 | NCR ID# | FRCC | 230 | 23086.6 | 9197.0478
52 | NCR ID# | FRCC | 230 | 17614.5 | 7017.1181
58 | NCR ID# | FRCC | 230 | 17039.4 | 6788.0145
56 | NCR ID# | FRCC | 230 | 16471.6 | 6561.8191
23 | NCR ID# | FRCC | 230 | 14270.8 | 5685.0827
31 | NCR ID# | FRCC | 230 | 14017.9 | 5584.3345
295 | NCR ID# | FRCC | 115 | 27867.5 | 5550.8115
294 | NCR ID# | FRCC | 115 | 27827.6 | 5542.864
315 | NCR ID# | FRCC | 230 | 13810.1 | 5501.5528
312 | NCR ID# | FRCC | 230 | 12018.2 | 4787.7106
51 | NCR ID# | FRCC | 230 | 10784.9 | 4296.3988
316 | NCR ID# | FRCC | 230 | 10616.4 | 4229.2732
314 | NCR ID# | FRCC | 230 | 10557.6 | 4205.8489
320 | NCR ID# | FRCC | 230 | 10552.4 | 4203.7774
53 | NCR ID# | FRCC | 230 | 10342 | 4119.96
317 | NCR ID# | FRCC | 230 | 10279.3 | 4094.9821
302 | NCR ID# | FRCC | 230 | 10102.5 | 4024.55
55 | NCR ID# | FRCC | 230 | 10075.9 | 4013.9533
59 | NCR ID# | FRCC | 230 | 9712.8 | 3869.3045
304 | NCR ID# | FRCC | 230 | 9617.9 | 3831.499
60 | NCR ID# | FRCC | 230 | 9604.6 | 3826.2007
299 | NCR ID# | FRCC | 230 | 9597.7 | 3823.4519
303 | NCR ID# | FRCC | 230 | 9542.3 | 3801.3821
54 | NCR ID# | FRCC | 230 | 9110.3 | 3629.2856
231 | NCR ID# | FRCC | 115 | 14834.8 | 2954.8821
215 | NCR ID# | FRCC | 115 | 14296.4 | 2847.6405
269 | NCR ID# | FRCC | 115 | 13211.9 | 2631.6234
309 | NCR ID# | FRCC | 115 | 12894.8 | 2568.4616
230 | NCR ID# | FRCC | 115 | 12888.6 | 2567.2267
301 | NCR ID# | FRCC | 115 | 12780.9 | 2545.7743
266 | NCR ID# | FRCC | 115 | 12722.5 | 2534.1419
238 | NCR ID# | FRCC | 115 | 12674.3 | 2524.5411
260 | NCR ID# | FRCC | 115 | 12674.3 | 2524.5411
306 | NCR ID# | FRCC | 115 | 11989.8 | 2388.1984
271 | NCR ID# | FRCC | 115 | 11826.3 | 2355.6315
249 | NCR ID# | FRCC | 115 | 11049 | 2200.8044
247 | NCR ID# | FRCC | 115 | 10974.5 | 2185.965
246 | NCR ID# | FRCC | 115 | 10901.7 | 2171.4643
313 | NCR ID# | FRCC | 115 | 10868.4 | 2164.8314
262 | NCR ID# | FRCC | 115 | 10472.1 | 2085.8941
242 | NCR ID# | FRCC | 115 | 10242.9 | 2040.2407
228 | NCR ID# | FRCC | 115 | 10089.3 | 2009.6457
248 | NCR ID# | FRCC | 115 | 9865.4 | 1965.048
217 | NCR ID# | FRCC | 115 | 9559.9 | 1904.1967
297 | NCR ID# | FRCC | 115 | 9521.2 | 1896.4882
209 | NCR ID# | FRCC | 115 | 9295.3 | 1851.4922
243 | NCR ID# | FRCC | 115 | 8969.1 | 1786.5177
218 | NCR ID# | FRCC | 115 | 8925.9 | 1777.9129
265 | NCR ID# | FRCC | 115 | 8913.4 | 1775.4231
232 | NCR ID# | FRCC | 115 | 8881.7 | 1769.1089
210 | NCR ID# | FRCC | 115 | 8874.5 | 1767.6748
240 | NCR ID# | FRCC | 115 | 8538.1 | 1700.6686
239 | NCR ID# | FRCC | 115 | 8441.6 | 1681.4472
307 | NCR ID# | FRCC | 115 | 8396.7 | 1672.5038
270 | NCR ID# | FRCC | 115 | 8349.2 | 1663.0424
272 | NCR ID# | FRCC | 115 | 8193.3 | 1631.9894
258 | NCR ID# | FRCC | 115 | 8000 | 1593.4867
310 | NCR ID# | FRCC | 115 | 7891.1 | 1571.7954
211 | NCR ID# | FRCC | 115 | 7836.8 | 1560.9796
261 | NCR ID# | FRCC | 115 | 7821.8 | 1557.9918
225 | NCR ID# | FRCC | 115 | 7729.5 | 1539.607
234 | NCR ID# | FRCC | 115 | 7556.5 | 1505.1478
233 | NCR ID# | FRCC | 115 | 7543.2 | 1502.4986
204 | NCR ID# | FRCC | 115 | 7385.9 | 1471.1667
259 | NCR ID# | FRCC | 115 | 7373.5 | 1468.6968
256 | NCR ID# | FRCC | 115 | 7313.5 | 1456.7457
298 | NCR ID# | FRCC | 115 | 7257.6 | 1445.6112
244 | NCR ID# | FRCC | 115 | 7248.5 | 1443.7986
222 | NCR ID# | FRCC | 115 | 7203.5 | 1434.8352
223 | NCR ID# | FRCC | 115 | 7132.8 | 1420.7528
263 | NCR ID# | FRCC | 115 | 7118 | 1417.8048
226 | NCR ID# | FRCC | 115 | 6988.9 | 1392.0899
254 | NCR ID# | FRCC | 115 | 6913.1 | 1376.9917
267 | NCR ID# | FRCC | 115 | 6851.2 | 1364.662
257 | NCR ID# | FRCC | 115 | 6845.7 | 1363.5665
253 | NCR ID# | FRCC | 115 | 6771.8 | 1348.8467
245 | NCR ID# | FRCC | 115 | 6703.5 | 1335.2423
308 | NCR ID# | FRCC | 115 | 6570.7 | 1308.7904
251 | NCR ID# | FRCC | 115 | 6473.2 | 1289.3698
241 | NCR ID# | FRCC | 115 | 6395.1 | 1273.8134
252 | NCR ID# | FRCC | 115 | 5556 | 1106.6765
255 | NCR ID# | FRCC | 115 | 5007.2 | 997.3634
5 | NCR ID# | FRCC | 13.2 | 39503.2 | 903.1645
9 | NCR ID# | FRCC | 13.2 | 39500.8 | 903.1096
13 | NCR ID# | FRCC | 13.2 | 39500.8 | 903.1096
1 | NCR ID# | FRCC | 13.2 | 39492.3 | 902.9152
17 | NCR ID# | FRCC | 13.2 | 39472.8 | 902.4694
6 | NCR ID# | FRCC | 13.2 | 39306.2 | 898.6604
10 | NCR ID# | FRCC | 13.2 | 39303.8 | 898.6056
14 | NCR ID# | FRCC | 13.2 | 39303.8 | 898.6056
2 | NCR ID# | FRCC | 13.2 | 39295.3 | 898.4112
18 | NCR ID# | FRCC | 13.2 | 39276.2 | 897.9745
214 | NCR ID# | FRCC | 115 | 4497.9 | 895.918
250 | NCR ID# | FRCC | 115 | 4328.6 | 862.1958
318 | NCR ID# | FRCC | 13.2 | 13237.8 | 302.6568

## Ex 2 with zero buses
Transmission Owner Name | Total Bus Count | Total DFR bus count | Top 10% Bus Count | 10% Distributed Bus Count | Median MVA (6th Bus from Top) | New Lowest Median Calc. MVA (20% of Median Value)
Base Values | 120 | 24 | 12 | 12 | 5685 | 1500
Median Method | 64 | 13 | 7 | 6 |  | 1500
Zero Busses | 24 | 5 | 3 | 2
Bus Coded Number | NCR-ID Number | Region | Bus kV (L-L) | Bus 3 Phase Fault--Current (amps) | Bus 3 Phase Fault MVA
0 | NCR ID# | FRCC | 230 | 42201.5 | 16811.8827
0 | NCR ID# | FRCC | 230 | 31932.1 | 12720.8445
0 | NCR ID# | FRCC | 230 | 31879.4 | 12699.8503
19 | NCR ID# | FRCC | 230 | 31119.8 | 12397.2472
319 | NCR ID# | FRCC | 230 | 23086.6 | 9197.0478
0 | NCR ID# | FRCC | 230 | 18604 | 7411.3068
52 | NCR ID# | FRCC | 230 | 17614.5 | 7017.1181
58 | NCR ID# | FRCC | 230 | 17039.4 | 6788.0145
56 | NCR ID# | FRCC | 230 | 16471.6 | 6561.8191
23 | NCR ID# | FRCC | 230 | 14270.8 | 5685.0827
31 | NCR ID# | FRCC | 230 | 14017.9 | 5584.3345
295 | NCR ID# | FRCC | 115 | 27867.5 | 5550.8115
294 | NCR ID# | FRCC | 115 | 27827.6 | 5542.864
315 | NCR ID# | FRCC | 230 | 13810.1 | 5501.5528
0 | NCR ID# | FRCC | 230 | 12551 | 4999.963
312 | NCR ID# | FRCC | 230 | 12018.2 | 4787.7106
51 | NCR ID# | FRCC | 230 | 10784.9 | 4296.3988
316 | NCR ID# | FRCC | 230 | 10616.4 | 4229.2732
314 | NCR ID# | FRCC | 230 | 10557.6 | 4205.8489
320 | NCR ID# | FRCC | 230 | 10552.4 | 4203.7774
53 | NCR ID# | FRCC | 230 | 10342 | 4119.96
317 | NCR ID# | FRCC | 230 | 10279.3 | 4094.9821
302 | NCR ID# | FRCC | 230 | 10102.5 | 4024.55
55 | NCR ID# | FRCC | 230 | 10075.9 | 4013.9533
59 | NCR ID# | FRCC | 230 | 9712.8 | 3869.3045
304 | NCR ID# | FRCC | 230 | 9617.9 | 3831.499
60 | NCR ID# | FRCC | 230 | 9604.6 | 3826.2007
299 | NCR ID# | FRCC | 230 | 9597.7 | 3823.4519
303 | NCR ID# | FRCC | 230 | 9542.3 | 3801.3821
54 | NCR ID# | FRCC | 230 | 9110.3 | 3629.2856
231 | NCR ID# | FRCC | 115 | 14834.8 | 2954.8821
215 | NCR ID# | FRCC | 115 | 14296.4 | 2847.6405
269 | NCR ID# | FRCC | 115 | 13211.9 | 2631.6234
309 | NCR ID# | FRCC | 115 | 12894.8 | 2568.4616
230 | NCR ID# | FRCC | 115 | 12888.6 | 2567.2267
301 | NCR ID# | FRCC | 115 | 12780.9 | 2545.7743
266 | NCR ID# | FRCC | 115 | 12722.5 | 2534.1419
260 | NCR ID# | FRCC | 115 | 12674.3 | 2524.5411
238 | NCR ID# | FRCC | 115 | 12674.3 | 2524.5411
0 | NCR ID# | FRCC | 115 | 12388.9 | 2467.6935
306 | NCR ID# | FRCC | 115 | 11989.8 | 2388.1984
271 | NCR ID# | FRCC | 115 | 11826.3 | 2355.6315
249 | NCR ID# | FRCC | 115 | 11049 | 2200.8044
247 | NCR ID# | FRCC | 115 | 10974.5 | 2185.965
246 | NCR ID# | FRCC | 115 | 10901.7 | 2171.4643
313 | NCR ID# | FRCC | 115 | 10868.4 | 2164.8314
262 | NCR ID# | FRCC | 115 | 10472.1 | 2085.8941
242 | NCR ID# | FRCC | 115 | 10242.9 | 2040.2407
228 | NCR ID# | FRCC | 115 | 10089.3 | 2009.6457
248 | NCR ID# | FRCC | 115 | 9865.4 | 1965.048
217 | NCR ID# | FRCC | 115 | 9559.9 | 1904.1967
297 | NCR ID# | FRCC | 115 | 9521.2 | 1896.4882
209 | NCR ID# | FRCC | 115 | 9295.3 | 1851.4922
243 | NCR ID# | FRCC | 115 | 8969.1 | 1786.5177
218 | NCR ID# | FRCC | 115 | 8925.9 | 1777.9129
265 | NCR ID# | FRCC | 115 | 8913.4 | 1775.4231
232 | NCR ID# | FRCC | 115 | 8881.7 | 1769.1089
210 | NCR ID# | FRCC | 115 | 8874.5 | 1767.6748
240 | NCR ID# | FRCC | 115 | 8538.1 | 1700.6686
239 | NCR ID# | FRCC | 115 | 8441.6 | 1681.4472
307 | NCR ID# | FRCC | 115 | 8396.7 | 1672.5038
270 | NCR ID# | FRCC | 115 | 8349.2 | 1663.0424
272 | NCR ID# | FRCC | 115 | 8193.3 | 1631.9894
258 | NCR ID# | FRCC | 115 | 8000 | 1593.4867
310 | NCR ID# | FRCC | 115 | 7891.1 | 1571.7954
211 | NCR ID# | FRCC | 115 | 7836.8 | 1560.9796
261 | NCR ID# | FRCC | 115 | 7821.8 | 1557.9918
225 | NCR ID# | FRCC | 115 | 7729.5 | 1539.607
234 | NCR ID# | FRCC | 115 | 7556.5 | 1505.1478
233 | NCR ID# | FRCC | 115 | 7543.2 | 1502.4986
204 | NCR ID# | FRCC | 115 | 7385.9 | 1471.1667
259 | NCR ID# | FRCC | 115 | 7373.5 | 1468.6968
256 | NCR ID# | FRCC | 115 | 7313.5 | 1456.7457
298 | NCR ID# | FRCC | 115 | 7257.6 | 1445.6112
244 | NCR ID# | FRCC | 115 | 7248.5 | 1443.7986
222 | NCR ID# | FRCC | 115 | 7203.5 | 1434.8352
223 | NCR ID# | FRCC | 115 | 7132.8 | 1420.7528
263 | NCR ID# | FRCC | 115 | 7118 | 1417.8048
226 | NCR ID# | FRCC | 115 | 6988.9 | 1392.0899
254 | NCR ID# | FRCC | 115 | 6913.1 | 1376.9917
267 | NCR ID# | FRCC | 115 | 6851.2 | 1364.662
257 | NCR ID# | FRCC | 115 | 6845.7 | 1363.5665
253 | NCR ID# | FRCC | 115 | 6771.8 | 1348.8467
245 | NCR ID# | FRCC | 115 | 6703.5 | 1335.2423
308 | NCR ID# | FRCC | 115 | 6570.7 | 1308.7904
251 | NCR ID# | FRCC | 115 | 6473.2 | 1289.3698
241 | NCR ID# | FRCC | 115 | 6395.1 | 1273.8134
0 | NCR ID# | FRCC | 13.2 | 53465.4 | 1222.3832
0 | NCR ID# | FRCC | 115 | 6044.4 | 1203.9589
252 | NCR ID# | FRCC | 115 | 5556 | 1106.6765
0 | NCR ID# | FRCC | 115 | 5011.7 | 998.2597
255 | NCR ID# | FRCC | 115 | 5007.2 | 997.3634
5 | NCR ID# | FRCC | 13.2 | 39503.2 | 903.1645
9 | NCR ID# | FRCC | 13.2 | 39500.8 | 903.1096
13 | NCR ID# | FRCC | 13.2 | 39500.8 | 903.1096
1 | NCR ID# | FRCC | 13.2 | 39492.3 | 902.9152
17 | NCR ID# | FRCC | 13.2 | 39472.8 | 902.4694
6 | NCR ID# | FRCC | 13.2 | 39306.2 | 898.6604
10 | NCR ID# | FRCC | 13.2 | 39303.8 | 898.6056
14 | NCR ID# | FRCC | 13.2 | 39303.8 | 898.6056
2 | NCR ID# | FRCC | 13.2 | 39295.3 | 898.4112
18 | NCR ID# | FRCC | 13.2 | 39276.2 | 897.9745
214 | NCR ID# | FRCC | 115 | 4497.9 | 895.918
0 | NCR ID# | FRCC | 13.8 | 36676.3 | 876.648
0 | NCR ID# | FRCC | 13.8 | 36345.7 | 868.7459
250 | NCR ID# | FRCC | 115 | 4328.6 | 862.1958
0 | NCR ID# | FRCC | 13.8 | 35973.7 | 859.8542
0 | NCR ID# | FRCC | 13.8 | 35973.7 | 859.8542
0 | NCR ID# | FRCC | 13.8 | 35927.7 | 858.7547
0 | NCR ID# | FRCC | 13.8 | 35927.7 | 858.7547
0 | NCR ID# | FRCC | 13.8 | 35661.2 | 852.3847
0 | NCR ID# | FRCC | 13.8 | 35661.2 | 852.3847
0 | NCR ID# | FRCC | 13.8 | 35616.5 | 851.3163
0 | NCR ID# | FRCC | 13.8 | 35616.5 | 851.3163
0 | NCR ID# | FRCC | 115 | 3584.4 | 713.9617
0 | NCR ID# | FRCC | 13.2 | 15213 | 347.8159
0 | NCR ID# | FRCC | 13.2 | 13741.7 | 314.1775
0 | NCR ID# | FRCC | 13.2 | 13587.3 | 310.6474
318 | NCR ID# | FRCC | 13.2 | 13237.8 | 302.6568
0 | NCR ID# | FRCC | 13.2 | 7057.7 | 161.3607