## Slide 1
Project 2009-01
Disturbance and Sabotage Reporting (Event Reporting) Project Webinar
July 30, 2012

## Slide 2: Project 2009-01 Event Reporting
On the webinar: Evans-Mongeon, DePoorter, Draxton, Hartmann, Canada, Crutchfield
Project 2009-01 Failed in last ballot with 46% support
SDT met in June to review comments and prepare for the next round.
Informal outreach during July

## Slide 3: Project 2009-01 Event Reporting
Standard has been revised based upon industry comments:
  3 Requirements – Have a Plan, Report, Validate
  Updated Attachments 1 and 2
  Modified Applicability
  Return CIP-008 R1.3 back …

## Slide 4: Project 2009-01 Event Reporting
Prior to the last comment period, the EOP-004-2 SDT received comments about the need to address the potential for double jeopardy with CIP-008-3 R1.3 and the term “reportable Cyber Security Incident”. Working with Steve Noess, we addressed both and offered the industry our thoughts on how best to incorporate the CIP reporting requirements into Project 2009-01.
  We were leaving the determination of a rCSI with CIP-008; however, reporting under R1.3 would eliminated in V3 and V4 upon FERC acceptance.
  Under V3 and V4, the term would remain “reportable Cyber Security Incident”; but upon the enforcement of V5, the term would be updated to “Reportable Cyber Security Incident” consistent with that new definition.

## Slide 5: Project 2009-01 Event Reporting
Project 2009-01 had previously determined that a FERC Order Directive needed to be addressed. Paragraph 407 of FERC Order 706 directed the CIP Reliability Standards be updated to reflect a one-hour reporting threshold for reportable Cyber Security Incidents. Project 2009-01 SDT decided to include the one-hour threshold for reporting to be consistent with the FERC directive.

## Slide 6: Project 2009-01 Event Reporting
During the Comment Period that followed, there were many comments, very few supportive of the SDT’s proposals:
  Given the number of rounds of comments that we have had, the incorporation of CIP-008 R1.3 has consistently noted in the negative votes.
  A couple of commenters pointed out a potential conflict with R1.6 which could pose a second double jeopardy scenario.
  Some still pointed out and believed there would be double jeopardy under R1.3.

## Slide 7: Project 2009-01 Event Reporting
  Some found that leaving the recognition in CIP-008 and reporting in EOP-004 would create confusion for the industry.
  Some felt that the unresolved nature of the overall Cyber Security requirements would impact the EOP-004-2 standard and would require future changes to the EOP standard as the CIP standards evolve.
  Due to future CIP Applicability changes that remove certain types of Registered Entities, EOP-004-2 would have to be modified to remove those entities as well.
  There was a concern that EOP-004 reporting would be required for incidences at a nuclear generating facility when they are not required under CIP-008.

## Slide 8: Project 2009-01 Event Reporting
As a result of these comments, the Project 2009-01 SDT is proposing that CIP-008 R1.3 be left in the original form under CIP-008 and that all provisions that were previously incorporated be removed. While we believe that the industry would like to see a single reporting clearinghouse structure, we feel that it’s best to keep things as currently structured.

## Slide 9: Project 2009-01 Event Reporting
New Proposed R1:
Each Responsible Entity shall have an event reporting Operating Plan that includes communication protocol(s) for applicable events listed in, and within the timeframes specified in EOP-004 Attachment 1 to the Electric Reliability Organization and other organizations based on the event type (e.g. the Regional Entity, company personnel, the Responsible Entity’s Reliability Coordinator, law enforcement, governmental or provincial agencies).

## Slide 10: Project 2009-01 Event Reporting
Expected intent by the SDT:
Similar to today’s CIP-001, Registered Entities will have a plan, procedure, or process including contact list(s) for the notification associated with the types of events identified in Attachment 1 for the type of functional registrant they are. Entities, at their choosing, can have one list for all types or can have separate lists for the different types of events. The ERO must be on all contact lists. The organization knows to whom it has obligations to for reporting to the rest of the parties to be notified.

## Slide 11: Project 2009-01 Event Reporting
New Proposed R2:
Each Responsible Entity shall implement its event reporting Operating Plan for applicable events listed in, and within the timeframes specified in, EOP-004 Attachment 1.

## Slide 12: Project 2009-01 Event Reporting
New Proposed R3:
Each Responsible Entity shall validate all contact information contained in the Operating Plan per Requirement R1 each calendar year.
Expected intent by the SDT: This requirement results from the FERC Directive in Order 693. The SDT has removed the language on drills, tests, and or exercises.

## Slide 13: Project 2009-01 Event Reporting
Event Type | Entity with Reporting Responsibility | Threshold for Reporting
Damage or destruction of a Facility | RC, BA, TOP | Damage or destruction of a Facility within its Reliability Coordinator Area, Balancing Authority Area or Transmission Operator Area that results in the need for actions to avoid a BES Emergency.
Damage or destruction of a Facility | BA, TO, TOP, GO, GOP, DP | Damage or destruction of its Facility that results from actual or suspected intentional human action.
Physical threats to a Facility | BA, TO, TOP, GO, GOP, DP | Physical threat to its Facility excluding weather related threat, which has the potential to degrade the normal operation of the Facility. OR Suspicious device or activity at a Facility. Do not report copper theft unless it degrades normal operation of a Facility.
Physical threats to a control center | RC, BA, TOP | Physical threat to its control center, excluding weather related threat, which has the potential to degrade the normal operation of the control center. OR Suspicious device or activity at a control center.

## Slide 14: Project 2009-01 Event Reporting
Event Type | Entity with Reporting Responsibility | Threshold for Reporting
BES Emergency requiring public appeal for load reduction | Initiating entity is responsible for reporting | Public appeal for load reduction event
BES Emergency requiring system-wide voltage reduction | Initiating entity is responsible for reporting | System wide voltage reduction of 3% or more
BES Emergency requiring manual firm load shedding | Initiating entity is responsible for reporting | Manual firm load shedding ≥ 100 MW
BES Emergency resulting in automatic firm load shedding | DP, TOP | Automatic firm load shedding ≥ 100 MW (via automatic undervoltage or underfrequency load shedding schemes, or SPS/RAS)
Voltage deviation on a Facility | TOP | Observed voltage deviation of ± 10% of nominal voltage sustained for ≥ 15 continuous minutes

## Slide 15: Project 2009-01 Event Reporting
Event Type | Entity with Reporting Responsibility | Threshold for Reporting
IROL Violation (all Interconnections) or SOL Violation for Major WECC Transfer Paths (WECC only) | RC | Operate outside the IROL for time greater than IROL Tv (all Interconnections) or Operate outside the SOL for more than 30 minutes for Major WECC Transfer Paths (WECC only).
Loss of firm load | BA, TOP, DP | Loss of firm load for ≥ 15 Minutes: ≥ 300 MW for entities with previous year’s demand ≥ 3,000 MW OR ≥ 200 MW for all other entities
System separation (islanding) | RC, BA, TOP | Each separation resulting in an island ≥ 100 MW
Generation loss | BA, GOP | Total generation loss, within one minute, of ≥ 2,000 MW for entities in the Eastern or Western Interconnection OR ≥ 1,000 MW for entities in the ERCOT or Quebec Interconnection

## Slide 16: Project 2009-01 Event Reporting
Event Type | Entity with Reporting Responsibility | Threshold for Reporting
Complete loss of off-site power to a nuclear generating plant (grid supply) | TO, TOP | Complete loss of off-site power affecting a nuclear generating station per the Nuclear Plant Interface Requirement
Transmission loss | TOP | Unexpected loss, contrary to design, of three or more BES Elements caused by a common disturbance (excluding successful automatic reclosing)
Unplanned control center evacuation | RC, BA, TOP | Unplanned evacuation from BES control center facility for 30 continuous minutes or more.
Complete loss of voice communication capability | RC, BA, TOP | Complete loss of voice communication capability affecting a BES control center for 30 continuous minutes or more
Complete loss of monitoring capability | RC, BA, TOP | Complete loss of monitoring capability affecting a BES control center for 30 continuous minutes or more such that analysis capability (State Estimator, Contingency Analysis) is rendered inoperable.

## Slide 17: Project 2009-01 Event Reporting
Listed below are the proposed changes to Attachment 2:
  Reorganized the event lists to match order listed in Attachment 1.
  Removed “Other”
  Updated ERO contact information
Other Changes:
  Removed timestamp language
  Adjusted VSL for R2 to change to days from hours
  Moved background to Guidance pages

## Slide 18: Project 2009-01 Event Reporting
Notes:
SDT looking to finalize proposal on July 31 and Aug 1
Post 30-day comment and ballot in mid-August
With approval, looking to go to BOT in November

## Slide 19: Questions?
Questions
Thank You!
From: Brian, Joe, Michelle, Jimmy, Steve, and Bob.