## Redacted for Public Posting
Reported quarter and year | Regional Entities | Registered Function | Nominal voltage rating of the circuit (kV) | Has the reported circuit experienced a previous vegetation-related transmission outage within the last eight reporting quarters? | Element of IROL or Major WECC Transfer Path? | Outage start date | Outage Duration (in minutes) | Detailed description of the cause of the outage | Category associated with the Sustained Outage per the | If the vegetation causing the outage was located outside of the ROW provide the horizontal distance to the edge of the ROW | If the vegetation causing the outage was located outside of the ROW provide the horizontal distance to the nearest conductor | Tree type | Tree height in feet | Tree condition | Mitigation/remediation actions taken by Registered Entity to address recurrence of the contact/encroachment.
Q4 2020 | NPCC | TO | 230 | No | Yes | 2020-11-15 | 1105 | A wind event caused two outage events due to a fall-in from outside the right-of-way by one tree at the same location. | 3 | 7 | 31 | White Pine | 99 | Healthy | The tree lot adjacent to the right-of-way had been partially cleared for a new development. Following the event, the entity received permission to remove additional trees that may be susceptible to wind due to the recent clearing on the adjacent lot.
Q4 2020 | NPCC | TO | 115 | No | Yes | 2020-11-15 | 1119 | A wind event caused two outage events due to a fall-in from outside the right-of-way by one tree at the same location. | 3 | 7 | 31 | White Pine | 99 | Healthy | The tree lot adjacent to the right-of-way had been partially cleared for a new development. Following the event, the entity received permission to remove additional trees that may be susceptible to wind due to the recent clearing on the adjacent lot.
Q4 2020 | WECC | TO | 115 | Yes | Yes | 2020-11-08 | 434 | A dead Lodgepole Pine tree fell into the line from outside the right-of-way. | 3 | 10 | 40 | Lodgepole Pine | 75 | Dead | Constant proactive analysis of vegetation on this line along with continuing coordination with the local Forest Service to remove appropriate trees outside of the cleared right-of-way.
Q4 2020 | WECC | TO | 230 | Yes | No | 2020-10-11 | 2547 | During a storm with high winds, a healthy Western Hemlock tree broke at 15' above the ground and fell from the edge of the right-of-way into the line. | 3 | 32 | 54 | Western Hemlock | 85 | Healthy | Tree was removed.
Q4 2020 | WECC | TO | 230 | Yes | No | 2020-11-25 | 918 | A healthy Birch tree fell into the right-of-way after a beaver gnawed the base of the tree. | 3 | 17.5 | 37.5 | Birch | 85 | Healthy | Continue to monitor surrounding property for signs of forest decline.
Q3 2020 | NPCC | GO | 345 | No | No | 2020-08-30 | 333 | A tree fell from outside the ROW and contacted the line. | 3 | 10 | 60 | Ash | 110 | Healthy appearance, interior rot | Inspection of the area of concern identified additional trees outside ROW but potential hazards; these trees are to be removed.
Q3 2020 | RF | TO | 230 | No | No | 2020-08-04 | 4561 | An off-corridor healthy White Pine tree approximately 71’ tall and 23” diameter at breast height uprooted due to high winds during Tropical Storm Isaias, and subsequently fell into the ROW, coming to rest approximately 7" from the conductor. Upon investigation, the tree was still leaning on fencing and suspended by distribution and communication wires. The White Pine tree was located approximately 9’ from the edge of the maintained ROW. No other trees in the surrounding spans uprooted during the tropical storm, but substantial damage was observed throughout. Radar indicates that the outage location experienced high winds in excess of 50 mph at the time of the outage. The National Weather Service issued a tropical storm warning for Tropical Storm Isaias that was travelling over the outage area, which indicated the storm may contain high winds in excess of 60 mph. | 3 | 9 | 59 | White Pine | 71 | Healthy | After the contact, surrounding spans were reviewed to ensure there were no other existing tree conditions.
Q3 2020 | RF | TO | 230 | No | No | 2020-08-27 | 284 | An off-corridor healthy Red Oak tree approximately 98’ tall and 29.4” diameter at breast height uprooted due to high winds and subsequently fell into the ROW contacting the conductor. The Red Oak tree was located approximately 20’ from the edge of the maintained ROW. Radar indicates that the outage location experienced high winds in excess of 50-60 mph at the time of the outage. National Weather Service had issued a severe thunderstorm warning for the outage area, which indicated the storm may contain high winds in excess of 55 mph. | 3 | 20 | 75 | Red Oak | 98 | Healthy | After the contact, surrounding spans were reviewed to ensure there were no other existing tree conditions. As information, three large trees, broken at base, were encountered on the access road and had to be removed to reach outage location.
Q3 2020 | RF | TO | 345 | No | No | 2020-07-12 | 5 | Fall-in from outside the ROW. An off-corridor healthy Red Oak tree approximately 91’ tall and 22” diameter at breast height uprooted due to saturated soil and a root system insufficient for the size of the tree, and subsequently fell into the ROW contacting the line. The Red Oak tree was located approximately 40’ from the edge of the maintained ROW. | 3 | 40 | 80 | Red Oak | 91 | Healthy | After the contact, surrounding spans were reviewed to ensure there were no other existing tree conditions; one tree was struck by the Red Oak and fell at the time of the outage, and one other tree was identified for removal in the span.
Q3 2020 | SERC | GO, TO | 230 | No | No | 2020-08-06 | 243 | A Loblolly Pine tree from off the ROW, which appeared to be healthy, made contact with the 230 kV line. No damage to facilities. Strong thunderstorms were in the area at the time of event. | 3 | 10 | 42 | Loblolly Pine | 83 | Healthy, no visible signs of decay | Vines were cut and removed and area was sprayed.
Q3 2020 | SERC | TO | 230 | No | No | 2020-07-23 | 990 | A healthy Poplar Tree 90' off the ROW broke off about 8-10 feet up the tree. | 3 | 1 | 43 | Poplar | 74 | Healthy tree sheared off 8-10 feet up tree. | Tree was cut down. Adjacent spans in both directions were evaluated and additional potential danger trees were also mitigated and cut.
Q3 2020 | SERC | TO | 230 | No | No | 2020-07-13 | 56 | Oak tree with root decay fell 35 feet from off the right-of-way. | 3 | 35 | 65 | Oak | 87 | Evidence of root decay. | Tree was cut down and other trees in the adjacent spans were evaluated for potential risk to facilities and cut down as needed.
Q3 2020 | SERC | DP, TO | 230 | No | No | 2020-07-28 | 551 | An 86 foot tall red oak tree uprooted during a storm and hit the line. The tree was outside the right of way, 4 feet from the ROW edge, and 38 feet from the nearest conductor. The tree was a hazard tree, with a small defect on the backside that might have affected root growth and might have contributed to the uprooting. | 3 | 4 | 38 | Red Oak | 86 | The tree had a small defect on the backside at the bottom that might have affected root growth and might have contributed to the uprooting. | Adjacent areas were patrolled for other trees with visible damage. None were found.
Q3 2020 | WECC | TO | 230 | No | No | 2020-08-09 | 474 | A dead Douglas fir tree back in the stand broke about 12 feet from ground level and hit the line. The tree broke from a healthy, unmanaged stand of Douglas firs and big leaf maples. | 3 | 41.5 | 61 | Douglas fir | 65 | dead | The stand was surveyed and 6 small, supressed dead Douglas firs were felled.
Q3 2020 | WECC | TO | 230 | Yes | No | 2020-09-08 | 3791 | 24" Hemlock was alive, root failure due to root rot with strong wind out of east. Tree is located on the south side of the ROW, sitting on the west bank of a steep uphill section | 3 | 32 | 52 | Western Hemlock | 124 | Healthy | Tree was removed.
Q3 2020 | WECC | TO | 230 | Yes | No | 2020-09-23 | 401 | Hemlock Tree fell through and contacted the line. | 3 | 27 | 47 | Hemlock | 110 | Healthy | Tree was removed. Continue to monitor surrounding property for signs of forest decline.
Q2 2020 | NPCC | TO | <200 | No | Yes | 2020-06-06 | 1416 | During a strong wind event, a healthy Red Oak tree snapped 6 feet up from the base of the trunk, falling into the transmission line. | 3 | 14 | 62 | Red Oak | 70 | Healthy tree with no evidence of internal decay | The tree was removed and the area was inspected with no findings of additional vegetation issues identified.
Q2 2020 | RF | TO | 345 | No | No | 2020-05-29 | 183 | During a high wind in excess of 55 mph weather condition, a healthy Tulip Poplar tree approximately 20” diameter at breast height (DBH) uprooted, falling into the transmission line and contacting a conductor. | 3 | 8 | 53 | Tulip Poplar | 95 | Healthy | The surrounding spans were reviewed to ensure there were no other existing tree conditions. A total of 20 trees were uprooted or damaged as a result of the severe thunderstorm and high winds. The Tulip Poplar tree and 7 other trees were uprooted. Due to the severity of the storm and winds, an aerial saw was brought in to remove 12 additional trees which were unsafe to climb.
Q2 2020 | SERC | TO, GO | 230 | No | No | 2020-06-27 | 855 | During a strong thunderstorms, a live healthy loblolly pine from outside of the ROW fell and made contact with the transmission line. There was no damage to the facilities. | 3 | 4 | 36 | Loblolly Pine | 84 | Healthy, no visible signs of decay | Tree was removed from area and right of way was inspected for any other hazards.
Q2 2020 | SERC | TO, GO | 230 | No | No | 2020-05-27 | 297 | During strong thunderstorm event, a tree off the ROW broke and pushed a healthy pine tree into the transmission lines. There were no damages to the facilities. | 3 | 22 | 54 | Pine | 86 | Healthy, no visible signs of decay. | Tree was removed from area and right of way was inspected for any other hazards.
Q2 2020 | SERC | TO, GO | 230 | No | No | 2020-06-30 | 329 | An off right-of-way live water oak tree with internal decay broke at base and made contact with the transmission line. Tree had signs of internal decay and root rot, but signs were not externally visible. Strong thunderstorms were in the area at the time of event. | 3 | 10 | 31 | Water Oak | 76 | Tree was alive with root rot | Tree was removed from area and right of way was inspected for any other hazards. There were no damages to the facilities.
Q2 2020 | SERC | TO | 230 | Yes | No | 2020-05-16 | 565 | A 103 feet tall oak tree , 28 feet off the ROW split 10 feet from the ground, making contact with the line and causing an outage. | 3 | 28 | 61 | Oak | 103 | Tree appeared healthy from an aerial inspection during the spring helicopter patrol. The large tree had 2 codominant stems that split 10’ from the ground. Age of the tree and the weight of the stem facing the conductor caused the tree to fail. The tree showed signs of internal rot at the split that could not be seen during a visual inspection. | A tree crew was called to site to remove the tree from the conductors and line was restored. Additional off right of way danger trees have been identified and scheduled for removal during the routine vegetation maintenance of this section of line.
Q2 2020 | SERC | TO | 230 | Yes | No | 2020-05-01 | 953 | A 115 ft. maple tree fell into 62 ft. sweetgum making the sweetgum to fall on the conductor. | 3 | 12 | 44 | Maple/Sweetgum | 62 | Healthy | Tree cut from conductor and other trees evaluated for condition with additional tree work completed the next day.
Q2 2020 | SERC | TO | 230 | Yes | No | 2020-06-22 | 1025 | Off right-of-way poplar tree fell on the conductor during thunderstorm. | 3 | 23 | 55 | Poplar | 98 | Healthy | Tree was cut off the line. The area was inspected and other trees and vegetation observed in the immediate area for additional vegetation threats were removed.
Q2 2020 | WECC | TO | 230 | No | No | 2020-06-01 | 197 | A hemlock tree fell into the transmission line due to laminated root rot disease. | 3 | 26 | 46 | Hemlock | 75 | Dying | Tree was removed off the line. The entity will continue to monitor vegetation for signs of rot.
Q2 2020 | WECC | TO | 230 | No | No | 2020-06-01 | 329 | A cottonwood tree fell from outside of the ROW and made contact with conductor. | 3 | 19 | 60 | Cottonwood | 70 | Healthy | Tree was removed off the line. The entity will continue to monitor surrounding property for signs of forest decline.
Q1 2020 | WECC | TO | 230 | Yes | Yes | 2020-01-12 | 7636 | A Douglas fir tree back in the stand uprooted and fell into the trunk/base of another Douglas fir tree closer to the edge of the ROW, causing this tree to uproot and hit the line. The tree was alive but the now-exposed roots showed evidence of a possible root rot. This occurred during a snow event with an accumulation of approximately 30 inches in 72 hours with sustained winds of 15 to 18 mph and gusts of 35 to 40 mph. | 3 | 8 | 36 | Douglas fir | 84 | Alive, but some rot present in the roots | The adjacent trees were surveyed for removal.
Q1 2020 | WECC | TO | 230 | Yes | Yes | 2020-01-22 | 17355 | A Douglas fir tree back in the stand uprooted and fell onto the line. The tree was alive and healthy. This occurred during a period in which the area received over 2 inches of rain in a 72 hour period and experienced sustained winds of 13-17mph and gusts of 32mph. | 3 | 34.5 | 83 | Douglas fir | 95 | Alive/healthy | An adjacent, uprooted tree was removed and the stand surveyed.
Q1 2020 | WECC | TO | 230 | Yes | No | 2020-01-12 | 3058 | A Douglas Fir tree fell into the line due to root failure caused by high water flow undermining the bank. | 3 | 22 | 42 | Douglas Fir | 124 | Healthy | None
Q1 2020 | WECC | TO | 230 | Yes | No | 2020-03-15 | 580 | Large dead tree fell from outside ROW and brushed through circuit and fell to ground. | 3 | 62 | 90 | Western Hemlock (Tsuga heterophylla) | 100 | Dead | Continue to monitor surrounding property for signs of forest decline.
Q4 2019 | SERC | TO | 230 | No | No | 2019-12-22 | 3267 | During a weather event a pine tree located 35 feet off the ROW fell into two structures, breaking insulators and conductors. | 3 | 35 | 77 | Loblolly Pine | 93 | Tree was still green in the top but had beetle damage and was rotten at the trunk. | Forester and contract tree crew checked the area and removed any other danger trees. The line was also patrolled for any other potential danger trees.
Q4 2019 | SERC | TO | 230 | No | No | 2019-10-19 | 583 | During a tropical storm, a live red oak tree located 26 feet off the ROW fell on a transmission structure breaking a cross arm and insulators. The tree had root rot that was not visible during routine inspections. | 3 | 26 | 74 | Red Oak | 94 | The tree had root damage that was not visible during routine inspections | Tree was removed from area and right of way was inspected for any other hazards.
Q4 2019 | WECC | TO | 230 | Yes | Yes | 2019-10-29 | 2109 | A healthy Douglas fir tree on a steep slope that was located nearly 30 feet off the ROW was uprooted and fell into the line during a wind storm. | 3 | 29.5 | 66 | Douglas fir | 88 | Alive healthy tree with no visible defects | The entity surveyed the outage site and took corrective action the following day to remove 2 additional trees that potentially could fall into the line.
Q3 2019 | RF | TO | 345 | No | Yes | 2019-07-20 | 1621 | A large tree was uprooted by strong wind moving through the area. | 3 | 2 | 40 | Ash | 88 | Live, healthy | Ground patrol was conducted to identify any hazards. The tree was safely removed to remediate the situation.
Q3 2019 | SERC | GO, TO | 230 | No | No | 2019-08-24 | 919 | During a thunderstorm, an off right-of-way live pine tree with internal decay at the base of the trunk broke at base and fell from outside ROW. | 3 | 6 | 38 | Loblolly Pine | 94 | Alive, but with decay at base of trunk. | None
Q2 2019 | RF | TO | 230 | No | No | 2019-06-29 | 1.63 | A healthy Red Oak tree was uprooted due to high winds in the area and subsequently falling into the ROW contacting the conductor, causing two sustained outages. | 3 | 8 | 41 | Red Oak | 65 | Healthy | The surrounding spans were reviewed to ensure there were no other existing tree conditions; no other issues were identified. This corridor is currently being worked for 2019 Maintenance.
Q2 2019 | SERC | TO | 230 | No | No | 2019-06-20 | 1077 | During a thundershower, a live pine tree broke approximately 14' above the ground contacting the transmission line. There were no damages to the facilities. | 3 | 5 | 58 | Pine | 78 | Healthy with no visible internal decay. | Tree was removed from area and right of way was inspected for any other hazards.
Q2 2019 | SERC | TO | 230 | Yes | No | 2019-04-19 | 6 | During a weather event, a healthy oak tree fell into the line making contact long enough to cause a sustained outage. | 3 | 30 | 66 | Oak | 86 | Healthy | Checked several spans adjacent to tree location for additional vegetation issues and none were found.
Q2 2019 | SERC | TO | 230 | Yes | No | 2019-05-30 | 892 | A double-stemmed poplar tree fell onto the line causing the outage. Tree was found in a wetland area on a section of line where a strip of danger trees adjacent to the right-of-way was left by a logging operation months after routine utility vegetation maintenance had occurred. Area of right-of-way had been previously maintained using side-trimming aerial saw. | 3 | 4 | 38 | Poplar | 68 | Healthy | Tree was cut off of line and several spans adjacent to the location was patrolled for any additional vegetation issues. Additional potential danger trees were found and removed. The removed trees were prone to future wind damage that had been previously left adjacent to the right-of-way by outside logging operations.
Q2 2019 | SERC | TO | 230 | No | No | 2019-06-27 | 158 | Recent storms caused the tree to lean towards the line. The tree broke approximately 40’ high resulting in the top falling into the line. | 3 | 1 | 30 | Green Pine | 51 | Healthy green Pine | An inspection of the area was performed and no other hazard tree related issues were identified.
Q2 2019 | SERC | TO | 230 | Yes | No | 2019-06-20 | 1 | Tree fell onto the line and fell in the clear during a thunderstorm weather event causing an approximate one-minute outage. | 3 | 27 | 77 | Maple | 95 | Healthy | Line was patrolled for additional vegetation issues in several adjacent spans. No issues were found.
Q2 2019 | SERC | TO | 230 | No | No | 2019-06-22 | 411 | A loblolly pine tree fell into the line during thunder storm. | 3 | 2 | 45 | Loblolly Pine | 65 | Dead | Tree was removed from the line. Forester inspected the area and removed other trees as needed.
Q2 2019 | SERC | TO | 230 | No | No | 2019-06-22 | 860 | During a thunderstorms in the area, a healthy Sweet Gum tree broke off about six feet from the ground and fell on the conductor. Tree had no visible issues. | 3 | 14 | 57 | Sweet Gum | 85 | Green tree broke with no visible issues. | Forester inspected the area and removed other trees as well.
Q2 2019 | SERC | TO | 230 | No | No | 2019-05-14 | 275 | A Red Oak with root rot uprooted hitting the conductor, causing the outage. | 3 | 30 | 75 | Red Oak | 98 | Tree had root rot causing the failure. | Tree did not have to be removed from the line it brushed the conductor and fell to the ground. Forester inspected the area and removed diseased trees.
Q2 2019 | SERC | TO | 230 | No | Yes | 2019-06-20 | 103 | Strong winds in the area caused green pine tree to break off approximately 10 ft. up from ground falling onto outside conductor closest to edge of right of way. | 3 | 10 | 35 | Pine | 70 | Healthy green pine | An inspection of the area was performed. No other hazard tree were identified.
Q2 2019 | SERC | TO | 230 | No | Yes | 2019-06-22 | 470 | Strong winds in the area caused green oak to be uprooted, falling into the conductor closest to the edge of the right of way. | 3 | 8 | 32 | Oak | 78 | Healthy green oak | An inspection of the area where the outage occurred was performed and no other hazard tree related issues were identified.
Q2 2019 | WECC | TO | 230 | Yes | No | 2019-06-06 | 621 | Wet soils in area caused a cedar tree to be uprooted, falling into a Hemlock and push it into line. | 3 | 25 | 45 | Western Hemlock | 60 | Healthy | An inspection of the area was performed.
Q2 2019 | MRO | TO | 345 | No | No | 2019-05-18 | 6919 | During strong wind gust in the area, an oak tree fell into the line. The tree appeared to be healthy with a dense green canopy and showed no signs of distress such as included bark, disease or decay that would lead to its failure. The area has also experienced tornadoes and record rainfall during the previous months. | 3 | 16 | 76 | Swamp Laurel Oak | 90 | Healthy | Other identified hazard trees off the ROW were removed.
Q2 2019 | MRO | TO | 345 | No | No | 2019-06-03 | 743 | Strong winds caused an oak tree to fall into the line. The area had received nearly 23 inches of rain prior to this event. | 3 | 9 | 60 | Southern Red Oak | 64 | Healthy | Other identified hazard trees off the ROW were removed.
Q2 2019 | MRO | TO | 345 | No | No | 2019-05-26 | 1094 | During severe thunderstorm with wind gust of over 40 mph a healthy oak tree fell into the line causing a sustained outage. The tree was standing in over 12 inches of water due to recent flooding in the area. | 3 | 10 | 47 | Red Oak | 90 | Healthy | Other identified hazard trees off the ROW were removed.
Q1 2019 | WECC | TO | 230 | No | No | 2019-02-15 | 10980 | Due to a 3 days of heavy rain and wind storm in the area, a large healthy tree located 30 feet outside of the ROW fell into the transmission line. The tree was located on property owned by the county. The maintenance crew removed the tree, assessed the area and determined that no further work is necessary. | 3 | 30 | 111 | Ponderosa Pine | 158 | Healthy | None
Q1 2019 | WECC | GO/TO | 230 | Yes | No | 2019-01-06 | 3494 | A healthy tree broke off 18 feet above the ground during high winds and freezing rain-snow, falling into the transmission line. | 3 | 12 | 32 | Western Hemlock | 100 | Healthy | None
Q1 2019 | SERC | TO | 230 | No | No | 2019-01-20 | 1415 | An off right-of-way live pine tree with internal decay at the base of the trunk broke at base and made contact with the 230 kV line. There was no damage to the facilities. Tree had signs of internal decay, but signs were not externally visible. The soil condition was wet. Storms and high winds were recorded in the area. | 3 | 27 | 57 | Loblolly Pine | 81 | Alive with visible signs of decay at the root | None
Q1 2019 | SERC | TO | 230 | No | No | 2019-01-19 | 556 | A healthy tree uprooted and fell onto the east phase of the line pinning it to the ground between two structures. The soil was saturated due to recent heavy rains. There was no damage to either the wires or conductors. A strong storm front was passing though at the time of the outage. | 3 | 31 | 63 | Oak | 93 | Healthy | None
Q4 2018 | WECC | GO/TO | 115 | Yes | Yes | 2018-11-14 | 156 | A 50-foot tall dead Larch tree located 35 feet outside the Right of Way (ROW) fell into a 115 kV transmission line. The contact resulted in a sustained outage that lasted for roughly 2.5 hours. | 3 | 35 | 45 | Larch | 50 | Dead | Proactive analysis of vegetation on this line is constant along with continuing coordination with the local Forest Service to remove appropriate trees outside of the cleared ROW.
Q4 2018 | WECC | GO/TO | 230 | No | No | 2018-12-14 | 1453 | During high winds and a heavy wet snow storm, a 120-foot tall healthy Western Hemlock tree located 25 feet outside the Right of Way (ROW) fell into a 230 kV transmission line resulting in a sustained outage. The tree uprooted in the heavy storms and the resulting outage lasted approximately 24 hours. There is some indication at the outage site that Phytophthora Root Rot may have been a contributing factor. | 3 | 25 | 45 | Western Hemlock | 120 | Healthy | Contacted property owner to discuss topping or removal of potentially diseased trees adjacent to lines.
Q4 2018 | WECC | GO/TO | 230 | Yes | No | 2018-12-20 | 3780 | During high winds and heavy wet snow storms over the course of several days, a 60-foot tall healthy Western Hemlock tree located 10 feet outside the Right of Way (ROW) fell into a 230 kV transmission line resulting in a sustained outage. The tree uprooted in the storm resulting in an outage that lasted approximately 63 hours. | 3 | 10 | 30 | Western Hemlock | 60 | Healthy | None
Q4 2018 | WECC | GO/TO | 230 | Yes | No | 2018-12-29 | 2437 | A 120-foot tall healthy Douglas Fir uprooted in saturated soils from snow melt fell into a 230 kV transmission line. The location had been battered by high winds and heavy snow storms in the week preceding the outage. The tree uprooted resulting in a sustained outage that lasted approximately 41 hours. | 3 | 25 | 45 | Douglas Fir | 120 | Healthy | None
Q4 2018 | WECC | GO/TO | 230 | Yes | Yes | 2018-12-18 | 2952 | A 95-foot tall healthy Douglas Fir fell into a 230 kV transmission line while being battered by high winds and heavy wet snow storms. The tree uprooted in the storm resulting in a sustained outage that lasted approximately 49 hours. | 3 | 14.5 | 55 | Douglas Fir | 95 | Healthy | The tree was removed.
Q4 2018 | WECC | TO | 230 | Yes | No | 2018-12-16 | 741 | A 90-foot healthy Western Hemlock tree located 28 feet outside the Right of Way (ROW) fell into a 230 kV transmission line during high winds and heavy snow storms. The resulting outage lasted approximately 12.5 hours. The tree top snapped on impact and fell to the ground. | 3 | 28 | 41 | Western Hemlock (Tsuga heterophylla) | 90 | Healthy | Continue to monitor surrounding property for signs of forest decline.
Q4 2018 | WECC | TO | 230 | Yes | No | 2018-12-20 | 1668 | During high winds and heavy snow storms, two healthy Western Hemlock trees fell into the same 230 kV transmission line. One tree snapped on impact and fell to the ground, the other ended up resting on the lines and required additional line deenergization for safety reasons. The Western Hemlock trees were 95 and 70 feet tall and located roughly 28 feet off the Right of Way. | 3 | 28 | 50 | Western Hemlock 2x (Tsuga heterophylla) | 95 and 70 | Healthy and Good | Continue to monitor surrounding property for signs of forest decline.
Q4 2018 | SERC | TO | 230 | No | No | 2018-10-25 | 1160 | A healthy 65-foot Sweet Gum Tree located 20 feet outside the Right of Way (ROW) fell and made contact with a 230 kV transmission line. The tree appeared to be healthy and it was noted that soil conditions were wet. There was no damage to facilities. During the patrol to assess the situation, it was noted that another tree located roughly 75 feet from the ROW initiated the issue. The second tree fell into another tree located 20 feet off the ROW causing it to fall into the line. This transmission line had been scheduled to come out of service on the day the outage occurred (October 25, 2018). This vegetation incident occurred before the line was switched out of service that day. After the patrol was completed, the line was left out-of-service for its scheduled outage which led to an extended outage of approximately 20 hours. | 3 | 20 | 51 | Sweet Gum | 65 | Healthy | The tree was removed from area and Right of Way was inspected for any other hazards. No other risks were identified in the area.
Q4 2018 | SERC | TO | 230 | No | No | 2018-11-12 | 1112 | A 67-foot tall healthy Sweet Gum tree located 15 feet off a 100-foot Right of Way (ROW) fell causing a sustained outage during a rain and thunderstorm event. The soil had suffered from erosion due to recent hurricanes and flooding which weakened the root system and contributed to the event. | 3 | 15 | 47 | Sweet Gum | 67 | Healthy | The tree fell in the clear. Adjacent spans patrolled and no additional risks identified.
Q4 2018 | SERC | TO | 230 | No | No | 2018-12-15 | 409 | A 67-foot tall healthy Oak tree located three feet off a 100-foot Right of Way (ROW) fell causing a sustained outage during a rain and thunderstorm event. The soil had suffered from erosion due to recent hurricanes and flooding which weakened the root system and contributed to the event. | 3 | 3 | 35 | Oak | 67 | Healthy | The tree fell into the clear and is no longer a threat. The surrounding spans were patrolled and no other issues were identified.
Q4 2018 | NPCC | TO | 115 | Yes | Yes | 2018-12-18 | 411 | During a high wind event of 30 mph (47 mph gusts) in the early morning of December 18, 2018, a 115 kV line locked out. A patrol determined that an 80-foot Eastern White Pine tree fell into the easement from eight feet outside the Right of Way. The tree snapped seven feet up from the base and fell downslope, where it landed on the field phase of the 115 kV transmission line. The top of the tree then snapped under the pressure, falling clear of the conductor. A visual examination of the tree found no externally identifiable defects, but internally both decay and insect activity were present. The poor structured pine along with the sustained winds caused the tree to fall resulting in the outage. | 3 | 8 | 42 | Eastern White Pine | 80 | Internal decay and insect activity | The area was inspected with no findings of additional vegetation issues identified. The tree was cut to ground level and the debris cleared.
Q3 2018 | WECC | TO | 230 | No | No | 2018-09-14 | 1002 | The area has been in a steady decline from a widespread infestation of several beetle populations for the past few years. While clearing large numbers of trees as a result of the infestation, a contact tree crew lost control of a live 135-foot tall Red-Fir tree located two feet off the Right-of-Way and it fell onto a 230 kV transmission line. The tree was alive but within a pocket of dead trees along a transmission ROW. The resulting outage lasted approximately 17 hours. | 3 | 50 | 85 | Red Fir - Abies Magnifica | 135 | Alive | Stood down crews and required contractors to perform follow-up tailboards regarding correct tree falling procedures.
Q3 2018 | SERC | TO | 230 | Yes | Yes | 2018-07-04 | 775 | An off right-of-way healthy 96-foot tall Pine tree broke during a localized overnight thunderstorm. The broke top pinned down the outside phase of a 230 kV line. There were no damages to facilities. The tree was located two feet outside the right-of-way. Similar tree damage was observed approximately 100 ft. away from the Pine that caused the outage which remained off the right-of-way and away from the facilities. Location of this outage is almost six miles away from the outage that occurred on this line during Q2 2018. The two events are unrelated as there is no indication to suggest that the storm which caused the outage in Q2 damaged the tree that caused this outage. Due to the high number of strong storms in this area, the entire line was patrolled to identify and remove any potential storm-related threats. | 3 | 2 | 50 | Pine | 96 | Healthy | The tree was removed and the entire line was patrolled to identify and remove any potential storm-related threats.
Q3 2018 | SERC | TO | 500 | No | No | 2018-07-31 | 210 | During a small pop-up thundershower, an off right-of-way live Pine tree with internal decay, broke at the base and made contact with a 500 kV line. The tree was 94 feet tall and located five feet off the right-of-way. There was no damage to facilities. The tree had signs of internal decay but signs were not externally visible. | 3 | 5 | 69 | Pine | 94 | Live tree with not visible signs of internal decay | The tree was removed from the area and the right-of-way was inspected for any other hazards.
Q3 2018 | SERC | GO, TO | 230 | No | No | 2018-07-22 | 795 | An off right-of-way live Water Oak tree, located 19 feet off the ROW broke at roughly six feet from the base and made contact with a 230kV transmission line (likely due to wind). The tree showed root rot signs and numerous indicators were noted on the trunk. Tree had signs of internal decay and they were externally visible. The soil was noted being wet at the time of the patrol next morning. | 3 | 19 | 51 | Water Oak | 68 | Live tree with visible signs of decay | The tree was removed from the area and the right-of-way was inspected for any other hazards. No hazards were identified in the area.
Q3 2018 | SERC | TO | 230 | Yes | Yes | 2018-07-30 | 1948 | A 90-foot tall healthy Oak tree fell onto a transmission line from 30-feet off the right-of-way during a localized thunderstorm/rain event. The resulting outage lasted approximately 32 hours. | 3 | 30 | 62 | Oak | 90 | Healthy | The tree was removed from the line and span plus adjacent spans were checked for at risk trees.
Q3 2018 | SERC | TO | 230 | Yes | Yes | 2018-09-28 | 488 | A healthy 39-foot tall Yellow Poplar tree broke at the root crown and fell into the line from seven feet outside the right-of-way. The tree was rooted on a bank beside a creek bed, and the creek had undercut the bank. Recent heavy rains from remnants of Hurricane Florence saturated the ground and contributed to the breaking of the trunk. It was raining with some wind at the time of the fault. | 3 | 7 | 39 | Yellow Poplar | 95 | Healthy | The tree was removed and the right-of-way was patrolled for additional hazard trees to be removed.
Q3 2018 | FRCC | GO, TO | 230 | No | No | 2018-07-21 | 129 | On July 21, 2018 during a severe thunderstorm, a dead 58-foot tall Black Gum tree fell from outside the right-of-way causing a C phase to ground fault. The fault tripped a 230 kV transmission line. The tree was located in a swamp. Wind gusts were recorded up to 52 mph and wind speed was recorded up to 41 mph. No damage resulted from the falling tree. No notable impact to the BES occurred. The outage lasted approximately two hours. | 3 | 23 | 36 | Black Gum | 58 | Dead | The tree was removed and continued bi-annual work plan.
Q3 2018 | FRCC | TO | 230 | No | No | 2018-07-21 | 43 | A 99-foot tall green Slash Pine tree located 21 feet off the Right of Way failed at the base due to internal rot and fell over into a phase conductor of a 230kV transmission line. The tree was suffering from internal rot. The resulting outage last 43 minutes. The tree was permanently removed afterword. This outage was not related to weather. | 3 | 21 | 42 | Slash Pine | 99 | Green Tree with internal rot | The tree was permanently removed.
Q2 2018 | MRO | TO/GO | 230 | No | No | 2018-06-06 | 491 | A 73-foot dead Poplar tree located 33-feet outside the Right of Way (ROW) fell into a 230 kV transmission line causing an 8 hour outage. The tree was rotting. The root system had been compromised by flooding during the previous year. The ground stopped supporting the tree and it fell into the line from outside the ROW. | 3 | 33 | 64 | Poplar | 73 | Dead with compromised rotting root system | Tree was safely removed by ground crews.
Q2 2018 | NPCC | TO | 230 | No | No | 2018-05-04 | 1251 | During a thunderstorm and high wind event, a healthy 120 foot tall, 29 inch diameter trunk, multi-stem White Pine tree had trunk failure at approximately 30 feet from the base of the tree. Approximately 90 feet of the tree fell and landed on the conductor. The tree was located approximately 4 feet outside of the ROW, 87 feet from the center-line of the ROW. The tree was located 67 feet to the nearest conductor. | 3 | 4 | 67 | White Pine | 120 | Healthy | The ROW sideline was inspected in the area of the fall-in from outside the ROW. No additional issues were identified.
Q2 2018 | NPCC | TO | <200 | No | Yes | 2018-04-04 | 1279 | During a high wind event, a 24 inch diameter multi-stem White Pine tree, that was 94 feet tall and in healthy condition located 8 feet outside the Right of Way (ROW), broke at the trunk and landed on a conductor. The tree was located 8 feet outside of the ROW. The distance from the base of the tree to the conductor was 52 feet. The distance from the center-line of the ROW to the cleared-edge of the ROW is 75 feet. | 3 | 8 | 52 | White Pine | 94 | Healthy | The ROW sideline was inspected in the area of the fall-in from outside the ROW. No additional issues were identified.
Q2 2018 | RF | TO | 230 | No | No | 2018-05-15 | 3196 | On May 15th a 230kV line tripped to lockout during a period of thunderstorms with heavy wind and rain. The cause of this event was determined to be due to an 89 foot tall White Pine tree uprooting from 40 feet outside of the 50 foot centerline Right Of Way edge. The tree made contact with the tower causing the tower to collapse. There were no indications that the tree made any contact with the conductor. The resulting outage lasted approximately 53 hours. | 3 | 40 | 67.5 | White Pine | 89 | Healthy | The entire right of way corridor including this specific area will be patrolled again for hazardous trees as part of the 2018 herbicide cycle. All White Pines will be inspected and evaluated as part of the patrol. These and any other hazard trees will be identified for removal and completed. Future reliability improvements include a data analytics effort to identify areas where hazard trees are most susceptible to fail and cause an outage such that these areas may be prioritized and addressed in a timely matter.
Q2 2018 | SERC | TO | 230 | No | No | 2018-06-08 | 1221 | An off Right of Way (ROW) live 81-foot tall Chestnut Oak tree located 16 feet outside the ROW broke at its base and made contact with a 230 kV line. The tree hung into outside phase causing the line to lock out. No damage to facilities. The tree had signs of root rot, but signs were not externally visible. A small thundershower went through the area at the time of event. The resulting outage lasted approximately 20 hours. | 3 | 16 | 60 | Chestnut Oak | 81 | Live tree with internal decay that was not externally visible upon inspection. | No action needed to address recurrence due to being live tree with internal decay that was not externally visible upon inspection.
Q1 2018 | WECC | GO, TO | 230 | No | Yes | 2018-02-18 | 2157 | A healthy 35-foot Pine tree located just outside the ROW (one foot) fell into a 230 kV transmission line. The location of the failure was initially identified through a helicopter patrol, though the patrol was delayed due to ongoing snow and wind storm conditions in the area. The location of the contact was a remote mountainous area difficult to access, hampering the restoration efforts. The resulting outage lasted nearly 36 hours. Wider inspections of surrounding vegetation are planned for the spring when the ROW is more easily accessible. | 3 | 1 | 33 | Pine | 35 | Healthy | Annual Aerial Assessment to determine Hot Spotting and Programmed Vegetation Management needs
Q1 2018 | SERC | TO | 230 | No | No | 2018-02-07 | 119 | A 100-foot live green Pine tree uprooted and hit a 230 kV transmission line. The tree struck the bottom conductor. The top of the tree broke from the contact with the conductor and passed through to the ground causing the line to lockout. The tree fell out into the right-of-way at a 20-degree angle during significant weather with wind speeds in excess of 20 MPH reported as a storm front passed through area. Heavy rain also occurred in area throughout the day. | 3 | 22 | 74 | Pine | 100 | Healthy | No other tree removal was necessary. In a conservative and precautionary measure, English Ivy that was around the base of the tree was cleared away from tree trunks on adjacent trees.
Q1 2018 | SERC | TO | 230 | No | No | 2018-03-01 | 147 | A live 79-foot Loblolly Pine tree located 23 feet outside the ROW fell during high winds. The tree broke at 23 feet from the ground and made contact with the outside phase of the transmission line. The line operated and locked out resulting in a nearly three hour outage. | 3 | 23 | 54 | Loblolly Pine | 79 | Alive | The tree was removed and the line restored to service at 7:05 pm. Five dead trees were also cut the following day in the area.
Q1 2018 | NPCC | TO | 345 | No | Yes | 2018-03-02 | 708 | During a Nor'Easter storm with heavy snow and severe winds, an 85-foot multi-leader White Pine tree outside the northern maintained edge of the ROW split near its base and made contact with the closest phase of a 345 kV transmission line. The tree was located in a slightly uphill configuration. | 3 | 13 | 63 | White Pine | 85 | Healthy | Remainder of the tree was removed. The surrounding area was inspected and no other critical vegetation issues were found. Routine removals identified for removal.
Q1 2018 | NPCC | TO | <200 | No | Yes | 2018-03-02 | 1290 | A 95-foot tall healthy White Pine tree fell from off the ROW into a transmission line. During Nor'Easter snowstorm Riley, a 115 kV transmission line locked out. A patrol determined an Eastern White Pine tree made contact from off easement as a "fall-in" as evidenced by one side of the co-dominant split away and came to rest on the 115 kV H-Frame lines. The extreme winds (over 85 mph) in combination with co-dominant pine resulted in the poor structured pine failing and causing an outage. Working the tree during the storm was difficult due to high winds and snowy wet weather. Tree was accessed from hilly wet area. The pine tree was on a ridge. All tree work was performed with manual climbing tree crews. | 3 | 14 | 49 | White Pine | 95 | Healthy | The remainder of the tree was removed. The area was inspected and no other vegetation issues were identified.
Q1 2018 | NPCC | TO | 345 | No | No | 2018-03-02 | 156 | A healthy 105-foot Eastern White Pine tree fell into a transmission line during a storm. During Nor'Easter snowstorm "Riley", a 345 kV line tripped, restored, and reclosed several times. Reclosing turned off due to voltage transients at a nearby Nuclear Power Plant. The transmission line tripped out. A vegetation ground patrol determined that an Eastern White Pine tree made contact from off easement as a "blow-in" as evidenced by carbon "burning" at the top of tree. The tree did not break or "wind throw." The extreme winds (over 85 mph) in combination with the tree in a wetland location appears to have caused enough movement of root cap and swaying of trunk of tree to draw an arc. | 3 | 8 | 23 | Eastern White Pine | 105 | Healthy | The tree was removed to prevent potential future contact. Two additional adjacent trees were also removed, being the same distance and having the same site conditions.
Q1 2018 | FRCC | TO | 230 | No | No | 2018-03-21 | 418 | An 85-foot Slash Pine tree located ten feet outside the Right of Way sustained a complete failure at its base due to fresh gale conditions. | 3 | 10 | 35 | Slash Pine | 85 | Failed at base | The tree that caused the vegetation contact has been removed.
Q4 2017 | SERC | TO | 230 | No | No | 2017-11-18 | 2857 | A live 70-foot Sycamore tree uprooted and fell into a 230 kV transmission line during storms and high winds on November 18. Wind and wet soil caused the tree to uproot. Due to the remote location and the weather, aerial patrols were not dispatched until early the following day. Line and vegetation crews worked together to remove the tree off the downed wires and remove the old structure. A new structure was installed and line was returned to service on November 20. The outage lasted approximately 48 hours. | 3 | 4 | 39 | Sycamore | 70 | Alive with no visual defects | Due to the remote location and weather, aerial patrols were dispatched early the next day. The line and vegetation crews worked together to remove the up-rooted tree off the downed wires and wreck out the old structure. At approximately 15:13 on November 20, the line crews completed installation of a new structure and returned the line back to service. No other tree issues were noted from ground inspections of the area.
Q4 2017 | WECC | TO | 115 | Yes | Yes | 2017-11-23 | 277 | During a snowstorm, a 90-foot tall dead Pine tree located 20 feet outside the right-of-way fell into a transmission line. The resulting outage lasted over four hours. | 3 | 20 | 35 | Pine | 90 | Dead | Constant proactive analysis of vegetation on this line along with continuing coordination with the local Forest Service to remove appropriate trees outside of the cleared Right of Way.
Q4 2017 | WECC | TO | 230 | No | No | 2017-11-13 | 1555 | An 85-foot Douglas Fir tree located 33 feet outside the right-of-way during high winds. The tree broke center phase and was leaning on the bottom phase. The resulting outage lasted approximately 26 hours. Along with the offending tree, additional trees in the immediate area with similar threat profiles were removed. | 3 | 33 | 56 | Douglas Fir | 85 | Tree Alive | Removed additional trees with similar threat-profiles in the immediate area.
Q4 2017 | FRCC | TO | 230 | Yes | No | 2017-09-10 | 1652 | A 65-foot tall healthy Oak tree located ten feet outside the right-of-way leaned in toward a transmission line in a swampy area due to wind and rain from Hurricane Irma. The tree rested against the “A” and “C” phase conductors causing the line to trip and lock out. The resulting outage lasted approximately 27 hours. The tree has been removed from the line. | 3 | 10 | 40 | Oak | 65 | Healthy | Removed the tree from the line.
Q3 2017 | RF | TO | 230 | No | No | 2017-08-05 | 612 | A 91-foot tall healthy Red Maple tree fell in from outside the Right-of-Way (ROW). An off corridor live Red Maple tree approximately 91’ tall and 17” diameter at breast height (DBH) uprooted due to high winds and subsequently fell into the ROW contacting the conductor (Z Phase). The Red Maple tree was located approximately 8’ from the edge of the maintained ROW. The service area experienced high winds and thunderstorms on August 4, 2017. Wind gusts of 40-50 mph were reported in the weather report for the closest location that day. Wind gusts of 30-40 mph were also reported the following day, the day of the outage. The multiple storms, high winds, and heavy rain caused the tree to slowly uproot and fall into the line causing the outage. The outage lasted approximately six hours. | 3 | 8 | 62 | Red Maple | 91 | Healthy | After the initial assessment, there was a thorough review of the surrounding spans via foot patrol to ensure that there were no other tree conditions that could cause any further reliability concerns. Two additional trees were identified for removal as a precaution, but no other issues were identified.
Q3 2017 | RF | TO | 230 | No | No | 2017-08-06 | 798 | Fall-in from outside the Right-of-Way (ROW). An off corridor healthy Basswood tree approximately 105 foot tall and 25 inch diameter at breast height (DBH) uprooted and fell into a Hickory tree, approximately 111 foot tall and 27 inch DBH, which uprooted and both trees fell into the ROW, contacting the conductor (Y Phase), due to high winds. The Basswood tree was located approximately 72 feet from the edge of the maintained ROW. The Hickory tree was located approximately 55 feet from the edge of the maintained ROW. The service area experienced high winds and thunderstorms on August 4th and August 5th. The high winds likely caused the Basswood to uproot into the Hickory and slowly uprooted the Hickory into the conductor on August 6, 2017. A week prior to the event (July 23-24), there was a major wind event in the area of the outage according to the forest service; a couple hundred trees came down but no outages resulted. On August 3, a scheduled aerial patrol was performed, and wind damage was found in the span from the prior wind event. Follow-up ground patrol was scheduled for the following week to remove trees showing signs of damage from the wind, but no reliability issues were found in the field during the patrol. | 3 | 72 | 100 | Basswood | 105 | Healthy Healthy | After the initial assessment, there was a thorough review of the surrounding spans via foot patrol to ensure that there were no other tree conditions that could cause any further reliability concerns. Six additional trees in the same span were identified for removal as a precaution, but no other issues were identified.
Q3 2017 | SERC | TO | 230 | No | No | 2017-08-23 | 1124 | A 65-foot healthy Poplar tree located eight feet outside the Right of Way fell into a 230 kV transmission line as rain and storms passed through the area. The resulting outage lasted approximately 18 hours. | 3 | 8 | 35 | Poplar | 65 | Alive with no external signs of decay. | The tree was removed and surrounding spans were checked on the line to ensure that no other trees in the area were impacted by the storm activity.
Q3 2017 | SERC | TO | 230 | No | No | 2017-07-08 | 109 | A 78-foot tall healthy green Pine tree fell into a 230 kV transmission line during severe winds and thunderstorm. The resulting outage lasted approximately 23 hours. The following day the entire line was patrolled by air and no other hazardous trees were noted. | 3 | 1 | 41 | Pine | 78 | Alive, green and healthy. No obvious defects. | The entire line was patrolled by air the following day and no other tree problems were noted.
Q2 2017 | RF | TO | 345 | No | No | 2017-04-03 | 1170 | A 105-foot Tulip Poplar tree located approximately 54 feet from the edge of the Right-of-Way (ROW) fell into another tree. The second tree was an approximately 99-foot tall Beech tree, which uprooted as a result of the falling Tulip Poplar tree and fell into the ROW contacting the conductor. The Beech tree was located approximately 24 feet from the edge of the ROW. After inspecting the fallen tree, it was determined that though the tree was alive, it had internal decay and was hollow. The inspection also discovered a noticeable water stain on the remaining stub, which began at the point of failure at 25 feet above the ground. Weather was not a contributing factor. An adjacent 345kV line was also affected during the outage from the off-ROW fall-in. At the time of the line trip, the entity was performing planned breaker maintenance on one of the three 345kV breakers in the ring bus configuration at a substation. When the off-ROW fall-in occurred, the two in-service 345kV breakers at the substation opened as designed; however, this open-ended another 345kV line at the substation because the other 345kV breaker was open for maintenance. | 3 | 24 | 75 | Beech | 99 | Healthy with Internal Decay and Hollow | After the contact, surrounding spans were reviewed to ensure there were no other existing tree conditions; no other issues were identified.
Q2 2017 | RF | TO | 230 | No | No | 2017-05-01 | 1487 | A healthy 92-foot tall Pine tree located 3 feet off the Right-of-Way (ROW) uprooted due to extremely high winds and subsequently fell into the ROW contacting the conductor (B Phase). The service area experienced a severe storm with high winds, thunderstorms, and tornado warnings. Wind gusts of 60-70 mph were reported in the weather report. | 3 | 3 | 58 | Pine | 92 | Healthy | Upon arrival at the site of the outage, it was identified that there were hundreds of trees uprooted and laying on the ground due to severe storms in the area. After the initial assessment found the pine tree on the conductor, there was a thorough review of the surrounding spans via foot patrol to ensure that there were no other tree conditions that could cause any further reliability concerns. None were identified. Following the outage, Emergency Aerial Patrols were performed on this circuit and additional circuits in the area, due to the severe storm. No additional vegetation reliability concerns were identified as a result of the aerial patrols.
Q2 2017 | SERC | TO | 230 | No | No | 2017-05-29 | 944 | An 80-foot apparently healthy Poplar tree located 18 feet outside the Right-of-Way fell on a transmission line during storm activity with high winds. The falling tree resulted in a sustained outage. The weather at the time of the interruption was 71 degrees with severe thunderstorms capable of producing hail, straight line winds and cloud to ground lightning. The outage lasted approximately 16 hours. Though the tree appeared to be healthy externally, internal decay was discovered after the failure. | 3 | 18 | 50 | Poplar | 79 | Healthy with Internal Decay | The remaining stem of the tree was removed and surrounding spans were checked on the line to ensure that no other trees in the area were impacted by the storm activity.
Q2 2017 | SERC | TO | 230 | No | No | 2017-05-22 | 1246 | A 70-foot tall apparently healthy Poplar tree located 8 feet off the Right-of-Way fell into a 230kV transmission line during a thunderstorm. The tree appeared healthy externally but root decay was detected after the failure. The contact resulted in an outage that lasted approximately 21 hours. | 3 | 8 | 40 | Poplar | 70 | Healthy with Root Decay | The tree cleared itself from the line but surrounding spans were checked on the line to ensure that no other trees in the area were impacted by the recent storm activity.
Q2 2017 | SERC | TO | 500 | No | No | 2017-05-20 | 165 | A 100-foot tall healthy Sweetgum tree located near a drain (and located only two feet off the Right-of-Way) fell into the outside phase of a transmission line causing the line to operate. Shallow roots and erosion played a role in creating the conditions for the fall, the soil was rocky and the root structure was shallow, but isolated thunderstorms were in the area with heavy rains and high winds provided the final catalyst. | 3 | 2 | 56 | Sweet Gum | 100 | Healthy | Tree did not have to be removed from line and no damage to the conductor. A Danger Tree crew cut several large trees nearby because of the root structure of the tree that failed and the rocky soil.
Q1 2017 | WECC | TO | 230 | Yes | No | 2017-01-02 | 1430 | A healthy 60-foot Hemlock tree, located 23 feet outside the Right-of-Way, fell south into a line during localized high wind conditions. The resulting outage lasted approximately 24 hours. | 3 | 23 | 39 | Hemlock | 60 | Healthy | Crews inspected the immediate area. No imminent threats were discovered.
Q1 2017 | WECC | TO | 230 | Yes | No | 2017-02-09 | 1888 | A 90-foot tall healthy Douglas Fir tree, located 21 feet off the Right-of-Way, was uprooted by the snow load and high winds resulting in an outage. The outage lasted approximately 31 hours. | 3 | 21 | 37 | Douglas Fir | 90 | Healthy | Crews inspected the immediate area. No imminent threats were discovered.
Q1 2017 | WECC | TO | 120 | No | No | 2017-01-10 | 645 | An apparently healthy 90-foot tall (approximately) Jeffery Pine tree located approximately 25 feet off the Right-of-Way, fell into power lines in January during a snow storm in the area. Though the tree appeared healthy, tree conditions were difficult to measure, the base was buried in snow and the fallen portion of the tree was buried in more than ten feet of snow. | 3 | 25 | 50 | Jeffrey Pine | 90 | Healthy | A contractor cleared the tree from the lines. The tree was on private property. It was deemed impractical to remove every tree within 50’ of the lines on a proactive basis. The area was under 7-8 feet of snow at the time, making difficult conditions.
Q1 2017 | SERC | TO | 230 | No | No | 2017-01-26 | 248 | During storm activity with high winds, a dual-stem 78-foot tall healthy pine tree fell causing a sustained outage. One stem broke about 12 feet above the ground and fell into transmission and distribution lines that share the ROW. The outages lasted a little over four hours. The tree was located 12 feet outside the ROW. | 3 | 12 | 48 | Pine | 78 | Healthy | The remaining stem of the pine tree was removed, and nearby trees and spans were checked on the line to ensure that no other trees in the area were impacted by the local storm event.
Q1 2017 | SERC | TO | 230 | Yes | No | 2017-03-01 | 267 | During weather conditions where wind gusts of 38 mph were reported, an off right-of-way green, 72-foot tall Sweetgum tree broke two feet up from the ground and made contact with a 230kV line. Line construction is on a single pole with three vertical phases. The tree passed through the top conductor and then hung on the middle and bottom phase locking the line out. The line on this right-of-way is built thirty feet from the western edge of the right of way. The tree measured thirty-one feet from the centerline of the stated line so the tree was one foot off right-of-way. The tree was covered with English ivy all around the base and ivy dominates floor cover in the area. The ivy had grown up the entire height of the tree. Though the tree was alive, it had heart rot/decay in the center of the trunk where the break point was located. | 3 | 1 | 31 | Sweetgum | 72 | Live Tree with Internal Decay | Ivy was cleared away from tree trunks on adjacent trees and crews performed detailed trunk inspections. As a result, additional trees off the right-of way were identified to be cut down.
Q1 2017 | SERC | TO | 230 | No | No | 2017-01-06 | 1139 | An apparently healthy 70-foot Water Oak tree, located 37.5 feet off the right of way (in a private backyard) was uprooted during inclement weather and fell into a line. The outage lasted just under 19 hours. | 3 | 37.5 | 47.5 | Water Oak | 70 | Healthy | Tree was removed and surrounding area inspected for similar potential issues.
Q1 2017 | FRCC | TO | 230 | Yes | No | 2017-02-07 | 2890 | A 105-foot Live Oak tree located on the west side of the ROW that appeared healthy caused an outage. The tree was 34 feet off the right of way. When the tree, fell it damaged the H-Frame structure. During the outage a weather station nearby documented wind gusts at 46 MPH. At the location of the outage, there were 8-10 other large trees that were either broken or uprooted. Several trees were entangled in the parallel distribution line on the easement. The outage lasted approximately 48 hours. | 3 | 34 | 67 | Oak | 105 | Tree appeared healthy "full leaf out" from the 2015 fall aerial inspection and when observed during the 2015 maintenance trimming of the entire line. A post job inspection following the 2015 maintenance trimming did not identify this tree as a hazard tree. Fungus was discovered growing on the west facing side of the tree (away from the cleared right of way) during an inspection of the tree following the outage. The tree showed signs of internal rot which could not be seen from the right of way. This line was also patrolled during the 2016 aerial patrols and no hazard trees were identified in this span. | A crew was called to site to remove the tree from the conductors and line was restored. Contractors performed an assessment to better identify where the outages have occurred. This area will have a thorough hazardous tree inspection performed and hazardous trees identified will be removed.
Q4 2016 | FRCC | GO, TO | 230 | Yes | No | 2016-10-07 | 550 | Due to Hurricane Matthew, powerful storms in the area resulted in gale force winds and a healthy 60-foot Water Oak tree growing just outside of the right-of-way falling into phases “A” & “C” of a 230 KV line. | 3 | 1 | 27.5 | Water Oak | 60 | Healthy | Line was de-energized and the tree was removed from the line(s) and disposed.
Q3 2016 | SERC | TO | 230 | No | No | 2016-07-16 | 136 | A live 72-foot Pine tree located 26-feet off the right-of-way broke approximately 10' above ground and fell through the line during high winds from a significant thunderstorm event. The surrounding area was inspected to be sure there were no other vegetation-related issues that could cause reliability threats; no other issues were identified. | 3 | 26 | 65 | Pine | 72 | Healthy | No action needed to address recurrence. This was a weather related event involving a Pine tree, located off right-of-way, caused by high winds due to a significant thunderstorm.
Q3 2016 | SERC | TO | 230 | No | No | 2016-07-22 | 483 | A 92-foot Poplar tree located 3-feet off the right-of-way appeared to have been uprooted during an afternoon thunderstorm the day before the event. The tree leaned up against a Pine tree and slowly started bowing out toward line and made contact with top and middle conductors. The tree appeared live but was suffering from internal decay that would not have been visible during inspections. | 3 | 3 | 85 | Poplar | 92 | Live tree with internal decay which would not have been evident during a visual inspection. | The surrounding area was inspected to ensure that there were no other vegetation-related issues that could cause reliability threats; no other issues were identified.
Q3 2016 | SERC | TO | 230 | Yes | No | 2016-07-28 | 413 | During an afternoon thunderstorm, an 87-foot Green Sweetgum tree located 22 feet off the right-of-way, broke eight and one-half (8.5) feet up from the ground and fell across all phases of two lines. The surrounding area was inspected for any other vegetation-related issues that could cause reliability threats; during this inspection two declining hardwoods were identified and were subsequently removed the following week. | 3 | 22 | 72 | Sweetgum | 87 | Live tree with internal decay. | The surrounding area was inspected for any other vegetation-related issues that could cause reliability threats; during this inspection two declining hardwoods were identified and were subsequently removed the following week.
Q3 2016 | SERC | TO | 230 | No | No | 2016-07-28 | 403 | During an afternoon thunderstorm, an 87-foot Green Sweetgum tree located 22 feet off the right-of-way, broke eight and one-half (8.5) feet up from the ground and fell across all phases of two lines. | 3 | 22 | 72 | Sweetgum | 87 | Live tree with internal decay. | The surrounding area was inspected for any other vegetation-related issues that could cause reliability threats; during this inspection two declining hardwoods were identified and were subsequently removed the following week.
Q3 2016 | SERC | GO, TO | 230 | No | No | 2016-07-05 | 200 | An 88-foot tall Loblolly Pine tree located 18 feet off the right-of-way was found on a transmission line. The tree was alive with some trunk rot causing it to snap 13 feet above the ground. The tree was removed. | 3 | 18 | 50 | Loblolly Pine | 88 | Tree was alive with some trunk rot, causing trunk to snap 13 feet above ground level. | The tree was removed and no additional issues were observed in the area.
Q3 2016 | SERC | GO, TO | 230 | No | No | 2016-07-08 | 606 | A 65-foot Loblolly Pine tree located 7 feet off the right-of-way fell into a transmission line causing an outage during strong winds. The tree was alive but rotted at the stump center. The tree was removed and no additional issues were observed. | 3 | 7 | 35 | Loblolly Pine | 65 | Tree was alive but was rotted at the stump center. | The tree was cut off of the wire and no additional issues were observed in the area.
Q3 2016 | SERC | GO, TO | 230 | No | No | 2016-07-20 | 386 | A healthy 115-foot tall Loblolly Pine tree located 57 feet off the right-of-way fell into the line causing an outage. The tree fell while there high winds in the area. The tree was removed and no additional issues were observed in the area. | 3 | 57 | 88 | Loblolly Pine | 115 | Healthy | The tree was cut off of the wire and no additional issues were observed in the area.
Q3 2016 | SERC | TO | 230 | No | No | 2016-07-03 | 322 | A 65-foot tall healthy Maple tree adjacent to the line and located 8 feet off the right-of-way, uprooted and fell into the line during thunderstorm activity and high winds resulting in a sustained outage. The 14 inch (DBH) tree was healthy but located in a wet area (due to recent rains) and fell onto the line during the local storm event. | 3 | 8 | 40 | Maple | 65 | Healthy | The tree that fell and other nearby trees were removed, and nearby spans were checked on the line to ensure that no other trees in the area were impacted by the local storm event.
Q3 2016 | NPCC | TO | <200 | No | Yes | 2016-07-25 | 608 | During a thunderstorm event, one leader of a twin stemmed Black Locust tree approximately 90 feet tall broke approximately 15 feet above ground and fell into the line contacting two phases. The contact resulted in the line locking out. The tree was removed and the line returned to service after approximately 10 hours (delays in switching at the UI Facilities). Upon further examination of the tree base, it appears there was extensive internal decay that was not visible prior to the tree failure. The tree was 16 feet outside the maintained and easement limit of the right-of-way. | 3 | 16 | 37 | Black Locust | 90 | Extensive internal decay that was not visible prior to the tree failure. | The tree and the tree parts that were the cause of the contact have been removed. The remaining locust leader as well as several other white pines in this location have been permissioned and are scheduled for removal.
Q2 2016 | SERC | GO, TO | 230 | No | No | 2016-04-02 | 569 | A 98-foot Pine tree located 22 feet outside the ROW fell into the line during a localized thunderstorm. The winds of the storm and the saturated soil may have contributed to the outage. | 3 | 22 | 54 | Pine | 98 | Healthy | Tree was cut to the ground. No other danger trees were identified for removal.
Q2 2016 | SERC | GO, TO | 230 | No | No | 2016-04-07 | 6 | A 104-foot tall Red Oak tree located 40-feet outside the ROW on a creek bank. The healthy tree was weakened due to the flowing water in the creek and a storm in the area. | 3 | 40 | 72 | Red Oak | 104 | Healthy | Tree was cut to the ground. No other danger trees were identified for removal.
Q2 2016 | SERC | GO, TO | 230 | No | No | 2016-06-12 | 246 | Storms in the area contributed winds and saturated soil causing a pine tree to fall into the line. The 89-foot Pine tree was located 14-feet outside the ROW. | 3 | 14 | 46 | Pine | 89 | Healthy | Tree was cut to the ground. No other danger trees were identified for removal.
Q2 2016 | SERC | GO, TO | 230 | No | No | 2016-06-17 | 1186 | Strong storms with high winds and heavy rains caused 88-foot Willow Oak tree located 14-feet outside the ROW to fall into a line. This caused the failure of several x-arms and broke several poles. The tree was alive but had some trunk decay. | 3 | 14 | 45 | Willow Oak | 88 | Healthy with some trunk decay | The transmission crew replaced the poles, corrected the associated damage, and returned the line to service. Back side of tree trunk had decay. The tree was removed along with one additional Oak tree that also had decay on its trunk.
Q2 2016 | SERC | TO | 230 | No | No | 2016-04-11 | 1113 | Weather reported to be in the area at time of outage caused a 90-foot Oak tree and a 110-foot Pine tree to fall into the line at the same span. Both trees appeared to be alive and healthy with no visible defects at the time of the outage restorations. Thunderstorms, winds, and wet ground conditions were all contributors to the tree becoming up-rooted. | 3 | 29 | 64 | Pine and Oak | 90 and 110 | Healthy | Patrolled area of outage with no other work actions required.
Q2 2016 | SERC | TO | 230 | No | No | 2016-06-05 | 956 | A healthy 75-foot tall Poplar located 17-feet outside the ROW fell during a supercell thunderstorm moving through the area, with estimated winds of roughly 55 mph. | 3 | 17 | 47 | Poplar | 75 | Healthy | Span 21-22 and adjacent spans were inspected to determine if any other fall-in risks were present, and none were found.
Q2 2016 | SERC | TO | 230 | No | No | 2016-06-17 | 152 | An outage was caused by high winds, generated from a severe thunderstorm event. The storm caused a healthy Pine tree located 15-feet off the ROW to snap 6 feet above ground level and fall into the line. The tree was approximately 60 feet tall and 16" DBH. | 3 | 15 | 47 | Pine | 60 | Healthy | An inspection of the area where the outage occurred was performed and no other hazard tree related issues were identified.
Q2 2016 | SERC | TO | 230 | No | No | 2016-05-10 | 225 | A healthy 54-foot tall Sweet Gum tree (that was located 49 feet from the centerline on a 90' ROW) fell into a line causing an outage during a localized thunderstorm. The Robinson Plant - Rockingham 230kV line was sectionalized, and load was restored from the Robinson Plant in 66 minutes. | 3 | 4 | 31 | Sweet Gum | 54 | Healthy | Adjacent spans where inspected to determine if any other off-ROW trees presented a similar fall-in risk, and none were found.
Q2 2016 | SERC | TO | 230 | No | No | 2016-04-09 | 362 | Winds gusting to 29 mph caused a 74-foot Red Oak tree located 30 feet off the easement to break 10 feet above ground. The tree fell into a Water Oak tree located 6 feet off the easement knocking it into the outside conductor. The terrain was difficult and damage to the conductor extended the outage duration. The Water Oak tree that struck the line was healthy but the larger Red Oak tree that initiated the fall had a hollow in the trunk. | 3 | 6 | 47 | Water Oak | 74 | Water Oak Healthy and Red Oak had a hollow in the trunk. | Other trees on this hillside were inspected by our contract Danger Tree crew. Several trees in this area were removed.
Q2 2016 | WECC | TO | 115 | Yes | Yes | 2016-06-01 | 87 | A 90-foot dead Pine tree located 50 feet outside the ROW fell into the line. | 3 | 50 | 85 | Pine | 90 | Dead | Constant proactive analysis of vegetation on this line along with continuing coordination with the local Forest Service to remove appropriate trees outside of the cleared ROW.
Q1 2016 | FRCC | TO | 230 | Yes | No | 2016-02-24 | 416 | At 7:07am a thunderstorm hit the area causing a 75 foot Oak tree to break 12’-15’ from the ground. The Oak tree was 10.5’ off the edge of the easement. The easement is 100’ wide (50’ east and west of the center line). No known service interruptions resulted. The outage ended at 14:03 the same day. | 3 | 10.5 | 33.5 | Oak | 75 | Tree appeared healthy "full leaf out" from the 2015 fall aerial inspection and when observed during the 2015 maintenance trimming of the entire line. A post job inspection following the 2015 maintenance trimming by a arborist did not identify this tree as a hazard tree. Fungus was discovered growing on the west facing side of the tree (away from the cleared right of way) during an inspection of the tree following the outage. The tree showed signs of internal rot which could not be seen from the right of way. | A crew was called to site to remove the tree from the conductors and line was restored. The crew also found 3 additional hazardous trees in the same area and those trees were removed.
Q1 2016 | NPCC | TO | 345 | No | No | 2016-03-01 | 727 | During a high wind event, a healthy single stem, 74-foot tall, 18-inch DBH (diameter at breast height) Eastern Hemlock located 22.5 feet outside the northern maintained edge of the ROW, broke near its base and made contact with the closest phase of the 312 transmission line. The base of the tree was 52 feet from the closest phase and the tree was located on the uphill, north side of the ROW. Hazard tree inspections and removals were completed on this section of the line in 2015. | 3 | 22.5 | 52 | Hemlock | 74 | Healthy | The tree that was the cause of the contact has been removed. Area inspected for other problematic conditions and are either being corrected or scheduled for corrective actions.
Q1 2016 | NPCC | TO | <200 | No | Yes | 2016-03-28 | 1079 | During a high wind event, a healthy, approximately 75-foot tall, 22 inch DBH, Eastern Hemlock tree located 25 feet outside the eastern limit of the easement edge of the ROW, broke about 25 feet above the ground and made contact with the outer phase of the transmission line. The base of the tree was 35 feet from the closest phase of the line and located on the east side of the north to south oriented ROW. There was no evidence of defect or decay. | 3 | 25 | 35 | Hemlock | 75 | Healthy | The tree that was the cause of the contact has been removed. Area inspected for other problematic conditions and are either being corrected or scheduled for corrective actions.
Q1 2016 | SERC | TO | 230 | No | No | 2016-02-24 | 592 | During a weather-related event, an 85-foot healthy Pine tree located three feet outside the ROW fell through several conductors. When the tree fell through the conductors, the circuit protection operated. However, a broken limb from the tree hung on the conductor and contacted the grounded structure resulting in the lockout. After the limb was removed the line was placed back in service. There was no conductor damage. The tree appeared healthy from the outside but was suffering from internal decay that would not be visible during routine inspections. | 3 | 3 | 73 | Pine | 85 | Live tree with internal decay that would not have been visible during routine inspections. | It is standard procedure to check multiple spans on either side of the affected span. The crews surveyed the additional spans at the time of the incident and no other issues were found. No other actions were necessary. This occurred during a weather related event in which high straight line wind gusts occurred throughout the day resulting in a large number of outages statewide.
Q1 2016 | SERC | TO | 230 | No | No | 2016-02-24 | 4 | A 102-foot healthy Loblolly Pine tree located in a private backyard uprooted during high winds. Wind gusts were reported at 43 miles per hour. It fell onto a shed and a 115kV de-energized transmission line that shared the same corridor as another 230 KV line. The tree rested just a few inches from the 230 kV middle phase, but close enough to cause the outage. | 3 | 33.5 | 101 | Pine | 102 | Healthy | It is standard procedure to check multiple spans on either side of the affected span. The crews surveyed the additional spans at the time of the incident and no other issues were found. No other actions were necessary. This occurred during a weather related event in which high straight line wind gusts occurred throughout the day resulting in a large number of outages statewide.
Q1 2016 | SERC | GO, TO | 230 | No | No | 2016-03-29 | 639 | A healthy 110-foot Oak tree located 39 feet outside the ROW fell during high winds. The soil condition was wet and the tree fell and came into contact with a 230 kV transmission line during a storm. A recloser failed to operate resulting in the outage. | 3 | 39 | 71 | Oak | 110 | Healthy | It is standard procedure to check multiple spans on either side of the affected span. The crews surveyed the additional spans at the time of the incident and no other issues were found. No additional actions were necessary.
Q1 2016 | SERC | TO | 230 | Yes | No | 2016-02-24 | 2690 | A 71-foot healthy Pine tree (10in. DBH) located 45 feet outside of a ROW corridor broke at ground level and fell into conductor during high winds. Following the outage, the line was sectionalized. The conductor and the cross-arm were damaged, requiring repairs to line prior to re-energizing. The outage lasted approximately 44 hours. | 3 | 45 | 32 | Pine | 71 | Healthy | The fallen tree and three others adjacent to it in the span were removed. Trees in adjacent spans were reviewed and no additional issues were found.
Q4 2015 | SERC | TO | 230 | No | No | 2015-11-09 | 1694 | A 112-foot healthy green Hickory tree located outside the right-of-way uprooted and fell into the outside conductor. The tree was green with no visible faults. The soil was saturated from recent rains. | 3 | 50 | 82 | Carya | 112 | Healthy | Tree was removed from conductor. The danger tree crew and foresters did a survey of all trees in this wetland. We removed several more trees because of the saturated soils and size of the trees.
Q4 2015 | SERC | TO | 230 | No | No | 2015-10-04 | 216 | Crew found a 70-foot green Loblolly Pine tree with root rot from outside the right-of-way on the line. Probable cause was root rot with wet soil and winds from a local storm. | 3 | 2.5 | 42.5 | Loblolly Pine | 70 | Tree was alive some present "root-rot," in wet soil. | Tree was cut down and removed. Line was placed back into service.
Q4 2015 | SERC | TO | 230 | No | No | 2015-10-04 | 271 | An 82-foot Loblolly Pine tree located 25 feet outside the right-of-way fell due to root rot in wet soil. The fallen tree caused an outage on a 230 kV line. A lineman found the tree in contact with a structure. | 3 | 25 | 45.5 | Loblolly Pine | 82 | Alive; some present "root-rot;" wet soil | Tree fell to ground. The line crew cut it away from the structure. No other remediation was necessary in the area.
Q4 2015 | SERC | TO | 230 | No | No | 2015-10-16 | 231 | A 65 foot tall dead Yellow Poplar tree that was rooted 35 feet from the edge of the right-of-way. The tree broke at its base and hit a conductor. Significant rotting was found at the base of the tree. Strong winds are believed to have pushed the tree over. | 3 | 35 | 50 | Yellow Poplar | 65 | Dead. With rotting around the base of the tree. | Other trees in the area were inspected, and no other vegetation/tree issues were found.
Q4 2015 | SERC | TO | 500 | Yes | No | 2015-12-31 | 734 | The area had experienced prolonged flooding and heavy rains that washed away a creek bank resulting in the uprooting of an 87-foot Oak tree located 35 feet outside the right-of-way. The tree fell into a second smaller hardwood, pushing the second tree to within three feet of conductors. The second tree was energized and tripped the line. | 3 | 35 | 90 | Oak | 87 | Healthy | No action needed to address recurrence. This was a weather related event involving two trees, off the right-of-way, which were impacted due to historical prolonged rainfall and flooding.
Q4 2015 | SPP | TO | 345 | No | No | 2015-11-17 | 497 | Heavy rains occurred off and on throughout the day with some severe storms and high winds. At the time of the outage, the closest weather station reported heavy thunderstorm and rain including 24-34 mph winds. The storm led to a 78-foot Loblolly Pine tree that was located 83 feet outside the right-of-way falling and causing an outage on a 345 kV line. | 3 | 83 | 58 | Loblolly Pine | 78 | Green tree with root rot | None
Q4 2015 | WECC | TO | 115 | Yes | Yes | 2015-12-24 | 720 | A healthy 80-foot Douglas Fir tree located 15 feet outside the right-of-way broke above the ground line during a snowstorm. The falling tree caused an outage on a 115 kV transmission line. | 3 | 15 | 50 | Douglas Fir | 80 | Healthy | Constant proactive analysis of vegetation on this line along with continuing coordination with the local Forest Service to remove appropriate trees outside of the cleared R-O-W.
Q4 2015 | WECC | TO | 230 | No | No | 2015-11-13 | 632 | A healthy 110-foot Douglas Fir tree located 55 feet outside the right-of-way uprooted during localized strong winds and fell east into a transmission line. This outage was weather related but did not occur during a major storm. | 3 | 55 | 67.5 | Douglas Fir | 110 | Healthy | None, tree was healthy, failure was due to high winds
Q3 2015 | FRCC | GO, TO | 230 | No | No | 2015-07-04 | 558 | Due to powerful storms in the area and resulting gale force winds, a healthy 80-foot pine tree, growing outside of the right-of-way fell into both a 115kV line as well as a 230kV line from beyond the right-of-way limits. | 3 | 5 | 45 | Pine | 80 | Healthy | Line was de-energized and the tree was removed from the line(s) and disposed of.
Q3 2015 | NPCC | TO | 345 | No | No | 2015-06-23 | 1188 | A major storm with winds in excess of 70 mph (with confirmed Micro-Bursts and Tornado warnings) caused an outage on a 345 kV line. The strong winds appear to have led to a 92-foot tall healthy hickory tree on the cleared edge outside of the ROW to have blown over and caused the top of the tree to come close enough to the conductor to cause a trip. The line reclosed and then tripped out after which the tree must have become free from the line. The line was patrolled and re-energized following the patrol. It was estimated that the tree bent over almost 90 degrees and covered the distance between the conductor and the tree branch, estimated to be over 50 feet. | 3 | 2 | 32 | Hickory | 92 | Healthy | The tree that was the cause of the contact has been removed. Area inspected for other problematic conditions and are either being corrected or scheduled for corrective actions.
Q3 2015 | SERC | TO | 500 | No | No | 2015-07-02 | 859 | During a thunderstorm, a 105-foot oak live tree with internal decay in the trunk, located 37 feet outside the ROW broke at its base and caused an outage on a 500kv line. The tree was approximately 90 feet from the nearest conductor. | 3 | 37 | 90 | Oak | 105 | It was a live tree that had internal decay in the trunk that would not have been visible during routine inspections. | This was a weather related event involving a single tree, and no other trees were endangering the line at this location. The tree was removed and no other action was needed to remediate the situation.
Q3 2015 | SERC | GO, TO | 230 | No | No | 2015-07-02 | 963 | A 57-foot tall maple tree with a rotten trunk due to an old cambium wound that never sealed fell in to a 230kv line causing an outage that lasted approximately 16 hours. The tree was located 7 feet off the ROW and was 37 feet from the nearest conductor. The stump of the tree was approximately 90% rotten. | 3 | 7 | 37 | Maple | 57 | Trunk rotten due to an old cambium wound that never sealed. Stump was approximately 90 % rotten. | Transmission crew removed the tree and returned the line to service. The area was surveyed and no additional action was necessary.
Q3 2015 | SERC | TO | 500 | No | No | 2015-07-01 | 1093 | During a severe thunderstorm strong winds broke a 107-foot green loblolly pine tree located 16 feet outside the ROW fell into the outside phase causing an outage on a 500kv line. The tree had a defect and the winds broke the tree at this spot. Several downed trees were noticed in the area near this outage. | 3 | 16 | 45 | Loblolly Pine | 107 | Tree was green but had a defect about 12 feet off the ground. The strong winds caused the tree to break at this point. | Contract tree crews were sent to the location and removed any damaged trees from the storm. Crews were also instructed to look for any possible hazardous trees off the easement. Several trees were removed in this area.
Q3 2015 | SERC | TO | 230 | No | No | 2015-08-17 | 1291 | A live 65-foot tall hickory tree located 4.5 feet outside the south side of the ROW fell during bad weather causing a line to trip and an outage that lasted approximately 21 hours. Follow-up ground patrols found a tree on the line between structures. The hickory tree had a growth defect approximately 3-feet above the ground level which caused the tree to fail and break during stormy weather. | 3 | 4.5 | 49 | Hickory | 65 | Healthy tree with a growth defect approximately 3-feet above the ground. | Follow-up ground and aerial inspections were performed and no other hazardous trees were noted.
Q3 2015 | SERC | TO | 230 | No | No | 2015-09-29 | 1357 | An approximately 40-inch diameter dead pine tree approximately 90-feet tall broke and hit a 100-feet tall live oak tree causing it to break approximately 20-feet above the ground level. The healthy oak tree fell into the line causing an outage lasting approximately 22 hours. | 3 | 20 | 60 | Oak | 100 | Healthy tree was struck by a dead tree and fell into the line. | Transmission vegetation personnel patrolled and inspected approximately five spans east and west of this outage location and found no other priority tree issues.
Q3 2015 | WECC | TO | 115 | Yes | Yes | 2015-08-22 | 36407.4 | An 80-foot tall healthy Douglas fir located 15 feet outside the ROW broke and caused a 115kv line to trip causing a sustained outage. | 3 | 15 | 50 | Douglas Fir | 80 | Healthy | Service to remove appropriate trees outside of the cleared ROW.
Q2 2015 | SERC | TO | 230 | No | No | 2015-04-27 | 61 | A dead Oak tree 5 feet off the Right-of-Way along a sloped bank up-rooted and fell through the conductors during a high-wind event. The 85-foot tall and 28-inch diameter dead Oak tree fell through the lines and damaged a lower davit arm. | 3 | 5 | 65 | Oak | 85 | Dead | An aerial line patrol was performed and no additional hazardous trees were identified on the line.
Q2 2015 | RF | TO | 138 | No | Yes | 2015-05-07 | 1438 | An 87-foot Black Cherry tree with internal rot in the lower section fell from outside the Right-of-Way into a 138 kV IROL line during a storm. | 3 | 4.5 | 36.5 | Black Cherry | 87 | Fair. Tree had internal rot that was not apparent from outside. Upon removal, rot was located only in bottom 20%. | The line was patrolled to look for other storm-damaged or hazardous trees likely to fall in. One additional tree was identified and removed.
Q2 2015 | FRCC | TO | 230 | No | No | 2015-05-11 | 460 | At 1800 a thunderstorm caused a 70-foot healthy Oak tree to uproot from 15 feet off the Right-of-Way and land on the west and center conductors of the H-frame 230kV line. The Right-of-Way is 100 feet wide and the base of the tree was 65 feet from the center line. | 3 | 15 | 38 | Oak | 70 | Healthy | A tree crew was called to site to remove the tree from the conductors and line was restored.
Q1 2015 | SERC | TO | 230 | Yes | No | 2015-03-18 | 97 | A dead Red Oak tree fell from outside the right of way and made contact with a conductor. There were strong winds in the area at the time. The conductor burned in two, and both burned ends fell to the ground in a swampy area. | 3 | 13 | 41 | Red Oak | 54 | Dead | Another tree near the fallen tree was found charred. The other tree has been removed. Vines in the fall path of the fallen tree were also removed.
Q4 2014 | NPCC | TO | 230 | No | Yes | 2014-10-24 | 444 | A healthy 83 foot tall red oak tree, located 12 feet outside of the west edge of the ROW, had a 52 foot limb break-out 30 feet from the ground, pinning the nearest conductor to the ground. The tree limb likely failed during a Nor'easter storm on the evening of October 22, 2014. The line was out of service for a scheduled outage from October 6, 2014 8:00 thru October 24, 2014 15:00 for a relay update. The relay work was complete and the line was being returned to service on October 24, 2014 at 11:25:06. The flow on the line was 0.00 because the line was in the process of being returned to service from the scheduled outage. The line was energized from one end and tripped-out. | 3 | 12 | 37 | Red Oak | 83 | Healthy | The tree limb was removed from the conductor. Nearby trees were inspected. No additional work was identified.
Q4 2014 | SERC | TO | 230 | No | No | 2014-12-23 | 1471 | During rain and windy weather, a live 36-inch diameter at breast height (DBH) and 100-foot tall Pecan tree located 32-feet from off the edge of the right-of-way, broke off at the root collar (up-rooted) and fell on the 230kV line and causing an outage. The Pecan tree was located 262 feet southwest from existing structure #6 and 583 feet from structure #7. Structure #6 is situated 845 feet structure #7, the next structure. Tree distance to the nearest conductor was 53 feet. The tree was later cut by a contractor crew and removed. | 3 | 32 | 53 | Pecan | 100 | Healthy | The entity reported that the area where this outage occurred has been inspected from the ground and there are no immediate threats in this area (1-16-2015).
Q4 2014 | SERC | TO | 230 | No | No | 2014-12-24 | 258 | A 104 foot yellow Poplar outside the edge of the right-of-way (ROW) uprooted due to erosion and fell into the line resulting in a sustained outage. The tree was 31.5 feet outside the ROW and was located on the slope of a stream/ditch. | 3 | 31.5 | 54 | Yellow Poplar | 104 | Healthy | Other trees adjacent and along the ditch/stream were inspected to determine if erosion was putting them at risk of uprooting (none were found). Trees in the span and adjacent spans were also inspected to identify any other risks and none were found.
Q3 2014 | NPCC | TO | 230 | No | Yes | 2014-07-05 | 445 | During the high winds and rain of tropical storm an off-right-of-way tree fell on the line. The auto-reclose attempt was unsuccessful. The line was later restored and was back to service. | 3 | 0 | 33 | White Ash | 66 | Live and healthy | The section was widened by removing similar trees and eliminating fall in threats.
Q3 2014 | SERC | TO | 230 | No | No | 2014-09-03 | 132 | Water Oak uprooted during very high winds associated with a thunder storm. The tree had some root rot but was otherwise a healthy green tree. | 3 | 9 | 54 | Water Oak | 85 | Live tree with root rot | Other trees in the immediate area were inspected to be sure no hazards were present.
Q3 2014 | SERC | TO | 230 | No | No | 2014-08-21 | 272 | A live Pine tree broke off approximately 17 feet above ground during a strong thunderstorm. The tree top tangled in the conductor resulting in the line locking out. | 3 | 1 | 50 | Pine | 90 | Live and healthy | Obtained Clearance, Grounded Line, and removed tree top from conductors. There was no damage to the conductor. The line was placed back in service.
Q3 2014 | SERC | TO | 230 | No | No | 2014-08-11 | 1255 | A green Tallow tree growing along a creek bank uprooted and fell onto a line during a very high wind event. The area experienced a tornado event and numerous trees were broken or uprooted. | 3 | 4 | 40 | Tallow | 72 | Live and healthy | Approximately ten additional trees were marked and removed from this area following this outage restoration.
Q3 2014 | SERC | TO | 230 | No | No | 2014-07-03 | 250 | The line locked out when a large tree uprooted and fell into the conductors during a strong thunderstorm. | 3 | 15 | 52 | Poplar | 93 | Live tree with root rot | Other trees in the area were inspected, and none showed any signs of poor health.
Q3 2014 | SERC | TO | 230 | No | No | 2014-08-18 | 154 | A visually healthy tree fell onto a line during high winds and wet conditions. Root rot was visible on the fallen tree. | 3 | 8 | 40 | Green Pine | 58 | Live tree with root rot | Crew removed tree; reenergized line. No other mitigation/remediation needed.
Q3 2014 | SERC | TO | 230 | No | No | 2014-09-22 | 241 | A tree fell on to a line due to high winds in wet conditions. | 3 | 3 | 35 | Green Pine | 60 | Live tree with root rot | Crew found a tree on the line, removed it, and re-energized the line. No other mitigation/remediation needed.
Q3 2014 | FRCC | TO | 230 | No | No | 2014-08-17 | 1 | A tree with rot at 10 ft. up the trunk broke off during light winds from the SE, the tree made contact with the line as it fell. The outage duration was 28 seconds. | 3 | 4 | 17 | Royal Palm | 47 | Live tree with rot present in the trunk | Worked with private residents that own the property where failed tree was planted to remove 12 adjacent trees that could pose future failure danger.
Q3 2014 | FRCC | TO | 230 | No | No | 2014-07-11 | 654 | A tree fell on the line during severe storm. The tree had rot in the base. | 3 | 6 | 29 | Sweet Gum | 65 | Live tree with rot present in the trunk | Area surrounding outage location has been patrolled on ground and by air. Sweet gum was part of multi lead tree. Remainder of tree has been removed.

## Tables Retired Nov 2018 (hidden)
Filed Date | (Multiple Items)
Row Labels
2012
2013
2014
2015
2016
2017
2018
Grand Total
Vegetation Contacts and Encroachments
Filed Date | (All)
Row Labels
2012
2013
2014
2015
2016
2017
2018
Grand Total
Projected 2019 Vegetation Contacts and Encroachments
Filed Date | (All)
Row Labels
2012
2013
2014
2015
2016
2017
2018
Grand Total
Projected 2019 Q3 Vegetation Contacts and Encroachments
Row Labels | Cat 1 | Cat 1B | Cat 3 | Cat 4B | Contacts without Sustained Outages | Grand Total
2012 | 1 |  | 16 |  |  | 17
2013 |  |  | 15 |  |  | 15
2014 |  |  | 19 |  |  | 19
2015 |  | 3 | 20 |  |  | 23
2016 |  |  | 27 |  | 1 | 28
2017 |  | 3 | 20 | 1 | 2 | 26
2018* |  | 5 | 22 |  |  | 17
2019** |  | 3 | 12
Grand Total | 1 | 11 | 129 | 1 | 3 | 145
2018-08-01
Reporting year | Cat 1 | Cat 1B | Contacts without Sustained Outages | Grand Total
2012 | 1 |  |  | 1
2013
2014
2015 |  | 3 |  | 3
2016 |  |  | 1 | 1
2017 |  | 2 | 2 | 4
2018 |  |  |  | 0

## snapshots from 2011 and 2010 re (hidden)
sn

## Old data from pre 2014 (hidden)
Figure 1: Category 1 — Grow-in Outages Caused by Vegetation Growing into Lines from Inside and/or Outside the ROW
| 1st Quarter | 2nd Quarter | 3rd Quarter | 4th Quarter | Total
2004 |  | 1 | 6 |  | 7
2005 |  | 6 | 9 |  | 15
2006 | 1 | 5 | 3 |  | 9
2007 |  | 5 | 11 |  | 16 | One outage of a regional designated critical line < 200kV
2008 |  | 6 | 5 |  | 11
2009 |  | 3 |  |  | 3
2010 |  |  | 2 |  | 2
2011 |  |  |  |  | 0
2012 |  |  | 1 |  | 1
2013 |  |  |  |  | 0
Figure 2: Category 1 —Grow-In Vegetation Related Outages of 230 kV and Higher
* Designated as critical by Regional Entity
| < 200kV * | 230kV | 345kV | 500kV/765kV | Total
2004 | 0 | 4 | 3 | 0 | 7
2005 | 0 | 5 | 4 | 6 | 15
2006 | 0 | 6 | 2 | 1 | 9
2007 | 1 | 9 | 5 | 1 | 15
2008 | 0 | 7 | 3 | 1 | 11
2009 | 4 | 0 | 2 | 1 | 3
2010 |  | 0 | 1 | 1 | 2
2011 |  | 0 | 0 | 0 | 0
2012 |  | 1 | 0 | 0 | 1
2013 |  | 0 | 0 | 0 | 0
Note on D12: Farzaneh: from NPCC--- one 230 kV line in Canada
Note on C31: Farzaneh: NPCC in 3rd Q 2012

## 2013 (hidden)
Confidential and Non-Public |  |  |  | Confidential and Non-Public |  |  |  | Confidential and Non-Public |  |  |  | Confidential and Non-Public |  |  |  | Confidential and Non-Public |  |  |  | Confidential and Non-Public
Registered Entity Identification |  |  |  | Transmission Circuit Information | [5 empty] | Transmission Outage Description |  |  |  |  | Vegetation Description *Horizontal along the ground – measured from tree stump to a point on the ground directly below the conductor | [5 empty] | Corrective and Preventive Actions |  | Other comments
Entity Name | NCR | Function TO; GO | Region | Name of the circuit(s) affected by the vegetation contact | Has the reported circuit experienced a previous vegetation-related transmission outage within the last eight reporting quarters? | State the quarter if the reported circuit has experienced a previous vegetation-related transmission outage (enter Q/yyyy) | Nominal voltage rating of the circuit (kV) | Element of IROL or Major WECC Transfer Path? | The flow (as a % of normal rating) on the facility just prior to the outage | Outage start date (enter mm/dd/yyyy) | Outage start time | Outage Duration (enter in minutes) | Detailed description of the cause of the outage | Category associated with the Sustained Outage. 1A&B; 2A&B; 3; 4A&B | Vegetation Location Inside or outside the ROW | If the vegetation causing the outage was located outside of the ROW provide the horizontal distance to the edge of the ROW (enter in feet) | If the vegetation causing the outage was located outside of the ROW provide the horizontal distance to the nearest conductor (enter in feet) | Tree type | Tree height (enter in feet) | Tree condition | Mitigation/remediation actions taken by Registered Entity to address recurrence of the contact/encroachment. | Actions taken by Regional Entity
Entergy | NCR01234 | TO | SERC |  |  |  | 230 |  | N/A | 2013-01-13 | 16:45 | 1438 | During thunderstorm, 108’ green pine tree had been washed out, slid 20' down the creek embankment, and fell across the conductor. The pine's base had been about 80' from the outside conductor placing the tree at 50’ outside the ROW boundary. Tree could not be removed from the line until wet conditions improved and allowed access. | Category 3 | outside | 50 | 80 | green pine | 108 |  | Two additional trees were identified as potential threats and were removed. | none
American Electric Power Corp. as agent for Public Service Company of Oklahoma & Southwest Electric Power Company (AEPW) | NCR01056 | TO | SPP |  |  |  | 345 |  | 45 | 2013-01-29 | 16:30 |  | Tree height 113 feet. Surrounding pines average 130 feet. Tree hit outside phase which is 60 feet from ROW edge. Outside phase tree came in contact with is 52 feet off ground. Green tree. Rotten in ground. Tree front as seen from inside ROW is healthy. Green top and no bark popping off. Back of tree has bark popping off. Other pines in immediate area does not show bark popping off. | Category 3 | outside | 60 |  | pine | 113 | rotten in ground, one side with bark popping off | Transmission forestry personnel look for danger trees outside the ROW during their aerial patrols future outages: (spring and fall) and while performing their normal duties. Once a danger tree has been identified the forester works with the land owner to remove the tree in question. | Follow-up with Entity for counter measures. | Reportable outage; not actionable.
Entergy | NCR01243 | TO | SERC |  |  |  | 230 |  | N/A | 2013-03-31 | 12:21 | 741 | Due to high winds during heavy rain, a 97’ live pine tree uprooted 13’ outside ROW; and fell across the 230 kV line. | Category 3 | outside | 13 |  | pine | 97 | live | Several structures north and south of this outage site were inspected for possible additional vegetation / line issues, and no additional issues were identified. | none | This outage occurred on the U S Forest Service property on 3/31/13. Forest Service personnel were notified on 4/1/13.
First Energy Utilities | NCR11315 | TO | RFC |  |  |  | 230 |  | 24 | 2013-04-02 | 18:46 | 1985 | The initiating cause was a 98’ tall Red Oak tree located 71' off ROW, which uprooted and fell into a 120' tall Tulip Poplar (#1) located 37' off ROW, which fell into another 100' tall Tulip Poplar (#2) located 16' off ROW. A historic water course from upslope was directed toward the base of Tulip Poplar #1, recent heavy rains saturated soils at base of Tulip Poplar #1, and pressure from uprooted Red Oak tree caused this Tulip Poplar tree to uproot into Tulip Poplar #2. Both Tulip Poplars, which were both live, healthy trees, struck the transmission line, breaking two cross-arms and interrupting the line. Customers from half of PSEG's Green Brook substation were momentarily interrupted (less than 1 minute) until the load transferred to an alternate feed. No other substations were interrupted. The Gillette Lake - Nelson 230 kV line was repaired and returned to service around 03:51 on July 4. | Category 3 | outside | 37, 16 |  | tulip poplars | 120, 100 | healthy | As a result of the First Energy's investigation other structurally damaged trees in the immediate area were removed. It is the opinion of First Energy that the nature of this outage was an anomaly due to the domino effect of trees uprooting into one another. FirstEnergy will continue its annual inspection that includes looking for off corridor priority trees .No additional course of action is necessary. | RFC agreed with the Registered Entity's investigation and conclusions. No other action was deemed necessary.
Entergy | NCR01234 | TO | SERC |  |  |  | 230 |  | N/A | 2013-04-14 |  | 1855 | During a localized storm, a 98 foot tall hollow trunk of a forked-trunk oak tree, located about 14 ft. off ROW near a creek bank, split and broke off. The trunk fell onto the line, and broke the x arm on a structure. It was later determined that, although the tree was located near a creek bank, neither the rising creek nor water conditions were contributory to the failure. | Category 3 | outside | 14 |  | oak | 98 | hollow inside | The area was inspected by ground patrol and no other trees were deemed to be a recognizable threat due to ground or visible tree conditions. | none
NorthWestern Corporation (NWC) | NCR05282 | TO | WECC |  |  |  | <200 |  |  | 2013-04-21 | 17:15 | 994 | A live healthy tree located outside of the transmission line Right-of-Way sheared off above groundline during a severe wind event and fell into the transmission line breaking a crossarm. | Category 3 | outside |  |  |  |  | healthy | Ongoing patrols for vegetation issues, including danger trees outside of R-O-W. |  | May not be a reportable outage due to the presence of the Microburst wind levels.
NorthWestern Corporation (NWC) | NCR05282 | TO | WECC |  |  |  | <200 |  |  | 2013-05-13 | 15:23 | 1456 | A live healthy tree located 20 feet outside of the transmission line Right-of-Way sheared off above groundline and fell into the transmission line. High winds were suspected at the time of the outage. | Category 3 | outside | 20 |  |  |  | healthy | Ongoing patrols for vegetation issues, including danger trees outside of R-O-W. | WECC has requested the entity submit additional information about this vegetation-caused outage.
Duke Energy Progress, Inc. | NCR01298 | TO | SERC |  |  |  | 230 |  | N/A | 2013-05-20 | 16:45 | 223 | During a localized thunderstorm a healthy 58 foot tall loblolly pine tree located 3.5 ft from the edge of the ROW fell onto the outside phase of the line. | Category 3 | outside |  | 3.5 | loblolly pine | 58 | healthy | tree was removed | SERC notes that this outage was reported too late to be included in the 2Q13 report. SERC will investigate and address the cause of the late report with the Registered Entity. | The number of Category 3 outages recorded on page 1 reflects the one reported in 2Q13 and the outage reported on this form for a total of two (2) outages experineced in 2Q13.
Virginia Electric and Power Company (DP, LSE) | NCR01214 | TO | SERC |  |  |  | 230 |  | N/A | 2013-08-22 | 1:42 | 145 | During a localized thunderstorm, a large tree fell into a smaller tree knocking the smaller tree into the conductors. The first tree to fall was a red oak, 79 feet tall, 59 feet from the right of way, and 81 feet from the conductor. The second tree, which was knocked over by the red oak, was a maple, 48 feet tall, 15 feet from the right of way, and 38 feet from the conductor. Neither tree showed any signs of disease, stress, rot, etc. Only the maple tree struck the conductor. | Category 3 | outside | 15 | 38 | maple | 48 | healthy | tree was removed | none
NorthWestern Corporation (NWC) | NCR05282 | TO | WECC |  |  |  | <200 |  |  | 2013-08-26 | 0:27 | 2274 | Violent localized storm uprooted a tree growing outside of the right-of-way, which fell into the transmission line. Localized wind storm with gusts estimated at 50 mph, uprooted a healthy Ponderosa Pine tree. The tree was growing outside ot the transmission line right-of-way, 2.3 miles from Thompson Falls substation. The tree had no apparent signs of damage from Mountain Pine Beetle. | Category 3 | outside |  |  | ponderosa pine |  | healthy |  | Ongoing patrols for vegetation issues, including danger trees outside of R-O-W
Seattle City Light | NCR05382 | TO | WECC |  |  |  | 230 |  | 19.5 | 2013-08-27 | 18:49 | 452.3 | Trees into wires between tower 53/42 & tower 54/9 relayed line out. Along the west side of the right-of-way (ROW) there were three separate areas of blow-down where trees were completely uprooted or had tops broken off 40 and 50 feet in the air. All of the uprooted trees were growing well off the ROW edge approximately 40 to 50 feet. These trees were not on SCL fee-owned or controlled property and were well outside the area where normal pruning and removal could be expected. The trees were of varying size classes but were generally 80 to 100 feet tall. About 80 trees were blown over or broken in these areas. It appeared that possibly only one tree was tall enough to have made contact with the overhead transmission line and had some physical evidence of having made contact with a broken top.Because of the intense localized damage, it appears that a microburst can be attributed to the damage. This outage appears to be a case of a tall tree outside the ROW with the capability of falling into energized circuits and causing an outage due to an unusual localized storm condition known as a microburst. Because of the facts of this investigation, this event can be classified as a Category 3 vegetation-caused outage. | Category 3 | outside | 40-50 |  |  | 80-100 |  |  |  | Event appeared to be caused by unusual localized microburst producing intense wind burst and tree damage in limited area.
National Grid USA | NCR11171 | TO | NPCC |  |  |  | 230 |  | 25 | 2013-08-31 |  | 1606 | During a thunderstorm a 88 foot Black Cherry tree loacted 11 feet outside the the ROW easement uprooted and fell on the transmission line. The tree showed no outward signs of rot but the tree was partly covered with Virginia Creeper vines. | Category 3 | outside | 11 |  | black cherry | 88 | covered with Virginia Creeper vines |  | Other trees in the area were reviewed to make sure no additional trees needed to be removed at this time.
NorthWestern Corporation (NWC) | NCR05282 | TO | WECC |  |  |  | <200k |  |  | 2013-10-30 | 15:17 | 105 | A tree located outside of the transmission line ROW fell into line. The otherwise healthy tree, was uprooted during a recent localized wind storm. A healthy Ponderosa Pine tree, located outside of the transmission line ROW, approximately 3 miles from the substation, was uprooted during a recent wind storm and fell into the transmission line. No customer load was lost. | Category 3 | outside |  |  | ponderosa pine |  | healthy |  | WECC continues to monitor all Category 3 Vegetation-Caused outages on two NWC 115kV transmission lines that traverse a rugged mountainous area in Western Montana
National Grid USA | NCR11171 | TO | NPCC |  |  |  | 230 |  | 16 | 2013-11-01 | 18:46 | 904 | During a wind event, a major lead broke-off from a 95-foot tall co-dominate white pine tree located 4.5 feet outside of the ROW easement and fell onto the transmission line. The tree had internal rot that was not visible from the outside. The tree was removed. The location was in Pownal, Vermont | Category 3 | outside | 4.5 |  | white pine | 95 | internal rot not visible from the outside | tree was removed | none
National Grid USA | NCR11171 | TO | NPCC |  |  |  | 230 |  | 11 | 2013-11-24 | 18:46 | 1715 | During a high wind event, a 95 foot-tall white pine tree located 11.5 feet outside the ROW easement, uprooted, fell, and stayed leaning on a single phase of the A201transmission line. The faulted location was found by helicopter patrol on November 25. The tree was removed. The location was in Hopkinton, New Hampshire. | Category 3 | outside | 11.5 |  | white pine | 95 | healthy | tree was removed

## all old stuff (hidden)
Region | Quarter | Year | Name of TO | NERC Compliance ID | NERC Violation ID | Name of Transmission Line | Voltage of Transmission Line | Date of Outage | Outage time and Date | Duration of Outage | Line-Loading of Outaged Line | Cause of Outage | Cat of Cause | Action(s) Taken By TO | Action(s) Taken By Region | Date Region Advised | Comments
FRCC | 1Q | 2004 |  |  |  |  | 230 kV | [5 empty] | 2 |  |  |  | Critical lines list in revision process. All other mileage provided is from the FRCC 2004 EIA 411 submittal. We have requested information regarding the one outage reported.
SERC | 2Q | 2004 |  |  |  |  | 230 kV | [5 empty] | 1
SERC | 2Q | 2004 |  |  |  |  | 230 kV | [5 empty] | 2
ECAR | 3Q | 2004 |  |  |  |  | 230 kV | [5 empty] | 1
ECAR | 3Q | 2004 |  |  |  |  | 345 kV | [5 empty] | 1
MAIN | 3Q | 2004 |  |  |  |  | 345 kV | [5 empty] | 2
MAPP | 3Q | 2004 |  |  |  |  | 230 kV | [5 empty] | 1
NPCC | 3Q | 2004 |  |  |  |  | 345 kV | [5 empty] | 1 |  |  |  | Tree was subsequently removed from right-of-way
SERC | 3Q | 2004 |  |  |  |  | 230 kV | [5 empty] | 1
SPP | 3Q | 2004 |  |  |  |  | <200 kV | [5 empty] | 3
NPCC | 1Q | 2005 |  |  |  |  | 230 kV | [5 empty] | 2 |  |  |  | The outage was the result of the transmission owner's crew removing a danger tree. A full internal investigation was conducted by the transmission owner following the incident and all work procedures were reviewed.
SERC | 1Q | 2005 | Dominion Virginia Power |  |  | Elmont - Cunningham | 500 kV | 2008-02-08 |  | 2 hr 27 min | Line 553 | Line locked out when loggers got a tree into the line and caused an A-phase to ground fault between structures 692 and 693 | 2 | None
WECC | 1Q | 2005 | Portland General Energy Company |  |  | Bethel - McLoughlin | 230 kV | 2005-01-18 |  | 50 min |  | A 75-ft Cottonwood tree uprooted and contacted the outside phase of the Bethel-McLoughlin line. The tree was located on an island in the Molalla River. The tree was located off the right-of-way and was in good condition with no obvious signs of a failure potential during the last inspection in October 2004. At the time of inspection, the tree was at least fifty feet from the edge of the river. During the three days prior to the incident, record rainfall resulted in an increase in water flow and the gradual change of river's course. The Island began to erode, eventually uprooting the Cottonwood tree. | 2 | Crews removed three other trees that were eminent threats. The PGE Forester will continue to monitor this site during annual patrols.
WECC | 1Q | 2005 | British Columbia Transmission Corp. |  |  | North Vancouver | 230 kV | 2005-03-20 |  | 11 hr 9 min | 2L09 | During a storm, a Hemlock tree that was off the row fell onto the right-of-way | 2 | Analysis of the failed tree indicated that laminated root rot was the cause. BCTC is examining the need for further tree removal in the area. BCTC instituted a Hazard Tree Program and is working with a forest pathologist to identify hazard trees. It is also working with municipal and other landowners in an environmentally sensitive area to remove hazard trees outside the transmission line right-of-way. |  |  | No customers were affected because the load was served by other lines.
WECC | 1Q | 2005 | Puget Sound Energy |  |  | White river - Cascade | 230 kV | 2005-01-18 |  | 29 hr 50 min |  | An off-the-row tree fell into the White River | 2 | The line crosses over the Cascade Mountains with a thick Fir, Hemlock and Cedar forest. The event occurred on January 18 during winter conditions, and the region was experiencing heavy snow and winds. On that day at Seatac Airport, weather data showed 1.97 inches of rain with 25 mph wind gusts. This tree event was considered an isolated event and no other danger trees were reported in the area. During the spring of 2005, the entire Cascade to White River Line was patrolled by helicopter.
APS | 2Q | 2005 |  |  |  |  | 500 kV | 2005-06-14 | 14:20 EST | [7 empty] | There was an outage at Cherry Creek due to Cottonwood trees growing up into the line. Outage start was 6/14/2005 at 2:30 pm. Return to service was 6/14/2005 at 11:20 am. Please see attached documents describing issues with the Tonto National Forest.
ECAR | 2Q | 2005 | ITC |  |  | Brownstone - Monroe | 230 kV | 2005-06-30 |  | 9.8 hrs |  | Line sagged into tree | 1 | The tree was cut down
ECAR | 2Q | 2005 | AEP |  |  | Kyger Creek - Sporn North | 345 kV | 2005-05-04 |  | 5.9 hrs |  | Tree encroached into the line | 1 | A crew was immediately dispatched and cut the tree down
ECAR | 2Q | 2005 | LGEE |  |  | Mill Creek - Paddys West | 345 kV | 2005-06-06 |  | 1.12 hrs |  | The line was patrolled and crews found that the line sagged into the trees | 1 | The tree was removed and the line was put back into service
SERC | 2Q | 2005 | Progress Energy Carolinas |  |  | Darlington County Plant - Sumter | 230 kV | 2005-06-06 |  | 4.9 hrs |  | Conductor contacted yard tree in residential area of this line. The contact resulted in a momentary operation at 14:39:40, with a sustained outage following at 15:22:30. | 1 | All but one of the yard trees in this span and the adjacent spans were removed immediately following the event. Other trimming locations on the line reviewed and actions completed as necessary. The scheduled mid-June aerial patrol was completed as necessary. The scheduled mid-June aerial patrol was completed with additional focus on reliability-related trimming locations |  |  | The annual work plan includes cycle-based trimming on this line scheduled for September 2005
WECC | 2Q | 2005 | Avista/Northwestern Energy |  |  | Burke - Thompson Falls A | <200 kV | 2005-05-19 | 5/19/2005 @ 13:52:00 PT | 2 hrs 52 min |  | Tree | 2 | none | WECC contacted the TO to follow up on the number of outages on lines into and out of Burke substation to determine if additional actions were necessary. |  | Assumed to be a danger tree
WECC | 2Q | 2005 | Western Area Power Administration - Sierra Nevada Regions (WASN) |  |  | Captain Jack - Olinda | 500 kV | 2005-05-25 |  | 3.08 hrs |  | During construction of the CA-OR Transmission Project (COTP), a number of trees were left intact to preserve habitat for the Spotted White Owl and to improve visual aesthetics with respect to clear cut areas and transmission line visibility. The tree that the line contacted was part of an aesthetic screen located in a remote, densely vegetated area. | 1 | Approximately 50 trees were removed immediately and the remaining trees in the area have adequate clearance and will be removed in July 2005. Western's Line Crew performed annual patrol June 6th through June 13th and all trees have adequate clearance. The crew fell numerous trees during the patrol and identified approximately sixty spans to be removed by contract. | WECC is reporting any 500 kV in right-of-way (ROW) vegetation outages to NERC within 49 hours of becoming aware of the outage. The Transmission Operator took appropriate actions and no other actions were required by WECC.
WECC | 2Q | 2005 | Arizona Power Service Company |  |  | Cherry Creek | 500 kV | 2005-06-14 |  | 21 hrs |  | Aspen Trees growing up into the line | 1 | Trimmed tree | WECC forwarded documentation from the TO to NERC, documenting efforts and difficulties in obtaining access to the ROW, and requested assistance with the matter |  | Since 1997, the TO notified the Forest Service multiple times that they were not getting adequate clearance on the line and were not permitted access. The TO notified WECC and asked for assistance.
WECC | 2Q | 2005 | NorthWestern Energy |  |  | Crow Creek - Burke | <200 kV | 2005-05-19 |  | 2.96 hrs |  | Tree fell into line from 30 feet outside of ROW | 2 | Tree removed from line | WECC contacted the TO to follow up on the number of outages on lines into and out of Burke substation to determine if additional actions were necessary. |  | TO reports that the ROW is cleared and the outage is a result of vegetation on a steep uphill area outside of ROW. Danger trees have been cleared from the area outside ROW
WECC | 2Q | 2005 | SMUD |  |  | Lake - Orangevale | 230 kV | 2005-06-30 |  | 3.5 hrs |  | Tree contact | 2 | Cut tree down |  |  | Very wet year
WECC | 2Q | 2005 | NorthWestern Energy |  |  | Thompson Falls - Burke | <200 kV | 2005-05-02 |  | 3.82 hrs |  | A 70' tree on uphill side of ROW fell into the line
WECC | 2Q | 2005 | NorthWestern Energy |  |  | Thompson Falls - Burke | <200 kV | 2005-06-17 |  | 12.93 hrs |  | Tree fell into line from outside of ROW | 2 | Tree removed from line | WECC contacted the TO to follow up on the number of outages on lines into and out of Burke substation to determine if additional actions were necessary. |  | TO reports that the ROW is cleared and that outage is the result of vegetation on a steep uphill area outside of ROW. Danger trees have been cleared from the are outside ROW.
ECAR | 3Q | 2005 | AEP |  |  | 04BP40 | 765 kV | 2005-07-05 |  | 0 | 13% | The presence of vegetation in the area where the line-vegetation contacts occurred had been noted on the most recent line patrol. However, the results of the aerial inspection were not communicating expeditiously to the forestry contractor | 1 | As a result of the vegetation contact and associated investigation, a clump of black Locust trees was removed from the right-of-way. Additionally AEP has taken steps to ensure prompt reporting of serious conditions identified during aerial patrols. AEP's Vegetation Management proactive were not violated. AEP possessed generally good inspection and vegetation pruning practices prior to the incident and has even more effective procedures as a result of the incident | AEP notified the ECAR Regional Manager, ECAR communicated this trip to NERC, and brief written explanation was provided
FRCC | 3Q | 2005 | Seminole Electric Cooperative |  |  | Rice - Seminole | 230 kV | 2005-07-05 |  | 1 hr 8 min | 2.2% | Line sag into tree | 1 | Tree has been trimmed
FRCC | 3Q | 2005 | Seminole Electric Cooperative |  |  | Rice - Seminole | 230 kV | 2005-07-05 |  | 1 hr 8 min |  | Line sag into tree | 1 | Tree has been trimmed
MRO | 3Q | 2005 | MEC |  |  | Booneville - Cooper | 345 kV | 2005-07-17 |  | 3 min | 24% | Tree came into contact | 1 | After coordination with NPPD, the line was reclosed. Line patrol was subsequently conducted at which time the tree was identified and removed
MRO | 3Q | 2005 | SaskPower |  |  | C1W (Condie to Wolverine) | 230 kV | 2005-07-12 |  | 7 hrs 33 min | 8.5% | A tree contacted the C1W line near Lockwood | 1 | No mitigating actions required on transmission system. Tree was cut down later the same day and the line returned to service
NPCC | 3Q | 2005 | Hydro One |  |  | D5H (Des Joachims - Holden) | 230 kV | 2005-08-09 | 8/9/2005 @ 17:26 | 23 hrs 48 min |  | Hydro One reports and has confirmed that several trees fell and made contact with the D5H line. The incident occurred off the right-of-way and during a significant storm. There was also a tornado warning in the area. Major wind damage was reported in the Mattawa area where the vegetation contacts occurred. | 2 | None
NPCC | 3Q | 2005 | Nova Scotia Power |  |  | Onslow - Port Hasting | 230 kV | 2005-08-22 | 8/22/2005 @ 10:02 | 7.25 hrs | 64% | Contact with vegetation in a water course buffer zone | 2 | Extra 1-meter margin of cut has been incorporated into Nova Scotia Power's standards for tree removals. Inspection data has been reviewed, and all water course and road side buffers have been re-scooped.
SERC | 3Q | 2005 | South Carolina Electric & Gas Co. |  |  | Canadys - Sntee | 230 kV | 2005-07-20 |  | 2 hrs 6 min |  | Non-SCE&G related logger working adjacent to the ROW accidentally pushed over a pine tree which came to rest upon the line | 2 | The logger was contacted by SCE&G personnel who explained the possible consequences to the logger and to our customers of his actions. It was determined that no further action was needed in this instance.
SERC | 3Q | 2005 | Georgia Transmission corporation |  |  | Hatch - North Tifton | 500 kV | 2005-07-09 |  | 3 hrs 3 min |  | Ornamental tree grew on ROW under power lines into power line causing outage | 1 | The tree causing the outage was removed and the line was patrolled
SERC | 3Q | 2005 | Georgia Transmission corporation |  |  | Klondike - Norcross | 500 kV | 2005-08-19 |  | 17 hrs 34 min | 45% | Silver Maple in ROW grew into power line causing outage. Silver Maple was 60 feet from centerline. ROW width is 75 feel from centerline. | 1 | The Silver Maple which caused the outage was removed. The line was inspected and the other tree work which was identified during the inspection Is being completed.
SERC | 3Q | 2005 | Southern Company Services, Inc. |  |  | McDonough - Peachtree | 230 kV | 2005-07-23 |  | 5 hrs 17 min |  | Healthy 19" diameter tree rooted 25 feet from ROW in intermittent creek bank. Fell on line between structures 53 and 54 in fair weather. |  | Unique event, no action can be taken to prevent similar occurrence.
SERC | 3Q | 2005 | Entergy |  |  | Sabine - Mid County | 230 kV | 2005-09-18 |  | 3 hrs 9 min |  | Tree cut into line by logger during fair weather | 2 | Logger notification program in place
SPP | 3Q | 2005 | Kansas City Board of Public Utilities |  |  | Barber to Shawnee Line | <200 kV | 2005-08-10 |  | 3 hrs 6 min | 35% | Tree limb contacted 161 phase wire | 2 | Promptly trimmed the tree back | Reported to NERC
SPP | 3Q | 2005 | American Electric Power West |  |  | Chambers spring - Clarksville | 345 kV | 2005-07-12 |  | 8 hrs | 34% | Vegetation overlooked on patrols | 1 | Tree clump was removed. Inspection processes were revised. | Reported to NERC
SPP | 3Q | 2005 |  |  |  |  | <200 kV
SPP | 3Q | 2005 |  |  |  |  | 345 kV
WECC | 3Q | 2005 | BC Hydro (managed by BCTC) |  |  | 1L274 | <200 kV | 2005-07-06 |  | 2 hrs 5 min | 27% | A large Spruce tree off the ROW came down in a storm and contacted the line. Lost 27 MW of load (Fording, Line Creek, Green Hiliss Coal as well as town of Elkford) | 2 | A hazard tree program has been initiated in this area in 2004 and tree removals are taking place in 2005. This tree was not marked as a hazard tree but it was a taller veteran left along the edge of a cut block and failed from wind throw during a storm. |  |  | This tree was analyzed by a forest pathologist and was determined to be healthy. It failed because of its height and "wind sail" during a storm. Its location along a recently logged edge made it more vulnerable. All trees along the edge of this cut block (about 80 trees) will be removed to avoid further wind throw events in this area. Line is also regularly patrolled to detect the presence of new cut blocks off the ROW that may create tree leave strips prone to wind throw so that they can be removed. BCTC is working with forest licensees and with Ministry of Forests to discourage the retention of aesthetic leave strips adjacent to power lines.
WECC | 3Q | 2005 | BC Hydro (managed by BCTC) |  |  | 1L274 | <200 kV | 2005-09-10 |  | 87 hrs 35 min | 12% | Severe snow storm | 2 | Repaired damage to circuit and removed storm-damaged trees | This circuit was damaged during a severe early fall snow storm that hit SE British Columbia and SW Alberta on September 10, 2005 causing widespread damage from heavy wet snow. Many damaged trees in the area, some of which came down on the circuit between Natal Sub and Line Creek Coal. Affected 1324 customer but damaged section was isolated and fed from Alberta side resulting in 485.47 customer hours lost. Not classified as a vegetation outage given the severe weather but reported here for background.
WECC | 3Q | 2005 | BC Hydro (managed by BCTC) |  |  | 1L274 | <200 kV | 2005-09-10 |  | 87 hrs 35 min | 12% | Severe snow storm | 2 | Repaired damage to circuit and removed storm damaged trees. |  |  | This circuit was damaged during a severe early fall snow storm that hit SE British Columbia and SW Alberta on 9/10/2005 causing widespread damage from heavy wet snow. Many damaged trees in the area, some of which came down on the circuit between Natal Sub and Line Creek Coal. Affected 1324 customers but damaged section was isolated and fed from Alberta side resulting in 485.47 customer hours lost. Not classified as a vegetation outage given the severe weather event but reported here for background.
WECC | 3Q | 2005 | BC Hydro (managed by BCTC) |  |  | 1L274 | <200 kV | 2009-09-10 |  | 87 hrs 35 min | 12% | Severe snow storm | 2 | Repaired damage to circuit and removed storm damaged trees |  |  | This circuit was damaged during a severe early fall snow storm that hit SE British Columbia and SW Alberta on September 10, 2005 causing widespread damage from heavy wet snow. Many damaged trees in the area, some of which came down on the circuit between Natal Sub and Line Creek Coal. Affected 1324 customers but damaged section was isolated and fed from Alberta side resulting in 485.47 customer hours lost. Not classified as a vegetation outage given the severe weather event but reported here for background.
WECC | 3Q | 2005 | BC Hydro (managed by BCTC) |  |  | 1L275 | <200 kV | 2005-09-10 |  | 94 hr 25 min | 14% | Severe snow storm | 2 | Repaired damage to circuit and removed storm damaged trees |  |  | This circuit was damaged during a severe early fall snow storm that hit SE British Columbia and SW Alberta on September 10, 2005 causing widespread damage from heavy wet snow. Many damaged trees in the area, some of which came down on this circuit. No customers lost in event. Not classified as a vegetation outage given the severe weather event, but reported here for background.
WECC | 3Q | 2005 | BC Hydro (managed by BCTC) |  |  | 1L275 | <200 kV | 2005-09-10 |  | 94 hrs 25 min | 14% | Severe snow storm | 2 | Repaired damage to circuit and removed storm damaged trees | This circuit was damaged during a severe early fall snow storm that hit WE British Columbia and SW Alberta on September 10, 2005 causing widespread damage from heavy wet snow. Many damaged trees in the area, some of which came down on this circuit. No customers lost in event. Not classified as a vegetation outage given the severe weather event but reported here for background.
WECC | 3Q | 2005 | BC Hydro (managed by BCTC) |  |  | 1L275 | <200 kV | 2009-09-10 |  | 94 hrs 25 min | 14% | Severe snow storm | 2 | Repaired damage to circuit and removed storm damaged trees |  |  | This circuit was damaged during a severe early fall snow storm that hit SE British Columbia and SW Alberta on September 10, 2005 causing widespread damage from heavy wet snow. Many damaged trees in the area, some of which came down on the circuit between Natal Sub and Line Creek Coal. Affected 1324 customers but damaged section was isolated and fed from Alberta side resulting in 485.47 customer hours lost. Not classified as a vegetation outage given the severe weather event but reported here for background.
WECC | 3Q | 2005 | BC Hydro (managed by BCTC) |  |  | Pocatera - Fording Coal Tap | <200 kV | 2005-07-06 |  | 2 hrs 5 min | 27% | A large Spruce tree off the ROW came down in a storm and contacted the line. Lost 27 MW of load (Fording, Line Creek, Green Hiliss Coal as well as town of Elkford) | 2 | A hazard tree program has been initiated in this area in 2004 and tree removals are taking place in 2005. This tree was not marked as a hazard tree but it was a taller veteran left along the edge of a cutblock and failed from wind throw during a storm. |  |  | This tree was analyzed by a forest pathologist and was determined to be healthy. It failed because of its height and "wind sail" during a storm. Its location along a recently logged edge made it more vulnerable. All trees along the edge of this cut block (about 80 trees) will be removed to avoid further wind throw events in this area. Line is also regularly patrolled to detect the presence of new cut blocks off the ROW that may create three leave strips prone to wind throw so that they can be removed. BCTC is working with forest licensees and with Ministry of Forests to discourage the retention of aesthetic leave strips adjacent to power lines.
WECC | 3Q | 2005 | Bonneville Power Administration |  |  | Tacoma - Raver - 1 | 500 kV | 2005-07-27 |  | 2 min | 529.8 MW | A Lombardi Poplar on the edge of the ROW bent into the power line causing a 2-minute outage. The arc ignited a nearby house and the line had to be removed from service to fight the fire. | 1 | BPZ has investigated the incident, documented findings and is implementing recommendations to review working patrol standards with field crews. | The investigation conclusion found that the combination of all missed opportunities to catch this tree before it got to within flashover distance, which ultimately led to the tree getting too close to the line. The programs and processes that BPA has implemented and refined over the years to prevent this type of event from happening failed to acknowledge that this tree was an imminent hazard
WECC | 3Q | 2005 | Bonneville Power Administration |  |  | Tacoma - Raver - 1 | 500 kV | 2005-07-30 |  | 6.85 hrs | 4997 MW | Landowner was using a crawler tractor to push trees over on his property and knocked one tree into another causing the second tree to fall into the line. The landowner was unaware of the incident until BPA crew notified him | 2 | Tree was removed |  |  | Discussed situation with landowner.
WECC | 3Q | 2005 | Bonneville Power Administration |  |  | Tacoma - Raver - 1 | 500 kV | 2005-07-30 |  | 8.3 hrs |  | Landowner was using a crawler tractor to push trees over on his property and knocked one tree into another causing the second tree to fall into the line. The landowner was unaware of the incident until BPA crew notified him | 2 | Tree was removed | Discussed situation with landowner
WECC | 3Q | 2005 | Bonneville Power Administration |  |  | Tacoma - Raver - 1 | 500 kV | 2005-07-30 |  | 6 hrs 50 min |  | Landowner was using a crawler tractor to push trees over on his property and knocked one tree into another causing the second tree to fall into the line. The landowner was unaware of the incident until BPA crew notified him | 2 | Tree was removed | Discussed situation with landowner
WECC | 3Q | 2005 | Bonneville Power Administration |  |  | Tacoma - Raver - 1 | 500 kV | 2005-07-30 |  | 6 hrs 51 min | 499.7 MW | Landowner was using a crawler tractor to push trees over on his property and knocked one tree into another causing the second tree to fall into the line. The landowner was unaware of the incident until BPA crew notified him | 2 | Tree was removed |  |  | Discussed situation with landowner
WECC | 3Q | 2005 | Bonneville Power Administration |  |  | Tacoma - Raver - 1 | 500 kV | 2009-07-27 |  | 2 min | 529.8 MW | A Lombardi Poplar on the edge of the ROW bent into the power line causing a 2-minute outage. The ac ignited a nearby house and the line had to be removed from service to fight the fire. | 1 |  |  |  | The investigation conclusion found: The combination of all the missed opportunities to catch this tree before it got to within flashover distance ultimately let to the tree getting too close to the line. The programs and processes that BPA has implemented and refined over the years to prevent this type of event from happening failed to acknowledge that this tree was a imminent hazard. The investigation found that the Transmission Owner was following its maintenance plan. The tree characteristics were not recognized by the inspectors as being a potential to reach the transmission line.
WECC | 3Q | 2005 | Los Angeles Department of Water and Power |  |  | Tarzana - Olympic Line 3 | 230 kV | 2005-09-12 |  | 6 min | 209% | Line sagged into a tree while operating well above its emergency rating following a major disturbance on the LDWP system. | 1 | Load was being shed to reduce line loading at time of relay | WECC is repairing a detailed disturbance report |  | Tree was properly trimmed to provide for necessary clearance for normal and emergency operation at the time of occurrence.
MAAC | 4Q | 2005 | Penelec (a FirstEnergy Company) |  |  | East Towanda - Moshannon (SET) | 230 kV | 2005-10-25 |  | 5 hrs 22 min | 32% | Heavy wet snow storm (w/leave still on trees) caused 2 Red Oaks approximately 15 feet off right-of-way located on hillside to topple into line | 2 | Trees removed and line patrolled |  |  | NOAA classified this storm event as one of the top PA storm events in 2005.
MRO | 4Q | 2005 | Xcel Energy - NSP Minnesota |  |  | Blue Lek - Inver Hills - Red Rock | 345 kV | 2005-10-07 |  | 0 min |  | Public damage. Tree contact by contractor to municipality adjacent to line ROW | 2 |  |  |  | A contractor working for the city of Inver Grove clearing trees off (outside) of the right-of-way with a Hydro Axe, cut a tree and lifted, contacting the line. There were no injuries reported.
NPCC | 4Q | 2005 | Hydro One |  |  | H23S (Mrtindale - Holden | 230 kV | 2005-11-28 |  | 14 hrs 33 min |  | A healthy 70-foot tall, 11-inch diameter tree fell into the line during conditions of high winds and wet soil. The tree was 15 feet off the edge of the right-of-way. The tree was reported to be healthy and would not be removed during normal line clearing completed in 2004. | 2
NPCC | 4Q | 2005 | Hydro One |  |  | H23S (Mrtindale - Holden) | 230 kV | 2005-11-28 |  | 14 hrs 33 min |  | A healthy 70-foot tall, 11-inch diameter tree fell into the line during conditions of high winds and wet soil. The tree was 15 feet off the edge of the right-of-way. The tree was reported to be healthy and would not be removed during normal line clearing completed in 2004. | 2
SERC | 4Q | 2005 | South Carolina Electric & Gas Co. |  |  | SRS - Vogtle | 230 kV | 2005-12-06 |  | 4 hrs 18 min |  | Logger working for US Forest Service cut tree outside of ROW that fell onto line | 2 | TO reviewed incident with logger and pointed out incorrect actions. SCE&G also discussed incident with US Forest Service Safety Group who in turn contacted logger. SCE&G will participate in meeting to be conducted by US Forest Service with their loggers to review logging practices. | SERC notes this outage is reportable to NERC but its cause not to do with inadequacies in the TO's vegetation management program.
SERC | 4Q | 2005 | South Carolina Electric & Gas Co. |  |  | Wateree - Summerville | 230 kV | 2005-11-09 |  | 2 hrs 19 min |  | A customer cut a tree that was approximately 20 feet outside of the right-of-way, which then fell into the transmission line. | 2 | A company representative met with the customer to discuss the event. The customer to agreed to let SCE&G cut any trees in the future that might contact the transmission line | SERC notes that this outage is reportable to NERC but is cause not do to inadequacies in the TO's vegetation management program
WECC | 4Q | 2005 | Bonneville Power Administration |  |  | 149227 (Carlton - Tillamook-1 19/8) | 230 kV | 2005-11-05 |  | 10 hrs 13 min | 61.7 MW | Outage caused by winds blowing against non-wind firm cut line in 3rd rotation forest. Tree was infected by root rot. | 2 | Tree was removed
WECC | 4Q | 2005 | Puget Sound Energy |  |  | BPA Monroe | 230 kV | 2005-12-19 |  | 11 hrs 34 min |  | Tree fell into the line | 2 | Removal of tree |  |  | Wind-related
WECC | 4Q | 2005 | Seattle City Light |  |  | MV-SK-1 | 230 kV | 2005-01-31 |  | 7 hrs 10 min | 7% | Tree fell down into the line causing relay action to trip and lock out line. Line did not sustain any damage but clearance was necessary to remove the tree. Tree was located outside of transmission ROW. | 2 | Patrolled the entire ROW to check for dangerous trees
WECC | 4Q | 2005 | Bonneville Power Administration |  |  | North Bonneville - Troutdale -1 | 230 kV | 2005-12-18 |  | 4 hrs 25 min | 105.1 MW | Logging activity adjacent to the transmission line left a fringe of trees along the edge of the transmission line. These trees were not wind firm and consequently blew into the line. | 2 | Trees were removed. The surrounding area was surveyed for additional imminent danger trees
FRCC | 1Q | 2006 | Tampa Electric Company |  |  | Circuit 230020 | 230 kV | 2006-03-09 |  | 54 sec | 7% | A Castor Bean plant had grown up into the energized conductor, made contact and tripped the circuit. The outage occurred directly behind a commercial nursery where peat and other soil nutrients had been discarded | 1 | A TEC right-of way supervisor completed a full circuit patrol on circuit 230020 and has ensured that this entire circuit is clear of any future vegetation issues. Additionally, TEC is completing a ground patrol of all 230 kV lines, having completed 50% of all circuits with the balance of this work scheduled to be completed by May 5, 2006
SERC | 1Q | 2006 | Duke Power Company |  |  | Tyro Black | 230 kV | 2006-01-06 |  | 1 hr 5 min |  | Property owner felled large Poplar tree into bottom conductor. The tree was 95 ft tall and measured 77 ft from center line. No damage was done to the conductor or structures. | 2 | None |  |  | This was a large healthy tree that was being harvested by the property owner. This tree did not show up as a threat during semi-annual helicopter patrol of this line. Outage resulted from human intervention and not an inadequacy in the TO's vegetation management program.
NPCC | 2Q | 2006 | Hydro One |  |  | X1P | 230 kV | 2006-06-08 |  | 12 hrs 20 min | 15% | It was reported that one (12-in diameter) healthy Poplar tree fell into the line from outside the right-of-way during gusting winds and wet soil after heavy rain | 3 | Hydro One has reportedly removed several danger trees in the same area in advance of regular maintenance as a precautionary measure.
SERC | 2Q | 2006 | Dominion Virginia Power |  |  | 2035 | 230 kV | 2006-06-22 | 6/22/2006 @ 08:50 | 2 hrs 10 min |  | Line 2035 locked out when a tree outside the right-of-way fell into the line at structure #70. The tree was a 90 to 100-foot tall Locust tree that had no external danger signs but it had rotted inside the butt and strong winds knocked it down. The tree was 35 feet off the right-of-way | 3 | Crews patrolled the line's corridor for signs of damaged or unhealthy trees and found no problems. Two trees were cut from outside the right-of-way as a precaution
SERC | 2Q | 2006 | Progress Energy Carolinas |  |  | Darlington Plant - sumter | 230 kV | 2006-06-29 | 6/29/2006 @ 15:17:06 | 2 hrs 19 min | 8% | A Pine tree in a fence row grew into the conductor maximum operating zone and caused an outage on the subject line. The tree was a property line screen of Pines along a fence between pasture fields | 1 | Trees in the screen were trimmed during the outage and the trees in that screen are scheduled to be removed at a later date. An additional crew has been secured to expedite scheduled work at other locations on the line. | TO was informed that this outage is being reported as a non-compliance under investigation |  | The line was auto-sectionalized and trees in the screen were trimmed while the section was out. The total outage duration of 259 minutes was for that section of line only. The screen was scheduled to be trimmed in July.
SPP | 2Q | 2006 | American Electric Power |  |  | Pittsburg - Valliant | 230 kV | 2006-06-28 |  | 9 hrs 44 min | 14.6% | A Willow tree growing on the right-of-way was not observed during aerial patrols. It subsequently grew and contacted the transmission line conductor | 1 | The offending tree was removed as well as an adjacent shorter tree. As a result of an investigation, the inspection process is being reviewed to identify remedial measures. | Non-compliance process has been started.
WECC | 2Q | 2006 | Puget Sound Energy |  |  | Cascade - rocky Reach | 230 kV | 2006-06-24 | 6/24/2006 @ 14:16 | 1 hr 55 min | 50% | Tree growing into sagging transmission line | 1 | A 40-foot tree made contact and a bell was broken. Asplundh will remove the tree. In addition, seven areas will either have trees trimmed or removed by June 30
WECC | 2Q | 2006 | Bonneville Power Administration |  |  | Monroe - Custer 1 | 500 kV | 2006-06-25 | 6/25/2006 @ 13:40 | 6 hrs 12 min | 3% | Conductor sagged into a 15-ft willow | 1 | Vegetation removed. Contract Statement of Work being reviewed and amended to clearly define acceptable work standards
WECC | 2Q | 2006 | ATCO Electric |  |  | 9L40 | 230 kV | 2006-06-27 | 6/27/2006 @ 12:57,;13;28 | 11 min; 3 hrs 1 min | 12% | Conductor contacted tree under line | 1 | Tree removed on June 28, 2006
RFC | 3Q | 2006 | Northern Indiana Public Service Co |  |  | Schahfer Generating Station - Babcock Substation | 345 kV | 2006-07-15 | 7/15/2006 @ 12:41:34 CT | 11 hrs 9 min | 26% | Emergency aerial helicopter line patrol and subsequent ground patrol confirmed that the line outage was caused by conductor sag into trees. A freshly scorched tree was identified and residences near the tree reported hearing loud sounds. Electric Transmission engineering states that the weather on that afternoon included a wind shift from a 10+ mph westerly breeze to a northerly 10+ mph late breeze off of Lake Michigan. During the wind shift, weather data for Valparaiso, IN (near the outage location show a brief period of calm to nearly calm winds at nearly the same time as the outage. The calm winds allowed for maximum conductor heating and sag. | 1 | The tree that made contact was cut down while the line was de-energized. Other trees within the same general area were trimmed for at least 25 feel of aerial clearance or removed entirely. On 7/17/06 an emergency aerial helicopter patrol was completed on 3 other 345 Kv lines. On 7/21/2006 NIPSCO conducted the annual aerial helicopter patrol dedicated to inspecting vegetation conditions on all lines 138 kV and above. All locations identified during these patrols where tree trimming or removal was required to meet our current "no closer than distance" for vegetation/conductor clearance were completed by vegetation management contractors between 7/21 and 7/31/2006. | Notice of violation is being processed and Mitigation Plan to prevent future violations will be required in accordance with ReliabilityFirst's Compliance and Enforcement Program. |  | Violation was reported to NERC within 48 hours of the region being aware of the violation
SERC | 3Q | 2006 | Dominion Virginia Power |  |  | 2035 | 230 kV | 2006-09-23 | 9/23/2006 @ 06:39 | 10 hrs 7 min |  | Line 2035 locked out when a tree fell into the conductors. A rotten Oak tree 100 feet off the right-of-way fell and hit an 80-ft Poplar at the edge of the right-of-way, uprooting the Poplar and ropping it on the line between structures 72 and 73 | 3 | Patrols on this line have been increased
SERC | 3Q | 2006 | Southern Company |  |  | Cartersville - South Acworth | 230 kV | 2006-07-03 | 7/3/2006 @ 14:32 | 6 hrs 21 min |  | Severe thunderstorm with high winds. 16" DAB (diameter breast high) Pine approximately 100 feet located 10 feel off right-of-way broke off about 6 feet above ground. Tree fell into the 230 kV line. Top of tree eventually contacted 116 kV. | 3 |  |  |  | Tree was cut from line
WECC | 3Q | 2006 | Bonneville Power Administration |  |  | Bell - Boundary 3 | 230 kV | 2006-08-30 | 8/30/2006@ 02:15:00 | 23.6 min | 5% | The area was burned over by a wildfire. The outage was caused by a dead standing tree 75 feet off the ROW. Trees in this area were evaluated in FY06 and marked for removal in FY07, as part of the annual work plan. | 3 | Tree was removed. Additional trees were evaluated and removed as a precaution
WECC | 3Q | 2006 | Public Service Company of Colorado |  |  | Malta - Rifle (5207) | 230 kV | 2006-07-16 | 7/16/2006 @ 15:21 | 7 min | 42% | Conductor sagged and caused flash into 20'-25' tall, 6" DAB Spruce inside wire zone | 1 | Current routine maintenance cycle in progress since 2005. USFS allowed only selective removal of tall-growing trees previous maintenance cycle. Complete removal of all tall-growing trees that should ever grow too close to conductors on the remaining portion of this line assuming USFS approval. Entire circuit will be completed in 2006 unless unusually early heavy snow pack stops work.
WECC | 3Q | 2006 | Public Service Company of Colorado |  |  | Smokey Hill - Sullivan (5167) | 230 kV | 2006-07-14 | 7/14/2006 @ 14:59 | 2 min | 43% | Conductor sagged and caused flash into 30'-35' tall Willow tree inside wire one. Tree was cleared back 20'-25' from conductor in late July 2004 | 1 | Routine maintenance completed in 1998, 2000, 2002 and 2004 and currently being worked in 2006 to be completed this year. Property owner refused removal/replacement offer in 2004
WECC | 3Q | 2006 | NorthWestern Energy |  |  | Thompson Falls - Burke "A" | <200 kV | 2006-07-30 | 7/30/2006 @ 11:54:20 | 2.64 hrs | 15% | Tree fell from outside of ROW into line | 3 | Have an annual proactive vegetation management program and have vegetation consultant analyzing our system. Tree has been removed.
WECC | 3Q | 2006 | NorthWestern Energy |  |  | Thompson Falls - Burke "A" | <200 kV | 2006-07-06 | 7/6/2006 @ 19:28:24 | 2.99 hours | 26% | Tree fell from outside of ROW into line | 3 | Have an annual proactive vegetation management program and have vegetation consultant analyzing our system. Tree has been removed.
WECC | 3Q | 2006 | NorthWestern Energy |  |  | Thompson Falls - Burke "A" | <200 kV | 2006-08-11 | 8/11/2006 @ 08:09:42 | 6.06 hrs | 11% | Tree fell from outside of ROW into line | 3 | Have an annual proactive vegetation management program and have vegetation consultant analyzing our system. Tree has been removed.
WECC | 3Q | 2006 | NorthWestern Energy |  |  | Thompson falls - Saltese "B" | <200 kV | 2006-07-06 | 7/6/2006 @ 19:22:25 | 2.99 hours | 28% | Tree fell outside of right-of-way | 3 | Have an annual proactive vegetation management program and have vegetation consultant analyzing our system. Tree has been removed.
RFC | 4Q | 2006 | Jersey Central Power & Light Co. |  |  | Bridgewater - Gillette - Lake Nelson | 230 kV | 2006-11-12 | 11/12/2006 @ 18:20 | 3 hrs 58 min |  | Relayed open and locked open after attempted reclose. Off-ROW tree pushed into conductor by tree from further outside of ROW which fell. The failure of the second tree was due to recent land clearing, excavation and changing of grade for new development | 3 | Other trees in the immediate area affected by the same land clearing were inspected. Three trees were identified as similarly being at risk of failing due to the land clearing. These trees were removed |  |  | Reporting to NERC per FAC-003-1. Oak Tree 35' off the ROW edge uprooted falling into the White Ash and causing the White Ash to fail, hitting the bottom phase of the 230 kV line. The Oak Tree uprooted most likely due to the recent lot clearing grade change and construction of a new home adjacent to the ROW and directly next to the Oak T,ree. This outage could be interpreted to have been caused by human activity (but for the lot clearing and grade change adjacent to the ROW, the incident likely would not are occurred) and therefore non-reportable. However, to avoid any interpretation issues, this outage is being reported as a Category 3
RFC | 4Q | 2006 | PECO - Exelon |  |  | Jenkintown - Tabor (220-26) | 230 kV | 2006-11-29 | 11/29/2006 @ 14:18 | 2 hrs 29 min |  | High winds in area. Measured wind speeds of up to 41 mph, with average wind speed of 20 mph recorded at Philadelphia International Airport. A large Hickory tree split at its base 30 feet from the edge of the right-of-way location and fell into the 230 kV conductors located on the railroad corridor (on the downhill side of the tree). The PECO 230 kV line is located on a shared railway (SEPTA) structure | 3 | Foot patrol of the area involved was performed after the event occurred. No new potential issues were identified and no further corrective actions were implemented |  |  | Reporting to NERC per FAC-003-1
WECC | 4Q | 2006 | Bonneville Power Administration |  |  | Carlton - Tillamook - 1 | 230 kV | 2006-12-14 | 12/14/2006 @ 18:32 | 5 days 18 hrs 52 min | 20% | A severe winter storm with heavy rain and sustained winds of 60 mph, gusting from 80-100 mph caused off-ROW trees to fall into the line | 3 | Trees were removed and area patrolled for additional hazards |  |  | Several prior momentary outages on the same line on the same day are compressed here to one reported outage per WECC guidelines. Noted as worst storm in 30 years,.
WECC | 4Q | 2006 | Puget Sound Energy |  |  | Cascade - White River | 230 kV | 2006-11-08 | 11/8/2006 @ 08:18 | 5 hrs 1 min |  | Landslide brought a tree down into the line | 3 | Tree will be removed
WECC | 4Q | 2006 | Puget Sound Energy |  |  | Cascade - White River | 230 kV | 2006-11-08 | 11/8/2006 @ 08:18 | 5 hrs 1 min |  | Land slide brought a tree down into the line | 3 | Tree will be removed
WECC | 4Q | 2006 | Bonneville Power Administration |  |  | Chehalis - Covington - 1 | 230 kV | 2006-12-14 | 12/14/2006 - 20:22 | 1 day 20 hrs 25 min | 43% | A severe winter storm with heavy rain and sustained winds of 60 mph, gusting from 80-100 mph caused off-ROW trees to fall into the line | 3 | Trees were removed and area patrolled for additional hazards |  |  | Noted as worst storm in 30 years
WECC | 4Q | 2006 | Bonneville Power Administration |  |  | Chehalis - Mayfield - 1 | 230 kV | 2006-11-13 | 11/13/2006 @ 01:30 | 3 hrs 29 min | 62% | Severe storm with heavy rain and high wind toppled an off-ROW tree into the line | 3 | BPA continues to inspect and monitor vegetation on and adjacent to the ROW. Tree has been removed.
WECC | 4Q | 2006 | Bonneville Power Administration |  |  | Chehalis - Olympia 1 | 230 kV | 2006-11-13 | 11/13/2006 @ 01:03 | 5 hrs 13 min | 38% | Heavy wind and rain caused an off-ROW Fir tree to fall into the line | 3 | BPA continues to inspect and monitor vegetation on and adjacent to the ROW. Tree has been removed.
WECC | 4Q | 2006 | Bonneville Power Administration |  |  | Chehalis - Olympia 1 | 230 kV | 2006-12-14 | 12/14/2006 @ 19:34 | 4 hrs 13 min | 38% | A severe winter storm with heavy rain and sustained winds of 60 mph, gusting from 80-100 mph, caused off-ROW trees to fall into the line | 3 | Trees were removed and area patrolled for additional hazards |  |  | Noted as worst storm in 30 years
WECC | 4Q | 2006 | Tacoma Power |  |  | Cowliz - SW #4 | 230 kV | 2006-12-15 | 12/15/2006 @ 00:27 | 7 hrs 3 min | 23% | The wind blew a tree down from outside the right-of-way that brushed the center phase (property side) of the transmission line | 3 | This tree contact was during the massive wind storm, December 15, causing unusual conditions. Since the tree was outside of the ROW and was literally uprooted by the wind, there is no planned preventative measures that Tacoma Power will be taking |  |  | Noted as the worst snow storm in 30 years
WECC | 4Q | 2006 | Seattle City Light |  |  | Diablo - Bothell #D-3 | 230 kV | 2006-11-26 | 11/26/2006 @ 07:52 | 3 sec |  | A 100-ft Hemlock tree located 40 feet outside of ROW fell down contacting the line. No damage to the line. | 3
WECC | 4Q | 2006 | NorthWestern Energy |  |  | Hot springs to Placid Lake | 230 kV | 2006-11-13 | 11/13/2006 @ 10:01:50 | 7.82 hrs | 4% | Tree fell from outside ROW into the line | 3 | Have an annual proactive vegetation management program and have vegetation consultant analyzing our system. Tree has been removed.
WECC | 4Q | 2006 | Bonneville Power Administration |  |  | John Day - Marion - 1 | 500 kV | 2006-12-14 | 12/14/2006 @ 21:31 | 3 days 2 hrs 49 min | 17% | A severe winter storm with heavy rain and sustained winds of 60 mph, gusting from 80-100 mph, caused off-ROW trees to fall into the line | 3 | Trees were removed and area patrolled for additional hazards |  |  | Noted as worst storm in 30 years
WECC | 4Q | 2006 | Bonneville Power Administration |  |  | Lancaster - Noxon - 1 | 230 kV | 2006-11-24 | 11/24/2006 @ 06:08 | 8 hrs 8 min | 7% | Heavy snow load in the top of a skinny off-ROW tree caused tree to bend into the line | 3 | BPA continues to inspect and monitor vegetation on and adjacent to the ROW. Tree has been removed.
WECC | 4Q | 2006 | Seattle City Light |  |  | Maple Valley - Snow King #2 | 230 kV | 2006-12-13 | 12/13/2006 @ 14:17 PT | 5 hrs 34 min | 5% | Large Fir tree blown by wind fell into line causing relay actions. No damage to the conductors. Line restored back to service after the tree was removed | 3 | Tree was removed
WECC | 4Q | 2006 | Bonneville Power Administration |  |  | McNary - Ross - 1 | 345 kV | 2006-12-14 | 12/14/2006 @ 20:36 | 12 hrs 18 min | 55% | A severe winter storm with heavy rain and sustained winds of 60 mph, gusting from 80-100 mph, caused off-ROW trees to fall into the line | 3 | Trees were removed and area patrolled for additional hazards |  |  | A prior momentary outage on the same line on the same day is compressed here to one reported outage per WECC guidelines. Noted as worst storm in 30 years,.
WECC | 4Q | 2006 | Bonneville Power Administration |  |  | Murray - Custer - 1 | 230 kV | 2006-11-15 | 11/15/2006 @ 14:05 | 25 hrs 52 min | 8% | Severe storm with heavy rain and high wind toppled an off-ROW tree into the line | 3 | BPA continues to inspect and monitor vegetation on and adjacent to the ROW. Tree has been removed.
WECC | 4Q | 2006 | Bonneville Power Administration |  |  | Murray - Custer - 1 | 230 kV | 2006-11-27 | 11/27/2006 @ 06:54 | 5.65 hrs | 5% | Severe storm with heavy rain and high wind toppled an off-ROW tree into the line | 3 | BPA continues to inspect and monitor vegetation on and adjacent to the ROW. Tree has been removed.
WECC | 4Q | 2006 | Bonneville Power Administration |  |  | Olympia - Grand Coulee - 1 | 230 kV | 2006-11-10 | 11/10/2006 @ 09:23 | 8 hrs 52 min | 53% | Severe storm with heavy rain and high wind toppled an off-ROW tree into the line | 3 | BPA continues to inspect and monitor vegetation on and adjacent to the ROW. Tree has been removed.
WECC | 4Q | 2006 | Bonneville Power Administration |  |  | Olympia - Grand Coulee - 1 | 230 kV | 2006-11-20 | 11/20/2006 @ 09:23 | 8 hrs 52 min | 53% | Severe storm with heavy rain and high wind topple an off-ROW tree into the line | 3 | BPA continues to inspect and monitor vegetation on and adjacent to the ROW. Tree has been removed.
WECC | 4Q | 2006 | Bonneville Power Administration |  |  | Olympia - Grand Coulee - 1 | 230 kV | 2006-12-14 | 12/14/2006 @ 12:36 | 4 hrs 36 min | 55% | A severe winter storm with heavy rain and sustained winds of 60 mph, gusting from 80-100 mph, caused off-ROW trees to fall into the line | 3 | Trees were removed and area patrolled for additional hazards |  |  | Noted as worst storm in 30 years
WECC | 4Q | 2006 | Bonneville Power Administration |  |  | Olympia - So. Tacoma - 1 | 230 kV | 2006-12-14 | 12/14/2006 @ 19;30 | 2 days 2 min | 4% | A severe winter storm with heavy rain and sustained winds of 60 mph, gusting from 80-100 mph, caused off-ROW trees to fall into the line | 3 | Trees were removed and area patrolled for additional hazards |  |  | Noted as worst storm in 30 years
WECC | 4Q | 2006 | Bonneville Power Administration |  |  | Reston - Fairview - 2 | 230 kV | 2006-11-12 | 11/12/2006 @ 17:30 | 10 hrs 44 min | 20% | A tree was blown into the line during a severe storm event causing the fault | 3 | TO is planning to remove additional trees located in a wet area to remove trees with restricted root development. The tree has been removed.
WECC | 4Q | 2006 | Bonneville Power Administration |  |  | Rocky Reach - Maple Valley - 1 | 345 kV | 2006-12-14 | 12/14/2006 @ 17:41 | 12 hrs 35 min | 51% | A severe winter storm with heavy rain and sustained winds of 60 mph, gusting from 80-100 mph, caused off-ROW trees to fall into the line | 3 | Trees were removed and area patrolled for additional hazards |  |  | Noted as worst storm in 30 years
WECC | 4Q | 2006 | Bonneville Power Administration |  |  | Santiam - Alvey - 1 | 230 kV | 2006-12-14 | 12/14/2006 @ 18:27 | 14 hrs 15 min | 37% | A severe winter storm with heavy rain and sustained winds of 60 mph, from 80-100 mph, caused off-ROW trees (70-100 feet tall) to fall into the line | 3 | Trees were removed and area patrolled for additional hazards |  |  | Prior outages on the same line on the same day compressed here to one reported outage (longest) per WECC guidelines. Noted as worst storm in 30 years.
WECC | 4Q | 2006 | Bonneville Power Administration |  |  | Santiam - Toledo - 1 | 230 kV | 2006-12-14 | 12/14/2006 @ 18.33 | 2 days 2 hrs 23 min | 29% | A severe winter storm with heavy rain and sustained winds of 60 mph, gusting from 80-100, mph caused off-ROW trees to fall into the line | 3 | Trees were removed and area patrolled for additional hazards |  |  | Noted as worst storm in 30 years
WECC | 4Q | 2006 | Bonneville Power Administration |  |  | Satsop - Aberdeen - 3 | 230 kV | 2006-11-12 | 11/12/2006 @ 05:19 | 0 min | 13% | An off-ROW tree was blown into the line during a severe storm event (heavy rain and high winds) causing momentary flashover | 3 | BPA continues to inspect and monitor vegetation on and adjacent to the ROW.
WECC | 4Q | 2006 | NorthWestern Energy |  |  | Thomason Falls - Burke "B" | <200 kV | 2006-11-13 | 11/13/2006 @ 09:50:03 | 1.73 hrs | 1.73% | Tree fell from outside of ROW into line | 3 | Have an annual proactive vegetation management program and have vegetation consultant analyzing our system. Tree has been removed.
WECC | 4Q | 2006 | NorthWestern Energy |  |  | Thomason Falls - Burke "B" | <200 kV | 2006-11-23 | 11/23/2006 @ 10:41:10 | .16 hrs | 1% | Tree fell from outside of ROW into line | 3 | Have an annual proactive vegetation management program and have vegetation consultant analyzing our system. Tree has been removed.
WECC | 4Q | 2006 | NorthWestern Energy |  |  | Thomason Falls - Burke "B" | <200 kV | 2006-11-25 | 11/25/2006 @ 04:04:49 | 32.09 hrs | 28% | Tree fell from outside of ROW into line | 3 | Have an annual proactive vegetation management program and have vegetation consultant analyzing our system. Tree has been removed.
WECC | 4Q | 2006 | NorthWestern Energy |  |  | Thomason Falls - Burke "B" | <200 kV | 2006-11-26 | 11/26/2006 @ 21:32:17 | 37.5 hrs | 19% | Tree fell from outside of ROW into line | 3 | Have an annual proactive vegetation management program and have vegetation consultant analyzing our system. Tree has been removed.
WECC | 4Q | 2006 | NorthWestern Energy |  |  | Thomason Falls - Burke "B" | <200 kV | 2006-11-28 | 11/28/2006 @ 11:20:14 | 2.94 hrs | 1% | Tree fell from outside of ROW into line | 3 | Have an annual proactive vegetation management program and have vegetation consultant analyzing our system. Tree has been removed.
WECC | 4Q | 2006 | NorthWestern Energy |  |  | Thomason Falls - Burke "B" | <200 kV | 2006-11-30 | 11/30/2006 @ 13:15:18 | 7.17 hrs | 23% | Tree fell from outside of ROW into line | 3 | Have an annual proactive vegetation management program and have vegetation consultant analyzing our system. Tree has been removed.
WECC | 4Q | 2006 | NorthWestern Energy |  |  | Thompson Falls - Burke "A" | <200 kV | 2006-11-07 | 11/7/2006 @ 19:49:17 | 17.27 hrs | 40% | Tree fell from outside of ROW into line | 3 | Have an annual proactive vegetation management program and have vegetation consultant analyzing our system. Tree has been removed.
WECC | 4Q | 2006 | NorthWestern Energy |  |  | Thompson - Saltese "B" | <200 kV | 2006-12-05 | 12/5/2006 @ 03:29:58 | 9/57 hrs | 12% | Tree fell from outside of ROW into line | 3 | Have an annual proactive vegetation management program and have vegetation consultant analyzing our system. Tree has been removed.
WECC | 4Q | 2006 | NorthWestern Energy |  |  | Thompson Falls - Burke "A" | <200 kV | 2006-10-18 | 10/18/2006 @ 17:51:50 | 15.93 hrs | 12% | Tree fell from outside of ROW into line | 3 | Have an annual proactive vegetation management program and have vegetation consultant analyzing our system. Tree has been removed.
WECC | 4Q | 2006 | NorthWestern Energy |  |  | Thompson Falls - Burke "A" | <200 kV | 2006-11-13 | 11/13/2006 @ 05:48:47 | 8.68 hrs | 26% | Tree fell from outside of ROW into line | 3 | Have an annual proactive vegetation management program and have vegetation consultant analyzing our system. Tree has been removed.
WECC | 4Q | 2006 | NorthWestern Energy |  |  | Thompson Falls - Burke "A" | <200 kV | 2006-11-26 | 11/26/2006 @ 06:58:46 | 5.22 hrs | 46% | Tree fell from outside of ROW into line | 3 | Have an annual proactive vegetation management program and have vegetation consultant analyzing our system. Tree has been removed.
WECC | 4Q | 2006 | NorthWestern Energy |  |  | Thompson Falls - Burke "A" | <200 kV | 2006-11-27 | 11/27/2006 @ 02:49:04 | 20.82 hrs | 48% | Tree fell from outside of ROW into line | 3 | Have an annual proactive vegetation management program and have vegetation consultant analyzing our system. Tree has been removed.
WECC | 4Q | 2006 | NorthWestern Energy |  |  | Thompson Falls - Burke "A" | <200 kV | 2006-11-07 | 11/7/2006 @ 19:49:17 | 17.27 hrs | 40% | Tree fell from outside of ROW into line | 3 | Have an annual proactive vegetation management program and have vegetation consultant analyzing our system. Tree has been removed.
WECC | 4Q | 2006 | NorthWestern Energy |  |  | Thompson Falls - Burke "B" | <200 kV | 2006-11-13 | 11/13/2006 @ 09:50:03 | 1.73 hrs | 44% | Tree fell from outside of ROW into line | 3 | Have an annual proactive vegetation management program and have vegetation consultant analyzing our system. Tree has been removed.
WECC | 4Q | 2006 | NorthWestern Energy |  |  | Thompson Falls - Burke "B" | <200 kV | 2006-11-14 | 11/14/2006 @ 01:02:06 | 13.48 hours | 33% | Tree fell from outside of ROW into line | 3 | Have an annual proactive vegetation management program and have vegetation consultant analyzing our system. Tree has been removed.
WECC | 4Q | 2006 | NorthWestern Energy |  |  | Thompson Falls - Burke "B" | <200 kV | 2006-11-23 | 11/23/2006 @ 10:41:10 | 0.16 hrs | 1% | Tree fell from outside of ROW into line | 3 | Have an annual proactive vegetation management program and have vegetation consultant analyzing our system. Tree has been removed.
WECC | 4Q | 2006 | NorthWestern Energy |  |  | Thompson Falls - Burke "B" | <200 kV | 2006-11-25 | 11/25/2006 @ 04:04:49 | 32.09 hrs | 28% | Tree fell from outside of ROW into line | 3 | Have an annual proactive vegetation management program and have vegetation consultant analyzing our system Tree has been removed
WECC | 4Q | 2006 | NorthWestern Energy |  |  | Thompson Falls - Burke "B" | <200 kV | 2006-11-26 | 11/26/2006 @ 21:32:17 | 37.5 hrs | 19% | Tree fell from outside of ROW into line | 3 | Have an annual proactive vegetation management program and have vegetation consultant analyzing our system. Tree has been removed.
WECC | 4Q | 2006 | NorthWestern Energy |  |  | Thompson Falls - Burke "B" | <200 kV | 2006-11-28 | 11/28/2006 @ 11:20:14 | 2.94 hrs | 1% | Tree fell from outside of ROW into line | 3 | Have an annual proactive vegetation management program and have vegetation consultant analyzing our system. Tree had been removed.
WECC | 4Q | 2006 | NorthWestern Energy |  |  | Thompson Falls - Burke "B" | <200 kV | 2006-11-30 | 11/30/2006 @ 13:15:18 | 7.17 hrs | 23% | Tree fell from outside of ROW into line | 3 | Have an annual proactive vegetation management program and have vegetation consultant analyzing our system. Tree has been removed.
WECC | 4Q | 2006 | NorthWestern Energy |  |  | Thompson Falls - Burke "B" | <200 kV | 2006-11-07 | 11/7/2006 @ 10:39:15 | 17.87 hrs | 23% | Tree fell from outside of ROW into line | 3 | Have an annual proactive vegetation management program and have vegetation consultant analyzing our system. Tree has been removed.
WECC | 4Q | 2006 | NorthWestern Energy |  |  | Thompson Falls - Burke "B" | <200 kV | 2006-12-05 | 12/5/2006 @ 03:29:58 | 9.57 hrs | 12% | Tree fell from outside of ROW into line | 3 | Have an annual proactive vegetation management program and have vegetation consultant analyzing our system. Tree has been removed.
MRO | 2Q | 2007 | Western Area Power Administration |  |  | VBI - Branch - N. Magazine (AEP) | 345 kV | 2007-11-16 | 11/16/2007 @ 13:20 CT | 33 min | 17% | Cottonwood tree grew into line | 1 | Tree removed entirely 6/19
RFC | 2Q | 2007 | American Electric Power |  |  | Fall Creek - Sunnyside | 345 kV | 2007-05-29 | 5/29/2007 @ 1:03 pm ET | 23 hrs 59 min | 16% | A Bittner Hickory tree grew into a conductor between towers 73 & 74 on the Fall Creek - Sunnyside circuit near the town of Eden, Indiana | 1 | A detailed mitigation plan was provided to ReliabilityFirst Corporation (RFC) on June 14, 2007 and approved by RFC on June 18, 2007. | Representatives from AEP are scheduled to visit RFC on 8/6/2007 to discuss the event and Vegetation Management Program |  | The contact occurred on the AEP-owned portion of a circuit with ownership between AEP and Indianapolis Power & Light (IP&L). AEP owns 21.03 miles and IP&L owns 10.42 miles
RFC | 2Q | 2007 | American Transmission Co. LLC |  |  | Forest Junction - Arcadian (971L51_ | 345 kV | 2007-05-24 | 5/24/2007 @ 20:08 | 29 hrs 42 min |  | During a planned line outage high winds (40-50 mph) caused a dead Elm tree off right-of-way (30 feet beyond the edge of the row) to fall into a healthy off right-of-way (10 feet beyond the right-of-way) tree. The healthy tree was bent over in close proximity (1 foot) to the A phase transmission line conductor. The Forest Junction breaker tripped during planned re-energization of the line. | 3 | The dead Elm and the healthy trees were removed on Saturday morning 5/26. The domino effect of one tree bending another tree towards the transmission line was documented for a "lessons learned" review scheduled for ATC's June ATC Transmission Line Maintenance Specialists (TLMS) meeting. The TMLS are to forward "lessons learned" to their patrollers. |  |  | Cat. 3 outage was also reported to MRO on 6/8/2007 in their May Monthly Vegetation Data Collection
RFC | 2Q | 2007 | Jacksonville Electric Authority |  |  | Greenland Switzerland | 230 kV | 2007-05-06 | 5/6/2007 @ 12:20, 13:27, and 15:39 | 4 min, 5 min and 4 min | 62%, 54%, and 50% | Tree fell during high winds which then touched the transmission line causing the line to trip | 2 | Inspected vegetation along the right-of-way for this event and addressed at risk vegetation |  |  | Three total trips over approximately a 2 to 3-hour period
RFC | 2Q | 2007 | Duke Energy Corporation |  |  | Lafayette - New London | 230 kV | 2007-05-08 | 5/8/2007 @ 12:59:19 | 8 hrs 3 min | 26% | Vegetation grow-in | 1 | Trees associated with this outage were trimmed within 24 hours and removed within 14 days of the incident. | Reviewed and accepted mitigation plan |  | Duke Energy self-reported a potential reliability standard violation and submitted a mitigation plan accepted by ReliabilityFirst prior to June 18, 2007
RFC | 2Q | 2007 | PPL Electric Utilities Corporation |  |  | Martins Creek - Monroe | 230 kV | 2007-06-24 |  | 17 hrs 4 min | 34% | A weakened Hickory tree located 50 feet off the edge of the ROW fell into a Tulip Poplar tree approximately 80-90 feet in height and 30 feet outside the ROW which uprooted and fell into the outside phase of the Martins Creek - Monroe 230 kV line | 3 | Tree was 30 feet outside of PPL Electric Utilities' defined ROW width of 150 feet
RFC | 2Q | 2007 | Jacksonville Electric Authority |  |  | Northside - West Jacksonville | 230 kV | 2007-06-13 | 6/13/2007 @ 13:32 | 2 hrs 4 min | 8% | Tree outside the ROW fell into the line. | 3 | Inspected vegetation along the right-of-way for this event
SERC | 2Q | 2007 | Georgia Power Company |  |  | Center Primary - Winder Primary | 230 kV | 2007-04-15 | 4/15/2007 @ 17:09:00 | 3 hrs 56 min |  | Green Oak Tree approximately 96' tall located 85.5 feet from center of line was uprooted by wind in thunderstorm and fell into north phase at structure 48. Right-of-way width on this line is 62.5 feet from center line | 3 | Cleared tree |  |  | Line had been patrolled by Danger Tree Crew weeks before and tree was not cut due to the apparent good health of the tree
SERC | 2Q | 2007 | Process Energy Carolinas |  |  | Fayetteville - Ft. Bragg Woodruff | 230 kV | 2007-06-04 | 6/4/2007 @ 13:53:05 | 45 min | 46% | Tree under line grew into line | 1 | Sixty-five trees were removed from the spans adjacent to the contact. Entity is performing additional surveillance and reprioritizing work. Will address all identified concerns by EOY 2007. Entity has also modified VM program to be more proactive and aggressive over three-year cycle. | Region has reported this event as a violation and will perform periodic checks to verify proposed corrective actions are being taken according to the schedule provided. |  | At the time of the outage, power was flowing into both ends of the line (no end-to-end through flow) supplying load at four PEC substations and one non-PEC point of delivery. Following the interruption, the line was sectionalized and all load was restored. The impacted section of line was isolated and system Operations provided clearance for the isolated line section. Clearance from System Operations on the isolated section was held until field personnel completed investigations, measurements and removals. The isolated section of line was out of service until June 6 at 11:53 am. This outage was self-reported to SERC on June 5, 2007 with a proposed mitigation plan submitted on June 15, 2007
SERC | 2Q | 2007 | Tennessee Valley Authority |  |  | Johnsonville - Cumberland | 500 kV | 2007-04-11 | 4/11/2007 @ 15:23:05 | 1 hr 50 min |  | A tree in the ROW had been pushed and caused to lean toward the line by a dead Pine snag that fell from father off the right-of-way | 2 | Tree was cleared in addition to additional vegetation in the area. The entire line was flown with no further problems indentified. |  |  | On 4/11/2007 at 15:03:25, the Cumberland - Johnsonville 500 kV line faulted. The reclosing relays reclosed twice before locking out. The fault occurred during stormy weather conditions. System operators chose not to perform the 1-minute or 5-minute manual tests since the system configuration and loading did not require this line to be returned to service immediately. An aerial line patrol was performed. A tree was found to be burnt on the patrol but the observer indicated that it was clear and the line was successfully reclosed at 17:53. The line remained in service. The next day the vegetation maintenance personnel requested the line be de-energized and the burnt tree was cut. The tree had been pushed and caused to lean towards the line by a dead Pine snag that fell from farther off the right-of-way. The tree that caught on fire on 4/11 was on the right-of-way and leaned towards the line such that under non-windy conditions the leaning top was approximately 10-15 feet from the line. Without the contribution to leaning caused by the fallen snag, the estimated clearance would have been 25-30 feet. The location was difficult to see on the aerial patrol because the span included a long low hollow for most of the span with a rise in the elevation on the edge of the hollow at the location of the subject trees. Numerous dead Pine snags had fallen over the surrounding area due to recent storms. It was sighted on the second patrol due to smoke from fire in the adjacent woods. The following day other brush and standing trees on the up-slope side of the hollow were removed. The rest of the line was flowing again and no further problems were found.
SERC | 2Q | 2007 | Georgia Power Company |  |  | Boulevard - Scottsdale Line 629028 | 230 kV | 2007-06-25 | 6/25/2007 @ 15:30:00 | 6 hrs 44 min |  | 70-ft sound Sweetgum tree located off the right-of-way fell during a thunderstorm with wind. | 3 | Cleared tree
SERC | 2Q | 2007 | Entergy |  |  | Carlyss - Sabine | 230 kV | 2007-06-04 | 6/4/2007 @ 17:02:13 | 2? |  | Line patrol found a green Pine tree off ROW that had fallen through the line between structure 26 & 26. There was no damage to the structures. | 3 | Aerial patrol was performed to determine outage cause. Crews remove the pine tree and inspected trees in area for other risk
SPP | 2Q | 2007 | OKGE |  |  | Sioux City - Split Rock | <200 kV | 2007-11-27 | 11/27/2007 @ 07:14 | 6 min | 27% | Willow tree grew into line | 1 | Removed tree from ROW | OG&E Asset Management Group is reviewing all lower voltage critical facilities to reduce possibility of future events |  | Record rainfall for March through June 2007 led to increased vegetation growth
FRCC | 1Q | 2008 | Florida Power & Light Company | NCR000024 |  | Duval - Springbank | 230 kV | 2008-03-08 | 3/8/2008 @ 10:58:40 and 11:04:34 | 8 hrs 12 min |  | Green Pine Tree from off right-of-way found blown over laying on phases at Str 256i5. Tree was removed and line restored to service. Winds were 30-50 mph. | 3 | Vegetation management re-patrolled this line after this event. No other off-ROW danger trees were present. An interim helicopter patrol was completed for 500 kV and 230 kV backbones. Danger trees were identified and have been mitigated. Examination of the failed tree indicated that root rot and height wind combined to cause the tree to fail. Root rot is difficult if not impossible to identify on a ground patrol. This tree had no outwards signs of root rot such as die back of canopy and was not identified as a danger tree.
SERC | 1Q | 2008 | Dominion Virginia Power | NCR01214 |  | Line 2029 | 230 kV | 2008-01-30 | 1/30/2008 @ 07:25 ET | 2 hrs 5 min |  | Wind uprooted a dead tree that was 30 feet off the right-of-way | 3 | Entity reports they have stepped up routine patrols |  |  | Tree had been identified for removal during next routine patrol
WECC | 1Q | 2008 | AVA | NCR05020 |  | Benewah - Pine Creek | 230 kV | 2008-01-27 | 1/27/2008 @ 17:38 | 21 hrs 12 min |  | Green healthy tree loaded with snow and ice fell in from outside the right-of-way | 3 | Line patrol did not find any other tree problems
WECC | 1Q | 2008 | Avista | NCR05020 |  | Cabinet - Rathdrum | 230 kV | 2008-01-29 | 1/29/2008 @ 18:29 | 19 hrs 37 min |  | Several small 8-10 inch DBH healthy trees loaded with snow and ice broke off and fell into right-of-way from outside the right-of-way | 3 | Line patrol did not find any other tree problems
WECC | 1Q | 2008 | British Coumbia Transmission Corp. | NCR05038 |  | Creekey - Cypress (2L13) | 230 l | 2007-01-07 | 1/72007 @ 12:50 PT | 26 hrs 19 min |  | Heavy wet snow loading brought down clump of Conifers from off-ROW, the largest of which contacted and rested on line. Trees slid off a rock outcrop 8-10 m inside forested edge. Cause was shallow rooting over bedrock and heavy snow load stress on tree clump. High avalanche risk reported for the area. Failure occurred in Phyllis Creek watershed between Str 31/1-31/2 uphill of line. Tree was 30-60 cm DBH and approximately 25 m tall. Delay in repair due to poor visibility and foggy conditions making helicopter access difficult. | 3 | This circuit has regular vegetation patrols twice/year and all scheduled ROW maintenance is up to date. Circuit has had detailed hazard tree program on it - this section had hazard trees removed in 2006. This clump of trees was not identified as at risk of failure. Weather conditions leading to height snow slides/avalanche risk identified as cause of failure. This section of circuit passes through Greater Vancouver Regional District Watershed and has restricted access. | None beyond patrolling area for further storm damage and removal of failed trees. Area of failure has poor winter access - helicopter access only. Further review of hazards at this site Is scheduled to take place during Spring 2008 when snow clears. |  | Cost of $10,000 CDN to fly in and remove tree. This outage caused no customer loss because it serves a load which has alternate feeds.
WECC | 1Q | 2008 | Bonneville Power Administration | NCR05038 |  | Lane - Wend son 2 | 230 kV | 2008-01-04 | 1/4/2008 @ 07:12 | 9 hrs 9 min | 24% | Single Douglas Fir uprooted and fell across C Phase | 3 | Tree removed and area analyzed for other potentially unstable trees. None found. | None beyond tree removal
WECC | 1Q | 2008 | NorthWestern Energy | NCR05282 |  | Thompson Falls - Burke "A" | <200 kV | 2008-01-03 | 1/3/2008 @ 23:40:05 | 16.62 hrs | 20.42% | Tree fell into line from edge of right-of-way | 3 | Ongoing vegetation management on this line | Removed tree
WECC | 1Q | 2008 | NorthWestern Energy | NCR05282 |  | Thompson Falls - Burke "A" | <200 kV | 2008-01-15 | 1/15/2008 @ 1:48:06 | 16.12 hrs | 14.79% | Tree fell into line from edge of right-of-way | 3 | Ongoing vegetation management on this line | Removed tree
WECC | 1Q | 2008 | Puget Sound Energy | NCR05345 |  | Cascade - White River | 230 kV | 2008-01-01 |  | 23 hrs |  | Tree fell in line from out of the right-of-way due to heavy snow conditions | 3 | Crew removed tree
WECC | 1Q | 2008 | Avista | NCR05020 |  | Benewah - Boulder | 230 kV | 2008-02-01 | 2/1/2008 @ 08:26 | 6 hrs 26 min |  |  | 3
WECC | 1Q | 2008 | Avista | NCR05020 |  | Thompson Falls - Burke "B" | <200 kV | 2008-02-07 | 2/7/2008 @ 00:36 | 2 hrs 48 min |  | Schweitzer Reading showed NWMT side, NWMT said they were unable to send anyone because avalanche danger was too high. Terry Skantel (AVA) went in on snow cat a few days later and found the tree was on our side. Green tree from outside the right-of-way uprooted and fell into the B line. | 3
WECC | 1Q | 2008 | NorthWestern Energy | NCR05282 |  | Thompson - Saltese - Burke | <200 kV | 2008-02-06 | 2/6/2008 @ 01:156:20 | 21.58 hrs | 12.68% | Tree fell into line from edge of right-of-way | 3 | Ongoing vegetation management on this line | Removed tree
WECC | 1Q | 2008 | Pacific Gas & Electric | NCR05299 |  | Pit #4 (off Pit #5 Road Mountain | 230 kV | 2008-02-02 | 2/2/2008 @ 5:31 pm | 24 hrs |  | An off-ROW 80-ft tall Ponderosa Pine fell into the Pit #4 230 tapline near structure 3/26 during a winter storm | 3 |  |  |  | No customers were affected
WECC | 1Q | 2008 | Portland General Energy Company | NCR05325 |  | Bethel - Round Butte | 230 kV | 2008-02-05 | 2/5/2008 @ 17:30 | 98 hrs 52 min |  | The tree was located in the higher elevations of State of Oregon lands just went of the Sardine drainage basin. Crew said there were spots that they estimated had 13 feet of snow. The tree causing the outage was a co-dominant stemmed Douglas Fir about 32" DBH. The stem broke out under gusty winds coupled with snow loading,. The stem broke at the stem attachment about 12' from the ground. The tree itself was off of the right-of-way 20 feet. The stem that broke was about 16-18" at the break. | 3 | When the snow melts, the line will be patrolled through the higher elevation areas (mile 35 - 40) to see if there are any co-dominant stemmed trees within close proximity to the right-of-way
FRCC | 2Q | 2008 | Progress Energy Florida | NCR00063 | FRCC200800080 | Crawfordville - Port St. Joe (CPS) | 230 kV | 2008-06-02 | 6/2/2008 @ 13:54:47 through 6/5/2008 @ 12:55:32 |  | 21% | Tree contacted conductor from underneath within right-of-way | 1 | 1. Crews were cutting the entire width of the right-of-way on Forbs Island to the full 100' width. Extra resources are being maintained until the work is complete. 2. The annual work plan will be revised to require Forbes Island be inspected from the ground annually in the month of May to ensure clearance distances are maintained to ensure the reliability of the line. The island will also be patrolled as part of our normally scheduled aerial cycle. 3. The annual work plan will be revised to require Forbes Island to be cleared annually in the month of February utilizing machinery and/or hand-cutting resources (if herbicides are permitted in the future, this cycle will be changed accordingly. | FRCC initiated a spot check investigation regarding the outage and requested the registered entity submit documentation regarding the NERC reliability Standard FAC-003. |  | 4. All tranmission lines >200 kV are being inspected aerially throughout the system ahead of their normal patrol schedules. Reliability risks will be assesed and removal/trimming will be performed. Cycle lengths according to Progress Energy's Transmission Vegetation Management Program (MNT-TRMX-00176 2.4.1) will be assessed during this patrol to ensure our current cycles for specific lines or segments are short enough to provide the desired reliability results to meet the requirements acording to FAC-003-1. any specific lines or segments that require a shorter cycle length due to environmental or other restricture factors will be documented and scheduled according to the conditions found in the field to ensure reliability is not compromised between clearing cycles. FRCC is submitting the Q2 Vegetation report as two separate reports. The Vegetation form template appeared to "locked" and would not allow the insertion of an additional table for the additional invormation
FRCC | 2Q | 2008 | Progress Energy Florida | NCR00063 | FRCC200800080 | Deland West - Silver Springs (SDW) | 230 kV | 2008-06-19 | 6/19/2008 @ 16:11:39 | 1 hr 48 min | 35% | This particular event was initated with a lightning strike on C-phase. Within milliseconds, there was an A-phase to B-phase fault. The C phase opened 1,969 cycle before relays operated and opened A and B phases. There was no phase-to-ground fault assocated with the event. Upon feild inspection the line crew found an uprooted tree lying parallel to the conductor. The top of the tree had contacted the A phase and bounced off. There was no charring or burn marks on the tree that contacted the line. The ground current associated with the fault was on 31 amps and is inconsistent with a tree-related fault. Our experience has been that there is always evidence of charring or burnt wood debris on the tree itself or on the ground when a tree causes a fault and outage. There was no indication of charring or burnt wood observed as a result of the tree's contact with the line. The uprooted tree contacted the line after the line had relayed out based on the lack of charring and low ground fault current. While there was contact between the tree and the line, evidence points to the lightning strike as the reason the Deland West Substation - Silver Springs Substation line (SDW) relayed out. PEF is reporting this event because a tree did contact the SDW line even though it did not cause the outage | 3 |  | Spot check investigation has been initiated by FRCC. The registered entity has been requested to submit documentation regarding the FAC-003 NERC Reliability Standard |  | FRCC is submitting the Q2 Vegetation report as two separate reports. The Vegetation Form template appeared to be "locked" and would not allow the insertion of an additional table for the additional information
NPCC | 2Q | 2008 | NYSEG | NCR07181 | NPCC200800041 | 67 Line | 230 kV | 2008-04-18 | 4/18/2008 @ 20:23 ET | 7 hrs 4 min | 104% | The 67 Line aged into an Apple tree in Bryncliff recreational area causing line to trip and lockout. The height of the apple tree when contact occurred is estimated to be approximately 22' and loading was 1120 amps. The NYSEG Transmission Vegetation Management Program was followed. It was determined during the last treatment in late 2001 that this Apple tree did not pose a risk and was considered a "desirable" ROW species. In 2001 the cycle for ROW clearing was 8 years per NYSEG's Long Range ROW Management Plan filed with the NY Department of Public Service. NYSEG is transitioning from an 8-year cycle to a 6-year cycle based upon requirements of the PSC ROW Management Order. | 1 | The Apple tree has been removed and wire zone has been cleared. The current treatment cycle for the ROW of this line is 6 years. The line was last treated in 2001 in compliance with the Vegetation Management policy and was scheduled for treatment this year, as we are transitioning from an 8-year to a 6-year cycle. The clearance between the conductor sag was estimated and determined to be adequate. An atypical amount of conductor sag occurred at the time of contact causing the event. We are investigating the reasons for the a typical amount of conductor sag and will work to continue to improve our Vegetation Management procedures and policies. | NPCC is investigating the violation |  | The event occurred on April 18, which was under winter ratings however the condition that occurred was summer as the temperature was around 70 degrees during the event. The actual loading was 1120 amps; the normal summer rating is 1080 amps and the winter normal rating is 1284 amps. The percentage that actual flow is based on normal is 103.7% based on summer and 87% based on winter.
SERC | 2Q | 2008 | Entergy | NCR01234 | SERC200800144 | Baxter Wilson SES SWYD - Grand Gulf | 500 kV | 2008-06-13 | 6/13/2008 @ 13:19:55 | 22.28 hrs | 12.3% | Following the line outage, an investigation identified a Eastern Cottonwood Tree showing evidence of flashover damages located below a 500 kV conductor | 1 | 1. Completed floor vegetation maintenance through the affected and adjacent spans from edge to edge of ROW 2. Completed aerial patrol of all lines in the state above 200 kV on June 18, 2008. 3. Completed aerial patrol of remaining entity lines | SERC staff is pursuing an investigation and compliance enforcement actions in accordance with the CMEP. |  | The entity self-reported the vegetation-related outage.
SERC | 2Q | 2008 | Georgia Power Company | NCR02147 |  | Bay Creek - Conyers | 230 kV | 2008-05-23 | 5/23/2008 @ 20:50:47 | 17.16 hrs |  | Outage was caused by a live Pine tree rooted on a sandy creek-bank five feet from ROW falling onto the conductor. Roots were undermined allowing the tree to fall. | 3 | Five adjacent trees that appeared to have destabilizing erosion around the roots were cut the same day. |  |  | An active sand dredging operation in the creek in the immediate vicinity of the fallen tree may have contributed to the undermining of the roots
SERC | 2Q | 2008 | Georgia Power Company | NCR01247 |  | East Point - Villa Rica | 230 kV | 2008-06-19 | 6/19/2008 @ 23:24:36 | 13.6 hrs |  | A 110-ft tall Red Oak on a 20-ft high ridge 35 feet from the ROW broke off about 6 feet above ground. The trunk of the tree was hollow but appeared healthy externally | 3 | The tree was removed. No other danger trees were identified in the immediate area
SERC | 2Q | 2008 | Virginia Electric & Power Company | NCR09027 |  | 2051 | 230 kV | 2008-06-18 | 6/18/2008 @ 04:08:28 | 7 hrs 25 min |  | A 106-ft tall Red Oak tree 35 free off the right-of-way was uprooted and fell onto a conductor. Root damage was apparent. | 3 | Tree was removed from conductor. The area was patrolled for any other potential hazard. None were found
SERC | 2Q | 2008 | Georgia Power Company | NCR01247 | SERC200800150 | Thomaston - Yates | 230 kV | 2008-06-11 | 6/11/2008 @ 12:15:39 | 1 hr 31 min | 50% | A tree rooted in a land owner's fence row and directly under a conductor grew close enough to the conductor to create a flashover and phase to ground fault. | 1 | The tree was removed by Transmission Specialist and the line was flown to identify any other issues. An investigation of the facts and circumstances around the event is still under way to determine appropriate changes to the TVMP and related tasks | The region has participated in the investigation of the event including a site visit and SERC staff is pursuing an investigation and compliance enforcement actions in accordance with the CMEP. |  | On June 11, 2008 at 12:15:39 a lockout occurred on a 230 kV transmission line. The line was de-energized to perform air and ground patrols of the facilities in spans indentified by relay data. Initial investigation did not identify the cause of the lookout and the line was determined safe to operate. The line was returned to service at 16:38:44. The cause of the lockout was categorized as "unknown" pending further investigation. On June 27, 2008, a Transmission Specialist investigating a property owner claim revisited the right-of-way and observed a probable cause of the June 11 lockout. Evidence at the site indicated probable contact with a tree.
WECC | 2Q | 2008 | Bonneville Power Administration | NCR05032 | WECC200800872 | Big Eddy - Chemawa | 230 kV | 2008-06-28 | 6/28/2008 @ 10:23 | 27.01 hrs | 22% | A wild cherry tree grew into the big Eddy - Chemawa line | 1 | Tree removed. Additional trees in span and along line cut | Root Cause Analysis initiated and in progress. Management on-site visit made |  | WECC representatives toured site with members of Root Cause Analysis team on 7/2/2008
WECC | 2Q | 2008 | NorthWestern Energy |  | NCR05282 | Thompson Falls - Saltese to Burke "B" | <200 kV | 2008-06-21 | 6/21/2008 @ 09:24:30 | 79.24 hrs | 46.5% | Tree fell into line | 3 | Ongoing vegetation management on this line | Removed tree |  | Tree broke crossarm
WECC | 2Q | 2008 | Puget Sound Energy | NCR05345 |  | Sedro Woolley - SCL Bothell | 230 kV | 2008-06-22 | 6/22/2008 @ 21:03 | 12 hrs | 31.3% | A Cottonwood tree from a tree farm nearby fell into two phases of the line | 3 | OSE will target several rows of these trees for removal in order to create more separation from the transmission line. This work will be completed in 2008
NPCC | 3Q | 2008 | NYSEG | NCR07181 | NPCC20080042 | Coopers Corners - Fraser Line 33 | 345 kV | 2008-07-11 | 7/11/2008 @ 2:46 pm | 4 hrs 51 min | 75.3% | The energized conductor on "A" phase sagged into a White Spruce tree between structure 147 and 148. This span of transmission line is located in a rural area of the Catskill Mountains. The Beaverkill river bisects this span of Line 33. The tree was measured to be 33 feet from the centerline of the circuit. The outside conductor is 28 feet from the centerline of the circuit. Span length was calculated (using NYSEG's GIS-based Vegetation Management System) at 1,343 feet long. While the line was de-energized, field personnel visually estimated that the conductor was 10-12 feet above the tree that caused the line to trip out of service. | 1 | NYSEG responded immediately after System Operation staff received alarms indicating a trip and lockout. Two NYSEG line crews and a construction supervisor were dispatched to the area where the problem was suspected to have occurred based upon information from the fault distance relay. Upon arrival at the site the crews immediately identified the cause of the trip to be a tree contact based on the discovery of a burned tree top. Once line clearance permission was received to work, the crews proceeded to cut down 2 to 3 trees and reduced the height of 4 to 5 more. Tree removal continued during the week of July 14. | Process of settlement | 2008-08-15
NPCC | 3Q | 2008 | NYSEG | NCR07181 | NPCC20080042 | Coopers Corners - Fraser Line 33 | 345 kV | 2008-07-11 | 7/11/2008 @ 2:46 pm | 4 hr 51 min | 75.3% | The energized conductor on "A" phase sagged into a White Spruce tree between structure 147 and 148. This span of transmission line is located in a rural area of the Catskill Mountains. The Beaverkill river bisects this span of Line 33. The tree that came in contact with the conductor was measured to be 51' feet tall and 16 inches in diameter at the base. The location of the tree was measured to be 33 feet from the centerline of the circuit. The outside conductor is 28 feet from the centerline of the circuit. Span length was calculated (using NYSEG's GIS-based Vegetation Management System (at 1,343 feet long). While the line was de-energized, field personnel visually estimated that the conductor was 10-12 feet above the tree that caused the line to trip out of service. | 1 | NYSEG responded immediately after System Operations staff received alarms indicating a trip and construction supervisor was dispatched to the area where the problem was suspected to have occurred based upon information from the fault distance relay. Upon arrival at the site, the crews immediately identified the cause of the trip to be a tree contact based on the discovery of a burned tree top. Once line clearance permission was received to work, the crews proceeded to cut down 2 to 3 trees and reduced the height of 4 to 5 more. Tree removal continued during the week of July 14 | Process of settlement | 2008-08-15
NPCC | 3Q | 2008 | Hydro-Quebec TransEnergie | NCR07112 | NPC 1200800039 | B5D (span 65) | 230 kV | 2008-07-17 |  | 5 hr 1 min | 87% | Line to ground faults caused by branches under the line. Upder span 65, distribton line crosses the B5D line. The need for pruning was identitifed earlier but it was delayed by the need to coordinate with the distributin crew | 1 | Following the Thrusday line trips a helpcopter was sent to patrol the B5D line. Span 63 and 65 were identified as a potential source of fault. Ground inspections was performed at those locations. No evidence of electric arc was found but trees were close to conductor at span 65. Action: Pruning was scheduled for Friday under the indentified span. Pruning was performed as scheduled on July 18 | issued PNOAV | 2008-07-22
NPCC | 3Q | 2008 | Hydro-Quebec TrnsEnergie | NCR07112 | NPCC20080040 | B5D (span 66) | 230 kV | 2008-07-21 |  | 11 hrs 15 min | 88% | Line to ground faults caused by branches under the line. It was found that a pile of rocks and dirt was pushed beside a farming field. The presence of low vegetation on that pile was enough to reduce considerably the clearing between the ground and the conductor | 1 | Following the Monday line trips, a helpicopter was sent to patrol the B5D line. Following the air inspection, two teams were sent on the ground, one at span 36 and one at span 39. The vegetation was cut. The line was back in service at 22:00 hours. Tuesday, a ground team patrolled the line. Preventative pruning work was coomleted by TransEnergie and a request was made to HQ Distribution for the vegetation control nearby the distribution line at span 65. Wednesday, HQ distruibuton committed to complete the work before the end of the day and HQT Control Room imposed a line limitation at 300 MW until work would be completed. Around 17:00 the same day, the work was done and the restriction removed | issued PNOAV | 2008-07-22 | Ground topgraphy was modified under span 36 without permission of the transmission owner. All lines cheduled in the 2009 vegetation control plan and all interconnexion lines are being inspectd by helicopter.
RFC | 3Q | 2008 | PECO Energy Company | NCR08024 |  | Bradford - Planebrook | 230 kV | 2008-09-07 | 9/7/20008 @ 11:34 | 3 hrs 30 min | 28% | The cause of the outage was a result of a tree falling into the conductor from outside the line right-of-way. The tree was approximately 60' from the nearest conductor, and approximately 24' outside of the right-of-way. This occurred during tropical storm Hanna, which had entered the PECO service territory | 3 | The tree was immediately removed from the right-of-way and the line was returned to service at 15:04 | Reported in accordance with FAC-003 |  | Telephone notification on 10/2/2008. Written notification via quarterly report, which was sent and received on 10/9/2008
SERC | 3Q | 2008 | Georgia Power Company | NCR01247 |  | Boulevard - Norcross | 230 kV | 2008-08-12 | 8/12/2008 @ 20:20 | 11.9 hrs |  | An 85' tall, 12" diameter live Pine tree split from ground to 20' above ground. Tree was located 30' off ROW and 50' from C/L of ROW. The single falling tree locked out both circuits of a double circuit pole-line. The outage of the other line is reported separately as Outage 2 in this report | 3 | Tree was removed | Region verified that this was not a compliance-related issue | 10/102008 | The single falling tree locked out both circuits of a double-circuit pole line. The outage of the other line is reported separately as Outage 2 in this report
SERC | 3Q | 2008 | Georgia Power Company | NCR01247 |  | Dering Circle - Norcross | 230 kV | 2008-08-12 | 8/12/2008 @ 20:20 | 11.6 hrs |  | An 85' tall, 12" diameter live pine tree split from ground to 20' above ground. Tree was located 30' off of ROW and 50' from C/L of ROW. The single falling tree locked out both circuits of a double circuit pole-line. The outage of the other line is reported separately as Outage 1 in this report. | 3 | Tree was removed and line restored | Region verified that this was not a compliance-related issue | 2008-10-10 | The single falling tree locked out both circuits of a double-circuit pole line. The outage of the other line is reported separately as Outage in this report.
SERC | 3Q | 2008 | Georgia Power Company | NCR01247 |  | Cartersville - Pinson | 230 kV | 2008-07-21 | 7/21/2008 @ 19:24 | 9 hrs 27 min |  | Live tree located 15' of ROW in a wet area was uprooted during a thunderstorm and leaned against outer phase of line. | 3 | Tree was removed and line restored | Region verified that this was not a compliance-related issue | 10/102008
TRE | 3Q | 2008 | Kiowa Power Partners | NCR04088 | TRE200800063 | KMCHI-KWAS | 345 kV | 2008-08-01 | 8/1/2008 @ 13:03 | 5 hrs 59 min | 55% | Tree growth near phase conductor, leading to trip of line connecting generation facility to grid. | 1 | Entity attempted to locate cause of phase ground trip but was not initially successful. After a second event two days later, tree was identified and promptly removed. Further analysis by the entity led to discovery of a design issue that resulted in clearance deficiency. The entity addressed this by adding a new pole to raise the line, all prior to initial notification | N/A at this point; save preliminary fact-fathering | 2008-09-25 | Supplemental self-report received from entity November 14
TRE | 3Q | 2008 | Kiowa Power Partners | NCR04088 |  | KMCHI-KWAS2 | 345 kV | 2008-08-03 | 8/3/2008 @ 14:47 | 2 hrs 5 min | 55% | Tree growth near phase conductor leading to trip of line connecting generating facility to grid | 1 | Entity located tree and promptly removed on August 4. Further analysis by the entity led to discovery of a design issue that resulted in clearance deficiency. The entity addressed this by adding a new pole to raise the line, all prior to initial notification | N/A at this point; save preliminary fact-fathering | 2008-09-15 | Supplemental self-report received from entity November 14
WECC | 3Q | 2008 | NWC | NCR05282 |  | Thompson Falls to Burke | <200 kV | 2008-08-19 |  | 2 hrs 33 min |  | Tree fell into line | 3 | Ongoing Vegetation Analysis and Management on this line | Ongoing Vegetation analysis and Management on this line | 2008-10-22
WECC | 3Q | 2008 | NWC | NCR05282 |  | Thompson Falls to Burke | <200 kV | 2008-09-22 |  | 3 hrs 8 min |  | Tree fell into line | 3 | Ongoing Vegetation Analysis and Management on this line | Ongoing Vegetation analysis and Management on this line | 10/222008
NPCC | 4Q | 2008 | Public Service Company of Colorado | NCR07203 |  | Newington to Deerfield 307 line | 345 kV | 2008-11-16 | 11/16/2008 @ 15:56 | 11.6 hrs | 11.9% | During high winds a 100-foot tall, 24-inch DBH White Pine leader of a twin leader tree 5 feet off the edge of the right-of-way (50 feet to the side of the conductor) broke 8 feet above ground and fell onto the 307 line causing the line to lock out. The location was between structures 38 and 39 just south of Cedar Road in Eliot, Maine. The 307 line is owned by Public Service Company of New Hampshire (PSNH). Investigation showed that the tree had internal decay not readily visible or identified during previous indpection. The 307 line was last inspected by Vegetation Management (VM) personnel during June of 2008 | 3 | No remedial actions required. Tree from ouside right-of-way maintenance area broke and fell into the line |  | 2009-01-14
WECC | 4Q | 2008 | Puget Sound Energy | NCR 05344 |  | BOS - SAM | 230 kV | 2008-12-24 | 12/24/2008 @ 12:01 | 12 hrs | 25.7% | Two trees, both Western Hemlock fell into the line from 41 and 38 feel off the right-of-way. Heavy snow load was the primary cause of failure | 3 | A follow-up inspection once the snow has melted will be conducted to determine if there are other threats in this area
WECC | 4Q | 2008 | Puget Sound Energy | NCR 05344 |  | CAS - WRT | 230 kV | 2008-12-13 | 12/13/2008 @ 01:42 | 42 min | 16.3% | Douglas Fir tree 80 to 90 feet tall located approximately 0' to the north of the right of way main stem snapped at approximagely 15-20 feet up due to snow load and high winds. Heavy timber area with steep terrain | 3 | No other threats were observed
WECC | 4Q | 2008 | Puget Sound Energy | NCR05344 |  | SAM - BMA | 230 kV | 2008-10-04 | 10/4/2008 @ 17:03 | 41.78 hrs | 24.4% | Black Cottownwood tree 80-90 feet tall located approximately 50' to the south of the right-of-way uprooted and fell into the line. Tree was growing in good soils and no evidence of root rot observed. High winds and wet soils were the cause in addition to leaf load adding to the sail factor for this tree | 3 | No other threats were observed
WECC | 4Q | 2008 | Puget Sound Energy | NCR05344 |  | SAM - BMA | 230 kV | 2008-12-21 | 12/21/2008 @ 00:01 | 27 hrs | 22.2% | Douglas Fir tree approximately 100 feet tall located approximately 50 feet to the east of the right-of-way uprooted under high wind and snow load | 3 | Additional Firs appear in good vigor. No other threats were observed.
WECC | 4Q | 2008 | Portland General Energy Company | NCR05325 |  | Bethel - Round Butte | 230 kV | 2008-12-22 | 12/22/2008 @ 16:40 | 431.16 hrs | 21.3% | On December 22, 2008 at 16:40:54 PT, an outage on the Bethel - Round Butte 230 kV line occurred when a 21" DBH Douglas Fir tree approxmiately 115' tall and located up a steep slope 40 feet outside of the right-of-way uprooted during heavy snowfall and landed on C phase conductor. The uprooted tree showed evidence of poor root development. The tree also had a very low live crown ratio (less than 15% of the tree had branches and then only the very top of the tree). It was a leave tree from a USFS thinning operationn conducted last year. The thinning of the surrounding trees allowed fewer trees and branches to inercept snow and wind causing this tree to become weighted with snow more than it normally would. That snow wweight on the few branches in the very upper portion of the tree coupled with poor root development and the high wind gusts caused the roots to fail allowing the tree to uproot onto the conductor. Extreme weather conditions and limited access to sections of the 100-mile transmission line prevented finding the cause as well as the fault location and subsequent removal of the uprooted tree until 1/10/2009 | 3 | On Saturday, January 10, 2009 a PGE crew cleared the tree from the conductor
WECC | 4Q | 2008 | NorthWestern Energy | NCR05282 |  | Thompson Falls to Saltese to Burke "B" | <200 kV | 2008-10-14 | 1014/2008 @ 05:28:18 | 5.99 hrs | 33.1% | Tree fell into line from just outside of the ROW
WECC | 4Q | 2008 | NorthWestern Energy | NCR05282 |  | Thompson Falls to Saltese to Burke "B" | <200 kV | 2008-11-21 | 11/21/2008 @ 01:50:53 | 8 hrs 33 min | 21.1% | Fault on Avista's side | 3 | Ongoing Vegetation Analysis and Management on this line
WECC | 4Q | 2008 | NorthWestern Energy | NCR05282 |  | Thompson Falls to Burke "A" | <200 kV | 2008-11-12 | 11/12/2008 @ 18:33:13 | 19.02 hrs | 14.8% | Trees down on Avista's side | 3 | Ongoing Vegetation Analysis and Management on this line
WECC | 4Q | 2008 | NorthWestern Energy | NCR05282 |  | Thompson Falls to Saltese to Burke "B" | <200 kV | 2008-11-12 | 11/12/2008 @ 10:53:08 | 23.48 hrs | 8.5% | Trees down on Avista's side | 3 | Ongoing Vegetation Analysis and Management on this line
WECC | 1Q | 2009 | Bonneville Power Administration | NCR05032 |  | Santiam-Alvey 1 & 2 | 230 kV | 2009-01-02 | 1/2/2009 @ 02:35 | 15.1 hrs | 12% | Single Douglas Fir from off-ROW uprooted by high winds after soil saturation | 3 | Tree was removed and area analyzed for other potentially unstable trees. None found |  | 2009-04-20
WECC | 1Q | 2009 | Bonneville Power Administration | NCR05032 |  | Chehalis - Mayfield 1 | 230 kV | 2009-03-15 | 3/15/2009@ 13:49 | 16 min | 22% | Tree blown | 3 | None necessary. Trees were off ROW and showed no evidence of defect and were not previously recorded as danger trees. Due to the associated storm caused windfall, 40 trees were marked as danger trees in the area from 1 - 700-ft AOL of 3/4 future follow-up acquisition and removal. |  | 2009-04-20 | Fall into was a result of wind, saturated soil and exposed west side from logging fringe. Will continue to wok with logging companies to minimize logging fringe.
WECC | 1Q | 2009 | NorthWestern Energy | NCR05282 |  | Thompson Falls to Saltese to Burke | <200 kV | 2009-01-05 |  | 13.7 hrs | 21.8% | Tree in line | 3 | Ongoing vegetation management on this line |  | 2009-04-20
WECC | 1Q | 2009 | NorthWestern Energy | NCR05282 |  | Thompson Falls to Saltese to Burke | <200 kV | 2009-01-07 |  | 11.01 hrs | 26% | Tree in line | 3 | Ongoing vegetation management on this line
WECC | 1Q | 2009 | Puget Sound Energy | NCR05344 |  | Bothell - Sammamish | 230 kV | 2009-03-15 | 3/15/2009 @ 15:56:00 | 10.3 hrs | 12.26% | Hemlock tree 90 to 100 fee tall fell 60' off the ROW in high winds and heavy rain. Evidence of root rot | 3 | No remedial actions taken |  | 2009-04-14
WECC | 1Q | 2009 | Puget Sound Energy | NCR05344 |  | Bothell - Sammamish | 230 kV | 2009-03-16 | 3/16/2009 @ 13:05:00 | 6.18 hrs | 17.56% | 80-ft Douglas Fir fell from 40' off ROW in heavy rain and moderate wind due to laminated root rot and saturated soils | 3 |  |  | 2009-04-14
SERC | 1Q | 2009 | Virginia Electric & Power Company | NCR01214 |  | 2035 | 230 kV | 2009-02-12 | 2/12/2009 @ 9:41:34 | 5.78 hrs |  | Line locked out when an 87-ft tall rooted 52 feet from the center of the ROW fell into the line during a wind storm. The tree was on a creek bank, and bank erosion and high winds contributed to the falling tree | 3 | An additional seven trees in close proximity to the fallen tree were removed. Four trees on the upslope of the hillside opposite the fallen tree were also removed. All 11 of the removed trees were outside the ROW. | SERC staff confirmed the facts related to this outage and determined that no additional compliance enforcement action was required
NPCC | 2Q | 2009 | Hydro-Quebec TransEnergie | NCR07112 | NPCC200900071 | L7023 | 765 kV | 2009-05-13 | 5/13/2009 @ 13:02:00 | 8 hrs |  | The line patrol found several trees on fire close to the right-of-way. An electric arc is suspected to have caused the line trip. | 1 | The fire was extinguished and the trees were cut. An investigation is underway. | NPCC has been I contact with HQ-TE and has requested a more detailed report of the event. NPCC issued violation | 2009-05-15
NPCC | 2Q | 2009 | Hydro-Quebec TransEnergie | NCR07112 | NPCC 200900072 | 3095 | 345 kV | 2009-05-21 | 5/21/2009 @ 14:28:00 | 4 hrs 39 min |  | Vegetation-related outage during strong winds | 1 | Further to the trip, a patrol found a tree with burned trunk and branches. The tree (spruce) was localized between the center and the left phase on a residential landscaped lot. The tree was cut at once. Another spruce was cut as a preventive measure as well as some broad-leave trees. |  | 2009-05-25 | The neighboring residents mentioned to have seen a ball of fire
FRCC | 2Q | 2009 | Tampa Electric Company | NCR00074 | FRCC200900178 | Fishhawk to Hampton Circuit 230403 | 230 kV | 2009-05-21 | 5/21/2009 @ 18:41:00 | 5 hrs 37 min | 20.7% | A Laurel Oak tree fell into the 230 kV line from outside the right of way. The base of this tree is 49 feet fro the outermost conductor. | 3 | Due to the heavy precipitation experienced from May 19-21, this tree became uprooted and fell. Examination revealed some root rot in the exposed rooting structure. These two factors were the major drivers for this tree failure. Tampa Electric maintains its rights-if-way 20 feet from the outermost transmission conductor, as such this tree was outside of our defined right-of-way. | The FRCC Compliance staff initiated a spot check of TEC. | 2009-05-22 | TEC self-reported a violation of FAC-003. However, the FRCC Compliance staff reviewed evidence provided by TEC and determined there was no substantial basis for finding a violation. Therefore, the violation was dismissed.
MRO | 2Q | 2009 | Nebraska Public Power District | NCR01018 | MRO200900089 | TL-3507 | 345 kV | 2009-04-04 | 4/4/2009 @ 17:58 | 16 hrs 2 min |  | Line contact with tree located inside ROW during a winter storm with high winds and ice/snow loading. | 1 | Suspect trees were cut down on 4/7/2009 | This issue is currently being processed through MRO enforcement | 2009-04-04 | Winter storm in progress with high winds and ice/snow loading. Multiple storm-related outages occurred throughout the system due to galloping
MRO | 2Q | 2009 | Manitoba Hydro | NCR01003 | None | G31V | 230 kV | 2009-04-23 | 04/23/2009 @ 02:08 | 12 hrs |  | The tree contact occurred at a river crossing. During spring 2009, Manitoba has experienced heavy flooding and snowmelt runoff conditions. High fast moving water in the Valley River caused significant erosion along the river bank. The resulting collapse of the river bank compromised the root structure of a healthy tree outside the easement, resulting in a fall which contacted the adjacent 230 kV transmission line G31V. | 3 | All other trees compromised by this erosion were removed immediately. | Category 3 vegetation outage - not a violation | 2009-04-24
SERC | 2Q | 2009 | South Carolina Electric & Gas Co. | NCR01312 | None | Jefferies-Charity | 230 kV | 2009-04-06 |  | 1 hr 14 min |  | The outage was the result of a pine tree falling into the transmission line from 25 feet off the ROW during high winds. It appears the pine tree had a large hollow at the base with signs of heart rot that was most likely caused fro years of prescribed burning. | 3 | Tree removed; additional inspections off the ROW in either direction from location of damage. Entity identified no additional risks. | SERC staff is working with SERC Vegetation Management Subcommittee to pursue methods of reducing the number of outages caused by trees fro off the ROW
SERC | 2Q | 2009 | Mississippi Power Company | NCR06050 | None | Laurel-Enterprise | 230 kV | 2009-04-10 | 4/10/2009 @ 16:45:05 | 6 hrs 5 min |  | This tree on the edge of the ROW was documented as being damaged during Hurricane Katrina in 2005. The damage caused internal decay in the first 3 feet of the tree above the ground weakened the tree allowing it to fall onto the conductor. | 3 | Entity moved a transmission line up on their annual work schedule to perform side trimming and have widened our ROW to remove the potential threat of another outage | SERC staff is working with SERC Vegetation Management Subcommittee to pursue methods of reducing the number of outages caused by trees from off the ROW
SERC | 2Q | 2009 | Entergy | NCR01234 | None | Montgomery to Winnfield | 230 kV | 2009-06-03 | 6/3/2009 @ 05:53:15 | 24 hrs 5 min |  | Outage was a result of root decay of the co-dominant stems of a 97 foot tall gum tree located 15 feet off the ROW, allowing the tree to fall during a thunderstorm moving through the area. | 3 | The line was inspected by aerial patrol. No other threats were found. | SERC staff is working with SERC Vegetation Management Subcommittee to pursue methods of reducing the number of outages caused by trees fro off the ROW
SERC | 3Q | 2009 | Georgia Transmission Corporation | NCR01249 | None | Bonaire Primary-South Macon | 230 kV | 2009-08-17 | 8/17/2009 @ ? | 1 hr 53 min |  | During an afternoon thunderstorm, a 90-foot tall Sweet Gum tree located 6 feet off the ROW broke off about 8 feet from the ground and fell into the easement. The tree made contact with the line causing an outage. The tree had no apparent defects and was splintered at the break | 3 | A contract tree crew and forester did an extensive patrol of this section of line and removed any possible danger trees that could cause future problems
SERC | 3Q | 2009 | Virginia Electric & Power Company | NCR09028 | None | 224 | 230 kV | 2009-07-26 | 7/26/2009 @ 16:21 | 28 hrs 41 min |  | A 95-foot poplar located 30 feet off the ROW was blown into the line during a strong thunderstorm. A crossarm broke off the structure, dropping a conductor onto a distribution line. | 3 | The area was patrolled for other storm damage that might threaten the line. No problems were found. |  |  | With the faulted section isolate, the line was re-energized from one end 76 minutes after the fault.
SERC | 3Q | 2009 | Entergy | NCR01234 | None | Romeville to Panama | 230 kV | 2009-09-06 | 9/6/2009 @ ? | 35 hrs 28 min |  | A 34-inch DBH 94-foot tall Water Oak fell from 30 feet off the ROW. The ground was saturated and some erosion had occurred at the base from rainy weather occurring in the days prior to the outage. | 3 | A contract tree crew and forester did an extensive patrol of this section of line and removed any possible danger trees that could cause future problems
WECC | 4Q | 2009 | NorthWestern Energy | NRC05282 | None | Thompson Falls to Saltese to Burke | <200 kV | 2009-10-09 | 10/9/2009 @ 01:17:46 | 6 hrs 22 min | 8.6% | Tree in line | 3 | Removed tree, continuing ongoing vegetation management efforts in conunction with Lolo National Forest
SERC | 4Q | 2009 | South Carolina Electric & Gas Co. | NCR00915 | None | Summerville to Wateree | 230 kV | 2009-12-19 | 12/19/2009 @ 17:30 | 15 hrs |  | A 71-foot tall Laurel Oak tree 12 inches in diameter and rooted 11 feet off the ROW fell through the line. The tree had some decay at the stump but the tree crown was healthy. The entity speculates that the tree fell due to weather-induced fatigue. | 3 | None. The tree fell through the line and it was unnecessary to cut it to restore the line.
Note on H1: Chrissy Vegso: 230 kV class 345 kV class 500 kV class 765 kV class
Note on L1: Chrissy Vegso: Line-loading (% of normal rating) of the outaged line at the time of line trip
Note on N1: Chrissy Vegso: 1 - Grow-ins; in/outside right-of-way 2 - Fall-ins inside right-of-way 3 - Fall-ins outside right-of-way Please check whether or not a Category 1 outage occurred as a result of a tree from inside or outside the right-of-way
Note on O1: Chrissy Vegso: Counter measures or corrective steps taken by TO including timeframe to prevent future outages

## 2012 (hidden)
Confidential and Non-Public |  |  |  | Confidential and Non-Public |  |  |  | Confidential and Non-Public |  |  |  | Confidential and Non-Public |  |  |  | Confidential and Non-Public |  |  |  | Confidential and Non-Public
Registered Entity Identification |  |  |  | Transmission Circuit Information | [5 empty] | Transmission Outage Description |  |  |  |  | Vegetation Description *Horizontal along the ground – measured from tree stump to a point on the ground directly below the conductor | [5 empty] | Corrective and Preventive Actions |  | Other comments
Entity Name | NCR | Function TO; GO | Region | Name of the circuit(s) affected by the vegetation contact | Has the reported circuit experienced a previous vegetation-related transmission outage within the last eight reporting quarters? | State the quarter if the reported circuit has experienced a previous vegetation-related transmission outage (enter Q/yyyy) | Nominal voltage rating of the circuit (kV) | Element of IROL or Major WECC Transfer Path? | The flow (as a % of normal rating) on the facility just prior to the outage | Outage start date (enter mm/dd/yyyy) | Outage start time | Outage Duration (enter in minutes) | Detailed description of the cause of the outage | Category associated with the Sustained Outage. 1A&B; 2A&B; 3; 4A&B | Vegetation Location Inside or outside the ROW | If the vegetation causing the outage was located outside of the ROW provide the horizontal distance to the edge of the ROW (enter in feet) | If the vegetation causing the outage was located outside of the ROW provide the horizontal distance to the nearest conductor (enter in feet) | Tree type | Tree height (enter in feet) | Tree condition | Mitigation/remediation actions taken by Registered Entity to address recurrence of the contact/encroachment. | Actions taken by Regional Entity
Georgia Transmission Corporation | NCR01249 | TO | SERC |  |  |  | 230 |  | N/A | 2012-07-06 | 18:07 | 632.2 | Green pine tree fell into line from over 10’ from edge of ROW during a summer thunderstorm. Wind was a factor in the tree’s failure, and several trees were down in the area near the easement. | Category 3 | outside | 10 |  | pine |  | green | The tree was removed from the line. TO sent a ground patrol to inspect the tree line for any other potential dangerous trees, and the crew removed several trees that were suspected as a threat. | none
South Carolina Electric & Gas Company | NCR00915 | TO | SERC |  |  |  | 230 |  | N/A | 2012-07-31 | 9:54 | 321 | A live green pine tree fell into a transmission line from 7’ off the ROW. The tree was found up-rooted. Wet ground and wind were contributing factors. | Category 3 | outside | 7 |  | pine |  | green | Tree had to be cut from the line. The area was patrolled, and one additional dead pine was removed. | none | none
South Carolina Electric & Gas Company | NCR00915 | TO | SERC |  |  |  | 230 |  | N/A | 2012-08-11 | 12:41 | 490 | One green tree, located approximately 16’ off the ROW, fell into another green tree located approximately 15’ off the ROW, which fell onto the line. | Category 3 | outside | 15 |  | pine |  | green | One tree was cut from the line; the other fell past the line. A patrol of the area found several dead trees off the ROW that were removed. | none | none
South Carolina Public Service Authority | NCR01312 | TO | SERC |  |  |  | 230 |  | N/A | 2012-09-11 | 12:50 | 143 | A live, green pine tree approximately 15" in diameter near the base and 60' tall, growing on edge of the ROW uprooted because of ground rot and windy conditions. | Category 3 | outside | edge |  | pine | 30 | green | Tree was removed from the line, and the area was inspected. Twenty-three trees that were either dead or suspected of disease were removed. | none | none
Nova Scotia Power Inc. | NCR07178 | TO | NPCC |  |  |  | 230 |  | 21 | 2012-08-07 | 15:52 | 168 | On August 7, 2012 at 15:52, 230kv transmission line L-7009 tripped; an auto-reclose was unsuccessful and the line tripped to lock-out. A fault was determined to be 19 kilometers from the substation. The area was patrolled in the area of the fault location and no cause was discovered. The line was re-energized successfully at 18:30. It was agreed that the line would undergo a complete detailed foot patrol the following day. On August 8, 2012 it was reported that a small hardwood tree was found near the fault location that showed signs of arcing to the A Phase of L7009. An NSPI investigation carried out by the Forestry Department on August 9th, determined that the tree which caused the fault on L-7009 was identified and recorded as not being a clearance threat during a field check of the site in the spring of 2011 by a forestry field inspector. The site was last foot-patrolled in 2009 by the Transmission Inspection group and tree height at that time was measured at 2.5 meters and therefore not deemed a threat. Subsequently, the 2011 sag analysis of the area identified the site as requiring field verification based on growth and line sag. As per Vegetation Management Procedure , the site was field verified and no management was recommended. | Category 1 |  |  |  | hardwood | 8 |  | Nova Scotia Power (NSP) reviewed the sag inspection process with NSP Forestry Staff and all contractors who assist with such inspections to ensure that all applicable personnel follow the proper inspection and reporting procedures. NSP Forestry Department completed a re-assessment of all sag locations identified during the 2012 sag analysis. 82 sites were re-issued for immediate field inspection and all locations were completed by August 17th. | Worked with NSPI in submitting Mitigation Plan that has been accepted by NPCC | NERC Violation ID: NPCC2012010888
PowerSouth Energy Cooperative | NCR10203 | TO | SERC |  |  |  | 230 |  | N/A | 2012-06-11 | 22:25 | 565 | A during a thunderstorm with winds exceeding 36 mph a 70 ft. tall pine tree located two feet off the right-of-way fell onto the line causing the line to lock out. The area appears to have been subjected to a fire in the last couple of years, which possibly stressed the tree. The tree showed no external signs of rot, but was rotting internally from ground level to the break point about 4 ft. above ground. Due to the difficult terrain, weather conditions, and darkness a search for the tree was not successful; and, after a consultation with the control center, it was decided to wait until daylight to continue the restoration efforts. | Category 3 | outside | 2 |  | pine | 70 | internal rot | The tree was removed. A line maintenance crew inspected the ROW in the area of the event and observed no other trees to be an immediate threat to the line. | none | none
Progress Energy Carolinas | NCR01298 | TO | SERC |  |  |  | 230 |  | N/A | 2012-04-24 | 18:55 | 1000 | As rain and wind storms with 24 kn winds passed through the area, a 67 ft. tall Loblolly Pine tree with its face front located 0.4 ft from edge of the ROW fell into the line at approximately 1/3 of span length resulting in a sustained outage. | Category 3 | outside | 0.4 |  | loblolly pine | 67 |  | The pine tree was removed from line, and spans in the area were assessed to determine if any additional trees in the area were impacted by the storms. None were found. | none | none
National Grid USA | NCR11171 | TO | NPCC |  |  |  | 230 |  | 15.38 | 2012-05-29 |  | 1293.36 | In an isolated, very steep, and rocky area of the E205W line in Readsboro, Vermont, it appeared that a microburst hit the area as multiple trees were uprooted and trunks twisted. Thunderstorms were in the area at the time of the line outage. A sugar maple fell into a birch tree which then hit the power line. The birch tree was located 15 feet outside of the right-of-way. It is approximately 62.5 feet from the conductor to the edge of the right-of-way, so the tree was located at approximately 77.5 feet from the conductor. | Category 3 | outside | 15 | 77.5 | birch |  |  | Trees in the area are being reviewed for additional storm damage and uprooting. Any trees deemed necessary for removal are being removed.
Mississippi Power Company | NCR01273 | TO | SERC |  |  |  | 230 |  | N/A | 2012-03-12 | 6:29 | 326.8 | The 70’ pine tree located 20’ off ROW had internal decay at ground line where the tree broke during a strong storm. | Category 3 | outside | 20 |  | pine | 70 | internal decay | The Right of Way will be side trimmed in 2012 and any danger trees will be cut during the side trimming process. | none | The tree did hang on the line causing it to lock out. There was no damage to the line so it was re-energized as soon as the crew cut it off the line.
Municipal Electric Authority of Georgia | NCR01278 | TO | SERC |  |  |  | 230 |  | N/A | 2012-03-04 | 14:09 | 156 | Outage caused when 80' tall green water oak tree located 3' off ROW fell into line during wind storm. The tree was completely uprooted due to high winds and rising water from weekend storms. | Category 3 | outside | 3 |  | green water oak | 80 | uprooted from weekend storms | Outage occurred while substation work was in progress preventing recloser action. There was no load lost due to the outage. The length of the outage was due to the fact the line was not really needed at the time so Entity took precaution to fly the line and also double check all the work in progress in the substation before re-energizing. | none | Tree fell past the line and did not need to be removed from the line.
NorthWestern Corporation | NCR05282 | TO | WECC |  |  |  | <200 |  |  | 2012-01-25 | 11:23 | 275 | Tree fell into line from outside of Right-Of-Way. | Category 3 | outside | [5 empty] | Quarterly Aerial Patrols to find danger trees, outside of Right-Of-Way, for removal. | WECC confirmed the outage was the result of a tree outside the transmission line right-of-way falling into lines and will monitor the entity for future vegetation caused outages.
Portland General Electric Company | NCR05325 | TO | WECC |  |  |  | 230 |  | 13.7 | 2012-03-29 | 15:13 | 358 | High winds (gusts over 35 mph) caused the 20' top of a 75' fir tree to break free and contact C-phase of the transmission Line. The tree top showed no decay, but remaining trees in stand showed evidence of a significant wind event. The tree was located 9' outside of the ROW. | Category 3 | outside | 9 |  | fir | 75 | wind damage | The stand was surveyed and all remaining trees appear healthy and are not endangering the line. | WECC confirmed the outage was the result of a tree outside the transmission line right-of-way falling into lines due to severe weather and will monitor the entity for future vegetation caused outages.
Puget Sound Energy Inc. | NCR05344 | TO | WECC |  |  |  | 230 |  | 9.5 | 2012-01-25 | 0:07 | 87 | A 15' foot long fir limb broke off a very large, mature fir tree. Branch showed burn marks. Tree is well off the ROW. The branch appeared to sail east in high winds and likely cross-phased the Transmission Line.. | Category 3 | outside |  |  | fir |  | large, mature | None needed. | WECC confirmed the outage was the result of a broken tree limb outside the transmission line right-of-way falling into lines and will monitor the entity for future vegetation caused outages.
Puget Sound Energy Inc. | NCR05344 | TO | WECC |  |  |  | 230 |  | 24 | 2012-02-06 | 18:35 | 1254 | A fir tree with two tops was located outside the ROW on the south side of the Transmission Line. One of the tops broke out 23 feet up the tree and fell north, hanging up in the southernmost phase of the line. Tree crew removed the tree top that fell on the Transmission Line as well as the remainder of the tree outside of the ROW. Several other trees (not imminent threats) were also removed in same area due to storm damage. | Category 3 | outside |  |  | fir |  |  | None needed. | WECC confirmed the outage was the results of a tree outside the transmission line right-of-way falling into lines due to severe weather and will monitor the entity for future vegetation caused outages.
Pacific Gas and Electric | NCR05299 | TO | WECC |  |  |  | 230 |  |  | 2012-03-16 | 0:19 | 961 | A healthy 106-foot-tall, 25-inch-DBH white fire uprooted during a winter storm with strong winds. The tree was 74 feet from the outer phase of the 230kv line, and it was off the right-of-way. | Category 3 | outside | 74 |  | white fir | 106 | healthy | PG&E annually inspects off-ROW trees for health and defects as part of its routine vegetation management program. In addition, trees in the vicinity of a tree failure are inspected for health and defects during the outage investigation. No remedial action was required in this case. | WECC confirmed the outage was the results of a tree outside the transmission line right-of-way falling into lines due to severe weather and will monitor the entity for future vegetation caused outages.
Pacific Gas and Electric | NCR05299 | TO | WECC |  |  |  | <200 |  |  | 2012-03-06 | 23:49 | 821 | The trunk of a healthy 106-foot-tall, 24-inch-DBH lodgepole pine broke at 21 feet above ground level during a winter storm with strong winds. The tree was 47 feet from the outer phase of the 115kv pole line and 21 feet off the right-of-way. | Category 3 | outside | 47 |  | lodgepole pine | 106 | healthy | PG&E annually inspects off-ROW trees for health and defects as part of its routine vegetation management program. In addition, trees in the vicinity of a tree failure are inspected for health and defecdts during the outage investigation. No remedial action was required in this case. | WECC confirmed the outage was the results of a tree outside the transmission line right-of-way falling into lines due to severe weather and will monitor the entity for future vegetation caused outages.
Public Service New Hampshire |  | TO | NPCC |  |  |  | 345 |  |  | 2012-02-25 |  | 361 | During a high wind event, a healthy approximately 95 feet tall, 14 inch DBH, White Pine located 22 feet outside the northern maintained edge of ROW, broke near its base and fell across the 3144 distribution line and made contact with the closest phase of the 326 transmission line. The base of the tree was 78 feet from the closest phase of the 326 line. The tree was located on the north side of the ROW in a slightly uphill orientation. | Category 3 | outside | 22 |  | white pine | 95 | healthy | Aerial patrols performed on the Lawrence Road to Scobie Pond section on February 27, 2012