## EI
Initial Start Time
(From Fnet)
UTC Initial t0
Event ID (From UTC Initial t0) | Local Date / Time (MM/DD/YY HH:MM:SS) | Day | Time Zone | Date / Time (MM/DD/YY HH:MM:SS) | NERC Confirmed MW Loss | A Value Hz | B Value Hz | Point C Hz | B-A Delta Hz | C-A Delta Hz | A to B IFRM | A to C IFRM | FWG Sel. M-4 | FWG Sel. BAL-003 | 1st Step UFLS Hz | C - UFLS Margin Hz | Oper Year (Local)
EI_2011-12-02_090007 | 2011-12-02 04:00 | 2011-12-02 04:00 | EST | 2011-12-02 09:00 | 0 | 59.9887 | 60.0216 | 60.02 | 0.03297 | 0.031333 |  |  | No | No | 59.5 | 0.52 | 2012
EI_2011-12-05_041530 | 2011-12-04 23:16 | 2011-12-04 23:16 | EST | 2011-12-05 04:16 | 0 | 59.9855 | 59.9379 | 59.943 | -0.047618 | -0.0425 |  |  | No | Yes | 59.5 | 0.443 | 2012
EI_2011-12-07_131600 | 2011-12-07 08:16 | 2011-12-07 08:16 | EST | 2011-12-07 13:16 | 0 | 60.0018 | 59.9546 | 59.959 | -0.047162 | -0.04275 |  |  | No | Yes | 59.5 | 0.459 | 2012
EI_2011-12-09_083804 | 2011-12-09 03:38 | 2011-12-09 03:38 | EST | 2011-12-09 08:38 | 0 | 59.9989 | 59.9658 | 59.963 | -0.03311 | -0.035875 |  |  | No | No | 59.5 | 0.463 | 2012
EI_2011-12-13_204940 | 2011-12-13 15:50 | 2011-12-13 15:50 | EST | 2011-12-13 20:50 | 0 | 59.966 | 59.9339 | 59.927 | -0.032059 | -0.039 |  |  | No | No | 59.5 | 0.427 | 2012
EI_2011-12-14_201042 | 2011-12-14 15:11 | 2011-12-14 15:11 | EST | 2011-12-14 20:11 | 0 | 60.0141 | 59.9678 | 59.975 | -0.046301 | -0.039125 |  |  | No | No | 59.5 | 0.475 | 2012
EI_2011-12-15_142606 | 2011-12-15 09:26 | 2011-12-15 09:26 | EST | 2011-12-15 14:26 | 0 | 60.0071 | 59.9667 | 59.982 | -0.040419 | -0.025125 |  |  | No | No | 59.5 | 0.482 | 2012
EI_2011-12-15_193216 | 2011-12-15 14:32 | 2011-12-15 14:32 | EST | 2011-12-15 19:32 | 1105 | 60.0074 | 59.9558 | 59.957 | -0.05161 | -0.050375 | -2141.0457 | -2193.5486 | Yes | Yes | 59.5 | 0.457 | 2012
EI_2011-12-16_095023 | 2011-12-16 04:50 | 2011-12-16 04:50 | EST | 2011-12-16 09:50 | 0 | 59.9671 | 60.019 | 59.957 | 0.051903 | -0.010067 |  |  | No | No | 59.5 | 0.457 | 2012
EI_2011-12-19_204854 | 2011-12-19 15:49 | 2011-12-19 15:49 | EST | 2011-12-19 20:49 | 0 | 59.998 | 59.973 | 59.973 | -0.025 | -0.025 |  |  | No | No | 59.5 | 0.473 | 2012
EI_2011-12-21_142354 | 2011-12-21 09:24 | 2011-12-21 09:24 | EST | 2011-12-21 14:24 | 0 | 59.9712 | 59.9314 | 59.935 | -0.039838 | -0.03625 |  |  | No | Yes | 59.5 | 0.435 | 2012
EI_2011-12-23_121012 | 2011-12-23 07:10 | 2011-12-23 07:10 | EST | 2011-12-23 12:10 | 0 | 59.9869 | 59.96 | 59.948 | -0.026875 | -0.038875 |  |  | No | No | 59.5 | 0.448 | 2012
EI_2011-12-24_111758 | 2011-12-24 06:18 | 2011-12-24 06:18 | EST | 2011-12-24 11:18 | 0 | 60.0086 | 59.9701 | 59.975 | -0.038566 | -0.033625 |  |  | No | No | 59.5 | 0.475 | 2012
EI_2012-01-03_164800 | 2012-01-03 11:48 | 2012-01-03 11:48 | EST | 2012-01-03 16:48 | 1200 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.5 | -59.5 | 2012
EI_2012-01-09_010552 | 2012-01-08 20:06 | 2012-01-08 20:06 | EST | 2012-01-09 01:06 | 0 | 59.9593 | 59.9869 | 59.994 | 0.027566 | 0.034687 |  |  | No | No | 59.5 | 0.494 | 2012
EI_2012-01-13_200257 | 2012-01-13 15:03 | 2012-01-13 15:03 | EST | 2012-01-13 20:03 | 0 | 59.9849 | 59.9488 | 59.942 | -0.03615 | -0.042938 |  |  | No | Yes | 59.5 | 0.442 | 2012
EI_2012-01-21_062641 | 2012-01-21 01:27 | 2012-01-21 01:27 | EST | 2012-01-21 06:27 | 0 | 60.0037 | 59.9639 | 59.965 | -0.039811 | -0.03875 |  |  | No | No | 59.5 | 0.465 | 2012
EI_2012-01-30_160157 | 2012-01-30 11:02 | 2012-01-30 11:02 | EST | 2012-01-30 16:02 | 1152 | 59.9826 | 59.9292 | 59.944 | -0.05332 | -0.038562 | -2160.5371 | -2987.3582 | Yes | Yes | 59.5 | 0.444 | 2012
EI_2012-02-05_233950 | 2012-02-05 18:40 | 2012-02-05 18:40 | EST | 2012-02-05 23:40 | 0 | 60.0517 | 59.9979 | 59.997 | -0.053778 | -0.054688 |  |  | No | No | 59.5 | 0.497 | 2012
EI_2012-02-06_001416 | 2012-02-05 19:14 | 2012-02-05 19:14 | EST | 2012-02-06 00:14 | 0 | 60.0046 | 60.0224 | 60.045 | 0.017799 | 0.040375 |  |  | No | No | 59.5 | 0.545 | 2012
EI_2012-02-06_003713 | 2012-02-05 19:37 | 2012-02-05 19:37 | EST | 2012-02-06 00:37 | 0 | 59.9974 | 59.956 | 59.958 | -0.041407 | -0.039437 |  |  | No | No | 59.5 | 0.458 | 2012
EI_2012-02-06_011042 | 2012-02-05 20:11 | 2012-02-05 20:11 | EST | 2012-02-06 01:11 | 0 | 60.0356 | 60.0567 | 60.076 | 0.021102 | 0.040375 |  |  | No | No | 59.5 | 0.576 | 2012
EI_2012-02-06_011516 | 2012-02-05 20:15 | 2012-02-05 20:15 | EST | 2012-02-06 01:15 | 0 | 60.0234 | 59.9975 | 59.986 | -0.02586 | -0.037375 |  |  | No | No | 59.5 | 0.486 | 2012
EI_2012-03-01_072600 | 2012-03-01 02:26 | 2012-03-01 02:26 | EST | 2012-03-01 07:26 | 1260 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.5 | -59.5 | 2012
EI_2012-03-02_195319 | 2012-03-02 14:53 | 2012-03-02 14:53 | EST | 2012-03-02 19:53 | 1300 | 60.0042 | 59.9399 | 60 | -0.064371 | -0.00425 | -2019.5363 | -30588.2353 | No | Yes | 59.5 | 0.5 | 2012
EI_2012-03-15_191447 | 2012-03-15 15:15 | 2012-03-15 15:15 | EDT | 2012-03-15 19:15 | 1200 | 60.0156 | 59.9499 | 59.963 | -0.065684 | -0.052563 | -1826.9369 | -2282.9964 | No | No | 59.5 | 0.463 | 2012
EI_2012-03-23_182826 | 2012-03-23 14:28 | 2012-03-23 14:28 | EDT | 2012-03-23 18:28 | 1228 | 60.0038 | 59.9473 | 59.945 | -0.056479 | -0.058813 | -2174.253 | -2087.9915 | Yes | Yes | 59.5 | 0.445 | 2012
EI_2012-03-31_173903 | 2012-03-31 13:39 | 2012-03-31 13:39 | EDT | 2012-03-31 17:39 | 1000 | 60.0015 | 59.9625 | 59.963 | -0.039015 | -0.0385 | -2563.1068 | -2597.4026 | No | No | 59.5 | 0.463 | 2012
EI_2012-04-01_040019 | 2012-04-01 | 2012-04-01 | EDT | 2012-04-01 04:00 | 1000 | 60.0092 | 59.9516 | 59.97 | -0.057612 | -0.039188 | -1735.7573 | -2551.8341 | No | No | 59.5 | 0.47 | 2012
EI_2012-04-05_000315 | 2012-04-04 20:03 | 2012-04-04 20:03 | EDT | 2012-04-05 00:03 | 1129 | 60.0089 | 59.9437 | 59.95 | -0.065241 | -0.058937 | -1730.5193 | -1915.5885 | No | No | 59.5 | 0.45 | 2012
EI_2012-04-14_174650 | 2012-04-14 13:47 | 2012-04-14 13:47 | EDT | 2012-04-14 17:47 | 1800 | 60.0111 | 59.9404 | 59.937 | -0.070669 | -0.074063 | -2547.1015 | -2430.3797 | Yes | Yes | 59.5 | 0.437 | 2012
EI_2012-04-16_111710 | 2012-04-16 07:17 | 2012-04-16 07:17 | EDT | 2012-04-16 11:17 | 1040 | 59.9731 | 59.9326 | 59.935 | -0.040489 | -0.038125 | -2568.6219 | -2727.8689 | No | No | 59.5 | 0.435 | 2012
EI_2012-04-27_121933 | 2012-04-27 08:20 | 2012-04-27 08:20 | EDT | 2012-04-27 12:20 |  | 60.0274 | 59.9712 | 59.987 | -0.056193 | -0.040375 |  |  | No | No | 59.5 | 0.487 | 2012
EI_2012-04-30_140241 | 2012-04-30 10:03 | 2012-04-30 10:03 | EDT | 2012-04-30 14:03 | 1237 | 59.9973 | 59.9392 | 59.939 | -0.058038 | -0.05825 | -2131.3667 | -2123.6052 | Yes | Yes | 59.5 | 0.439 | 2012
EI_2012-05-01_032727 | 2012-04-30 23:27 | 2012-04-30 23:27 | EDT | 2012-05-01 03:27 |  | 60.0233 | 59.9757 | 59.975 | -0.047616 | -0.048313 |  |  | No | No | 59.5 | 0.475 | 2012
EI_2012-05-04_173404 | 2012-05-04 13:34 | 2012-05-04 13:34 | EDT | 2012-05-04 17:34 | 1300 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.5 | -59.5 | 2012
EI_2012-05-12_192956 | 2012-05-12 15:30 | 2012-05-12 15:30 | EDT | 2012-05-12 19:30 | 1547 | 60.0217 | 59.9483 | 59.947 | -0.073417 | -0.07475 | -2107.151 | -2069.5652 | No | No | 59.5 | 0.447 | 2012
EI_2012-05-14_032145 | 2012-05-13 23:22 | 2012-05-13 23:22 | EDT | 2012-05-14 03:22 | 1123 | 60.0281 | 59.9464 | 59.957 | -0.081731 | -0.071125 | -1374.0186 | -1578.9104 | No | No | 59.5 | 0.457 | 2012
EI_2012-05-14_162043 | 2012-05-14 12:21 | 2012-05-14 12:21 | EDT | 2012-05-14 16:21 |  | 59.9898 | 59.9529 | 59.952 | -0.036811 | -0.03775 |  |  | No | No | 59.5 | 0.452 | 2012
EI_2012-05-18_044520 | 2012-05-18 00:45 | 2012-05-18 00:45 | EDT | 2012-05-18 04:45 |  | 60.0125 | 59.9699 | 59.972 | -0.042561 | -0.0405 |  |  | No | No | 59.5 | 0.472 | 2012
EI_2012-05-21_195215 | 2012-05-21 15:52 | 2012-05-21 15:52 | EDT | 2012-05-21 19:52 |  | 59.9968 | 59.9524 | 59.95 | -0.044419 | -0.046812 |  |  | No | No | 59.5 | 0.45 | 2012
EI_2012-06-02_233541 | 2012-06-02 19:36 | 2012-06-02 19:36 | EDT | 2012-06-02 23:36 | 0 | 60.0209 | 59.9598 | 59.971 | -0.061117 | -0.049875 |  |  | No | No | 59.5 | 0.471 | 2012
EI_2012-06-26_175002 | 2012-06-26 13:50 | 2012-06-26 13:50 | EDT | 2012-06-26 17:50 | 1320 | 60.0018 | 59.9383 | 59.942 | -0.063417 | -0.05975 | -2081.4717 | -2209.205 | Yes | Yes | 59.5 | 0.442 | 2012
EI_2012-06-29_224723 | 2012-06-29 18:47 | 2012-06-29 18:47 | EDT | 2012-06-29 22:47 | 1995 | 60.0199 | 59.969 | 59.974 | -0.050875 | -0.045875 | -3921.3759 | -4348.7738 | No | No | 59.5 | 0.474 | 2012
EI_2012-07-02_025225 | 2012-07-01 22:52 | 2012-07-01 22:52 | EDT | 2012-07-02 02:52 | 1200 | 60.0104 | 59.9559 | 59.958 | -0.054528 | -0.052438 | -2200.6877 | -2288.4386 | Yes | Yes | 59.5 | 0.458 | 2012
EI_2012-07-12_062105 | 2012-07-12 02:21 | 2012-07-12 02:21 | EDT | 2012-07-12 06:21 | 1194 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.5 | -59.5 | 2012
EI_2012-07-18_122000 | 2012-07-18 08:20 | 2012-07-18 08:20 | EDT | 2012-07-18 12:20 | 1050 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.5 | -59.5 | 2012
EI_2012-07-19_135131 | 2012-07-19 09:52 | 2012-07-19 09:52 | EDT | 2012-07-19 13:52 | 0 | 60.0199 | 59.9669 | 59.974 | -0.052998 | -0.045938 |  |  | No | No | 59.5 | 0.474 | 2012
EI_2012-08-03_124122 | 2012-08-03 08:41 | 2012-08-03 08:41 | EDT | 2012-08-03 12:41 | 1186 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.5 | -59.5 | 2012
EI_2012-08-05_191448 | 2012-08-05 15:15 | 2012-08-05 15:15 | EDT | 2012-08-05 19:15 | 1175 | 60.0192 | 59.9729 | 59.972 | -0.046248 | -0.047187 | -2540.6446 | -2490.0662 | No | No | 59.5 | 0.472 | 2012
EI_2012-08-16_232649 | 2012-08-16 19:27 | 2012-08-16 19:27 | EDT | 2012-08-16 23:27 | 1150 | 60.0044 | 59.9647 | 59.964 | -0.03971 | -0.040438 | -2895.9794 | -2843.8949 | No | No | 59.5 | 0.464 | 2012
EI_2012-08-28_073034 | 2012-08-28 03:31 | 2012-08-28 03:31 | EDT | 2012-08-28 07:31 | 1150 | 59.9983 | 59.95 | 59.954 | -0.048343 | -0.044312 | -2378.8443 | -2595.2045 | Yes | Yes | 59.5 | 0.454 | 2012
EI_2012-09-08_080814 | 2012-09-08 04:08 | 2012-09-08 04:08 | EDT | 2012-09-08 08:08 | 0 | 60.0101 | 59.9449 | 59.951 | -0.065153 | -0.059062 |  |  | No | No | 59.5 | 0.451 | 2012
EI_2012-09-09_145954 | 2012-09-09 11:00 | 2012-09-09 11:00 | EDT | 2012-09-09 15:00 | 0 | 59.9923 | 59.9505 | 59.952 | -0.041828 | -0.040312 |  |  | No | Yes | 59.5 | 0.452 | 2012
EI_2012-09-15_002520 | 2012-09-14 20:25 | 2012-09-14 20:25 | EDT | 2012-09-15 00:25 | 1061 | 60.0119 | 59.9638 | 59.97 | -0.048087 | -0.041875 | -2206.412 | -2533.7313 | No | No | 59.5 | 0.47 | 2012
EI_2012-09-15_055418 | 2012-09-15 01:54 | 2012-09-15 01:54 | EDT | 2012-09-15 05:54 | 0 | 60.0037 | 59.95 | 59.957 | -0.05378 | -0.04675 |  |  | No | Yes | 59.5 | 0.457 | 2012
EI_2012-09-18_192050 | 2012-09-18 15:21 | 2012-09-18 15:21 | EDT | 2012-09-18 19:21 | 0 | 60.0228 | 59.9715 | 59.978 | -0.051358 | -0.044812 |  |  | No | No | 59.5 | 0.478 | 2012
EI_2012-09-20_140512 | 2012-09-20 10:05 | 2012-09-20 10:05 | EDT | 2012-09-20 14:05 | 1210 | 60.0051 | 59.9697 | 59.961 | -0.035458 | -0.044125 | -3412.4559 | -2742.2096 | No | No | 59.5 | 0.461 | 2012
EI_2012-09-22_193805 | 2012-09-22 15:38 | 2012-09-22 15:38 | EDT | 2012-09-22 19:38 | 0 | 59.9986 | 59.9577 | 59.954 | -0.040866 | -0.044562 |  |  | No | Yes | 59.5 | 0.454 | 2012
EI_2012-09-23_043008 | 2012-09-23 00:30 | 2012-09-23 00:30 | EDT | 2012-09-23 04:30 | 0 | 60.0092 | 59.9447 | 59.958 | -0.06452 | -0.051175 |  |  | No | No | 59.5 | 0.458 | 2012
EI_2012-09-28_211100 | 2012-09-28 17:11 | 2012-09-28 17:11 | EDT | 2012-09-28 21:11 | 1170 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.5 | -59.5 | 2012
EI_2012-10-02_161152 | 2012-10-02 12:12 | 2012-10-02 12:12 | EDT | 2012-10-02 16:12 | 0 | 59.9868 | 59.9527 | 59.952 | -0.034146 | -0.034813 |  |  | No | No | 59.5 | 0.452 | 2012
EI_2012-10-04_113646 | 2012-10-04 07:37 | 2012-10-04 07:37 | EDT | 2012-10-04 11:37 | 0 | 60.0057 | 59.9631 | 59.963 | -0.042659 | -0.04275 |  |  | No | No | 59.5 | 0.463 | 2012
EI_2012-10-07_064309 | 2012-10-07 02:43 | 2012-10-07 02:43 | EDT | 2012-10-07 06:43 | 0 | 60.032 | 59.9791 | 59.991 | -0.052909 | -0.041 |  |  | No | No | 59.5 | 0.491 | 2012
EI_2012-10-07_094647 | 2012-10-07 05:47 | 2012-10-07 05:47 | EDT | 2012-10-07 09:47 | 0 | 60.0228 | 59.9869 | 59.985 | -0.035873 | -0.037813 |  |  | No | No | 59.5 | 0.485 | 2012
EI_2012-10-11_090159 | 2012-10-11 05:02 | 2012-10-11 05:02 | EDT | 2012-10-11 09:02 | 0 | 59.9521 | 59.9985 | 59.982 | 0.046453 | 0.029938 |  |  | No | No | 59.5 | 0.482 | 2012
EI_2012-10-17_070800 | 2012-10-17 03:08 | 2012-10-17 03:08 | EDT | 2012-10-17 07:08 | 1500 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.5 | -59.5 | 2012
EI_2012-10-17_182522 | 2012-10-17 14:25 | 2012-10-17 14:25 | EDT | 2012-10-17 18:25 | 720 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.5 | -59.5 | 2012
EI_2012-10-19_183612 | 2012-10-19 14:36 | 2012-10-19 14:36 | EDT | 2012-10-19 18:36 | 0 | 59.9933 | 59.9565 | 59.955 | -0.036797 | -0.038313 |  |  | No | No | 59.5 | 0.455 | 2012
EI_2012-10-23_222807 | 2012-10-23 18:28 | 2012-10-23 18:28 | EDT | 2012-10-23 22:28 | 1234 | 60 | 59.9557 | 59.946 | -0.044333 | -0.054 | -2783.4586 | -2285.1852 | Yes | Yes | 59.5 | 0.446 | 2012
EI_2012-10-24_054717 | 2012-10-24 01:47 | 2012-10-24 01:47 | EDT | 2012-10-24 05:47 | 0 | 60.0104 | 59.9462 | 59.958 | -0.064195 | -0.052438 |  |  | No | No | 59.5 | 0.458 | 2012
EI_2012-10-29_091955 | 2012-10-29 05:20 | 2012-10-29 05:20 | EDT | 2012-10-29 09:20 | 0 | 60.0061 | 60.0435 | 60.041 | 0.03742 | 0.034875 |  |  | No | No | 59.5 | 0.541 | 2012
EI_2012-10-30_010040 | 2012-10-29 21:01 | 2012-10-29 21:01 | EDT | 2012-10-30 01:01 | 0 | 60.0111 | 59.9742 | 59.979 | -0.036881 | -0.032063 |  |  | No | No | 59.5 | 0.479 | 2012
EI_2012-10-30_024110 | 2012-10-29 22:41 | 2012-10-29 22:41 | EDT | 2012-10-30 02:41 | 0 | 60.0283 | 59.9573 | 59.974 | -0.071009 | -0.054313 |  |  | No | No | 59.5 | 0.474 | 2012
EI_2012-10-30_050928 | 2012-10-30 01:09 | 2012-10-30 01:09 | EDT | 2012-10-30 05:09 | 0 | 60.0156 | 59.9462 | 59.96 | -0.06932 | -0.055563 |  |  | No | Yes | 59.5 | 0.46 | 2012
EI_2012-10-30_100814 | 2012-10-30 06:08 | 2012-10-30 06:08 | EDT | 2012-10-30 10:08 | 0 | 59.9921 | 59.9515 | 59.955 | -0.040517 | -0.037063 |  |  | No | No | 59.5 | 0.455 | 2012
EI_2012-11-05_105555 | 2012-11-05 05:56 | 2012-11-05 05:56 | EST | 2012-11-05 10:56 | 0 | 59.9909 | 59.9508 | 59.959 | -0.040117 | -0.031875 |  |  | No | No | 59.5 | 0.459 | 2012
EI_2012-11-09_061752 | 2012-11-09 01:18 | 2012-11-09 01:18 | EST | 2012-11-09 06:18 | 1165 | 60.0002 | 59.9492 | 59.958 | -0.051006 | -0.042188 | -2284.0593 | -2761.4815 | Yes | Yes | 59.5 | 0.458 | 2012
EI_2012-11-11_085431 | 2012-11-11 03:55 | 2012-11-11 03:55 | EST | 2012-11-11 08:55 | 0 | 60.003 | 59.9558 | 59.961 | -0.047242 | -0.042 |  |  | No | Yes | 59.5 | 0.461 | 2012
EI_2012-11-12_163246 | 2012-11-12 11:33 | 2012-11-12 11:33 | EST | 2012-11-12 16:33 | 0 | 60.0194 | 59.9762 | 59.982 | -0.043223 | -0.037375 |  |  | No | No | 59.5 | 0.482 | 2012
EI_2012-11-13_091045 | 2012-11-13 04:11 | 2012-11-13 04:11 | EST | 2012-11-13 09:11 | 0 | 59.9833 | 59.9472 | 59.949 | -0.036161 | -0.034312 |  |  | No | No | 59.5 | 0.449 | 2012
EI_2012-11-18_095910 | 2012-11-18 04:59 | 2012-11-18 04:59 | EST | 2012-11-18 09:59 | 0 | 59.9711 | 60.021 | 60.007 | 0.049937 | 0.035937 |  |  | No | No | 59.5 | 0.507 | 2012
EI_2012-11-19_190007 | 2012-11-19 14:00 | 2012-11-19 14:00 | EST | 2012-11-19 19:00 | 0 | 59.9883 | 59.9545 | 59.96 | -0.033765 | -0.02825 |  |  | No | No | 59.5 | 0.46 | 2012
EI_2012-11-24_195807 | 2012-11-24 14:58 | 2012-11-24 14:58 | EST | 2012-11-24 19:58 | 0 | 59.9848 | 59.9578 | 59.951 | -0.026964 | -0.033812 |  |  | No | No | 59.5 | 0.451 | 2012
EI_2012-11-25_163029 | 2012-11-25 11:30 | 2012-11-25 11:30 | EST | 2012-11-25 16:30 | 0 | 60.0183 | 59.9525 | 59.962 | -0.065735 | -0.05625 |  |  | No | No | 59.5 | 0.462 | 2012
EI_2012-11-26_204029 | 2012-11-26 15:40 | 2012-11-26 15:40 | EST | 2012-11-26 20:40 | 0 | 59.9943 | 59.9533 | 59.956 | -0.04104 | -0.038312 |  |  | No | No | 59.5 | 0.456 | 2012
EI_2012-12-01_093207 | 2012-12-01 04:32 | 2012-12-01 04:32 | EST | 2012-12-01 09:32 | 0 | 60.0181 | 59.9774 | 59.983 | -0.040638 | -0.035063 |  |  | No | No | 59.5 | 0.483 | 2013
EI_2012-12-02_103958 | 2012-12-02 05:40 | 2012-12-02 05:40 | EST | 2012-12-02 10:40 | 0 | 60.0219 | 60.0542 | 60.059 | 0.032305 | 0.037062 |  |  | No | No | 59.5 | 0.559 | 2013
EI_2012-12-02_111508 | 2012-12-02 06:15 | 2012-12-02 06:15 | EST | 2012-12-02 11:15 | 0 | 59.9896 | 60.0403 | 60.026 | 0.05071 | 0.036438 |  |  | No | No | 59.5 | 0.526 | 2013
EI_2012-12-04_062940 | 2012-12-04 01:30 | 2012-12-04 01:30 | EST | 2012-12-04 06:30 | 0 | 60.0034 | 59.9617 | 59.971 | -0.041648 | -0.032375 |  |  | No | No | 59.5 | 0.471 | 2013
EI_2012-12-06_183919 | 2012-12-06 13:39 | 2012-12-06 13:39 | EST | 2012-12-06 18:39 | 0 | 60.0201 | 59.9787 | 59.985 | -0.041396 | -0.035063 |  |  | No | No | 59.5 | 0.485 | 2013
EI_2012-12-07_105836 | 2012-12-07 05:59 | 2012-12-07 05:59 | EST | 2012-12-07 10:59 | 0 | 60.031 | 59.9873 | 59.998 | -0.043697 | -0.033 |  |  | No | No | 59.5 | 0.498 | 2013
EI_2012-12-16_060312 | 2012-12-16 01:03 | 2012-12-16 01:03 | EST | 2012-12-16 06:03 | 0 | 59.9845 | 59.9606 | 59.954 | -0.023864 | -0.0305 |  |  | No | No | 59.5 | 0.454 | 2013
EI_2012-12-16_065724 | 2012-12-16 01:57 | 2012-12-16 01:57 | EST | 2012-12-16 06:57 | 1300 | 60.0318 | 59.9606 | 59.976 | -0.071174 | -0.05575 | -1826.5035 | -2331.8386 | No | No | 59.5 | 0.476 | 2013
EI_2012-12-16_205959 | 2012-12-16 16:00 | 2012-12-16 16:00 | EST | 2012-12-16 21:00 | 0 | 59.9892 | 60.0288 | 60.022 | 0.039661 | 0.032812 |  |  | No | No | 59.5 | 0.522 | 2013
EI_2012-12-21_054926 | 2012-12-21 00:49 | 2012-12-21 00:49 | EST | 2012-12-21 05:49 | 1330 | 60.011 | 59.9548 | 59.9573 | -0.056189 | -0.053739 | -2367.0048 | -2474.9109 | No | No | 59.5 | 0.4573 | 2013
EI_2012-12-21_102734 | 2012-12-21 05:28 | 2012-12-21 05:28 | EST | 2012-12-21 10:28 | 1239 | 59.9897 | 59.9458 | 59.9527 | -0.043865 | -0.036967 | -2824.5497 | -3351.6344 | No | No | 59.5 | 0.4527 | 2013
EI_2012-12-22_175209 | 2012-12-22 12:52 | 2012-12-22 12:52 | EST | 2012-12-22 17:52 | 1135 | 60.0115 | 59.9561 | 59.968 | -0.055409 | -0.0435 | -2048.4003 | -2609.1954 | No | No | 59.5 | 0.468 | 2013
EI_2012-12-28_132112 | 2012-12-28 08:21 | 2012-12-28 08:21 | EST | 2012-12-28 13:21 | 1125 | 60.0135 | 59.9608 | 59.97 | -0.052652 | -0.0435 | -2136.6906 | -2586.2069 | No | No | 59.5 | 0.47 | 2013
EI_2012-12-29_061816 | 2012-12-29 01:18 | 2012-12-29 01:18 | EST | 2012-12-29 06:18 | 1300 | 60.0003 | 59.9337 | 59.942 | -0.066585 | -0.058312 | -1952.385 | -2229.3676 | Yes | Yes | 59.5 | 0.442 | 2013
EI_2013-01-04_095906 | 2013-01-04 04:59 | 2013-01-04 04:59 | EST | 2013-01-04 09:59 | 0 | 60.0143 | 60.0571 | 60.049 | 0.042778 | 0.034687 |  |  | No | No | 59.5 | 0.549 | 2013
EI_2013-01-05_053700 | 2013-01-05 00:37 | 2013-01-05 00:37 | EST | 2013-01-05 05:37 | 1360 | 60.001 | 59.9407 | 59.946 | -0.060312 | -0.054994 | -2254.9484 | -2472.9816 | Yes | Yes | 59.5 | 0.446 | 2013
EI_2013-01-06_092505 | 2013-01-06 04:25 | 2013-01-06 04:25 | EST | 2013-01-06 09:25 | 619 | 59.99 | 59.9496 | 59.955 | -0.040364 | -0.035 | -1533.5586 | -1768.5714 | No | No | 59.5 | 0.455 | 2013
EI_2013-01-13_002358 | 2013-01-12 19:24 | 2013-01-12 19:24 | EST | 2013-01-13 00:24 | 0 | 59.9721 | 59.9262 | 59.934 | -0.04582 | -0.038063 |  |  | No | No | 59.5 | 0.434 | 2013
EI_2013-01-13_193108 | 2013-01-13 14:31 | 2013-01-13 14:31 | EST | 2013-01-13 19:31 | 0 | 60.008 | 59.9729 | 59.967 | -0.035061 | -0.041 |  |  | No | No | 59.5 | 0.467 | 2013
EI_2013-01-15_000504 | 2013-01-14 19:05 | 2013-01-14 19:05 | EST | 2013-01-15 00:05 | 1360 | 59.9865 | 59.9274 | 59.928 | -0.059076 | -0.0585 | -2302.1288 | -2324.7863 | No | No | 59.5 | 0.428 | 2013
EI_2013-01-20_104649 | 2013-01-20 05:47 | 2013-01-20 05:47 | EST | 2013-01-20 10:47 | 0 | 59.9893 | 59.9612 | 59.958 | -0.028131 | -0.031312 |  |  | No | No | 59.5 | 0.458 | 2013
EI_2013-01-21_055248 | 2013-01-21 00:53 | 2013-01-21 00:53 | EST | 2013-01-21 05:53 | 0 | 60.0171 | 59.9707 | 59.983 | -0.046398 | -0.034125 |  |  | No | No | 59.5 | 0.483 | 2013
EI_2013-01-21_150001 | 2013-01-21 10:00 | 2013-01-21 10:00 | EST | 2013-01-21 15:00 | 0 | 59.9934 | 59.9434 | 59.954 | -0.049981 | -0.039375 |  |  | No | No | 59.5 | 0.454 | 2013
EI_2013-01-21_215259 | 2013-01-21 16:53 | 2013-01-21 16:53 | EST | 2013-01-21 21:53 | 0 | 60.0211 | 59.9656 | 59.976 | -0.055549 | -0.045125 |  |  | No | No | 59.5 | 0.476 | 2013
EI_2013-01-22_083259 | 2013-01-22 03:33 | 2013-01-22 03:33 | EST | 2013-01-22 08:33 | 1276 | 60 | 59.9418 | 59.949 | -0.058182 | -0.051 | -2193.125 | -2501.9608 | Yes | Yes | 59.5 | 0.449 | 2013
EI_2013-01-30_141817 | 2013-01-30 09:18 | 2013-01-30 09:18 | EST | 2013-01-30 14:18 | 799 | 59.9887 | 59.9445 | 59.951 | -0.044233 | -0.037687 | -1806.3455 | -2120.0663 | No | No | 59.5 | 0.451 | 2013
EI_2013-02-01_120736 | 2013-02-01 07:08 | 2013-02-01 07:08 | EST | 2013-02-01 12:08 | 0 | 59.9856 | 59.9537 | 59.957 | -0.031866 | -0.028562 |  |  | No | No | 59.5 | 0.457 | 2013
EI_2013-02-03_090736 | 2013-02-03 04:08 | 2013-02-03 04:08 | EST | 2013-02-03 09:08 | 770 | 59.9774 | 59.9488 | 59.948 | -0.028557 | -0.029375 | -2696.3788 | -2621.2766 | No | No | 59.5 | 0.448 | 2013
EI_2013-02-03_235737 | 2013-02-03 18:58 | 2013-02-03 18:58 | EST | 2013-02-03 23:58 | 0 | 59.9944 | 60.0036 | 60.027 | 0.0091383 | 0.032563 |  |  | No | No | 59.5 | 0.527 | 2013
EI_2013-02-03_235809 | 2013-02-03 18:58 | 2013-02-03 18:58 | EST | 2013-02-03 23:58 | 0 | 60.0234 | 59.9793 | 59.981 | -0.044104 | -0.042437 |  |  | No | No | 59.5 | 0.481 | 2013
EI_2013-02-04_013720 | 2013-02-03 20:37 | 2013-02-03 20:37 | EST | 2013-02-04 01:37 | 0 | 59.9894 | 60.0262 | 60.041 | 0.036805 | 0.051562 |  |  | No | No | 59.5 | 0.541 | 2013
EI_2013-02-04_022640 | 2013-02-03 21:27 | 2013-02-03 21:27 | EST | 2013-02-04 02:27 | 0 | 60.0252 | 59.992 | 59.994 | -0.033188 | -0.031188 |  |  | No | No | 59.5 | 0.494 | 2013
EI_2013-02-04_023434 | 2013-02-03 21:35 | 2013-02-03 21:35 | EST | 2013-02-04 02:35 | 0 | 59.9689 | 60.0028 | 60.006 | 0.033913 | 0.037125 |  |  | No | No | 59.5 | 0.506 | 2013
EI_2013-02-04_110410 | 2013-02-04 06:04 | 2013-02-04 06:04 | EST | 2013-02-04 11:04 | 0 | 59.9798 | 59.9445 | 59.951 | -0.035328 | -0.028813 |  |  | No | No | 59.5 | 0.451 | 2013
EI_2013-02-05_062600 | 2013-02-05 01:26 | 2013-02-05 01:26 | EST | 2013-02-05 06:26 | 600 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.5 | -59.5 | 2013
EI_2013-02-09_110520 | 2013-02-09 06:05 | 2013-02-09 06:05 | EST | 2013-02-09 11:05 | 0 | 60.0036 | 60.0396 | 60.037 | 0.036011 | 0.033375 |  |  | No | No | 59.5 | 0.537 | 2013
EI_2013-02-10_220508 | 2013-02-10 17:05 | 2013-02-10 17:05 | EST | 2013-02-10 22:05 | 0 | 59.9916 | 60.0322 | 60.028 | 0.04068 | 0.036437 |  |  | No | No | 59.5 | 0.528 | 2013
EI_2013-02-14_010003 | 2013-02-13 20:00 | 2013-02-13 20:00 | EST | 2013-02-14 01:00 | 0 | 59.9864 | 59.9555 | 59.9599 | -0.030894 | -0.026519 |  |  | No | No | 59.5 | 0.4599 | 2013
EI_2013-02-20_211900 | 2013-02-20 16:19 | 2013-02-20 16:19 | EST | 2013-02-20 21:19 | 500 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.5 | -59.5 | 2013
EI_2013-02-21_145659 | 2013-02-21 09:57 | 2013-02-21 09:57 | EST | 2013-02-21 14:57 | 1300 | 60.0072 | 59.9718 | 59.9706 | -0.035461 | -0.036625 | -3665.9911 | -3549.4969 | No | No | 59.5 | 0.4706 | 2013
EI_2013-02-21_150229 | 2013-02-21 10:02 | 2013-02-21 10:02 | EST | 2013-02-21 15:02 | 0 | 59.9904 | 59.9514 | 59.946 | -0.039044 | -0.044438 |  |  | No | No | 59.5 | 0.446 | 2013
EI_2013-02-23_094320 | 2013-02-23 04:43 | 2013-02-23 04:43 | EST | 2013-02-23 09:43 | 0 | 59.9884 | 59.9502 | 59.952 | -0.038223 | -0.036375 |  |  | No | No | 59.5 | 0.452 | 2013
EI_2013-02-24_020410 | 2013-02-23 21:04 | 2013-02-23 21:04 | EST | 2013-02-24 02:04 | 1350 | 60.0064 | 59.9498 | 59.946 | -0.056527 | -0.060375 | -2388.2597 | -2236.0248 | Yes | Yes | 59.5 | 0.446 | 2013
EI_2013-02-24_031739 | 2013-02-23 22:18 | 2013-02-23 22:18 | EST | 2013-02-24 03:18 | 0 | 59.9716 | 59.9413 | 59.937 | -0.03029 | -0.034562 |  |  | No | No | 59.5 | 0.437 | 2013
EI_2013-02-25_191231 | 2013-02-25 14:13 | 2013-02-25 14:13 | EST | 2013-02-25 19:13 | 1170 | 59.9976 | 59.9462 | 59.95 | -0.051443 | -0.047625 | -2274.3539 | -2456.6929 | Yes | Yes | 59.5 | 0.45 | 2013
EI_2013-02-27_040158 | 2013-02-26 23:02 | 2013-02-26 23:02 | EST | 2013-02-27 04:02 | 1200 | 59.9829 | 59.9315 | 59.934 | -0.05133 | -0.048875 | -2337.8348 | -2455.243 | No | No | 59.5 | 0.434 | 2013
EI_2013-02-28_234800 | 2013-02-28 18:48 | 2013-02-28 18:48 | EST | 2013-02-28 23:48 | 0 | 59.9793 | 59.9419 | 59.945 | -0.037371 | -0.03425 |  |  | No | No | 59.5 | 0.445 | 2013
EI_2013-03-02_161241 | 2013-03-02 11:13 | 2013-03-02 11:13 | EST | 2013-03-02 16:13 | 0 | 59.9838 | 59.9485 | 59.952 | -0.035265 | -0.03175 |  |  | No | No | 59.5 | 0.452 | 2013
EI_2013-03-05_191528 | 2013-03-05 14:15 | 2013-03-05 14:15 | EST | 2013-03-05 19:15 | 0 | 60.0251 | 59.9825 | 59.989 | -0.042608 | -0.036062 |  |  | No | No | 59.5 | 0.489 | 2013
EI_2013-03-07_135838 | 2013-03-07 08:59 | 2013-03-07 08:59 | EST | 2013-03-07 13:59 | 1097 | 60.0142 | 59.9658 | 59.97 | -0.048462 | -0.04425 | -2263.6236 | -2479.096 | No | No | 59.5 | 0.47 | 2013
EI_2013-03-11_000741 | 2013-03-10 20:08 | 2013-03-10 20:08 | EDT | 2013-03-11 00:08 | 0 | 60.004 | 59.9598 | 59.968 | -0.044152 | -0.036 |  |  | No | No | 59.5 | 0.468 | 2013
EI_2013-03-11_001733 | 2013-03-10 20:18 | 2013-03-10 20:18 | EDT | 2013-03-11 00:18 | 0 | 59.9888 | 59.9519 | 59.958 | -0.036871 | -0.03075 |  |  | No | No | 59.5 | 0.458 | 2013
EI_2013-03-12_185153 | 2013-03-12 14:52 | 2013-03-12 14:52 | EDT | 2013-03-12 18:52 | 1040 | 59.996 | 59.9542 | 59.955 | -0.041818 | -0.041 | -2486.9565 | -2536.5854 | Yes | Yes | 59.5 | 0.455 | 2013
EI_2013-03-19_032440 | 2013-03-18 23:25 | 2013-03-18 23:25 | EDT | 2013-03-19 03:25 | 0 | 60.0209 | 59.9822 | 59.984 | -0.038633 | -0.036875 |  |  | No | No | 59.5 | 0.484 | 2013
EI_2013-03-19_090046 | 2013-03-19 05:01 | 2013-03-19 05:01 | EDT | 2013-03-19 09:01 | 770 | 60.0012 | 59.9496 | 59.962 | -0.051644 | -0.03925 | -1490.9784 | -1961.7834 | No | No | 59.5 | 0.462 | 2013
EI_2013-03-21_005146 | 2013-03-20 20:52 | 2013-03-20 20:52 | EDT | 2013-03-21 00:52 | 1152 | 60.0241 | 59.9515 | 59.963 | -0.07261 | -0.061125 | -1586.5616 | -1884.6626 | No | No | 59.5 | 0.463 | 2013
EI_2013-03-21_142508 | 2013-03-21 10:25 | 2013-03-21 10:25 | EDT | 2013-03-21 14:25 | 0 | 60.0152 | 59.9495 | 59.957 | -0.065672 | -0.058188 |  |  | No | No | 59.5 | 0.457 | 2013
EI_2013-03-28_125027 | 2013-03-28 08:50 | 2013-03-28 08:50 | EDT | 2013-03-28 12:50 | 0 | 60.0186 | 59.9728 | 59.977 | -0.045714 | -0.041563 |  |  | No | No | 59.5 | 0.477 | 2013
EI_2013-03-30_135615 | 2013-03-30 09:56 | 2013-03-30 09:56 | EDT | 2013-03-30 13:56 | 580 | 60.0289 | 60.0054 | 59.995 | -0.023511 | -0.033875 | -2466.8922 | -1712.1771 | No | No | 59.5 | 0.495 | 2013
EI_2013-03-31_124923 | 2013-03-31 08:49 | 2013-03-31 08:49 | EDT | 2013-03-31 12:49 | 1005 | 59.9854 | 59.9415 | 59.937 | -0.043892 | -0.048438 | -2289.7087 | -2074.8387 | No | No | 59.5 | 0.437 | 2013
EI_2013-04-01_170733 | 2013-04-01 13:08 | 2013-04-01 13:08 | EDT | 2013-04-01 17:08 | 865 | 60.0039 | 59.969 | 59.966 | -0.034907 | -0.037937 | -2477.999 | -2280.0659 | Yes | No | 59.5 | 0.466 | 2013
EI_2013-04-03_084015 | 2013-04-03 04:40 | 2013-04-03 04:40 | EDT | 2013-04-03 08:40 | 0 | 59.9731 | 60.0199 | 60.007 | 0.046784 | 0.033875 |  |  | No | No | 59.5 | 0.507 | 2013
EI_2013-04-04_194957 | 2013-04-04 15:50 | 2013-04-04 15:50 | EDT | 2013-04-04 19:50 | 750 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.5 | -59.5 | 2013
EI_2013-04-04_195900 | 2013-04-04 15:59 | 2013-04-04 15:59 | EDT | 2013-04-04 19:59 | 1706 | 59.9886 | 59.9364 | 59.932 | -0.052261 | -0.056625 | -3264.3618 | -3012.8035 | Yes | Yes | 59.5 | 0.432 | 2013
EI_2013-04-05_124723 | 2013-04-05 08:47 | 2013-04-05 08:47 | EDT | 2013-04-05 12:47 | 0 | 59.9795 | 59.969 | 59.952 | -0.0105 | -0.0275 |  |  | No | No | 59.5 | 0.452 | 2013
EI_2013-04-07_181700 | 2013-04-07 14:17 | 2013-04-07 14:17 | EDT | 2013-04-07 18:17 | 480 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.5 | -59.5 | 2013
EI_2013-04-08_203750 | 2013-04-08 16:38 | 2013-04-08 16:38 | EDT | 2013-04-08 20:38 | 624 | 59.9894 | 59.9471 | 59.952 | -0.042314 | -0.037375 | -1474.6755 | -1669.5652 | No | No | 59.5 | 0.452 | 2013
EI_2013-04-09_043431 | 2013-04-09 00:35 | 2013-04-09 00:35 | EDT | 2013-04-09 04:35 | 0 | 60.0181 | 59.9805 | 59.979 | -0.037608 | -0.039062 |  |  | No | No | 59.5 | 0.479 | 2013
EI_2013-04-16_051129 | 2013-04-16 01:11 | 2013-04-16 01:11 | EDT | 2013-04-16 05:11 | 0 | 60.0131 | 59.9673 | 59.972 | -0.04579 | -0.041062 |  |  | No | No | 59.5 | 0.472 | 2013
EI_2013-04-17_195940 | 2013-04-17 16:00 | 2013-04-17 16:00 | EDT | 2013-04-17 20:00 | 2344 | 59.9904 | 59.9169 | 59.909 | -0.073496 | -0.081375 | -3189.28 | -2880.4916 | Yes | Yes | 59.5 | 0.409 | 2013
EI_2013-04-18_100001 | 2013-04-18 06:00 | 2013-04-18 06:00 | EDT | 2013-04-18 10:00 | 0 | 59.9832 | 60.0118 | 60.02 | 0.0286 | 0.036813 |  |  | No | No | 59.5 | 0.52 | 2013
EI_2013-04-18_132706 | 2013-04-18 09:27 | 2013-04-18 09:27 | EDT | 2013-04-18 13:27 | 852 | 59.9933 | 59.9478 | 59.952 | -0.045492 | -0.04125 | -1872.8393 | -2065.4545 | Yes | Yes | 59.5 | 0.452 | 2013
EI_2013-04-20_044506 | 2013-04-20 00:45 | 2013-04-20 00:45 | EDT | 2013-04-20 04:45 | 852 | 60.0059 | 59.9642 | 59.962 | -0.041723 | -0.043875 | -2042.0154 | -1941.8803 | Yes | No | 59.5 | 0.462 | 2013
EI_2013-04-21_024552 | 2013-04-20 22:46 | 2013-04-20 22:46 | EDT | 2013-04-21 02:46 | 543 | 60.0205 | 59.9678 | 59.983 | -0.052742 | -0.0375 | -1029.5317 | -1448 | No | No | 59.5 | 0.483 | 2013
EI_2013-04-22_183610 | 2013-04-22 14:36 | 2013-04-22 14:36 | EDT | 2013-04-22 18:36 | 0 | 59.9836 | 59.9582 | 59.944 | -0.025383 | -0.039625 |  |  | No | No | 59.5 | 0.444 | 2013
EI_2013-04-26_135529 | 2013-04-26 09:55 | 2013-04-26 09:55 | EDT | 2013-04-26 13:55 | 0 | 59.9825 | 59.9398 | 59.944 | -0.042682 | -0.0385 |  |  | No | No | 59.5 | 0.444 | 2013
EI_2013-04-27_110013 | 2013-04-27 07:00 | 2013-04-27 07:00 | EDT | 2013-04-27 11:00 | 371 | 59.9949 | 59.9518 | 59.959 | -0.043089 | -0.035937 | -861.0083 | -1032.3478 | No | No | 59.5 | 0.459 | 2013
EI_2013-04-29_200711 | 2013-04-29 16:07 | 2013-04-29 16:07 | EDT | 2013-04-29 20:07 | 0 | 60.032 | 59.9824 | 59.991 | -0.049576 | -0.041 |  |  | No | No | 59.5 | 0.491 | 2013
EI_2013-05-01_003739 | 2013-04-30 20:38 | 2013-04-30 20:38 | EDT | 2013-05-01 00:38 | 368 | 59.9889 | 59.9491 | 59.951 | -0.039754 | -0.037875 | -925.698 | -971.6172 | No | No | 59.5 | 0.451 | 2013
EI_2013-05-01_004516 | 2013-04-30 20:45 | 2013-04-30 20:45 | EDT | 2013-05-01 00:45 | 858 | 59.9718 | 59.9484 | 59.941 | -0.023356 | -0.03075 | -3673.5647 | -2790.2439 | No | No | 59.5 | 0.441 | 2013
EI_2013-05-01_161303 | 2013-05-01 12:13 | 2013-05-01 12:13 | EDT | 2013-05-01 16:13 | 852 | 60.0033 | 59.9561 | 59.964 | -0.047191 | -0.039313 | -1805.418 | -2167.2496 | Yes | No | 59.5 | 0.464 | 2013
EI_2013-05-04_044152 | 2013-05-04 00:42 | 2013-05-04 00:42 | EDT | 2013-05-04 04:42 | 0 | 59.9876 | 59.9522 | 59.948 | -0.035383 | -0.039625 |  |  | No | No | 59.5 | 0.448 | 2013
EI_2013-05-04_130734 | 2013-05-04 09:08 | 2013-05-04 09:08 | EDT | 2013-05-04 13:08 | 900 | 60.0103 | 59.9592 | 59.957 | -0.051131 | -0.053312 | -1760.1956 | -1688.1594 | Yes | No | 59.5 | 0.457 | 2013
EI_2013-05-07_173106 | 2013-05-07 13:31 | 2013-05-07 13:31 | EDT | 2013-05-07 17:31 | 1275 | 59.985 | 59.9191 | 59.926 | -0.065879 | -0.059 | -1935.3726 | -2161.0169 | Yes | No | 59.5 | 0.426 | 2013
EI_2013-05-08_090006 | 2013-05-08 05:00 | 2013-05-08 05:00 | EDT | 2013-05-08 09:00 | 0 | 59.9859 | 60.0201 | 60.025 | 0.034186 | 0.039125 |  |  | No | No | 59.5 | 0.525 | 2013
EI_2013-05-09_014744 | 2013-05-08 21:48 | 2013-05-08 21:48 | EDT | 2013-05-09 01:48 | 875 | 60.0223 | 59.9764 | 59.983 | -0.045949 | -0.039313 | -1904.2908 | -2225.7552 | Yes | No | 59.5 | 0.483 | 2013
EI_2013-05-09_063515 | 2013-05-09 02:35 | 2013-05-09 02:35 | EDT | 2013-05-09 06:35 | 0 | 60.0273 | 59.9763 | 59.989 | -0.050917 | -0.03825 |  |  | No | No | 59.5 | 0.489 | 2013
EI_2013-05-10_145753 | 2013-05-10 10:58 | 2013-05-10 10:58 | EDT | 2013-05-10 14:58 | 1298 | 60.0202 | 59.956 | 59.959 | -0.064218 | -0.061187 | -2021.2464 | -2121.3483 | Yes | No | 59.5 | 0.459 | 2013
EI_2013-05-11_034043 | 2013-05-10 23:41 | 2013-05-10 23:41 | EDT | 2013-05-11 03:41 | 0 | 59.9943 | 59.9498 | 59.957 | -0.044492 | -0.03725 |  |  | No | No | 59.5 | 0.457 | 2013
EI_2013-05-12_114503 | 2013-05-12 07:45 | 2013-05-12 07:45 | EDT | 2013-05-12 11:45 | 0 | 60.0117 | 60.0368 | 60.043 | 0.025008 | 0.03125 |  |  | No | No | 59.5 | 0.543 | 2013
EI_2013-05-15_190441 | 2013-05-15 15:05 | 2013-05-15 15:05 | EDT | 2013-05-15 19:05 | 0 | 60.0067 | 59.969 | 59.966 | -0.03772 | -0.04075 |  |  | No | No | 59.5 | 0.466 | 2013
EI_2013-05-16_141546 | 2013-05-16 10:16 | 2013-05-16 10:16 | EDT | 2013-05-16 14:16 | 0 | 59.9808 | 59.9185 | 59.927 | -0.062295 | -0.05375 |  |  | No | Yes | 59.5 | 0.427 | 2013
EI_2013-05-17_001125 | 2013-05-16 20:11 | 2013-05-16 20:11 | EDT | 2013-05-17 00:11 | 0 | 60.0016 | 59.9671 | 59.964 | -0.034472 | -0.037562 |  |  | No | No | 59.5 | 0.464 | 2013
EI_2013-05-21_093347 | 2013-05-21 05:34 | 2013-05-21 05:34 | EDT | 2013-05-21 09:34 | 0 | 59.9896 | 59.9562 | 59.954 | -0.033383 | -0.035625 |  |  | No | No | 59.5 | 0.454 | 2013
EI_2013-05-27_083959 | 2013-05-27 04:40 | 2013-05-27 04:40 | EDT | 2013-05-27 08:40 | 0 | 60.0027 | 59.9691 | 59.97 | -0.033566 | -0.032688 |  |  | No | No | 59.5 | 0.47 | 2013
EI_2013-05-27_184106 | 2013-05-27 14:41 | 2013-05-27 14:41 | EDT | 2013-05-27 18:41 | 0 | 60.0104 | 59.9469 | 59.953 | -0.063528 | -0.057437 |  |  | No | Yes | 59.5 | 0.453 | 2013
EI_2013-05-28_182410 | 2013-05-28 14:24 | 2013-05-28 14:24 | EDT | 2013-05-28 18:24 | 0 | 59.9984 | 59.9501 | 59.957 | -0.048284 | -0.041375 |  |  | No | No | 59.5 | 0.457 | 2013
EI_2013-05-28_190756 | 2013-05-28 15:08 | 2013-05-28 15:08 | EDT | 2013-05-28 19:08 | 1006 | 60.0083 | 59.9564 | 59.961 | -0.051888 | -0.047313 | -1938.7816 | -2126.288 | Yes | No | 59.5 | 0.461 | 2013
EI_2013-05-29_031224 | 2013-05-28 23:12 | 2013-05-28 23:12 | EDT | 2013-05-29 03:12 | 0 | 59.9908 | 59.9517 | 59.955 | -0.039116 | -0.035812 |  |  | No | No | 59.5 | 0.455 | 2013
EI_2013-06-05_145414 | 2013-06-05 10:54 | 2013-06-05 10:54 | EDT | 2013-06-05 14:54 | 1600 | 60.0079 | 59.9355 | 59.944 | -0.072453 | -0.063937 | -2208.3388 | -2502.4438 | Yes | Yes | 59.5 | 0.444 | 2013
EI_2013-06-05_152324 | 2013-06-05 11:23 | 2013-06-05 11:23 | EDT | 2013-06-05 15:23 | 858 | 59.9961 | 59.9586 | 59.96 | -0.037426 | -0.036062 | -2292.5156 | -2379.2028 | Yes | No | 59.5 | 0.46 | 2013
EI_2013-06-05_185244 | 2013-06-05 14:53 | 2013-06-05 14:53 | EDT | 2013-06-05 18:53 | 1340 | 59.995 | 59.94 | 59.936 | -0.055 | -0.059 | -2436.3636 | -2271.1864 | Yes | Yes | 59.5 | 0.436 | 2013
EI_2013-06-08_151817 | 2013-06-08 11:18 | 2013-06-08 11:18 | EDT | 2013-06-08 15:18 | 1096 | 59.9803 | 59.9395 | 59.937 | -0.040797 | -0.043312 | -2686.4491 | -2530.4473 | Yes | No | 59.5 | 0.437 | 2013
EI_2013-06-09_115952 | 2013-06-09 08:00 | 2013-06-09 08:00 | EDT | 2013-06-09 12:00 | 0 | 59.9856 | 60.0165 | 60.02 | 0.03083 | 0.034375 |  |  | No | No | 59.5 | 0.52 | 2013
EI_2013-06-11_173955 | 2013-06-11 13:40 | 2013-06-11 13:40 | EDT | 2013-06-11 17:40 | 500 | 59.9829 | 59.9568 | 59.96 | -0.026119 | -0.022937 | -1914.2919 | -2179.8365 | No | No | 59.5 | 0.46 | 2013
EI_2013-06-12_141858 | 2013-06-12 10:19 | 2013-06-12 10:19 | EDT | 2013-06-12 14:19 | 778 | 60.008 | 59.9592 | 59.965 | -0.048848 | -0.043 | -1592.6799 | -1809.3023 | No | No | 59.5 | 0.465 | 2013
EI_2013-06-12_173909 | 2013-06-12 13:39 | 2013-06-12 13:39 | EDT | 2013-06-12 17:39 | 1191 | 60.0009 | 59.9845 | 59.996 | -0.01642 | -0.004875 | -7253.1488 | -24430.7692 | No | No | 59.5 | 0.496 | 2013
EI_2013-06-16_033226 | 2013-06-15 23:32 | 2013-06-15 23:32 | EDT | 2013-06-16 03:32 | 0 | 60.007 | 59.9557 | 59.961 | -0.051273 | -0.046 |  |  | No | No | 59.5 | 0.461 | 2013
EI_2013-06-17_154948 | 2013-06-17 11:50 | 2013-06-17 11:50 | EDT | 2013-06-17 15:50 | 0 | 60.0002 | 59.9462 | 59.949 | -0.053975 | -0.051188 |  |  | No | Yes | 59.5 | 0.449 | 2013
EI_2013-06-18_171702 | 2013-06-18 13:17 | 2013-06-18 13:17 | EDT | 2013-06-18 17:17 | 904 | 59.9859 | 59.9514 | 59.954 | -0.034574 | -0.031937 | -2614.6919 | -2830.5284 | No | No | 59.5 | 0.454 | 2013
EI_2013-06-18_184336 | 2013-06-18 14:44 | 2013-06-18 14:44 | EDT | 2013-06-18 18:44 | 0 | 59.9986 | 59.957 | 59.963 | -0.041532 | -0.035562 |  |  | No | No | 59.5 | 0.463 | 2013
EI_2013-06-27_055904 | 2013-06-27 01:59 | 2013-06-27 01:59 | EDT | 2013-06-27 05:59 | 0 | 59.9886 | 59.9526 | 59.956 | -0.035926 | -0.032562 |  |  | No | No | 59.5 | 0.456 | 2013
EI_2013-06-27_222331 | 2013-06-27 18:24 | 2013-06-27 18:24 | EDT | 2013-06-27 22:24 | 850 | 60.0061 | 59.962 | 59.968 | -0.044032 | -0.038062 | -1930.4056 | -2233.1691 | Yes | No | 59.5 | 0.468 | 2013
EI_2013-06-28_172946 | 2013-06-28 13:30 | 2013-06-28 13:30 | EDT | 2013-06-28 17:30 | 1180 | 59.9982 | 59.942 | 59.946 | -0.056218 | -0.052188 | -2098.9792 | -2261.0778 | Yes | Yes | 59.5 | 0.446 | 2013
EI_2013-06-28_234703 | 2013-06-28 19:47 | 2013-06-28 19:47 | EDT | 2013-06-28 23:47 | 0 | 60.0264 | 59.9844 | 59.994 | -0.042011 | -0.032375 |  |  | No | No | 59.5 | 0.494 | 2013
EI_2013-06-30_012022 | 2013-06-29 21:20 | 2013-06-29 21:20 | EDT | 2013-06-30 01:20 | 906 | 59.9897 | 59.9463 | 59.95 | -0.043354 | -0.039687 | -2089.7645 | -2282.8346 | Yes | No | 59.5 | 0.45 | 2013
EI_2013-07-03_114057 | 2013-07-03 07:41 | 2013-07-03 07:41 | EDT | 2013-07-03 11:41 | 0 | 60.0043 | 59.9692 | 59.9737 | -0.035097 | -0.030599 |  |  | No | No | 59.5 | 0.4737 | 2013
EI_2013-07-03_203826 | 2013-07-03 16:38 | 2013-07-03 16:38 | EDT | 2013-07-03 20:38 | 0 | 59.949 | 59.9273 | 59.9188 | -0.021614 | -0.03015 |  |  | No | No | 59.5 | 0.4188 | 2013
EI_2013-07-09_151425 | 2013-07-09 11:14 | 2013-07-09 11:14 | EDT | 2013-07-09 15:14 | 830 | 59.9961 | 59.9616 | 59.9609 | -0.034492 | -0.035168 | -2406.3353 | -2360.0726 | No | No | 59.5 | 0.4609 | 2013
EI_2013-07-13_191411 | 2013-07-13 15:14 | 2013-07-13 15:14 | EDT | 2013-07-13 19:14 | 0 | 60.0018 | 59.9563 | 59.9583 | -0.045562 | -0.043542 |  |  | No | Yes | 59.5 | 0.4583 | 2013
EI_2013-07-14_215209 | 2013-07-14 17:52 | 2013-07-14 17:52 | EDT | 2013-07-14 21:52 | 0 | 59.9883 | 59.959 | 59.9579 | -0.029226 | -0.030367 |  |  | No | No | 59.5 | 0.4579 | 2013
EI_2013-07-27_043432 | 2013-07-27 00:35 | 2013-07-27 00:35 | EDT | 2013-07-27 04:35 | 1298 | 60.0094 | 59.954 | 59.9565 | -0.055338 | -0.052886 | -2345.5832 | -2454.3353 | Yes | Yes | 59.5 | 0.4565 | 2013
EI_2013-07-27_043946 | 2013-07-27 00:40 | 2013-07-27 00:40 | EDT | 2013-07-27 04:40 | 0 | 59.9839 | 60.0264 | 60.021 | 0.0425 | 0.037106 |  |  | No | No | 59.5 | 0.521 | 2013
EI_2013-07-28_141819 | 2013-07-28 10:18 | 2013-07-28 10:18 | EDT | 2013-07-28 14:18 | 0 | 59.9884 | 59.9515 | 59.9518 | -0.036857 | -0.036586 |  |  | No | No | 59.5 | 0.4518 | 2013
EI_2013-07-28_211049 | 2013-07-28 17:11 | 2013-07-28 17:11 | EDT | 2013-07-28 21:11 | 0 | 59.981 | 59.9482 | 59.9508 | -0.032769 | -0.030167 |  |  | No | No | 59.5 | 0.4508 | 2013
EI_2013-07-30_193153 | 2013-07-30 15:32 | 2013-07-30 15:32 | EDT | 2013-07-30 19:32 | 1400 | 59.9664 | 59.9404 | 59.9409 | -0.026017 | -0.025482 | -5381.016 | -5494.0359 | No | No | 59.5 | 0.4409 | 2013
EI_2013-08-05_010055 | 2013-08-04 21:01 | 2013-08-04 21:01 | EDT | 2013-08-05 01:01 | 0 | 59.9879 | 59.9454 | 59.945 | -0.042432 | -0.042874 |  |  | No | Yes | 59.5 | 0.44498 | 2013
EI_2013-08-05_113819 | 2013-08-05 07:38 | 2013-08-05 07:38 | EDT | 2013-08-05 11:38 | 0 | 59.997 | 60.0266 | 60.0345 | 0.029562 | 0.037468 |  |  | No | No | 59.5 | 0.5345 | 2013
EI_2013-08-08_180156 | 2013-08-08 14:02 | 2013-08-08 14:02 | EDT | 2013-08-08 18:02 | 1262 | 60 | 59.9495 | 59.9453 | -0.050475 | -0.054686 | -2500.2363 | -2307.7074 | Yes | Yes | 59.5 | 0.4453 | 2013
EI_2013-08-10_011837 | 2013-08-09 21:19 | 2013-08-09 21:19 | EDT | 2013-08-10 01:19 | 1250 | 60.012 | 59.9591 | 59.9641 | -0.052986 | -0.047938 | -2359.0934 | -2607.5288 | No | No | 59.5 | 0.4641 | 2013
EI_2013-08-18_160402 | 2013-08-18 12:04 | 2013-08-18 12:04 | EDT | 2013-08-18 16:04 | 0 | 59.9631 | 59.9549 | 59.9568 | -0.0082272 | -0.0062952 |  |  | No | No | 59.5 | 0.4568 | 2013
EI_2013-08-19_181404 | 2013-08-19 14:14 | 2013-08-19 14:14 | EDT | 2013-08-19 18:14 | 0 | 59.9775 | 59.9308 | 59.9361 | -0.046672 | -0.041412 |  |  | No | Yes | 59.5 | 0.4361 | 2013
EI_2013-08-20_095038 | 2013-08-20 05:51 | 2013-08-20 05:51 | EDT | 2013-08-20 09:51 | 0 | 59.9816 | 60.0188 | 60.016 | 0.037195 | 0.034437 |  |  | No | No | 59.5 | 0.516 | 2013
EI_2013-08-30_155631 | 2013-08-30 11:57 | 2013-08-30 11:57 | EDT | 2013-08-30 15:57 | 0 | 60.0057 | 59.9638 | 59.9664 | -0.041971 | -0.039344 |  |  | No | No | 59.5 | 0.4664 | 2013
EI_2013-08-31_171556 | 2013-08-31 13:16 | 2013-08-31 13:16 | EDT | 2013-08-31 17:16 | 0 | 59.9914 | 59.9527 | 59.9598 | -0.038715 | -0.031581 |  |  | No | No | 59.5 | 0.4598 | 2013
EI_2013-09-03_140957 | 2013-09-03 10:10 | 2013-09-03 10:10 | EDT | 2013-09-03 14:10 | 1200 | 60.0007 | 59.9564 | 59.955 | -0.044294 | -0.045687 | -2709.1974 | -2626.539 | Yes | Yes | 59.5 | 0.455 | 2013
EI_2013-09-08_002039 | 2013-09-07 20:21 | 2013-09-07 20:21 | EDT | 2013-09-08 00:21 | 0 | 59.9921 | 59.9713 | 59.957 | -0.020729 | -0.035063 |  |  | No | No | 59.5 | 0.457 | 2013
EI_2013-09-08_192823 | 2013-09-08 15:28 | 2013-09-08 15:28 | EDT | 2013-09-08 19:28 | 0 | 60.0026 | 59.965 | 59.968 | -0.037593 | -0.034562 |  |  | No | No | 59.5 | 0.468 | 2013
EI_2013-09-10_054231 | 2013-09-10 01:43 | 2013-09-10 01:43 | EDT | 2013-09-10 05:43 | 1200 | 60.0346 | 59.9739 | 59.975 | -0.060686 | -0.059625 | -1977.4047 | -2012.5786 | No | No | 59.5 | 0.475 | 2013
EI_2013-09-11_102718 | 2013-09-11 06:27 | 2013-09-11 06:27 | EDT | 2013-09-11 10:27 | 1115 | 59.9925 | 59.954 | 59.97 | -0.0385 | -0.0225 | -2896.1039 | -4955.5556 | No | No | 59.5 | 0.47 | 2013
EI_2013-09-13_094538 | 2013-09-13 05:46 | 2013-09-13 05:46 | EDT | 2013-09-13 09:46 | 0 | 59.9781 | 60.0133 | 60.017 | 0.035208 | 0.038875 |  |  | No | No | 59.5 | 0.517 | 2013
EI_2013-09-16_162113 | 2013-09-16 12:21 | 2013-09-16 12:21 | EDT | 2013-09-16 16:21 | 845 | 59.9838 | 59.9457 | 59.947 | -0.038146 | -0.036812 | -2215.183 | -2295.416 | No | No | 59.5 | 0.447 | 2013
EI_2013-09-19_005730 | 2013-09-18 20:58 | 2013-09-18 20:58 | EDT | 2013-09-19 00:58 | 0 | 60.0034 | 59.9673 | 59.964 | -0.036165 | -0.039437 |  |  | No | No | 59.5 | 0.464 | 2013
EI_2013-09-24_100059 | 2013-09-24 06:01 | 2013-09-24 06:01 | EDT | 2013-09-24 10:01 | 0 | 59.9924 | 59.9432 | 59.956 | -0.049163 | -0.036375 |  |  | No | No | 59.5 | 0.456 | 2013
EI_2013-09-26_164213 | 2013-09-26 12:42 | 2013-09-26 12:42 | EDT | 2013-09-26 16:42 | 0 | 59.9858 | 59.9645 | 59.959 | -0.021328 | -0.026812 |  |  | No | No | 59.5 | 0.459 | 2013
EI_2013-09-27_051807 | 2013-09-27 01:18 | 2013-09-27 01:18 | EDT | 2013-09-27 05:18 | 0 | 59.9951 | 59.9533 | 59.957 | -0.041852 | -0.038125 |  |  | No | No | 59.5 | 0.457 | 2013
EI_2013-09-28_052854 | 2013-09-28 01:29 | 2013-09-28 01:29 | EDT | 2013-09-28 05:29 | 0 | 60.0053 | 59.9585 | 59.969 | -0.046797 | -0.036313 |  |  | No | No | 59.5 | 0.469 | 2013
EI_2013-09-29_055959 | 2013-09-29 02:00 | 2013-09-29 02:00 | EDT | 2013-09-29 06:00 | 0 | 59.9939 | 59.9529 | 59.96 | -0.040998 | -0.033938 |  |  | No | No | 59.5 | 0.46 | 2013
EI_2013-09-29_132500 | 2013-09-29 09:25 | 2013-09-29 09:25 | EDT | 2013-09-29 13:25 | 0 | 59.9879 | 60.0309 | 60.022 | 0.043002 | 0.034062 |  |  | No | No | 59.5 | 0.522 | 2013
EI_2013-09-29_171545 | 2013-09-29 13:16 | 2013-09-29 13:16 | EDT | 2013-09-29 17:16 | 0 | 60.011 | 59.9754 | 59.981 | -0.035606 | -0.03 |  |  | No | No | 59.5 | 0.481 | 2013
EI_2013-10-01_150357 | 2013-10-01 11:04 | 2013-10-01 11:04 | EDT | 2013-10-01 15:04 | 910 | 59.9804 | 59.9558 | 59.948 | -0.024619 | -0.032438 | -3696.2843 | -2805.395 | No | No | 59.5 | 0.448 | 2013
EI_2013-10-04_075600 | 2013-10-04 03:56 | 2013-10-04 03:56 | EDT | 2013-10-04 07:56 | 800 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.5 | -59.5 | 2013
EI_2013-10-06_121506 | 2013-10-06 08:15 | 2013-10-06 08:15 | EDT | 2013-10-06 12:15 | 0 | 59.9944 | 60.035 | 60.038 | 0.040563 | 0.043563 |  |  | No | No | 59.5 | 0.538 | 2013
EI_2013-10-06_234125 | 2013-10-06 19:41 | 2013-10-06 19:41 | EDT | 2013-10-06 23:41 | 0 | 59.9867 | 59.9435 | 59.955 | -0.043233 | -0.031688 |  |  | No | No | 59.5 | 0.455 | 2013
EI_2013-10-07_041327 | 2013-10-07 00:13 | 2013-10-07 00:13 | EDT | 2013-10-07 04:13 | 0 | 60.0201 | 59.9769 | 59.98 | -0.043123 | -0.040063 |  |  | No | No | 59.5 | 0.48 | 2013
EI_2013-10-07_113536 | 2013-10-07 07:36 | 2013-10-07 07:36 | EDT | 2013-10-07 11:36 | 0 | 59.9865 | 59.9642 | 59.96 | -0.022288 | -0.0265 |  |  | No | No | 59.5 | 0.46 | 2013
EI_2013-10-08_094458 | 2013-10-08 05:45 | 2013-10-08 05:45 | EDT | 2013-10-08 09:45 | 0 | 60.0131 | 60.0577 | 60.054 | 0.044602 | 0.040875 |  |  | No | No | 59.5 | 0.554 | 2013
EI_2013-10-13_102959 | 2013-10-13 06:30 | 2013-10-13 06:30 | EDT | 2013-10-13 10:30 | 0 | 59.988 | 60.0404 | 60.025 | 0.052424 | 0.037 |  |  | No | No | 59.5 | 0.525 | 2013
EI_2013-10-14_100507 | 2013-10-14 06:05 | 2013-10-14 06:05 | EDT | 2013-10-14 10:05 | 0 | 59.9789 | 60.0224 | 60.017 | 0.043456 | 0.038063 |  |  | No | No | 59.5 | 0.517 | 2013
EI_2013-10-14_200250 | 2013-10-14 16:03 | 2013-10-14 16:03 | EDT | 2013-10-14 20:03 | 0 | 59.9853 | 59.9547 | 59.947 | -0.030585 | -0.038312 |  |  | No | No | 59.5 | 0.447 | 2013
EI_2013-10-15_012050 | 2013-10-14 21:21 | 2013-10-14 21:21 | EDT | 2013-10-15 01:21 | 0 | 59.9699 | 59.9328 | 59.938 | -0.037027 | -0.031875 |  |  | No | No | 59.5 | 0.438 | 2013
EI_2013-10-19_104205 | 2013-10-19 06:42 | 2013-10-19 06:42 | EDT | 2013-10-19 10:42 | 1204 | 59.9847 | 59.9415 | 59.9357 | -0.043166 | -0.049006 | -2789.2224 | -2456.8308 | Yes | Yes | 59.5 | 0.4357 | 2013
EI_2013-10-21_133557 | 2013-10-21 09:36 | 2013-10-21 09:36 | EDT | 2013-10-21 13:36 | 0 | 59.9895 | 59.9543 | 59.956 | -0.035197 | -0.0335 |  |  | No | No | 59.5 | 0.456 | 2013
EI_2013-10-21_214300 | 2013-10-21 17:43 | 2013-10-21 17:43 | EDT | 2013-10-21 21:43 | 800 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.5 | -59.5 | 2013
EI_2013-10-24_010203 | 2013-10-23 21:02 | 2013-10-23 21:02 | EDT | 2013-10-24 01:02 | 0 | 59.9844 | 59.9418 | 59.948 | -0.04268 | -0.036437 |  |  | No | No | 59.5 | 0.448 | 2013
EI_2013-10-24_095319 | 2013-10-24 05:53 | 2013-10-24 05:53 | EDT | 2013-10-24 09:53 | 0 | 59.9771 | 59.9386 | 59.943 | -0.038426 | -0.034063 |  |  | No | No | 59.5 | 0.443 | 2013
EI_2013-10-29_035942 | 2013-10-29 | 2013-10-29 | EDT | 2013-10-29 04:00 | 0 | 59.9853 | 59.9584 | 59.956 | -0.026856 | -0.02925 |  |  | No | No | 59.5 | 0.456 | 2013
EI_2013-10-30_074124 | 2013-10-30 03:41 | 2013-10-30 03:41 | EDT | 2013-10-30 07:41 | 0 | 59.9821 | 59.9512 | 59.954 | -0.030913 | -0.028125 |  |  | No | No | 59.5 | 0.454 | 2013
EI_2013-10-30_153701 | 2013-10-30 11:37 | 2013-10-30 11:37 | EDT | 2013-10-30 15:37 | 0 | 60.0057 | 59.9747 | 59.969 | -0.03096 | -0.036687 |  |  | No | No | 59.5 | 0.469 | 2013
EI_2013-11-04_152826 | 2013-11-04 10:28 | 2013-11-04 10:28 | EST | 2013-11-04 15:28 | 0 | 60.0057 | 59.9668 | 59.965 | -0.038869 | -0.040687 |  |  | No | No | 59.5 | 0.465 | 2013
EI_2013-11-04_222322 | 2013-11-04 17:23 | 2013-11-04 17:23 | EST | 2013-11-04 22:23 | 0 | 59.9883 | 59.9618 | 59.958 | -0.026402 | -0.03025 |  |  | No | No | 59.5 | 0.458 | 2013
EI_2013-11-05_213704 | 2013-11-05 16:37 | 2013-11-05 16:37 | EST | 2013-11-05 21:37 | 0 | 59.9939 | 59.9474 | 59.948 | -0.046451 | -0.045875 |  |  | No | No | 59.5 | 0.448 | 2013
EI_2013-11-08_061316 | 2013-11-08 01:13 | 2013-11-08 01:13 | EST | 2013-11-08 06:13 | 0 | 60.0174 | 59.9747 | 59.978 | -0.042708 | -0.039375 |  |  | No | No | 59.5 | 0.478 | 2013
EI_2013-11-09_201410 | 2013-11-09 15:14 | 2013-11-09 15:14 | EST | 2013-11-09 20:14 | 869 | 59.9929 | 59.942 | 59.946 | -0.050907 | -0.046937 | -1707.0278 | -1851.3981 | Yes | Yes | 59.5 | 0.446 | 2013
EI_2013-11-10_114955 | 2013-11-10 06:50 | 2013-11-10 06:50 | EST | 2013-11-10 11:50 | 0 | 59.9801 | 60.027 | 60.018 | 0.046905 | 0.037875 |  |  | No | No | 59.5 | 0.518 | 2013
EI_2013-11-12_050258 | 2013-11-12 00:03 | 2013-11-12 00:03 | EST | 2013-11-12 05:03 | 900 | 60.012 | 59.9712 | 59.983 | -0.040818 | -0.029 | -2204.8998 | -3103.4483 | No | No | 59.5 | 0.483 | 2013
EI_2013-11-12_225914 | 2013-11-12 17:59 | 2013-11-12 17:59 | EST | 2013-11-12 22:59 | 0 | 59.9943 | 59.9477 | 59.947 | -0.046523 | -0.04725 |  |  | No | Yes | 59.5 | 0.447 | 2013
EI_2013-11-14_171809 | 2013-11-14 12:18 | 2013-11-14 12:18 | EST | 2013-11-14 17:18 | 1042 | 60.0035 | 59.9513 | 59.953 | -0.052197 | -0.0505 | -1996.2845 | -2063.3663 | Yes | No | 59.5 | 0.453 | 2013
EI_2013-11-14_181327 | 2013-11-14 13:13 | 2013-11-14 13:13 | EST | 2013-11-14 18:13 | 1200 | 59.9941 | 59.9402 | 59.941 | -0.053881 | -0.053062 | -2227.1433 | -2261.4841 | Yes | No | 59.5 | 0.441 | 2013
EI_2013-11-14_192016 | 2013-11-14 14:20 | 2013-11-14 14:20 | EST | 2013-11-14 19:20 | 0 | 60.0014 | 59.964 | 59.972 | -0.037405 | -0.029375 |  |  | No | No | 59.5 | 0.472 | 2013
EI_2013-11-18_031713 | 2013-11-17 22:17 | 2013-11-17 22:17 | EST | 2013-11-18 03:17 | 0 | 59.9868 | 59.955 | 59.961 | -0.03178 | -0.02575 |  |  | No | No | 59.5 | 0.461 | 2013
EI_2013-11-20_035759 | 2013-11-19 22:58 | 2013-11-19 22:58 | EST | 2013-11-20 03:58 | 0 | 60.0051 | 59.9637 | 59.966 | -0.041428 | -0.039125 |  |  | No | No | 59.5 | 0.466 | 2013
EI_2013-11-20_233212 | 2013-11-20 18:32 | 2013-11-20 18:32 | EST | 2013-11-20 23:32 | 0 | 59.9864 | 59.9485 | 59.94 | -0.037953 | -0.046438 |  |  | No | Yes | 59.5 | 0.44 | 2013
EI_2013-11-21_175813 | 2013-11-21 12:58 | 2013-11-21 12:58 | EST | 2013-11-21 17:58 | 700 | 60.0302 | 59.9849 | 59.987 | -0.045248 | -0.043187 | -1547.0261 | -1620.8394 | No | No | 59.5 | 0.487 | 2013
EI_2013-11-22_153806 | 2013-11-22 10:38 | 2013-11-22 10:38 | EST | 2013-11-22 15:38 | 620 | 60.0124 | 59.9656 | 59.966 | -0.046739 | -0.046375 | -1326.5257 | -1336.9272 | No | No | 59.5 | 0.466 | 2013
EI_2013-11-23_144447 | 2013-11-23 09:45 | 2013-11-23 09:45 | EST | 2013-11-23 14:45 | 0 | 60.0014 | 59.9444 | 59.951 | -0.056981 | -0.050375 |  |  | No | No | 59.5 | 0.451 | 2013
EI_2013-11-27_152941 | 2013-11-27 10:30 | 2013-11-27 10:30 | EST | 2013-11-27 15:30 | 760 | 60.0101 | 59.9765 | 59.976 | -0.033608 | -0.034062 | -2261.3694 | -2231.1927 | No | No | 59.5 | 0.476 | 2013
EI_2013-11-29_213126 | 2013-11-29 16:31 | 2013-11-29 16:31 | EST | 2013-11-29 21:31 | 800 | 60.0036 | 59.9608 | 59.959 | -0.042775 | -0.044562 | -1870.2679 | -1795.2314 | Yes | No | 59.5 | 0.459 | 2013
EI_2013-12-01_111318 | 2013-12-01 06:13 | 2013-12-01 06:13 | EST | 2013-12-01 11:13 | 1282 | 60.0101 | 59.9629 | 59.954 | -0.047186 | -0.056125 | -2716.9302 | -2284.1871 | Yes | Yes | 59.5 | 0.454 | 2014
EI_2013-12-01_170506 | 2013-12-01 12:05 | 2013-12-01 12:05 | EST | 2013-12-01 17:05 | 0 | 59.9817 | 59.9482 | 59.948 | -0.033475 | -0.033687 |  |  | No | No | 59.5 | 0.448 | 2014
EI_2013-12-02_140400 | 2013-12-02 09:04 | 2013-12-02 09:04 | EST | 2013-12-02 14:04 | 460 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.5 | -59.5 | 2014
EI_2013-12-05_082516 | 2013-12-05 03:25 | 2013-12-05 03:25 | EST | 2013-12-05 08:25 | 914 | 60.0189 | 59.9665 | 59.971 | -0.05233 | -0.047875 | -1746.6232 | -1909.1384 | No | No | 59.5 | 0.471 | 2014
EI_2013-12-07_194244 | 2013-12-07 14:43 | 2013-12-07 14:43 | EST | 2013-12-07 19:43 | 1152 | 60.0222 | 59.96 | 59.973 | -0.062218 | -0.049188 | -1851.5601 | -2342.0584 | No | No | 59.5 | 0.473 | 2014
EI_2013-12-08_194720 | 2013-12-08 14:47 | 2013-12-08 14:47 | EST | 2013-12-08 19:47 | 0 | 60.0125 | 59.978 | 59.975 | -0.0345 | -0.0375 |  |  | No | No | 59.5 | 0.475 | 2014
EI_2013-12-09_023631 | 2013-12-08 21:37 | 2013-12-08 21:37 | EST | 2013-12-09 02:37 | 1043 | 60.0256 | 59.9734 | 59.989 | -0.052231 | -0.036625 | -1996.8961 | -2847.7816 | No | No | 59.5 | 0.489 | 2014
EI_2013-12-09_104449 | 2013-12-09 05:45 | 2013-12-09 05:45 | EST | 2013-12-09 10:45 | 0 | 59.999 | 60.0471 | 60.031 | 0.048091 | 0.032 |  |  | No | No | 59.5 | 0.531 | 2014
EI_2013-12-09_134654 | 2013-12-09 08:47 | 2013-12-09 08:47 | EST | 2013-12-09 13:47 | 1004 | 59.9946 | 59.9472 | 59.948 | -0.047381 | -0.046563 | -2119.0071 | -2156.2416 | Yes | Yes | 59.5 | 0.448 | 2014
EI_2013-12-10_145517 | 2013-12-10 09:55 | 2013-12-10 09:55 | EST | 2013-12-10 14:55 | 740 | 60.0194 | 59.9746 | 59.98 | -0.044799 | -0.039375 | -1651.8136 | -1879.3651 | No | No | 59.5 | 0.48 | 2014
EI_2013-12-10_221418 | 2013-12-10 17:14 | 2013-12-10 17:14 | EST | 2013-12-10 22:14 | 0 | 59.9928 | 59.9545 | 59.955 | -0.038297 | -0.037813 |  |  | No | No | 59.5 | 0.455 | 2014
EI_2013-12-12_102038 | 2013-12-12 05:21 | 2013-12-12 05:21 | EST | 2013-12-12 10:21 | 0 | 60.0094 | 59.9709 | 59.972 | -0.038466 | -0.037375 |  |  | No | No | 59.5 | 0.472 | 2014
EI_2013-12-13_235611 | 2013-12-13 18:56 | 2013-12-13 18:56 | EST | 2013-12-13 23:56 | 188 | 60.0199 | 59.993 | 60.006 | -0.026907 | -0.013937 | -698.6978 | -1348.8789 | No | No | 59.5 | 0.506 | 2014
EI_2013-12-14_083700 | 2013-12-14 03:37 | 2013-12-14 03:37 | EST | 2013-12-14 08:37 | 636 | 59.9984 | 59.9713 | 59.973 | -0.027165 | -0.025438 | -2341.2675 | -2500.2457 | No | No | 59.5 | 0.473 | 2014
EI_2013-12-15_105410 | 2013-12-15 05:54 | 2013-12-15 05:54 | EST | 2013-12-15 10:54 | 0 | 60.0079 | 59.9697 | 59.968 | -0.038271 | -0.039937 |  |  | No | No | 59.5 | 0.468 | 2014
EI_2013-12-16_120152 | 2013-12-16 07:02 | 2013-12-16 07:02 | EST | 2013-12-16 12:02 | 996 | 59.9696 | 59.9404 | 59.934 | -0.029138 | -0.035563 | -3418.1865 | -2800.703 | No | No | 59.5 | 0.434 | 2014
EI_2013-12-18_052308 | 2013-12-18 00:23 | 2013-12-18 00:23 | EST | 2013-12-18 05:23 | 480 | 60.0116 | 59.9807 | 59.982 | -0.030928 | -0.029625 | -1551.9902 | -1620.2532 | No | No | 59.5 | 0.482 | 2014
EI_2013-12-24_040658 | 2013-12-23 23:07 | 2013-12-23 23:07 | EST | 2013-12-24 04:07 | 474 | 59.9776 | 59.9533 | 59.956 | -0.024322 | -0.021625 | -1948.8553 | -2191.9075 | No | No | 59.5 | 0.456 | 2014
EI_2013-12-24_153126 | 2013-12-24 10:31 | 2013-12-24 10:31 | EST | 2013-12-24 15:31 | 745 | 59.9887 | 59.9533 | 59.951 | -0.035415 | -0.037687 | -2103.6419 | -1976.7828 | No | No | 59.5 | 0.451 | 2014
EI_2013-12-28_035957 | 2013-12-27 23:00 | 2013-12-27 23:00 | EST | 2013-12-28 04:00 | 658 | 60.0216 | 59.9776 | 59.983 | -0.043987 | -0.038563 | -1495.9053 | -1706.3209 | No | No | 59.5 | 0.483 | 2014
EI_2013-12-28_224716 | 2013-12-28 17:47 | 2013-12-28 17:47 | EST | 2013-12-28 22:47 | 800 | 59.9875 | 59.9508 | 59.954 | -0.036742 | -0.0335 | -2177.3196 | -2388.0597 | No | No | 59.5 | 0.454 | 2014
EI_2014-01-01_182729 | 2014-01-01 13:27 | 2014-01-01 13:27 | EST | 2014-01-01 18:27 | 0 | 59.9871 | 59.9593 | 59.956 | -0.02779 | -0.031062 |  |  | No | No | 59.5 | 0.456 | 2014
EI_2014-01-02_182136 | 2014-01-02 13:22 | 2014-01-02 13:22 | EST | 2014-01-02 18:22 | 1043 | 59.9977 | 59.9508 | 59.956 | -0.04693 | -0.041687 | -2222.4626 | -2501.949 | Yes | No | 59.5 | 0.456 | 2014
EI_2014-01-03_001216 | 2014-01-02 19:12 | 2014-01-02 19:12 | EST | 2014-01-03 00:12 | 0 | 60.0175 | 59.9714 | 59.984 | -0.046076 | -0.0335 |  |  | No | No | 59.5 | 0.484 | 2014
EI_2014-01-04_223104 | 2014-01-04 17:31 | 2014-01-04 17:31 | EST | 2014-01-04 22:31 | 570 | 59.9844 | 59.9783 | 59.967 | -0.0061042 | -0.017437 | -9337.884 | -3268.8172 | No | No | 59.5 | 0.467 | 2014
EI_2014-01-06_003712 | 2014-01-05 19:37 | 2014-01-05 19:37 | EST | 2014-01-06 00:37 | 0 | 60.0373 | 60.0046 | 60.001 | -0.032644 | -0.03625 |  |  | No | No | 59.5 | 0.501 | 2014
EI_2014-01-06_154747 | 2014-01-06 10:48 | 2014-01-06 10:48 | EST | 2014-01-06 15:48 | 570 | 59.9744 | 59.9496 | 59.949 | -0.024801 | -0.025438 | -2298.2818 | -2240.7862 | No | No | 59.5 | 0.449 | 2014
EI_2014-01-06_215909 | 2014-01-06 16:59 | 2014-01-06 16:59 | EST | 2014-01-06 21:59 | 950 | 59.9946 | 59.9495 | 59.958 | -0.04514 | -0.036625 | -2104.5565 | -2593.8567 | Yes | No | 59.5 | 0.458 | 2014
EI_2014-01-06_215940 | 2014-01-06 17:00 | 2014-01-06 17:00 | EST | 2014-01-06 22:00 | 602 | 59.9597 | 59.946 | 59.941 | -0.013718 | -0.018687 | -4388.4578 | -3221.4047 | No | No | 59.5 | 0.441 | 2014
EI_2014-01-07_021527 | 2014-01-06 21:15 | 2014-01-06 21:15 | EST | 2014-01-07 02:15 | 1025 | 59.9752 | 59.9479 | 59.945 | -0.027309 | -0.030187 | -3753.381 | -3395.4451 | No | No | 59.5 | 0.445 | 2014
EI_2014-01-07_132058 | 2014-01-07 08:21 | 2014-01-07 08:21 | EST | 2014-01-07 13:21 | 0 | 59.9877 | 59.9564 | 59.958 | -0.031263 | -0.029688 |  |  | No | No | 59.5 | 0.458 | 2014
EI_2014-01-07_184351 | 2014-01-07 13:44 | 2014-01-07 13:44 | EST | 2014-01-07 18:44 | 505 | 60.0159 | 59.9994 | 59.997 | -0.016451 | -0.018875 | -3069.7674 | -2675.4967 | No | No | 59.5 | 0.497 | 2014
EI_2014-01-09_091500 | 2014-01-09 04:15 | 2014-01-09 04:15 | EST | 2014-01-09 09:15 | 470 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.5 | -59.5 | 2014
EI_2014-01-10_033426 | 2014-01-09 22:34 | 2014-01-09 22:34 | EST | 2014-01-10 03:34 | 750 | 60.0091 | 59.9801 | 59.979 | -0.028941 | -0.030062 | -2591.4534 | -2494.8025 | No | No | 59.5 | 0.479 | 2014
EI_2014-01-10_164236 | 2014-01-10 11:43 | 2014-01-10 11:43 | EST | 2014-01-10 16:43 | 620 | 60.0185 | 59.9789 | 59.988 | -0.039561 | -0.0305 | -1567.2156 | -2032.7869 | No | No | 59.5 | 0.488 | 2014
EI_2014-01-10_164441 | 2014-01-10 11:45 | 2014-01-10 11:45 | EST | 2014-01-10 16:45 | 792 | 59.9896 | 59.9676 | 59.961 | -0.022019 | -0.028625 | -3596.9035 | -2766.8122 | No | No | 59.5 | 0.461 | 2014
EI_2014-01-11_061531 | 2014-01-11 01:16 | 2014-01-11 01:16 | EST | 2014-01-11 06:16 | 0 | 60.0168 | 59.9575 | 59.979 | -0.059297 | -0.037813 |  |  | No | No | 59.5 | 0.479 | 2014
EI_2014-01-11_230037 | 2014-01-11 18:01 | 2014-01-11 18:01 | EST | 2014-01-11 23:01 | 0 | 60.0061 | 59.9825 | 59.978 | -0.02358 | -0.028125 |  |  | No | No | 59.5 | 0.478 | 2014
EI_2014-01-12_000936 | 2014-01-11 19:10 | 2014-01-11 19:10 | EST | 2014-01-12 00:10 | 0 | 60.0267 | 59.9797 | 59.999 | -0.046991 | -0.027687 |  |  | No | No | 59.5 | 0.499 | 2014
EI_2014-01-14_063011 | 2014-01-14 01:30 | 2014-01-14 01:30 | EST | 2014-01-14 06:30 | 0 | 60.0201 | 60.0614 | 60.061 | 0.041331 | 0.040937 |  |  | No | No | 59.5 | 0.561 | 2014
EI_2014-01-15_072356 | 2014-01-15 02:24 | 2014-01-15 02:24 | EST | 2014-01-15 07:24 | 0 | 59.9904 | 59.9635 | 59.96 | -0.026892 | -0.030437 |  |  | No | No | 59.5 | 0.46 | 2014
EI_2014-01-15_235224 | 2014-01-15 18:52 | 2014-01-15 18:52 | EST | 2014-01-15 23:52 | 761 | 60.0112 | 59.9799 | 59.972 | -0.031311 | -0.03925 | -2430.4863 | -1938.8535 | No | No | 59.5 | 0.472 | 2014
EI_2014-01-16_082133 | 2014-01-16 03:22 | 2014-01-16 03:22 | EST | 2014-01-16 08:22 | 1023 | 59.9869 | 59.9571 | 59.953 | -0.029754 | -0.033875 | -3438.2177 | -3019.9262 | No | No | 59.5 | 0.453 | 2014
EI_2014-01-16_202959 | 2014-01-16 15:30 | 2014-01-16 15:30 | EST | 2014-01-16 20:30 | 0 | 59.9956 | 60.0407 | 60.031 | 0.045042 | 0.035375 |  |  | No | No | 59.5 | 0.531 | 2014
EI_2014-01-18_012900 | 2014-01-17 20:29 | 2014-01-17 20:29 | EST | 2014-01-18 01:29 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.5 | -59.5 | 2014
EI_2014-01-18_075436 | 2014-01-18 02:55 | 2014-01-18 02:55 | EST | 2014-01-18 07:55 | 435 | 59.9944 | 59.9758 | 59.975 | -0.018587 | -0.019375 | -2340.3301 | -2245.1613 | No | No | 59.5 | 0.475 | 2014
EI_2014-01-18_105849 | 2014-01-18 05:59 | 2014-01-18 05:59 | EST | 2014-01-18 10:59 | 0 | 59.9698 | 59.9468 | 59.94 | -0.022964 | -0.029813 |  |  | No | No | 59.5 | 0.44 | 2014
EI_2014-01-18_143038 | 2014-01-18 09:31 | 2014-01-18 09:31 | EST | 2014-01-18 14:31 | 0 | 60.0019 | 59.9635 | 59.961 | -0.03833 | -0.040875 |  |  | No | No | 59.5 | 0.461 | 2014
EI_2014-01-19_221200 | 2014-01-19 17:12 | 2014-01-19 17:12 | EST | 2014-01-19 22:12 | 0 | 59.9765 | 60.0216 | 60.017 | 0.045076 | 0.0405 |  |  | No | No | 59.5 | 0.517 | 2014
EI_2014-01-21_024711 | 2014-01-20 21:47 | 2014-01-20 21:47 | EST | 2014-01-21 02:47 | 0 | 60.0017 | 59.9563 | 59.9625 | -0.045449 | -0.039223 |  |  | No | No | 59.5 | 0.4625 | 2014
EI_2014-01-21_104601 | 2014-01-21 05:46 | 2014-01-21 05:46 | EST | 2014-01-21 10:46 | 241 | 60.0094 | 60.0009 | 60.007 | -0.0084981 | -0.0024375 | -2835.926 | -9887.1795 | No | No | 59.5 | 0.507 | 2014
EI_2014-01-21_185002 | 2014-01-21 13:50 | 2014-01-21 13:50 | EST | 2014-01-21 18:50 | 1320 | 60.0115 | 59.9541 | 59.9566 | -0.057361 | -0.0549 | -2301.215 | -2404.3537 | Yes | Yes | 59.5 | 0.4566 | 2014
EI_2014-01-22_022529 | 2014-01-21 21:25 | 2014-01-21 21:25 | EST | 2014-01-22 02:25 | 1863 | 59.9794 | 59.9361 | 59.939 | -0.043284 | -0.040375 | -4304.1218 | -4614.2415 | Yes | No | 59.5 | 0.439 | 2014
EI_2014-01-22_093653 | 2014-01-22 04:37 | 2014-01-22 04:37 | EST | 2014-01-22 09:37 | 857 | 60.0048 | 59.9726 | 59.976 | -0.032176 | -0.028813 | -2663.4646 | -2974.4035 | No | No | 59.5 | 0.476 | 2014
EI_2014-01-24_133605 | 2014-01-24 08:36 | 2014-01-24 08:36 | EST | 2014-01-24 13:36 | 847 | 60.0281 | 60.0021 | 60.002 | -0.026002 | -0.026062 | -3257.455 | -3249.8801 | No | No | 59.5 | 0.502 | 2014
EI_2014-01-24_185442 | 2014-01-24 13:55 | 2014-01-24 13:55 | EST | 2014-01-24 18:55 | 505 | 60.0009 | 59.9717 | 59.971 | -0.029178 | -0.029875 | -1730.7543 | -1690.3766 | No | No | 59.5 | 0.471 | 2014
EI_2014-01-26_170924 | 2014-01-26 12:09 | 2014-01-26 12:09 | EST | 2014-01-26 17:09 | 1241 | 59.9993 | 59.9555 | 59.95 | -0.043705 | -0.04925 | -2839.5216 | -2519.797 | Yes | Yes | 59.5 | 0.45 | 2014
EI_2014-01-31_142352 | 2014-01-31 09:24 | 2014-01-31 09:24 | EST | 2014-01-31 14:24 | 915 | 60.0032 | 59.9719 | 59.9705 | -0.03126 | -0.032699 | -2927.0262 | -2798.2211 | No | No | 59.5 | 0.4705 | 2014
EI_2014-01-31_150018 | 2014-01-31 10:00 | 2014-01-31 10:00 | EST | 2014-01-31 15:00 | 1130 | 59.9841 | 59.9633 | 59.9627 | -0.020796 | -0.021381 | -5433.7101 | -5285.0316 | No | No | 59.5 | 0.4627 | 2014
EI_2014-02-02_064342 | 2014-02-02 01:44 | 2014-02-02 01:44 | EST | 2014-02-02 06:44 | 0 | 60.009 | 59.9718 | 59.973 | -0.037138 | -0.035963 |  |  | No | No | 59.5 | 0.473 | 2014
EI_2014-02-02_135846 | 2014-02-02 08:59 | 2014-02-02 08:59 | EST | 2014-02-02 13:59 | 1032 | 59.9894 | 59.9554 | 59.9454 | -0.034017 | -0.043981 | -3033.7605 | -2346.4892 | Yes | Yes | 59.5 | 0.4454 | 2014
EI_2014-02-02_232438 | 2014-02-02 18:25 | 2014-02-02 18:25 | EST | 2014-02-02 23:25 | 0 | 60.0188 | 59.9695 | 59.9821 | -0.049242 | -0.036674 |  |  | No | No | 59.5 | 0.4821 | 2014
EI_2014-02-02_234434 | 2014-02-02 18:45 | 2014-02-02 18:45 | EST | 2014-02-02 23:45 | 0 | 60.0516 | 60.0037 | 60.0153 | -0.047918 | -0.036311 |  |  | No | No | 59.5 | 0.5153 | 2014
EI_2014-02-02_235404 | 2014-02-02 18:54 | 2014-02-02 18:54 | EST | 2014-02-02 23:54 | 0 | 60.0454 | 60.0098 | 60.0117 | -0.035592 | -0.033669 |  |  | No | No | 59.5 | 0.5117 | 2014
EI_2014-02-03_011900 | 2014-02-02 20:19 | 2014-02-02 20:19 | EST | 2014-02-03 01:19 | 0 | 60.0184 | 60.0358 | 60.06 | 0.01739 | 0.041589 |  |  | No | No | 59.5 | 0.56 | 2014
EI_2014-02-03_011942 | 2014-02-02 20:20 | 2014-02-02 20:20 | EST | 2014-02-03 01:20 | 0 | 60.0279 | 60.0566 | 60.0573 | 0.028712 | 0.029401 |  |  | No | No | 59.5 | 0.5573 | 2014
EI_2014-02-03_012224 | 2014-02-02 20:22 | 2014-02-02 20:22 | EST | 2014-02-03 01:22 | 0 | 60.0253 | 60.0021 | 59.9874 | -0.023243 | -0.037894 |  |  | No | No | 59.5 | 0.4874 | 2014
EI_2014-02-03_021325 | 2014-02-02 21:13 | 2014-02-02 21:13 | EST | 2014-02-03 02:13 | 0 | 60.0219 | 59.9849 | 59.9905 | -0.03704 | -0.031423 |  |  | No | No | 59.5 | 0.4905 | 2014
EI_2014-02-03_041817 | 2014-02-02 23:18 | 2014-02-02 23:18 | EST | 2014-02-03 04:18 | 880 | 60.0186 | 59.9633 | 59.9696 | -0.055319 | -0.049049 | -1590.7603 | -1794.1192 | No | No | 59.5 | 0.4696 | 2014
EI_2014-02-07_105213 | 2014-02-07 05:52 | 2014-02-07 05:52 | EST | 2014-02-07 10:52 | 837 | 60.0261 | 59.9663 | 59.985 | -0.059764 | -0.041106 | -1400.5112 | -2036.2116 | No | No | 59.5 | 0.485 | 2014
EI_2014-02-16_035350 | 2014-02-15 22:54 | 2014-02-15 22:54 | EST | 2014-02-16 03:54 | 1236 | 60.0044 | 59.9568 | 59.9526 | -0.047534 | -0.05177 | -2600.217 | -2387.4954 | Yes | Yes | 59.5 | 0.4526 | 2014
EI_2014-02-16_075409 | 2014-02-16 02:54 | 2014-02-16 02:54 | EST | 2014-02-16 07:54 | 0 | 59.9986 | 59.9553 | 59.9617 | -0.04329 | -0.036887 |  |  | No | No | 59.5 | 0.4617 | 2014
EI_2014-02-18_213341 | 2014-02-18 16:34 | 2014-02-18 16:34 | EST | 2014-02-18 21:34 | 0 | 60.0098 | 59.9739 | 59.9686 | -0.035888 | -0.041199 |  |  | No | No | 59.5 | 0.4686 | 2014
EI_2014-02-19_023753 | 2014-02-18 21:38 | 2014-02-18 21:38 | EST | 2014-02-19 02:38 | 917 | 60.0036 | 59.9606 | 59.9625 | -0.043049 | -0.041136 | -2130.1124 | -2229.2154 | No | No | 59.5 | 0.4625 | 2014
EI_2014-02-19_053233 | 2014-02-19 00:33 | 2014-02-19 00:33 | EST | 2014-02-19 05:33 | 846 | 60.0015 | 59.9588 | 59.96 | -0.042764 | -0.041526 | -1978.2889 | -2037.2857 | Yes | Yes | 59.5 | 0.46 | 2014
EI_2014-02-22_140306 | 2014-02-22 09:03 | 2014-02-22 09:03 | EST | 2014-02-22 14:03 | 0 | 59.9836 | 59.9498 | 59.9489 | -0.033806 | -0.034714 |  |  | No | No | 59.5 | 0.4489 | 2014
EI_2014-02-23_063423 | 2014-02-23 01:34 | 2014-02-23 01:34 | EST | 2014-02-23 06:34 | 0 | 60.0204 | 59.971 | 59.9806 | -0.049405 | -0.039851 |  |  | No | No | 59.5 | 0.4806 | 2014
EI_2014-02-23_173202 | 2014-02-23 12:32 | 2014-02-23 12:32 | EST | 2014-02-23 17:32 | 1070 | 59.985 | 59.936 | 59.9436 | -0.049083 | -0.04145 | -2179.9968 | -2581.4516 | Yes | Yes | 59.5 | 0.4436 | 2014
EI_2014-02-27_151400 | 2014-02-27 10:14 | 2014-02-27 10:14 | EST | 2014-02-27 15:14 | 1059 | 59.9659 | 59.9283 | 59.9301 | -0.037598 | -0.035807 | -2816.6687 | -2957.531 | No | No | 59.5 | 0.4301 | 2014
EI_2014-03-01_042612 | 2014-02-28 23:26 | 2014-02-28 23:26 | EST | 2014-03-01 04:26 | 0 | 59.9901 | 59.9498 | 59.9584 | -0.040247 | -0.031668 |  |  | No | No | 59.5 | 0.4584 | 2014
EI_2014-03-01_051317 | 2014-03-01 00:13 | 2014-03-01 00:13 | EST | 2014-03-01 05:13 | 0 | 59.9845 | 59.9505 | 59.9522 | -0.033944 | -0.032261 |  |  | No | No | 59.5 | 0.4522 | 2014
EI_2014-03-02_000006 | 2014-03-01 19:00 | 2014-03-01 19:00 | EST | 2014-03-02 | 0 | 60.0057 | 59.9601 | 59.9658 | -0.045625 | -0.03993 |  |  | No | No | 59.5 | 0.4658 | 2014
EI_2014-03-04_064205 | 2014-03-04 01:42 | 2014-03-04 01:42 | EST | 2014-03-04 06:42 | 0 | 59.9995 | 59.9545 | 59.9613 | -0.045096 | -0.03825 |  |  | No | No | 59.5 | 0.4613 | 2014
EI_2014-03-05_042258 | 2014-03-04 23:23 | 2014-03-04 23:23 | EST | 2014-03-05 04:23 | 1170 | 59.9958 | 59.9684 | 59.9686 | -0.027363 | -0.027173 | -4275.9231 | -4305.7002 | No | No | 59.5 | 0.4686 | 2014
EI_2014-03-05_212417 | 2014-03-05 16:24 | 2014-03-05 16:24 | EST | 2014-03-05 21:24 | 1170 | 59.9852 | 59.9449 | 59.9461 | -0.040334 | -0.039126 | -2900.8008 | -2990.3086 | Yes | Yes | 59.5 | 0.4461 | 2014
EI_2014-03-09_110948 | 2014-03-09 07:10 | 2014-03-09 07:10 | EDT | 2014-03-09 11:10 | 0 | 59.9634 | 60.0138 | 60.0043 | 0.050463 | 0.040931 |  |  | No | No | 59.5 | 0.5043 | 2014
EI_2014-03-10_183139 | 2014-03-10 14:32 | 2014-03-10 14:32 | EDT | 2014-03-10 18:32 | 0 | 59.9963 | 59.9531 | 59.9612 | -0.043203 | -0.035124 |  |  | No | No | 59.5 | 0.4612 | 2014
EI_2014-03-13_203347 | 2014-03-13 16:34 | 2014-03-13 16:34 | EDT | 2014-03-13 20:34 | 1000 | 60.021 | 59.9618 | 59.9666 | -0.059217 | -0.054376 | -1688.6915 | -1839.0343 | No | No | 59.5 | 0.4666 | 2014
EI_2014-03-14_043017 | 2014-03-14 00:30 | 2014-03-14 00:30 | EDT | 2014-03-14 04:30 | 0 | 59.9996 | 59.9611 | 59.9647 | -0.038536 | -0.034889 |  |  | No | No | 59.5 | 0.4647 | 2014
EI_2014-03-19_085844 | 2014-03-19 04:59 | 2014-03-19 04:59 | EDT | 2014-03-19 08:59 | 0 | 60.0011 | 60.0397 | 60.0378 | 0.038587 | 0.036693 |  |  | No | No | 59.5 | 0.5378 | 2014
EI_2014-03-25_195832 | 2014-03-25 15:59 | 2014-03-25 15:59 | EDT | 2014-03-25 19:59 | 0 | 59.9914 | 59.9579 | 59.9563 | -0.033473 | -0.035113 |  |  | No | No | 59.5 | 0.4563 | 2014
EI_2014-03-27_160808 | 2014-03-27 12:08 | 2014-03-27 12:08 | EDT | 2014-03-27 16:08 | 0 | 59.9928 | 59.9679 | 59.9601 | -0.024959 | -0.032739 |  |  | No | No | 59.5 | 0.4601 | 2014
EI_2014-03-27_220449 | 2014-03-27 18:05 | 2014-03-27 18:05 | EDT | 2014-03-27 22:05 | 0 | 59.9715 | 60.0341 | 60.0166 | 0.06262 | 0.045146 |  |  | No | No | 59.5 | 0.5166 | 2014
EI_2014-03-29_113931 | 2014-03-29 07:40 | 2014-03-29 07:40 | EDT | 2014-03-29 11:40 | 0 | 59.9734 | 60.0218 | 60.0148 | 0.048405 | 0.04137 |  |  | No | No | 59.5 | 0.5148 | 2014
EI_2014-03-29_150742 | 2014-03-29 11:08 | 2014-03-29 11:08 | EDT | 2014-03-29 15:08 | 1228 | 60.0066 | 59.9513 | 59.9525 | -0.055278 | -0.054088 | -2221.4819 | -2270.3693 | Yes | No | 59.5 | 0.4525 | 2014
EI_2014-03-30_170511 | 2014-03-30 13:05 | 2014-03-30 13:05 | EDT | 2014-03-30 17:05 | 824 | 60.0101 | 59.9722 | 59.9746 | -0.037933 | -0.035498 | -2172.2472 | -2321.2638 | No | No | 59.5 | 0.4746 | 2014
EI_2014-03-30_213747 | 2014-03-30 17:38 | 2014-03-30 17:38 | EDT | 2014-03-30 21:38 | 435 | 59.9945 | 59.9727 | 59.9695 | -0.021782 | -0.024999 | -1997.0664 | -1740.0929 | No | No | 59.5 | 0.4695 | 2014
EI_2014-04-01_090331 | 2014-04-01 05:04 | 2014-04-01 05:04 | EDT | 2014-04-01 09:04 | 0 | 59.9771 | 60.0245 | 60.0161 | 0.047459 | 0.039051 |  |  | No | No | 59.5 | 0.5161 | 2014
EI_2014-04-01_165420 | 2014-04-01 12:54 | 2014-04-01 12:54 | EDT | 2014-04-01 16:54 | 0 | 60.0003 | 59.9597 | 59.9623 | -0.04065 | -0.038044 |  |  | No | No | 59.5 | 0.4623 | 2014
EI_2014-04-03_032739 | 2014-04-02 23:28 | 2014-04-02 23:28 | EDT | 2014-04-03 03:28 | 694 | 60.0243 | 59.9791 | 59.9851 | -0.045244 | -0.039244 | -1533.9131 | -1768.4261 | No | No | 59.5 | 0.4851 | 2014
EI_2014-04-03_123635 | 2014-04-03 08:37 | 2014-04-03 08:37 | EDT | 2014-04-03 12:37 | 1268 | 59.9866 | 59.9462 | 59.9433 | -0.040414 | -0.043288 | -3137.5506 | -2929.1865 | Yes | Yes | 59.5 | 0.4433 | 2014
EI_2014-04-03_180037 | 2014-04-03 14:01 | 2014-04-03 14:01 | EDT | 2014-04-03 18:01 | 1004 | 59.9762 | 59.9435 | 59.9325 | -0.03266 | -0.043689 | -3074.1063 | -2298.0857 | Yes | Yes | 59.5 | 0.4325 | 2014
EI_2014-04-03_183201 | 2014-04-03 14:32 | 2014-04-03 14:32 | EDT | 2014-04-03 18:32 | 547 | 59.9913 | 59.9581 | 59.9602 | -0.033196 | -0.031092 | -1647.7644 | -1759.2856 | No | No | 59.5 | 0.4602 | 2014
EI_2014-04-03_204724 | 2014-04-03 16:47 | 2014-04-03 16:47 | EDT | 2014-04-03 20:47 | 0 | 60.0059 | 59.9738 | 59.9681 | -0.032102 | -0.037767 |  |  | No | No | 59.5 | 0.4681 | 2014
EI_2014-04-04_163058 | 2014-04-04 12:31 | 2014-04-04 12:31 | EDT | 2014-04-04 16:31 | 800 | 59.9921 | 59.9458 | 59.9478 | -0.046373 | -0.044331 | -1725.1295 | -1804.5935 | Yes | No | 59.5 | 0.4478 | 2014
EI_2014-04-05_232700 | 2014-04-05 19:27 | 2014-04-05 19:27 | EDT | 2014-04-05 23:27 | 0 | 60.0083 | 59.9744 | 59.9705 | -0.033921 | -0.037786 |  |  | No | No | 59.5 | 0.4705 | 2014
EI_2014-04-07_092318 | 2014-04-07 05:23 | 2014-04-07 05:23 | EDT | 2014-04-07 09:23 | 0 | 59.981 | 60.0368 | 60.0172 | 0.05578 | 0.036207 |  |  | No | No | 59.5 | 0.5172 | 2014
EI_2014-04-08_024842 | 2014-04-07 22:49 | 2014-04-07 22:49 | EDT | 2014-04-08 02:49 | 0 | 59.999 | 59.9622 | 59.9572 | -0.036807 | -0.041832 |  |  | No | No | 59.5 | 0.4572 | 2014
EI_2014-04-08_082756 | 2014-04-08 04:28 | 2014-04-08 04:28 | EDT | 2014-04-08 08:28 | 1225 | 60.0038 | 59.9476 | 59.9432 | -0.056236 | -0.060589 | -2178.3233 | -2021.8325 | Yes | Yes | 59.5 | 0.4432 | 2014
EI_2014-04-09_011418 | 2014-04-08 21:14 | 2014-04-08 21:14 | EDT | 2014-04-09 01:14 | 0 | 59.984 | 59.9569 | 59.9571 | -0.02705 | -0.026856 |  |  | No | No | 59.5 | 0.4571 | 2014
EI_2014-04-10_051012 | 2014-04-10 01:10 | 2014-04-10 01:10 | EDT | 2014-04-10 05:10 | 0 | 59.9679 | 60.0128 | 60.0133 | 0.044903 | 0.045403 |  |  | No | No | 59.5 | 0.5133 | 2014
EI_2014-04-11_094935 | 2014-04-11 05:50 | 2014-04-11 05:50 | EDT | 2014-04-11 09:50 | 0 | 59.9806 | 60.0317 | 60.0293 | 0.051034 | 0.048656 |  |  | No | No | 59.5 | 0.5293 | 2014
EI_2014-04-11_101044 | 2014-04-11 06:11 | 2014-04-11 06:11 | EDT | 2014-04-11 10:11 | 0 | 59.9821 | 60.0418 | 60.0242 | 0.059665 | 0.042075 |  |  | No | No | 59.5 | 0.5242 | 2014
EI_2014-04-12_151155 | 2014-04-12 11:12 | 2014-04-12 11:12 | EDT | 2014-04-12 15:12 | 0 | 59.9812 | 59.9515 | 59.9464 | -0.029752 | -0.034826 |  |  | No | No | 59.5 | 0.4464 | 2014
EI_2014-04-13_004832 | 2014-04-12 20:49 | 2014-04-12 20:49 | EDT | 2014-04-13 00:49 | 0 | 59.9977 | 59.9544 | 59.9573 | -0.043314 | -0.040452 |  |  | No | No | 59.5 | 0.4573 | 2014
EI_2014-04-13_172438 | 2014-04-13 13:25 | 2014-04-13 13:25 | EDT | 2014-04-13 17:25 | 0 | 60.0018 | 59.9494 | 59.9585 | -0.052344 | -0.043281 |  |  | No | No | 59.5 | 0.4585 | 2014
EI_2014-04-14_011231 | 2014-04-13 21:13 | 2014-04-13 21:13 | EDT | 2014-04-14 01:13 | 0 | 60.0216 | 59.9574 | 59.958 | -0.064253 | -0.06362 |  |  | No | No | 59.5 | 0.458 | 2014
EI_2014-04-17_160948 | 2014-04-17 12:10 | 2014-04-17 12:10 | EDT | 2014-04-17 16:10 | 0 | 60.0184 | 59.9662 | 59.9724 | -0.052189 | -0.046037 |  |  | No | No | 59.5 | 0.4724 | 2014
EI_2014-04-18_183405 | 2014-04-18 14:34 | 2014-04-18 14:34 | EDT | 2014-04-18 18:34 | 0 | 59.9899 | 59.9636 | 59.9557 | -0.026353 | -0.034232 |  |  | No | No | 59.5 | 0.4557 | 2014
EI_2014-04-20_033143 | 2014-04-19 23:32 | 2014-04-19 23:32 | EDT | 2014-04-20 03:32 | 824 | 60.0338 | 59.9965 | 59.9998 | -0.037242 | -0.033986 | -2212.5501 | -2424.5552 | No | No | 59.5 | 0.4998 | 2014
EI_2014-04-20_152125 | 2014-04-20 11:21 | 2014-04-20 11:21 | EDT | 2014-04-20 15:21 | 790 | 60.0043 | 59.9508 | 59.9536 | -0.05355 | -0.050724 | -1475.2628 | -1557.4619 | No | No | 59.5 | 0.4536 | 2014
EI_2014-04-20_153717 | 2014-04-20 11:37 | 2014-04-20 11:37 | EDT | 2014-04-20 15:37 | 0 | 60.0084 | 59.9689 | 59.9716 | -0.039528 | -0.036831 |  |  | No | No | 59.5 | 0.4716 | 2014
EI_2014-04-24_162210 | 2014-04-24 12:22 | 2014-04-24 12:22 | EDT | 2014-04-24 16:22 | 398 | 60.0108 | 59.9871 | 59.9906 | -0.023755 | -0.020205 | -1675.4606 | -1969.7842 | No | No | 59.5 | 0.4906 | 2014
EI_2014-04-25_101440 | 2014-04-25 06:15 | 2014-04-25 06:15 | EDT | 2014-04-25 10:15 | 0 | 59.9876 | 60.0256 | 60.0298 | 0.037926 | 0.042156 |  |  | No | No | 59.5 | 0.5298 | 2014
EI_2014-04-25_173023 | 2014-04-25 13:30 | 2014-04-25 13:30 | EDT | 2014-04-25 17:30 | 1692 | 60.0004 | 59.9395 | 59.9378 | -0.060872 | -0.062562 | -2779.6052 | -2704.5279 | Yes | Yes | 59.5 | 0.4378 | 2014
EI_2014-04-30_084301 | 2014-04-30 04:43 | 2014-04-30 04:43 | EDT | 2014-04-30 08:43 | 930 | 59.9816 | 59.9463 | 59.9433 | -0.035238 | -0.038257 | -2639.2246 | -2430.9048 | Yes | No | 59.5 | 0.4433 | 2014
EI_2014-04-30_202811 | 2014-04-30 16:28 | 2014-04-30 16:28 | EDT | 2014-04-30 20:28 | 0 | 60.0079 | 59.9711 | 59.9723 | -0.036821 | -0.035605 |  |  | No | No | 59.5 | 0.4723 | 2014
EI_2014-05-01_100353 | 2014-05-01 06:04 | 2014-05-01 06:04 | EDT | 2014-05-01 10:04 | 0 | 59.9588 | 60.0004 | 59.992 | 0.041578 | 0.033172 |  |  | No | No | 59.5 | 0.49202 | 2014
EI_2014-05-01_141700 | 2014-05-01 10:17 | 2014-05-01 10:17 | EDT | 2014-05-01 14:17 | 942 | 59.996 | 59.9447 | 59.9462 | -0.051302 | -0.049851 | -1836.185 | -1889.6424 | Yes | Yes | 59.5 | 0.44616 | 2014
EI_2014-05-01_142237 | 2014-05-01 10:23 | 2014-05-01 10:23 | EDT | 2014-05-01 14:23 | 0 | 59.985 | 59.9692 | 59.9515 | -0.015782 | -0.033514 |  |  | No | No | 59.5 | 0.45148 | 2014
EI_2014-05-02_031652 | 2014-05-01 23:17 | 2014-05-01 23:17 | EDT | 2014-05-02 03:17 | 625 | 60.0072 | 59.9846 | 59.984 | -0.022589 | -0.023218 | -2766.7975 | -2691.9143 | No | No | 59.5 | 0.48397 | 2014
EI_2014-05-02_191459 | 2014-05-02 15:15 | 2014-05-02 15:15 | EDT | 2014-05-02 19:15 | 0 | 60.007 | 59.9667 | 59.9709 | -0.040319 | -0.036151 |  |  | No | No | 59.5 | 0.47087 | 2014
EI_2014-05-03_041830 | 2014-05-03 00:19 | 2014-05-03 00:19 | EDT | 2014-05-03 04:19 | 0 | 60.0112 | 59.9685 | 59.9694 | -0.042722 | -0.041883 |  |  | No | No | 59.5 | 0.46935 | 2014
EI_2014-05-03_170936 | 2014-05-03 13:10 | 2014-05-03 13:10 | EDT | 2014-05-03 17:10 | 792 | 59.9712 | 59.9434 | 59.9296 | -0.027754 | -0.041575 | -2853.6832 | -1905.004 | No | No | 59.5 | 0.4296 | 2014
EI_2014-05-04_004811 | 2014-05-03 20:48 | 2014-05-03 20:48 | EDT | 2014-05-04 00:48 | 0 | 59.9854 | 59.9532 | 59.949 | -0.032185 | -0.036358 |  |  | No | No | 59.5 | 0.44905 | 2014
EI_2014-05-04_021250 | 2014-05-03 22:13 | 2014-05-03 22:13 | EDT | 2014-05-04 02:13 | 792 | 59.9947 | 59.9472 | 59.9491 | -0.047476 | -0.045607 | -1668.2013 | -1736.5812 | No | No | 59.5 | 0.44912 | 2014
EI_2014-05-04_121152 | 2014-05-04 08:12 | 2014-05-04 08:12 | EDT | 2014-05-04 12:12 | 0 | 59.9604 | 60.0068 | 59.9932 | 0.046359 | 0.03284 |  |  | No | No | 59.5 | 0.49324 | 2014
EI_2014-05-06_133123 | 2014-05-06 09:31 | 2014-05-06 09:31 | EDT | 2014-05-06 13:31 | 1067 | 59.9981 | 59.9435 | 59.9566 | -0.054613 | -0.041482 | -1953.7321 | -2572.2165 | Yes | No | 59.5 | 0.45662 | 2014
EI_2014-05-07_085639 | 2014-05-07 04:57 | 2014-05-07 04:57 | EDT | 2014-05-07 08:57 | 1204 | 60.0137 | 59.9671 | 59.9631 | -0.046595 | -0.050645 | -2583.9589 | -2377.3383 | No | No | 59.5 | 0.46305 | 2014
EI_2014-05-07_093502 | 2014-05-07 05:35 | 2014-05-07 05:35 | EDT | 2014-05-07 09:35 | 0 | 59.9563 | 59.9839 | 59.9876 | 0.027631 | 0.031332 |  |  | No | No | 59.5 | 0.48761 | 2014
EI_2014-05-07_182713 | 2014-05-07 14:27 | 2014-05-07 14:27 | EDT | 2014-05-07 18:27 | 642 | 59.9888 | 59.9595 | 59.9588 | -0.029315 | -0.029955 | -2189.972 | -2143.1871 | No | No | 59.5 | 0.45884 | 2014
EI_2014-05-09_020608 | 2014-05-08 22:06 | 2014-05-08 22:06 | EDT | 2014-05-09 02:06 | 0 | 59.9883 | 59.9697 | 59.9549 | -0.018604 | -0.033487 |  |  | No | No | 59.5 | 0.45486 | 2014
EI_2014-05-11_110205 | 2014-05-11 07:02 | 2014-05-11 07:02 | EDT | 2014-05-11 11:02 | 0 | 59.9603 | 60.0109 | 59.9951 | 0.050641 | 0.034765 |  |  | No | No | 59.5 | 0.49506 | 2014
EI_2014-05-11_231914 | 2014-05-11 19:19 | 2014-05-11 19:19 | EDT | 2014-05-11 23:19 | 590 | 60.0046 | 59.973 | 59.9771 | -0.031678 | -0.027483 | -1862.4651 | -2146.82 | No | No | 59.5 | 0.47715 | 2014
EI_2014-05-11_233755 | 2014-05-11 19:38 | 2014-05-11 19:38 | EDT | 2014-05-11 23:38 | 887 | 60.017 | 59.9487 | 59.9507 | -0.068217 | -0.066206 | -1300.2641 | -1339.7533 | Yes | No | 59.5 | 0.45075 | 2014
EI_2014-05-13_101836 | 2014-05-13 06:19 | 2014-05-13 06:19 | EDT | 2014-05-13 10:19 | 0 | 60.0043 | 60.0466 | 60.0426 | 0.042373 | 0.038293 |  |  | No | No | 59.5 | 0.54256 | 2014
EI_2014-05-14_005534 | 2014-05-13 20:56 | 2014-05-13 20:56 | EDT | 2014-05-14 00:56 | 0 | 59.9924 | 59.9657 | 59.9578 | -0.026687 | -0.034602 |  |  | No | No | 59.5 | 0.45776 | 2014
EI_2014-05-14_013457 | 2014-05-13 21:35 | 2014-05-13 21:35 | EDT | 2014-05-14 01:35 | 1475 | 60.0051 | 59.95 | 59.9647 | -0.055142 | -0.040433 | -2674.9097 | -3648.0381 | No | No | 59.5 | 0.46467 | 2014
EI_2014-05-14_060355 | 2014-05-14 02:04 | 2014-05-14 02:04 | EDT | 2014-05-14 06:04 | 419 | 60.0147 | 59.9769 | 59.9816 | -0.037863 | -0.0331 | -1106.6127 | -1265.8652 | No | No | 59.5 | 0.48162 | 2014
EI_2014-05-15_003805 | 2014-05-14 20:38 | 2014-05-14 20:38 | EDT | 2014-05-15 00:38 | 202 | 59.9906 | 59.9708 | 59.9657 | -0.019865 | -0.024968 | -1016.8402 | -809.0385 | No | No | 59.5 | 0.46567 | 2014
EI_2014-05-16_175025 | 2014-05-16 13:50 | 2014-05-16 13:50 | EDT | 2014-05-16 17:50 | 470 | 60.0096 | 59.9622 | 59.9717 | -0.047396 | -0.037879 | -991.6385 | -1240.8012 | No | No | 59.5 | 0.47168 | 2014
EI_2014-05-17_000939 | 2014-05-16 20:10 | 2014-05-16 20:10 | EDT | 2014-05-17 00:10 | 0 | 59.9921 | 59.9534 | 59.9574 | -0.0387 | -0.03476 |  |  | No | No | 59.5 | 0.45736 | 2014
EI_2014-05-18_000907 | 2014-05-17 20:09 | 2014-05-17 20:09 | EDT | 2014-05-18 00:09 | 467 | 60.0041 | 59.9894 | 59.9856 | -0.014702 | -0.018457 | -3176.41 | -2530.1488 | No | No | 59.5 | 0.48561 | 2014
EI_2014-05-18_142701 | 2014-05-18 10:27 | 2014-05-18 10:27 | EDT | 2014-05-18 14:27 | 590 | 60.014 | 59.9604 | 59.9641 | -0.053675 | -0.049885 | -1099.1991 | -1182.7307 | No | No | 59.5 | 0.46415 | 2014
EI_2014-05-20_120346 | 2014-05-20 08:04 | 2014-05-20 08:04 | EDT | 2014-05-20 12:04 | 0 | 59.9949 | 60.0422 | 60.0331 | 0.047313 | 0.038226 |  |  | No | No | 59.5 | 0.5331 | 2014
EI_2014-05-20_194855 | 2014-05-20 15:49 | 2014-05-20 15:49 | EDT | 2014-05-20 19:49 | 0 | 59.9817 | 59.9512 | 59.9442 | -0.030513 | -0.037526 |  |  | No | No | 59.5 | 0.44415 | 2014
EI_2014-05-21_165753 | 2014-05-21 12:58 | 2014-05-21 12:58 | EDT | 2014-05-21 16:58 | 0 | 59.9962 | 59.9735 | 59.9628 | -0.022655 | -0.033412 |  |  | No | No | 59.5 | 0.46277 | 2014
EI_2014-05-22_161017 | 2014-05-22 12:10 | 2014-05-22 12:10 | EDT | 2014-05-22 16:10 | 1500 | 60.0096 | 59.9429 | 59.9448 | -0.06677 | -0.064857 | -2246.5333 | -2312.7972 | No | Yes | 59.5 | 0.44477 | 2014
EI_2014-05-23_092015 | 2014-05-23 05:20 | 2014-05-23 05:20 | EDT | 2014-05-23 09:20 | 0 | 59.9824 | 60.0209 | 60.0173 | 0.038501 | 0.0349 |  |  | No | No | 59.5 | 0.51734 | 2014
EI_2014-05-24_083843 | 2014-05-24 04:39 | 2014-05-24 04:39 | EDT | 2014-05-24 08:39 | 600 | 60.0016 | 59.9678 | 59.9746 | -0.033747 | -0.026938 | -1777.9137 | -2227.3597 | No | No | 59.5 | 0.47464 | 2014
EI_2014-05-24_215344 | 2014-05-24 17:54 | 2014-05-24 17:54 | EDT | 2014-05-24 21:54 | 790 | 60.0158 | 59.9622 | 59.9682 | -0.053583 | -0.047565 | -1474.3466 | -1660.9023 | No | No | 59.5 | 0.46824 | 2014
EI_2014-05-25_110146 | 2014-05-25 07:02 | 2014-05-25 07:02 | EDT | 2014-05-25 11:02 | 2103 | 59.9734 | 59.9147 | 59.9103 | -0.058705 | -0.063116 | -3582.3322 | -3331.9689 | Yes | Yes | 59.5 | 0.41031 | 2014
EI_2014-05-29_002344 | 2014-05-28 20:24 | 2014-05-28 20:24 | EDT | 2014-05-29 00:24 | 685 | 60.0057 | 59.9559 | 59.9645 | -0.049856 | -0.041228 | -1373.9515 | -1661.4995 | No | No | 59.5 | 0.46449 | 2014
EI_2014-05-29_142022 | 2014-05-29 10:20 | 2014-05-29 10:20 | EDT | 2014-05-29 14:20 | 709 | 59.9904 | 59.9564 | 59.9569 | -0.034077 | -0.033504 | -2080.5588 | -2116.1345 | No | No | 59.5 | 0.45692 | 2014
EI_2014-05-30_222713 | 2014-05-30 18:27 | 2014-05-30 18:27 | EDT | 2014-05-30 22:27 | 0 | 59.974 | 59.9422 | 59.9421 | -0.03175 | -0.031888 |  |  | No | No | 59.5 | 0.44207 | 2014
EI_2014-06-06_161144 | 2014-06-06 12:12 | 2014-06-06 12:12 | EDT | 2014-06-06 16:12 | 637 | 59.9722 | 59.9457 | 59.9482 | -0.026512 | -0.024011 | -2402.6782 | -2652.9095 | No | No | 59.5 | 0.4482 | 2014
EI_2014-06-07_103422 | 2014-06-07 06:34 | 2014-06-07 06:34 | EDT | 2014-06-07 10:34 | 505 | 59.9992 | 59.9827 | 59.9811 | -0.016526 | -0.018146 | -3055.8005 | -2782.9766 | No | No | 59.5 | 0.4811 | 2014
EI_2014-06-07_153120 | 2014-06-07 11:31 | 2014-06-07 11:31 | EDT | 2014-06-07 15:31 | 0 | 59.9857 | 60.0266 | 60.0219 | 0.040921 | 0.0362 |  |  | No | No | 59.5 | 0.5219 | 2014
EI_2014-06-08_040636 | 2014-06-08 00:07 | 2014-06-08 00:07 | EDT | 2014-06-08 04:07 | 0 | 59.9917 | 59.9668 | 59.9598 | -0.024928 | -0.031912 |  |  | No | No | 59.5 | 0.4598 | 2014
EI_2014-06-08_050250 | 2014-06-08 01:03 | 2014-06-08 01:03 | EDT | 2014-06-08 05:03 | 0 | 60.0132 | 59.9706 | 59.9743 | -0.042601 | -0.038937 |  |  | No | No | 59.5 | 0.4743 | 2014
EI_2014-06-12_065004 | 2014-06-12 02:50 | 2014-06-12 02:50 | EDT | 2014-06-12 06:50 | 530 | 60.002 | 59.9837 | 59.9791 | -0.018245 | -0.022851 | -2904.9164 | -2319.3259 | No | No | 59.5 | 0.4791 | 2014
EI_2014-06-18_203552 | 2014-06-18 16:36 | 2014-06-18 16:36 | EDT | 2014-06-18 20:36 | 0 | 59.9974 | 59.9651 | 59.9599 | -0.032352 | -0.037519 |  |  | No | No | 59.5 | 0.4599 | 2014
EI_2014-06-25_205558 | 2014-06-25 16:56 | 2014-06-25 16:56 | EDT | 2014-06-25 20:56 | 0 | 59.9926 | 59.9711 | 59.9612 | -0.021517 | -0.031393 |  |  | No | No | 59.5 | 0.4612 | 2014
EI_2014-07-05_191608 | 2014-07-05 15:16 | 2014-07-05 15:16 | EDT | 2014-07-05 19:16 | 195 | 59.9899 | 59.9756 | 59.9712 | -0.014319 | -0.018695 | -1361.8743 | -1043.0532 | No | No | 59.5 | 0.4712 | 2014
EI_2014-07-07_012413 | 2014-07-06 21:24 | 2014-07-06 21:24 | EDT | 2014-07-07 01:24 | 680 | 59.9717 | 59.9464 | 59.9445 | -0.025268 | -0.027169 | -2691.1649 | -2502.8974 | No | No | 59.5 | 0.4445 | 2014
EI_2014-07-09_151234 | 2014-07-09 11:13 | 2014-07-09 11:13 | EDT | 2014-07-09 15:13 | 0 | 60.0083 | 59.9688 | 59.9721 | -0.039524 | -0.036194 |  |  | No | No | 59.5 | 0.4721 | 2014
EI_2014-07-10_014230 | 2014-07-09 21:42 | 2014-07-09 21:42 | EDT | 2014-07-10 01:42 | 968 | 60.0181 | 59.9795 | 59.982 | -0.038547 | -0.036076 | -2511.1926 | -2683.2014 | No | No | 59.5 | 0.482 | 2014
EI_2014-07-10_212134 | 2014-07-10 17:22 | 2014-07-10 17:22 | EDT | 2014-07-10 21:22 | 0 | 59.9829 | 59.9517 | 59.9493 | -0.031176 | -0.033563 |  |  | No | No | 59.5 | 0.4493 | 2014
EI_2014-07-13_200931 | 2014-07-13 16:10 | 2014-07-13 16:10 | EDT | 2014-07-13 20:10 | 0 | 59.9893 | 59.9475 | 59.9506 | -0.041852 | -0.038738 |  |  | No | No | 59.5 | 0.4506 | 2014
EI_2014-07-13_233617 | 2014-07-13 19:36 | 2014-07-13 19:36 | EDT | 2014-07-13 23:36 | 1117 | 59.9693 | 59.9492 | 59.9371 | -0.020118 | -0.032212 | -5552.3559 | -3467.6241 | No | No | 59.5 | 0.4371 | 2014
EI_2014-07-16_060019 | 2014-07-16 02:00 | 2014-07-16 02:00 | EDT | 2014-07-16 06:00 | 325 | 60.0136 | 59.9965 | 59.9923 | -0.017126 | -0.021346 | -1897.6998 | -1522.5269 | No | No | 59.5 | 0.4923 | 2014
EI_2014-07-20_233159 | 2014-07-20 19:32 | 2014-07-20 19:32 | EDT | 2014-07-20 23:32 | 0 | 60.0161 | 59.9763 | 59.9769 | -0.039764 | -0.039202 |  |  | No | No | 59.5 | 0.4769 | 2014
EI_2014-07-23_172153 | 2014-07-23 13:22 | 2014-07-23 13:22 | EDT | 2014-07-23 17:22 | 0 | 60.0241 | 59.9859 | 59.9891 | -0.038189 | -0.034999 |  |  | No | No | 59.5 | 0.4891 | 2014
EI_2014-07-24_161401 | 2014-07-24 12:14 | 2014-07-24 12:14 | EDT | 2014-07-24 16:14 | 1812 | 59.9961 | 59.9357 | 59.9375 | -0.060372 | -0.058594 | -3001.3814 | -3092.4926 | Yes | Yes | 59.5 | 0.4375 | 2014
EI_2014-07-25_191632 | 2014-07-25 15:17 | 2014-07-25 15:17 | EDT | 2014-07-25 19:17 | 1678 | 59.999 | 59.9533 | 59.9529 | -0.045687 | -0.046076 | -3672.7844 | -3641.8422 | Yes | Yes | 59.5 | 0.4529 | 2014
EI_2014-07-27_180932 | 2014-07-27 14:10 | 2014-07-27 14:10 | EDT | 2014-07-27 18:10 | 1195 | 60.0043 | 59.9549 | 59.9579 | -0.049387 | -0.046386 | -2419.6701 | -2576.2081 | Yes | Yes | 59.5 | 0.4579 | 2014
EI_2014-07-29_180915 | 2014-07-29 14:09 | 2014-07-29 14:09 | EDT | 2014-07-29 18:09 | 385 | 60.0112 | 59.9778 | 59.9864 | -0.033411 | -0.02478 | -1152.3082 | -1553.6552 | No | No | 59.5 | 0.4864 | 2014
EI_2014-07-31_123126 | 2014-07-31 08:31 | 2014-07-31 08:31 | EDT | 2014-07-31 12:31 | 954 | 59.9758 | 59.9468 | 59.9443 | -0.029032 | -0.031485 | -3285.9892 | -3029.9836 | No | No | 59.5 | 0.4443 | 2014
EI_2014-08-02_045322 | 2014-08-02 00:53 | 2014-08-02 00:53 | EDT | 2014-08-02 04:53 | 353 | 60.023 | 59.9843 | 59.9874 | -0.038635 | -0.035575 | -913.6851 | -992.2789 | No | No | 59.5 | 0.4874 | 2014
EI_2014-08-03_053021 | 2014-08-03 01:30 | 2014-08-03 01:30 | EDT | 2014-08-03 05:30 | 0 | 60.0047 | 59.9681 | 59.9659 | -0.03661 | -0.038831 |  |  | No | No | 59.5 | 0.4659 | 2014
EI_2014-08-05_093748 | 2014-08-05 05:38 | 2014-08-05 05:38 | EDT | 2014-08-05 09:38 | 560 | 60.0254 | 59.986 | 59.9986 | -0.039407 | -0.026815 | -1421.0835 | -2088.4068 | No | No | 59.5 | 0.49855 | 2014
EI_2014-08-05_165346 | 2014-08-05 12:54 | 2014-08-05 12:54 | EDT | 2014-08-05 16:54 | 567 | 60.0383 | 60.0241 | 60.0204 | -0.014189 | -0.017931 | -3995.9929 | -3162.2083 | No | No | 59.5 | 0.5204 | 2014
EI_2014-08-05_223435 | 2014-08-05 18:35 | 2014-08-05 18:35 | EDT | 2014-08-05 22:35 | 1132 | 60.0102 | 59.9642 | 59.9736 | -0.046073 | -0.036694 | -2456.9949 | -3084.9688 | No | No | 59.5 | 0.47355 | 2014
EI_2014-08-09_121456 | 2014-08-09 08:15 | 2014-08-09 08:15 | EDT | 2014-08-09 12:15 | 0 | 59.9761 | 60.0168 | 60.0175 | 0.040613 | 0.041358 |  |  | No | No | 59.5 | 0.5175 | 2014
EI_2014-08-09_213533 | 2014-08-09 17:36 | 2014-08-09 17:36 | EDT | 2014-08-09 21:36 | 1200 | 59.9839 | 59.9375 | 59.9545 | -0.046388 | -0.029407 | -2586.8962 | -4080.6246 | No | No | 59.5 | 0.4545 | 2014
EI_2014-08-11_054749 | 2014-08-11 01:48 | 2014-08-11 01:48 | EDT | 2014-08-11 05:48 | 777 | 60.0035 | 59.9672 | 59.9719 | -0.03623 | -0.031574 | -2144.6225 | -2460.8475 | No | No | 59.5 | 0.4719 | 2014
EI_2014-08-12_042657 | 2014-08-12 00:27 | 2014-08-12 00:27 | EDT | 2014-08-12 04:27 | 876 | 59.9791 | 59.9536 | 59.9443 | -0.025489 | -0.03483 | -3436.8178 | -2515.1009 | No | No | 59.5 | 0.4443 | 2014
EI_2014-08-13_050128 | 2014-08-13 01:01 | 2014-08-13 01:01 | EDT | 2014-08-13 05:01 | 0 | 60.0162 | 59.976 | 59.9766 | -0.040258 | -0.039624 |  |  | No | No | 59.5 | 0.4766 | 2014
EI_2014-08-13_155744 | 2014-08-13 11:58 | 2014-08-13 11:58 | EDT | 2014-08-13 15:58 | 1025 | 60.0018 | 59.9603 | 59.9592 | -0.041509 | -0.042598 | -2469.3315 | -2406.2023 | Yes | Yes | 59.5 | 0.4592 | 2014
EI_2014-08-14_124859 | 2014-08-14 08:49 | 2014-08-14 08:49 | EDT | 2014-08-14 12:49 | 598 | 59.9899 | 59.9675 | 59.9668 | -0.022374 | -0.023118 | -2672.795 | -2586.7001 | No | No | 59.5 | 0.4668 | 2014
EI_2014-08-15_125500 | 2014-08-15 08:55 | 2014-08-15 08:55 | EDT | 2014-08-15 12:55 | 420 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.5 | -59.5 | 2014
EI_2014-08-17_001535 | 2014-08-16 20:16 | 2014-08-16 20:16 | EDT | 2014-08-17 00:16 | 865 | 59.9917 | 59.9537 | 59.959 | -0.037982 | -0.03263 | -2277.4226 | -2650.9181 | No | No | 59.5 | 0.45905 | 2014
EI_2014-08-23_131433 | 2014-08-23 09:15 | 2014-08-23 09:15 | EDT | 2014-08-23 13:15 | 0 | 59.9687 | 60.025 | 60.0108 | 0.056342 | 0.042099 |  |  | No | No | 59.5 | 0.51078 | 2014
EI_2014-08-26_223011 | 2014-08-26 18:30 | 2014-08-26 18:30 | EDT | 2014-08-26 22:30 | 1120 | 60.013 | 59.9646 | 59.9694 | -0.048396 | -0.043552 | -2314.2183 | -2571.6431 | No | No | 59.5 | 0.46944 | 2014
EI_2014-08-28_211804 | 2014-08-28 17:18 | 2014-08-28 17:18 | EDT | 2014-08-28 21:18 | 658 | 59.9872 | 59.9633 | 59.9572 | -0.023938 | -0.030027 | -2748.7969 | -2191.3327 | No | No | 59.5 | 0.45719 | 2014
EI_2014-08-30_051923 | 2014-08-30 01:19 | 2014-08-30 01:19 | EDT | 2014-08-30 05:19 | 0 | 59.9901 | 59.9663 | 59.9522 | -0.02381 | -0.037908 |  |  | No | No | 59.5 | 0.4522 | 2014
EI_2014-08-30_052042 | 2014-08-30 01:21 | 2014-08-30 01:21 | EDT | 2014-08-30 05:21 | 0 | 59.9856 | 60.0321 | 60.0303 | 0.046488 | 0.044757 |  |  | No | No | 59.5 | 0.53034 | 2014
EI_2014-09-06_133047 | 2014-09-06 09:31 | 2014-09-06 09:31 | EDT | 2014-09-06 13:31 | 674 | 59.9528 | 59.9261 | 59.9287 | -0.026694 | -0.024082 | -2524.9145 | -2798.7772 | No | No | 59.5 | 0.4287 | 2014
EI_2014-09-14_042522 | 2014-09-14 00:25 | 2014-09-14 00:25 | EDT | 2014-09-14 04:25 | 427 | 60.0161 | 59.9983 | 59.9968 | -0.017849 | -0.01932 | -2392.2244 | -2210.1709 | No | No | 59.5 | 0.4968 | 2014
EI_2014-09-14_193729 | 2014-09-14 15:37 | 2014-09-14 15:37 | EDT | 2014-09-14 19:37 | 770 | 59.9877 | 59.9543 | 59.956 | -0.033397 | -0.031718 | -2305.5852 | -2427.6789 | No | No | 59.5 | 0.456 | 2014
EI_2014-09-18_100014 | 2014-09-18 06:00 | 2014-09-18 06:00 | EDT | 2014-09-18 10:00 | 0 | 60.0024 | 59.9422 | 59.9594 | -0.060212 | -0.043019 |  |  | No | No | 59.5 | 0.4594 | 2014
EI_2014-09-20_002355 | 2014-09-19 20:24 | 2014-09-19 20:24 | EDT | 2014-09-20 00:24 | 429 | 59.9853 | 59.9803 | 59.9664 | -0.0049689 | -0.018881 | -8633.7461 | -2272.1442 | No | No | 59.5 | 0.4664 | 2014
EI_2014-09-20_234111 | 2014-09-20 19:41 | 2014-09-20 19:41 | EDT | 2014-09-20 23:41 | 1250 | 60.0217 | 59.9731 | 59.9686 | -0.048535 | -0.053073 | -2575.4575 | -2355.2391 | No | No | 59.5 | 0.4686 | 2014
EI_2014-09-21_101155 | 2014-09-21 06:12 | 2014-09-21 06:12 | EDT | 2014-09-21 10:12 | 0 | 60.0214 | 59.986 | 59.991 | -0.035394 | -0.030411 |  |  | No | No | 59.5 | 0.491 | 2014
EI_2014-09-26_124504 | 2014-09-26 08:45 | 2014-09-26 08:45 | EDT | 2014-09-26 12:45 | 779 | 60.0265 | 59.9916 | 59.9869 | -0.034911 | -0.039638 | -2231.3854 | -1965.2956 | No | No | 59.5 | 0.4869 | 2014
EI_2014-09-26_133513 | 2014-09-26 09:35 | 2014-09-26 09:35 | EDT | 2014-09-26 13:35 | 685 | 60.0012 | 59.9805 | 59.9687 | -0.020762 | -0.032537 | -3299.3055 | -2105.2812 | No | No | 59.5 | 0.4687 | 2014
EI_2014-09-27_153845 | 2014-09-27 11:39 | 2014-09-27 11:39 | EDT | 2014-09-27 15:39 | 465 | 59.9944 | 59.9768 | 59.9675 | -0.017644 | -0.026933 | -2635.4675 | -1726.5247 | No | No | 59.5 | 0.4675 | 2014
EI_2014-09-29_150405 | 2014-09-29 11:04 | 2014-09-29 11:04 | EDT | 2014-09-29 15:04 | 0 | 59.9963 | 59.953 | 59.9552 | -0.043371 | -0.041131 |  |  | No | No | 59.5 | 0.4552 | 2014
EI_2014-10-01_131509 | 2014-10-01 09:15 | 2014-10-01 09:15 | EDT | 2014-10-01 13:15 | 0 | 59.9873 | 60.0243 | 60.0275 | 0.037068 | 0.040238 |  |  | No | No | 59.5 | 0.5275 | 2014
EI_2014-10-04_081916 | 2014-10-04 04:19 | 2014-10-04 04:19 | EDT | 2014-10-04 08:19 | 753 | 60.005 | 59.9576 | 59.9555 | -0.047358 | -0.049492 | -1590.0327 | -1521.447 | No | Yes | 59.5 | 0.4555 | 2014
EI_2014-10-04_232828 | 2014-10-04 19:28 | 2014-10-04 19:28 | EDT | 2014-10-04 23:28 | 0 | 59.9927 | 60.0272 | 60.0262 | 0.034461 | 0.033488 |  |  | No | No | 59.5 | 0.5262 | 2014
EI_2014-10-05_110553 | 2014-10-05 07:06 | 2014-10-05 07:06 | EDT | 2014-10-05 11:06 | 0 | 59.9874 | 60.033 | 60.0332 | 0.045567 | 0.045787 |  |  | No | No | 59.5 | 0.5332 | 2014
EI_2014-10-07_201154 | 2014-10-07 16:12 | 2014-10-07 16:12 | EDT | 2014-10-07 20:12 | 0 | 60.007 | 59.9652 | 59.9611 | -0.041837 | -0.045893 |  |  | No | No | 59.5 | 0.4611 | 2014
EI_2014-10-08_102847 | 2014-10-08 06:29 | 2014-10-08 06:29 | EDT | 2014-10-08 10:29 | 0 | 59.9623 | 60.0035 | 60.0009 | 0.04125 | 0.03865 |  |  | No | No | 59.5 | 0.5009 | 2014
EI_2014-10-09_133005 | 2014-10-09 09:30 | 2014-10-09 09:30 | EDT | 2014-10-09 13:30 | 848 | 59.9925 | 59.9557 | 59.9543 | -0.036751 | -0.038169 | -2307.4273 | -2221.6898 | Yes | No | 59.5 | 0.4543 | 2014
EI_2014-10-11_205713 | 2014-10-11 16:57 | 2014-10-11 16:57 | EDT | 2014-10-11 20:57 | 810 | 60.022 | 59.9779 | 59.979 | -0.044036 | -0.042957 | -1839.4123 | -1885.6245 | No | No | 59.5 | 0.479 | 2014
EI_2014-10-13_115753 | 2014-10-13 07:58 | 2014-10-13 07:58 | EDT | 2014-10-13 11:58 | 906 | 60.0252 | 59.9711 | 59.9724 | -0.054095 | -0.052755 | -1674.8167 | -1717.3612 | No | No | 59.5 | 0.4724 | 2014
EI_2014-10-13_191126 | 2014-10-13 15:11 | 2014-10-13 15:11 | EDT | 2014-10-13 19:11 | 627 | 60.0121 | 59.9793 | 59.9754 | -0.032763 | -0.036664 | -1913.7608 | -1710.1462 | No | No | 59.5 | 0.4754 | 2014
EI_2014-10-13_204805 | 2014-10-13 16:48 | 2014-10-13 16:48 | EDT | 2014-10-13 20:48 | 0 | 60.0112 | 59.971 | 59.9707 | -0.040211 | -0.040469 |  |  | No | No | 59.5 | 0.4707 | 2014
EI_2014-10-14_084115 | 2014-10-14 04:41 | 2014-10-14 04:41 | EDT | 2014-10-14 08:41 | 764 | 59.9957 | 59.9617 | 59.9554 | -0.034039 | -0.040301 | -2244.4629 | -1895.7194 | No | Yes | 59.5 | 0.4554 | 2014
EI_2014-10-15_065313 | 2014-10-15 02:53 | 2014-10-15 02:53 | EDT | 2014-10-15 06:53 | 789 | 59.9963 | 59.9587 | 59.9591 | -0.037595 | -0.037245 | -2098.7 | -2118.4303 | No | No | 59.5 | 0.4591 | 2014
EI_2014-10-16_173240 | 2014-10-16 13:33 | 2014-10-16 13:33 | EDT | 2014-10-16 17:33 | 590 | 59.9917 | 59.9663 | 59.9607 | -0.025413 | -0.031018 | -2321.6398 | -1902.1202 | No | No | 59.5 | 0.4607 | 2014
EI_2014-10-17_080322 | 2014-10-17 04:03 | 2014-10-17 04:03 | EDT | 2014-10-17 08:03 | 0 | 59.9967 | 59.9502 | 59.9592 | -0.046527 | -0.037517 |  |  | No | No | 59.5 | 0.4592 | 2014
EI_2014-10-17_183115 | 2014-10-17 14:31 | 2014-10-17 14:31 | EDT | 2014-10-17 18:31 | 0 | 60.0103 | 59.9717 | 59.9705 | -0.038612 | -0.039787 |  |  | No | No | 59.5 | 0.4705 | 2014
EI_2014-10-18_064844 | 2014-10-18 02:49 | 2014-10-18 02:49 | EDT | 2014-10-18 06:49 | 739 | 60.0019 | 59.9614 | 59.9656 | -0.040495 | -0.03632 | -1824.9226 | -2034.6932 | No | No | 59.5 | 0.4656 | 2014
EI_2014-10-18_105944 | 2014-10-18 07:00 | 2014-10-18 07:00 | EDT | 2014-10-18 11:00 | 0 | 59.989 | 60.0266 | 60.0281 | 0.037658 | 0.03913 |  |  | No | No | 59.5 | 0.5281 | 2014
EI_2014-10-18_134406 | 2014-10-18 09:44 | 2014-10-18 09:44 | EDT | 2014-10-18 13:44 | 0 | 59.9839 | 60.0299 | 60.025 | 0.04591 | 0.041057 |  |  | No | No | 59.5 | 0.525 | 2014
EI_2014-10-20_061839 | 2014-10-20 02:19 | 2014-10-20 02:19 | EDT | 2014-10-20 06:19 | 1320 | 59.9899 | 59.9447 | 59.9408 | -0.04516 | -0.049063 | -2922.9502 | -2690.3941 | Yes | Yes | 59.5 | 0.4408 | 2014
EI_2014-10-20_204110 | 2014-10-20 16:41 | 2014-10-20 16:41 | EDT | 2014-10-20 20:41 | 0 | 59.9882 | 59.962 | 59.9524 | -0.026191 | -0.0358 |  |  | No | No | 59.5 | 0.4524 | 2014
EI_2014-10-22_063123 | 2014-10-22 02:31 | 2014-10-22 02:31 | EDT | 2014-10-22 06:31 | 454 | 60.0045 | 59.9764 | 59.9721 | -0.028054 | -0.032358 | -1618.2793 | -1403.0563 | No | No | 59.5 | 0.4721 | 2014
EI_2014-10-22_170820 | 2014-10-22 13:08 | 2014-10-22 13:08 | EDT | 2014-10-22 17:08 | 311 | 60.0026 | 59.9909 | 59.9802 | -0.011766 | -0.022416 | -2643.1167 | -1387.38 | No | No | 59.5 | 0.4802 | 2014
EI_2014-10-23_110004 | 2014-10-23 07:00 | 2014-10-23 07:00 | EDT | 2014-10-23 11:00 | 756 | 60.0264 | 59.9513 | 59.9709 | -0.07503 | -0.055461 | -1007.6017 | -1363.11 | No | No | 59.5 | 0.4709 | 2014
EI_2014-10-23_204153 | 2014-10-23 16:42 | 2014-10-23 16:42 | EDT | 2014-10-23 20:42 | 602 | 59.9885 | 59.958 | 59.9518 | -0.030523 | -0.036736 | -1972.2582 | -1638.6977 | No | No | 59.5 | 0.4518 | 2014
EI_2014-10-24_224323 | 2014-10-24 18:43 | 2014-10-24 18:43 | EDT | 2014-10-24 22:43 | 861 | 59.991 | 59.9549 | 59.9515 | -0.036113 | -0.039519 | -2384.1981 | -2178.7081 | Yes | Yes | 59.5 | 0.4515 | 2014
EI_2014-10-26_153110 | 2014-10-26 11:31 | 2014-10-26 11:31 | EDT | 2014-10-26 15:31 | 0 | 60.0057 | 59.9484 | 59.9554 | -0.05734 | -0.050308 |  |  | No | Yes | 59.5 | 0.4554 | 2014
EI_2014-10-27_062925 | 2014-10-27 02:29 | 2014-10-27 02:29 | EDT | 2014-10-27 06:29 | 502 | 59.9999 | 59.9777 | 59.9744 | -0.022255 | -0.02555 | -2255.6464 | -1964.7835 | No | No | 59.5 | 0.4744 | 2014
EI_2014-10-27_085947 | 2014-10-27 05:00 | 2014-10-27 05:00 | EDT | 2014-10-27 09:00 | 0 | 59.9984 | 60.0376 | 60.0375 | 0.039194 | 0.039098 |  |  | No | No | 59.5 | 0.5375 | 2014
EI_2014-10-30_093920 | 2014-10-30 05:39 | 2014-10-30 05:39 | EDT | 2014-10-30 09:39 | 0 | 59.9892 | 60.0144 | 60.0254 | 0.025156 | 0.03616 |  |  | No | No | 59.5 | 0.5254 | 2014
EI_2014-11-01_064938 | 2014-11-01 02:50 | 2014-11-01 02:50 | EDT | 2014-11-01 06:50 | 1554 | 59.988 | 59.9398 | 59.9421 | -0.048225 | -0.045937 | -3222.3749 | -3382.8894 | Yes | Yes | 59.5 | 0.4421 | 2014
EI_2014-11-01_084037 | 2014-11-01 04:41 | 2014-11-01 04:41 | EDT | 2014-11-01 08:41 | 0 | 59.9984 | 59.9618 | 59.9609 | -0.036612 | -0.037525 |  |  | No | No | 59.5 | 0.4609 | 2014
EI_2014-11-01_135118 | 2014-11-01 09:51 | 2014-11-01 09:51 | EDT | 2014-11-01 13:51 | 586 | 59.9815 | 59.9507 | 59.9455 | -0.030855 | -0.036026 | -1899.2132 | -1626.6137 | No | No | 59.5 | 0.4455 | 2014
EI_2014-11-03_051201 | 2014-11-03 00:12 | 2014-11-03 00:12 | EST | 2014-11-03 05:12 | 693 | 59.9987 | 59.965 | 59.9642 | -0.033642 | -0.034476 | -2059.9311 | -2010.0776 | No | No | 59.5 | 0.4642 | 2014
EI_2014-11-03_192114 | 2014-11-03 14:21 | 2014-11-03 14:21 | EST | 2014-11-03 19:21 | 1532 | 59.9943 | 59.9439 | 59.9349 | -0.050325 | -0.059358 | -3044.1975 | -2580.965 | Yes | Yes | 59.5 | 0.4349 | 2014
EI_2014-11-05_152229 | 2014-11-05 10:22 | 2014-11-05 10:22 | EST | 2014-11-05 15:22 | 0 | 60.0108 | 59.9418 | 59.9441 | -0.068975 | -0.066694 |  |  | No | Yes | 59.5 | 0.4441 | 2014
EI_2014-11-05_212547 | 2014-11-05 16:26 | 2014-11-05 16:26 | EST | 2014-11-05 21:26 | 784 | 59.978 | 59.9497 | 59.9544 | -0.028226 | -0.023576 | -2777.5795 | -3325.4463 | No | No | 59.5 | 0.4544 | 2014
EI_2014-11-07_134803 | 2014-11-07 08:48 | 2014-11-07 08:48 | EST | 2014-11-07 13:48 | 1270 | 59.9956 | 59.9592 | 59.9459 | -0.036409 | -0.049706 | -3488.1386 | -2555.0245 | Yes | Yes | 59.5 | 0.4459 | 2014
EI_2014-11-12_204830 | 2014-11-12 15:48 | 2014-11-12 15:48 | EST | 2014-11-12 20:49 | 0 | 60.0144 | 59.9501 | 59.9604 | -0.064318 | -0.053976 |  |  | No | No | 59.5 | 0.4604 | 2014
EI_2014-11-13_094951 | 2014-11-13 04:50 | 2014-11-13 04:50 | EST | 2014-11-13 09:50 | 0 | 59.9848 | 60.0308 | 60.0242 | 0.045956 | 0.039357 |  |  | No | No | 59.5 | 0.5242 | 2014
EI_2014-11-15_213510 | 2014-11-15 16:35 | 2014-11-15 16:35 | EST | 2014-11-15 21:35 | 0 | 59.9809 | 60.0375 | 60.0246 | 0.056634 | 0.043745 |  |  | No | No | 59.5 | 0.5246 | 2014
EI_2014-11-20_145320 | 2014-11-20 09:53 | 2014-11-20 09:53 | EST | 2014-11-20 14:53 | 0 | 60.0106 | 59.9656 | 59.9712 | -0.044979 | -0.039407 |  |  | No | No | 59.5 | 0.4712 | 2014
EI_2014-11-22_081815 | 2014-11-22 03:18 | 2014-11-22 03:18 | EST | 2014-11-22 08:18 | 911 | 59.9942 | 59.9647 | 59.9491 | -0.0295 | -0.045105 | -3088.1855 | -2019.7219 | Yes | Yes | 59.5 | 0.4491 | 2014
EI_2014-11-22_222241 | 2014-11-22 17:23 | 2014-11-22 17:23 | EST | 2014-11-22 22:23 | 0 | 59.9866 | 60.039 | 60.0263 | 0.052405 | 0.039655 |  |  | No | No | 59.5 | 0.5263 | 2014
EI_2014-11-30_110002 | 2014-11-30 06:00 | 2014-11-30 06:00 | EST | 2014-11-30 11:00 | 0 | 60.0017 | 60.0428 | 60.0379 | 0.041069 | 0.036174 |  |  | No | No | 59.5 | 0.5379 | 2014
EI_2014-12-03_062255 | 2014-12-03 01:23 | 2014-12-03 01:23 | EST | 2014-12-03 06:23 | 1234 | 59.983 | 59.9293 | 59.9283 | -0.053678 | -0.054658 | -2298.8875 | -2257.6776 | Yes | Yes | 59.5 | 0.4283 | 2015
EI_2014-12-04_155801 | 2014-12-04 10:58 | 2014-12-04 10:58 | EST | 2014-12-04 15:58 | 0 | 59.9895 | 59.949 | 59.9446 | -0.04054 | -0.04492 |  |  | No | Yes | 59.5 | 0.4446 | 2015
EI_2014-12-10_185741 | 2014-12-10 13:58 | 2014-12-10 13:58 | EST | 2014-12-10 18:58 | 1280 | 60.0036 | 59.9456 | 59.9486 | -0.057945 | -0.054975 | -2208.9756 | -2328.3297 | Yes | Yes | 59.5 | 0.4486 | 2015
EI_2014-12-12_134958 | 2014-12-12 08:50 | 2014-12-12 08:50 | EST | 2014-12-12 13:50 | 899 | 59.9983 | 59.9673 | 59.9612 | -0.030972 | -0.037056 | -2902.6451 | -2426.0755 | No | No | 59.5 | 0.4612 | 2015
EI_2014-12-15_222653 | 2014-12-15 17:27 | 2014-12-15 17:27 | EST | 2014-12-15 22:27 | 846 | 59.9728 | 59.9371 | 59.9408 | -0.035721 | -0.032 | -2368.3381 | -2643.7249 | No | No | 59.5 | 0.4408 | 2015
EI_2014-12-16_172036 | 2014-12-16 12:21 | 2014-12-16 12:21 | EST | 2014-12-16 17:21 | 0 | 59.989 | 59.9619 | 59.9609 | -0.027137 | -0.028113 |  |  | No | No | 59.5 | 0.4609 | 2015
EI_2014-12-18_021657 | 2014-12-17 21:17 | 2014-12-17 21:17 | EST | 2014-12-18 02:17 | 0 | 60.0104 | 59.9694 | 59.9733 | -0.041006 | -0.037074 |  |  | No | No | 59.5 | 0.4733 | 2015
EI_2014-12-18_085908 | 2014-12-18 03:59 | 2014-12-18 03:59 | EST | 2014-12-18 08:59 | 0 | 59.9957 | 60.017 | 60.0292 | 0.021336 | 0.033495 |  |  | No | No | 59.5 | 0.5292 | 2015
EI_2015-01-01_023732 | 2014-12-31 21:38 | 2014-12-31 21:38 | EST | 2015-01-01 02:38 | 825 | 59.9976 | 59.9608 | 59.9612 | -0.036777 | -0.036418 | -2243.2566 | -2265.3657 | No | No | 59.5 | 0.4612 | 2015
EI_2015-01-01_123014 | 2015-01-01 07:30 | 2015-01-01 07:30 | EST | 2015-01-01 12:30 | 703 | 59.992 | 59.9541 | 59.9559 | -0.037854 | -0.03607 | -1857.1577 | -1948.9693 | No | No | 59.5 | 0.4559 | 2015
EI_2015-01-03_114305 | 2015-01-03 06:43 | 2015-01-03 06:43 | EST | 2015-01-03 11:43 | 0 | 59.9694 | 60.0215 | 60.0093 | 0.052053 | 0.039862 |  |  | No | No | 59.5 | 0.5093 | 2015
EI_2015-01-09_211608 | 2015-01-09 16:16 | 2015-01-09 16:16 | EST | 2015-01-09 21:16 | 0 | 59.9994 | 59.9604 | 59.964 | -0.039033 | -0.035399 |  |  | No | No | 59.5 | 0.464 | 2015
EI_2015-01-11_052320 | 2015-01-11 00:23 | 2015-01-11 00:23 | EST | 2015-01-11 05:23 | 624 | 59.9969 | 59.9593 | 59.9677 | -0.037526 | -0.029174 | -1662.8282 | -2138.8842 | No | No | 59.5 | 0.4677 | 2015
EI_2015-01-11_084031 | 2015-01-11 03:41 | 2015-01-11 03:41 | EST | 2015-01-11 08:41 | 810 | 59.9984 | 59.9766 | 59.9757 | -0.021748 | -0.022692 | -3724.557 | -3569.4704 | No | No | 59.5 | 0.4757 | 2015
EI_2015-01-12_045255 | 2015-01-11 23:53 | 2015-01-11 23:53 | EST | 2015-01-12 04:53 | 815 | 59.9984 | 59.9639 | 59.963 | -0.034531 | -0.035418 | -2360.203 | -2301.1186 | No | No | 59.5 | 0.463 | 2015
EI_2015-01-14_010407 | 2015-01-13 20:04 | 2015-01-13 20:04 | EST | 2015-01-14 01:04 | 940 | 59.9846 | 59.9582 | 59.9573 | -0.026352 | -0.027296 | -3567.1571 | -3443.7497 | No | No | 59.5 | 0.4573 | 2015
EI_2015-01-15_050425 | 2015-01-15 00:04 | 2015-01-15 00:04 | EST | 2015-01-15 05:04 | 877 | 60.0078 | 59.9683 | 59.9712 | -0.039418 | -0.036564 | -2224.8806 | -2398.5424 | No | No | 59.5 | 0.4712 | 2015
EI_2015-01-23_033251 | 2015-01-22 22:33 | 2015-01-22 22:33 | EST | 2015-01-23 03:33 | 814 | 60.0316 | 59.9766 | 59.9869 | -0.054951 | -0.044681 | -1481.312 | -1821.7908 | No | No | 59.5 | 0.4869 | 2015
EI_2015-01-24_043329 | 2015-01-23 23:33 | 2015-01-23 23:33 | EST | 2015-01-24 04:33 | 945 | 59.9986 | 59.9598 | 59.9654 | -0.038748 | -0.033193 | -2438.8494 | -2846.9558 | No | No | 59.5 | 0.4654 | 2015
EI_2015-01-24_153138 | 2015-01-24 10:32 | 2015-01-24 10:32 | EST | 2015-01-24 15:32 | 503 | 59.9924 | 59.9601 | 59.9635 | -0.032288 | -0.028936 | -1557.8382 | -1738.3245 | No | No | 59.5 | 0.4635 | 2015
EI_2015-01-25_000036 | 2015-01-24 19:01 | 2015-01-24 19:01 | EST | 2015-01-25 00:01 | 535 | 59.9897 | 59.9566 | 59.9559 | -0.03315 | -0.033845 | -1613.8935 | -1580.7159 | No | No | 59.5 | 0.4559 | 2015
EI_2015-01-25_001054 | 2015-01-24 19:11 | 2015-01-24 19:11 | EST | 2015-01-25 00:11 | 307 | 59.9855 | 59.972 | 59.9628 | -0.013491 | -0.022707 | -2275.5457 | -1351.9785 | No | No | 59.5 | 0.4628 | 2015
EI_2015-01-27_042753 | 2015-01-26 23:28 | 2015-01-26 23:28 | EST | 2015-01-27 04:28 | 480 | 60.004 | 59.9839 | 59.9848 | -0.020056 | -0.019157 | -2393.2778 | -2505.5579 | No | No | 59.5 | 0.4848 | 2015
EI_2015-01-28_184150 | 2015-01-28 13:42 | 2015-01-28 13:42 | EST | 2015-01-28 18:42 | 735 | 60.0131 | 59.9694 | 59.9807 | -0.043645 | -0.032368 | -1684.0417 | -2270.7651 | No | No | 59.5 | 0.4807 | 2015
EI_2015-01-29_202758 | 2015-01-29 15:28 | 2015-01-29 15:28 | EST | 2015-01-29 20:28 | 800 | 60.0002 | 59.9755 | 59.9741 | -0.024789 | -0.026145 | -3227.2632 | -3059.8328 | No | No | 59.5 | 0.4741 | 2015
EI_2015-01-31_193145 | 2015-01-31 14:32 | 2015-01-31 14:32 | EST | 2015-01-31 19:32 | 846 | 60.0008 | 59.9597 | 59.9569 | -0.041118 | -0.043917 | -2057.4757 | -1926.3532 | Yes | Yes | 59.5 | 0.4569 | 2015
EI_2015-02-01_223057 | 2015-02-01 17:31 | 2015-02-01 17:31 | EST | 2015-02-01 22:31 | 0 | 60.0111 | 59.956 | 59.9711 | -0.055026 | -0.039957 |  |  | No | No | 59.5 | 0.4711 | 2015
EI_2015-02-01_232859 | 2015-02-01 18:29 | 2015-02-01 18:29 | EST | 2015-02-01 23:29 | 0 | 60.0528 | 60.0304 | 60.0213 | -0.022368 | -0.031449 |  |  | No | No | 59.5 | 0.5213 | 2015
EI_2015-02-02_002216 | 2015-02-01 19:22 | 2015-02-01 19:22 | EST | 2015-02-02 00:22 | 0 | 60.029 | 59.9993 | 60.0018 | -0.02973 | -0.027224 |  |  | No | No | 59.5 | 0.5018 | 2015
EI_2015-02-02_014146 | 2015-02-01 20:42 | 2015-02-01 20:42 | EST | 2015-02-02 01:42 | 0 | 59.9754 | 60.0012 | 60.0173 | 0.025804 | 0.041943 |  |  | No | No | 59.5 | 0.5173 | 2015
EI_2015-02-02_015613 | 2015-02-01 20:56 | 2015-02-01 20:56 | EST | 2015-02-02 01:56 | 0 | 59.9846 | 60.0046 | 60.0247 | 0.020053 | 0.040126 |  |  | No | No | 59.5 | 0.5247 | 2015
EI_2015-02-02_025207 | 2015-02-01 21:52 | 2015-02-01 21:52 | EST | 2015-02-02 02:52 | 0 | 60.0369 | 60.0145 | 60.0024 | -0.022449 | -0.034519 |  |  | No | No | 59.5 | 0.5024 | 2015
EI_2015-02-02_143333 | 2015-02-02 09:34 | 2015-02-02 09:34 | EST | 2015-02-02 14:34 | 257 | 59.9931 | 59.9747 | 59.9756 | -0.018437 | -0.017549 | -1393.9064 | -1464.4876 | No | No | 59.5 | 0.4756 | 2015
EI_2015-02-03_233347 | 2015-02-03 18:34 | 2015-02-03 18:34 | EST | 2015-02-03 23:34 | 604 | 59.9841 | 59.9592 | 59.9568 | -0.024884 | -0.027277 | -2427.2392 | -2214.3591 | No | No | 59.5 | 0.4568 | 2015
EI_2015-02-07_015608 | 2015-02-06 20:56 | 2015-02-06 20:56 | EST | 2015-02-07 01:56 | 494 | 59.995 | 59.9685 | 59.9712 | -0.026463 | -0.023776 | -1866.774 | -2077.6999 | No | No | 59.5 | 0.4712 | 2015
EI_2015-02-07_025532 | 2015-02-06 21:56 | 2015-02-06 21:56 | EST | 2015-02-07 02:56 | 849 | 60.0151 | 59.9718 | 59.9724 | -0.043242 | -0.042687 | -1963.3624 | -1988.9099 | No | No | 59.5 | 0.4724 | 2015
EI_2015-02-08_005517 | 2015-02-07 19:55 | 2015-02-07 19:55 | EST | 2015-02-08 00:55 | 1478 | 60.0094 | 59.9491 | 59.9453 | -0.06024 | -0.064055 | -2453.4989 | -2307.3933 | Yes | Yes | 59.5 | 0.4453 | 2015
EI_2015-02-08_142808 | 2015-02-08 09:28 | 2015-02-08 09:28 | EST | 2015-02-08 14:28 | 645 | 60.0198 | 59.9807 | 59.9881 | -0.039116 | -0.031733 | -1648.9623 | -2032.5973 | No | No | 59.5 | 0.4881 | 2015
EI_2015-02-15_005416 | 2015-02-14 19:54 | 2015-02-14 19:54 | EST | 2015-02-15 00:54 | 1282 | 60.013 | 59.9709 | 59.9683 | -0.042048 | -0.044688 | -3048.8641 | -2868.78 | No | No | 59.5 | 0.4683 | 2015
EI_2015-02-15_173405 | 2015-02-15 12:34 | 2015-02-15 12:34 | EST | 2015-02-15 17:34 | 755 | 60.0165 | 59.9831 | 59.9883 | -0.033401 | -0.028244 | -2260.3792 | -2673.1775 | No | No | 59.5 | 0.4883 | 2015
EI_2015-02-16_143747 | 2015-02-16 09:38 | 2015-02-16 09:38 | EST | 2015-02-16 14:38 | 756 | 60.0139 | 59.9788 | 59.9773 | -0.035051 | -0.036595 | -2156.8314 | -2065.8635 | No | No | 59.5 | 0.4773 | 2015
EI_2015-02-17_181147 | 2015-02-17 13:12 | 2015-02-17 13:12 | EST | 2015-02-17 18:12 | 876 | 60.0006 | 59.9697 | 59.9666 | -0.030913 | -0.034045 | -2833.7812 | -2573.0845 | No | No | 59.5 | 0.4666 | 2015
EI_2015-02-18_190613 | 2015-02-18 14:06 | 2015-02-18 14:06 | EST | 2015-02-18 19:06 | 1110 | 60.0257 | 59.9709 | 59.9847 | -0.054787 | -0.040957 | -2026.0241 | -2710.1454 | No | No | 59.5 | 0.4847 | 2015
EI_2015-02-19_074713 | 2015-02-19 02:47 | 2015-02-19 02:47 | EST | 2015-02-19 07:47 | 595 | 60.0197 | 59.982 | 59.9901 | -0.037725 | -0.02963 | -1577.2191 | -2008.0874 | No | No | 59.5 | 0.4901 | 2015
EI_2015-02-19_135714 | 2015-02-19 08:57 | 2015-02-19 08:57 | EST | 2015-02-19 13:57 | 586 | 59.9979 | 59.9848 | 59.9753 | -0.013035 | -0.022556 | -4495.7354 | -2597.9982 | No | No | 59.5 | 0.4753 | 2015
EI_2015-02-21_090837 | 2015-02-21 04:09 | 2015-02-21 04:09 | EST | 2015-02-21 09:09 | 1100 | 59.9905 | 59.9627 | 59.9597 | -0.027833 | -0.030792 | -3952.1484 | -3572.3014 | No | No | 59.5 | 0.4597 | 2015
EI_2015-02-21_153119 | 2015-02-21 10:31 | 2015-02-21 10:31 | EST | 2015-02-21 15:31 | 1251 | 59.9821 | 59.9508 | 59.9439 | -0.031299 | -0.038204 | -3996.9155 | -3274.4892 | Yes | No | 59.5 | 0.4439 | 2015
EI_2015-02-22_061105 | 2015-02-22 01:11 | 2015-02-22 01:11 | EST | 2015-02-22 06:11 | 700 | 59.9921 | 59.9524 | 59.9611 | -0.039659 | -0.030967 | -1765.0492 | -2260.4884 | No | No | 59.5 | 0.4611 | 2015
EI_2015-02-24_024019 | 2015-02-23 21:40 | 2015-02-23 21:40 | EST | 2015-02-24 02:40 | 1197 | 60.0219 | 59.9802 | 59.9877 | -0.041695 | -0.034229 | -2870.8805 | -3497.0062 | No | No | 59.5 | 0.4877 | 2015
EI_2015-02-24_091915 | 2015-02-24 04:19 | 2015-02-24 04:19 | EST | 2015-02-24 09:19 | 610 | 60.0037 | 59.9732 | 59.9713 | -0.030537 | -0.032421 | -1997.608 | -1881.5177 | No | No | 59.5 | 0.4713 | 2015
EI_2015-02-25_183856 | 2015-02-25 13:39 | 2015-02-25 13:39 | EST | 2015-02-25 18:39 | 572 | 60.0003 | 59.9752 | 59.97 | -0.025171 | -0.030325 | -2272.4213 | -1886.2513 | No | No | 59.5 | 0.47 | 2015
EI_2015-02-26_201105 | 2015-02-26 15:11 | 2015-02-26 15:11 | EST | 2015-02-26 20:11 | 986 | 59.9952 | 59.9625 | 59.9637 | -0.032711 | -0.031482 | -3014.2878 | -3131.9977 | No | No | 59.5 | 0.4637 | 2015
EI_2015-02-28_123140 | 2015-02-28 07:32 | 2015-02-28 07:32 | EST | 2015-02-28 12:32 | 1330 | 60.0047 | 59.9488 | 59.9512 | -0.055944 | -0.053551 | -2377.385 | -2483.6046 | Yes | Yes | 59.5 | 0.4512 | 2015
EI_2015-03-02_033708 | 2015-03-01 22:37 | 2015-03-01 22:37 | EST | 2015-03-02 03:37 | -600 | 60.0226 | 60.048 | 60.0433 | 0.025493 | 0.020745 | -2353.5919 | -2892.2578 | No | No | 59.5 | 0.5433 | 2015
EI_2015-03-02_114539 | 2015-03-02 06:46 | 2015-03-02 06:46 | EST | 2015-03-02 11:46 | 1160 | 60.0031 | 59.953 | 59.9585 | -0.050101 | -0.044619 | -2315.3432 | -2599.7984 | Yes | No | 59.5 | 0.4585 | 2015
EI_2015-03-03_170120 | 2015-03-03 12:01 | 2015-03-03 12:01 | EST | 2015-03-03 17:01 | 1190 | 60.0027 | 59.9437 | 59.9476 | -0.059025 | -0.055093 | -2016.0999 | -2159.9727 | Yes | Yes | 59.5 | 0.4476 | 2015
EI_2015-03-05_041858 | 2015-03-04 23:19 | 2015-03-04 23:19 | EST | 2015-03-05 04:19 | 521 | 60.0027 | 59.9591 | 59.967 | -0.043615 | -0.035689 | -1194.5558 | -1459.8483 | No | No | 59.5 | 0.467 | 2015
EI_2015-03-11_102155 | 2015-03-11 06:22 | 2015-03-11 06:22 | EDT | 2015-03-11 10:22 | 1154 | 59.9899 | 59.9519 | 59.9511 | -0.038023 | -0.038832 | -3035.0223 | -2971.7432 | Yes | No | 59.5 | 0.4511 | 2015
EI_2015-03-14_082945 | 2015-03-14 04:30 | 2015-03-14 04:30 | EDT | 2015-03-14 08:30 | 1235 | 59.9927 | 59.9416 | 59.9395 | -0.051067 | -0.053201 | -2418.4056 | -2321.3763 | Yes | Yes | 59.5 | 0.4395 | 2015
EI_2015-03-14_142657 | 2015-03-14 10:27 | 2015-03-14 10:27 | EDT | 2015-03-14 14:27 | 624 | 59.9884 | 59.951 | 59.9563 | -0.037399 | -0.032094 | -1668.4946 | -1944.2741 | No | No | 59.5 | 0.4563 | 2015
EI_2015-03-16_175351 | 2015-03-16 13:54 | 2015-03-16 13:54 | EDT | 2015-03-16 17:54 | 862 | 59.9882 | 59.9458 | 59.944 | -0.042437 | -0.044206 | -2031.2665 | -1949.9658 | Yes | Yes | 59.5 | 0.444 | 2015
EI_2015-03-17_012547 | 2015-03-16 21:26 | 2015-03-16 21:26 | EDT | 2015-03-17 01:26 | 0 | 60.0035 | 60.0447 | 60.0462 | 0.04124 | 0.042737 |  |  | No | No | 59.5 | 0.5462 | 2015
EI_2015-03-18_000928 | 2015-03-17 20:09 | 2015-03-17 20:09 | EDT | 2015-03-18 00:09 | 0 | 60.0022 | 59.9538 | 59.9631 | -0.048353 | -0.03905 |  |  | No | No | 59.5 | 0.4631 | 2015
EI_2015-03-21_202256 | 2015-03-21 16:23 | 2015-03-21 16:23 | EDT | 2015-03-21 20:23 | 436 | 60.01 | 59.9773 | 59.9845 | -0.032717 | -0.025468 | -1332.6283 | -1711.9608 | No | No | 59.5 | 0.4845 | 2015
EI_2015-03-22_181501 | 2015-03-22 14:15 | 2015-03-22 14:15 | EDT | 2015-03-22 18:15 | 0 | 60.0117 | 59.9708 | 59.9756 | -0.040943 | -0.036118 |  |  | No | No | 59.5 | 0.4756 | 2015
EI_2015-03-25_104510 | 2015-03-25 06:45 | 2015-03-25 06:45 | EDT | 2015-03-25 10:45 | 506 | 59.9917 | 59.9803 | 59.9719 | -0.011426 | -0.01978 | -4428.3309 | -2558.1498 | No | No | 59.5 | 0.4719 | 2015
EI_2015-03-27_034145 | 2015-03-26 23:42 | 2015-03-26 23:42 | EDT | 2015-03-27 03:42 | 720 | 59.9972 | 59.959 | 59.9609 | -0.038151 | -0.036276 | -1887.2391 | -1984.7777 | No | No | 59.5 | 0.4609 | 2015
EI_2015-03-27_223826 | 2015-03-27 18:38 | 2015-03-27 18:38 | EDT | 2015-03-27 22:38 | 0 | 59.9854 | 60.0279 | 60.0224 | 0.042531 | 0.037019 |  |  | No | No | 59.5 | 0.5224 | 2015
EI_2015-03-29_221603 | 2015-03-29 18:16 | 2015-03-29 18:16 | EDT | 2015-03-29 22:16 | 0 | 59.9895 | 60.0229 | 60.0254 | 0.03344 | 0.035923 |  |  | No | No | 59.5 | 0.5254 | 2015
EI_2015-03-31_010326 | 2015-03-30 21:03 | 2015-03-30 21:03 | EDT | 2015-03-31 01:03 | 0 | 59.9791 | 59.946 | 59.9468 | -0.033066 | -0.032275 |  |  | No | No | 59.5 | 0.4468 | 2015
EI_2015-03-31_140741 | 2015-03-31 10:08 | 2015-03-31 10:08 | EDT | 2015-03-31 14:08 | 720 | 59.9988 | 59.957 | 59.9616 | -0.041785 | -0.037193 | -1723.1009 | -1935.8698 | No | No | 59.5 | 0.4616 | 2015
EI_2015-04-01_163532 | 2015-04-01 12:36 | 2015-04-01 12:36 | EDT | 2015-04-01 16:36 | 565 | 59.989 | 59.9634 | 59.9575 | -0.025529 | -0.031461 | -2213.1755 | -1795.847 | No | No | 59.5 | 0.4575 | 2015
EI_2015-04-01_210219 | 2015-04-01 17:02 | 2015-04-01 17:02 | EDT | 2015-04-01 21:02 | 0 | 59.988 | 59.9568 | 59.9537 | -0.031247 | -0.034324 |  |  | No | No | 59.5 | 0.4537 | 2015
EI_2015-04-02_020154 | 2015-04-01 22:02 | 2015-04-01 22:02 | EDT | 2015-04-02 02:02 | 0 | 59.981 | 59.9431 | 59.9475 | -0.037964 | -0.033526 |  |  | No | No | 59.5 | 0.4475 | 2015
EI_2015-04-02_082510 | 2015-04-02 04:25 | 2015-04-02 04:25 | EDT | 2015-04-02 08:25 | 973 | 60.0034 | 59.9519 | 59.9504 | -0.051531 | -0.053024 | -1888.1752 | -1835.0163 | Yes | Yes | 59.5 | 0.4504 | 2015
EI_2015-04-03_014709 | 2015-04-02 21:47 | 2015-04-02 21:47 | EDT | 2015-04-03 01:47 | 1168 | 59.9919 | 59.9446 | 59.9439 | -0.047374 | -0.048049 | -2465.4816 | -2430.8653 | Yes | Yes | 59.5 | 0.4439 | 2015
EI_2015-04-03_115301 | 2015-04-03 07:53 | 2015-04-03 07:53 | EDT | 2015-04-03 11:53 | 600 | 60.0052 | 59.9855 | 59.9796 | -0.019673 | -0.025583 | -3049.9346 | -2345.3266 | No | No | 59.5 | 0.4796 | 2015
EI_2015-04-04_094629 | 2015-04-04 05:46 | 2015-04-04 05:46 | EDT | 2015-04-04 09:46 | 0 | 59.9701 | 60.031 | 60.0116 | 0.060836 | 0.041476 |  |  | No | No | 59.5 | 0.5116 | 2015
EI_2015-04-05_145959 | 2015-04-05 11:00 | 2015-04-05 11:00 | EDT | 2015-04-05 15:00 | 0 | 60.0269 | 59.9671 | 59.9763 | -0.059817 | -0.050638 |  |  | No | No | 59.5 | 0.4763 | 2015
EI_2015-04-06_141326 | 2015-04-06 10:13 | 2015-04-06 10:13 | EDT | 2015-04-06 14:13 | 850 | 59.9829 | 59.9502 | 59.9419 | -0.032723 | -0.040982 | -2597.5728 | -2074.0568 | Yes | Yes | 59.5 | 0.4419 | 2015
EI_2015-04-06_145116 | 2015-04-06 10:51 | 2015-04-06 10:51 | EDT | 2015-04-06 14:51 | 831 | 59.9916 | 59.9534 | 59.9514 | -0.038289 | -0.040243 | -2170.3375 | -2064.96 | Yes | No | 59.5 | 0.4514 | 2015
EI_2015-04-07_163941 | 2015-04-07 12:40 | 2015-04-07 12:40 | EDT | 2015-04-07 16:40 | 1724 | 59.9995 | 59.931 | 59.9364 | -0.068445 | -0.063055 | -2518.8284 | -2734.109 | No | No | 59.5 | 0.4364 | 2015
EI_2015-04-12_033057 | 2015-04-11 23:31 | 2015-04-11 23:31 | EDT | 2015-04-12 03:31 | 0 | 60.0189 | 59.9857 | 59.9863 | -0.033249 | -0.032605 |  |  | No | No | 59.5 | 0.4863 | 2015
EI_2015-04-12_114849 | 2015-04-12 07:49 | 2015-04-12 07:49 | EDT | 2015-04-12 11:49 | 0 | 60.0119 | 59.9586 | 59.9637 | -0.053269 | -0.048169 |  |  | No | No | 59.5 | 0.4637 | 2015
EI_2015-04-12_155858 | 2015-04-12 11:59 | 2015-04-12 11:59 | EDT | 2015-04-12 15:59 | 725 | 59.9991 | 59.9659 | 59.9581 | -0.033212 | -0.041 | -2182.9594 | -1768.2769 | No | No | 59.5 | 0.4581 | 2015
EI_2015-04-13_190430 | 2015-04-13 15:05 | 2015-04-13 15:05 | EDT | 2015-04-13 19:04 | 620 | 60.0166 | 59.9701 | 59.9815 | -0.046536 | -0.035101 | -1332.3117 | -1766.3466 | No | No | 59.5 | 0.4815 | 2015
EI_2015-04-13_200013 | 2015-04-13 16:00 | 2015-04-13 16:00 | EDT | 2015-04-13 20:00 | 0 | 60.0137 | 59.9716 | 59.9745 | -0.042056 | -0.03917 |  |  | No | No | 59.5 | 0.4745 | 2015
EI_2015-04-14_021738 | 2015-04-13 22:18 | 2015-04-13 22:18 | EDT | 2015-04-14 02:18 | 0 | 60.0112 | 59.966 | 59.9779 | -0.045226 | -0.033324 |  |  | No | No | 59.5 | 0.4779 | 2015
EI_2015-04-14_120341 | 2015-04-14 08:04 | 2015-04-14 08:04 | EDT | 2015-04-14 12:04 | 561 | 59.9974 | 59.966 | 59.9653 | -0.031465 | -0.032142 | -1782.9206 | -1745.3711 | No | No | 59.5 | 0.4653 | 2015
EI_2015-04-15_081148 | 2015-04-15 04:12 | 2015-04-15 04:12 | EDT | 2015-04-15 08:12 | 916 | 59.9975 | 59.9694 | 59.9597 | -0.028056 | -0.037755 | -3264.8634 | -2426.1986 | Yes | No | 59.5 | 0.4597 | 2015
EI_2015-04-15_155952 | 2015-04-15 12:00 | 2015-04-15 12:00 | EDT | 2015-04-15 16:00 | 0 | 60.0149 | 59.9567 | 59.9688 | -0.058198 | -0.046144 |  |  | No | No | 59.5 | 0.4688 | 2015
EI_2015-04-19_195657 | 2015-04-19 15:57 | 2015-04-19 15:57 | EDT | 2015-04-19 19:57 | 628 | 59.9919 | 59.9544 | 59.9501 | -0.037545 | -0.0418 | -1672.6591 | -1502.4001 | No | No | 59.5 | 0.4501 | 2015
EI_2015-04-20_223435 | 2015-04-20 18:35 | 2015-04-20 18:35 | EDT | 2015-04-20 22:35 | 739 | 59.9772 | 59.9553 | 59.9471 | -0.021857 | -0.030092 | -3381.033 | -2455.8021 | No | No | 59.5 | 0.4471 | 2015
EI_2015-04-21_060444 | 2015-04-21 02:05 | 2015-04-21 02:05 | EDT | 2015-04-21 06:05 | 0 | 59.975 | 60.0281 | 60.0184 | 0.053122 | 0.043417 |  |  | No | No | 59.5 | 0.5184 | 2015
EI_2015-04-22_091800 | 2015-04-22 05:18 | 2015-04-22 05:18 | EDT | 2015-04-22 09:18 | 707 | 60.0053 | 59.9699 | 59.9679 | -0.035416 | -0.037432 | -1996.2625 | -1888.7485 | No | No | 59.5 | 0.4679 | 2015
EI_2015-04-24_041015 | 2015-04-24 00:10 | 2015-04-24 00:10 | EDT | 2015-04-24 04:10 | 0 | 60.018 | 59.987 | 59.9847 | -0.031064 | -0.033332 |  |  | No | No | 59.5 | 0.4847 | 2015
EI_2015-04-24_041532 | 2015-04-24 00:16 | 2015-04-24 00:16 | EDT | 2015-04-24 04:16 | 772 | 60.0113 | 59.9724 | 59.9737 | -0.038909 | -0.037568 | -1984.1281 | -2054.9484 | No | No | 59.5 | 0.4737 | 2015
EI_2015-04-24_222333 | 2015-04-24 18:24 | 2015-04-24 18:24 | EDT | 2015-04-24 22:24 | 0 | 60.0037 | 59.9684 | 59.9619 | -0.035312 | -0.041776 |  |  | No | No | 59.5 | 0.4619 | 2015
EI_2015-04-25_031918 | 2015-04-24 23:19 | 2015-04-24 23:19 | EDT | 2015-04-25 03:19 | 1172 | 60.0044 | 59.9496 | 59.953 | -0.054841 | -0.051439 | -2137.1028 | -2278.4248 | Yes | Yes | 59.5 | 0.453 | 2015
EI_2015-04-25_044423 | 2015-04-25 00:44 | 2015-04-25 00:44 | EDT | 2015-04-25 04:44 | 0 | 59.9821 | 59.9625 | 59.9523 | -0.019654 | -0.029804 |  |  | No | No | 59.5 | 0.4523 | 2015
EI_2015-04-26_121914 | 2015-04-26 08:19 | 2015-04-26 08:19 | EDT | 2015-04-26 12:19 | 0 | 59.9688 | 60.0173 | 60.0081 | 0.048515 | 0.039292 |  |  | No | No | 59.5 | 0.5081 | 2015
EI_2015-05-01_095455 | 2015-05-01 05:55 | 2015-05-01 05:55 | EDT | 2015-05-01 09:55 | 0 | 59.9894 | 60.0329 | 60.0233 | 0.043494 | 0.033912 |  |  | No | No | 59.5 | 0.5233 | 2015
EI_2015-05-01_172045 | 2015-05-01 13:21 | 2015-05-01 13:21 | EDT | 2015-05-01 17:21 | 750 | 60.0074 | 59.9586 | 59.9634 | -0.048851 | -0.04401 | -1535.2692 | -1704.1426 | No | No | 59.5 | 0.4634 | 2015
EI_2015-05-03_123955 | 2015-05-03 08:40 | 2015-05-03 08:40 | EDT | 2015-05-03 12:40 | 0 | 59.9889 | 60.0377 | 60.0302 | 0.048813 | 0.041332 |  |  | No | No | 59.5 | 0.5302 | 2015
EI_2015-05-04_222153 | 2015-05-04 18:22 | 2015-05-04 18:22 | EDT | 2015-05-04 22:22 | 0 | 60.0107 | 59.9729 | 59.9764 | -0.037814 | -0.034276 |  |  | No | No | 59.5 | 0.4764 | 2015
EI_2015-05-05_021738 | 2015-05-04 22:18 | 2015-05-04 22:18 | EDT | 2015-05-05 02:18 | 785 | 59.9856 | 59.9541 | 59.9488 | -0.031513 | -0.036833 | -2490.9962 | -2131.2658 | No | No | 59.5 | 0.4488 | 2015
EI_2015-05-07_131830 | 2015-05-07 09:19 | 2015-05-07 09:19 | EDT | 2015-05-07 13:19 | 0 | 59.9826 | 60.0167 | 60.0177 | 0.034104 | 0.035119 |  |  | No | No | 59.5 | 0.5177 | 2015
EI_2015-05-07_183439 | 2015-05-07 14:35 | 2015-05-07 14:35 | EDT | 2015-05-07 18:35 | 632 | 60.0054 | 59.9738 | 59.9716 | -0.031558 | -0.033807 | -2002.6558 | -1869.4463 | No | No | 59.5 | 0.4716 | 2015
EI_2015-05-07_212735 | 2015-05-07 17:28 | 2015-05-07 17:28 | EDT | 2015-05-07 21:28 | 614.5 | 60.012 | 59.9777 | 59.9691 | -0.03431 | -0.0429 | -1791.0252 | -1432.406 | No | No | 59.5 | 0.4691 | 2015
EI_2015-05-09_215100 | 2015-05-09 17:51 | 2015-05-09 17:51 | EDT | 2015-05-09 21:51 | 1020 | 60.002 | 59.9428 | 59.9499 | -0.059123 | -0.052061 | -1725.2063 | -1959.2281 | Yes | Yes | 59.5 | 0.4499 | 2015
EI_2015-05-10_122122 | 2015-05-10 08:21 | 2015-05-10 08:21 | EDT | 2015-05-10 12:21 | 0 | 59.9779 | 60.0257 | 60.019 | 0.047865 | 0.041145 |  |  | No | No | 59.5 | 0.519 | 2015
EI_2015-05-12_194028 | 2015-05-12 15:40 | 2015-05-12 15:40 | EDT | 2015-05-12 19:40 | 635 | 60.0104 | 59.9769 | 59.9739 | -0.033495 | -0.036538 | -1895.7775 | -1737.9221 | No | No | 59.5 | 0.4739 | 2015
EI_2015-05-13_123751 | 2015-05-13 08:38 | 2015-05-13 08:38 | EDT | 2015-05-13 12:38 | 640 | 60.0131 | 59.9733 | 59.9832 | -0.039728 | -0.029855 | -1610.9484 | -2143.6765 | No | No | 59.5 | 0.4832 | 2015
EI_2015-05-14_144845 | 2015-05-14 10:49 | 2015-05-14 10:49 | EDT | 2015-05-14 14:49 | 0 | 59.9877 | 59.9567 | 59.955 | -0.031011 | -0.032697 |  |  | No | No | 59.5 | 0.455 | 2015
EI_2015-05-14_204142 | 2015-05-14 16:42 | 2015-05-14 16:42 | EDT | 2015-05-14 20:42 | 418 | 60.0015 | 59.9682 | 59.9693 | -0.033244 | -0.032157 | -1257.3601 | -1299.8651 | No | No | 59.5 | 0.4693 | 2015
EI_2015-05-15_185418 | 2015-05-15 14:54 | 2015-05-15 14:54 | EDT | 2015-05-15 18:54 | 0 | 60.0115 | 59.9692 | 59.964 | -0.042304 | -0.047461 |  |  | No | No | 59.5 | 0.464 | 2015
EI_2015-05-15_223842 | 2015-05-15 18:39 | 2015-05-15 18:39 | EDT | 2015-05-15 22:39 | 0 | 60.0234 | 59.9767 | 59.9812 | -0.046685 | -0.042181 |  |  | No | No | 59.5 | 0.4812 | 2015
EI_2015-05-16_095753 | 2015-05-16 05:58 | 2015-05-16 05:58 | EDT | 2015-05-16 09:58 | 0 | 60.0182 | 59.9658 | 59.9717 | -0.052379 | -0.04647 |  |  | No | No | 59.5 | 0.4717 | 2015
EI_2015-05-17_184840 | 2015-05-17 14:49 | 2015-05-17 14:49 | EDT | 2015-05-17 18:49 | 750 | 60.0005 | 59.9594 | 59.9639 | -0.041032 | -0.036555 | -1827.8315 | -2051.7134 | No | No | 59.5 | 0.4639 | 2015
EI_2015-05-17_211406 | 2015-05-17 17:14 | 2015-05-17 17:14 | EDT | 2015-05-17 21:14 | 780 | 60.0049 | 59.9695 | 59.9717 | -0.035406 | -0.033177 | -2203.0337 | -2351.0335 | No | No | 59.5 | 0.4717 | 2015
EI_2015-05-20_042724 | 2015-05-20 00:27 | 2015-05-20 00:27 | EDT | 2015-05-20 04:27 | 600 | 59.988 | 59.9506 | 59.959 | -0.037313 | -0.028956 | -1608.0175 | -2072.0798 | No | No | 59.5 | 0.459 | 2015
EI_2015-05-20_062720 | 2015-05-20 02:27 | 2015-05-20 02:27 | EDT | 2015-05-20 06:27 | 0 | 59.9886 | 59.952 | 59.9556 | -0.036606 | -0.033 |  |  | No | No | 59.5 | 0.4556 | 2015
EI_2015-05-20_212040 | 2015-05-20 17:21 | 2015-05-20 17:21 | EDT | 2015-05-20 21:21 | 700 | 59.9713 | 59.962 | 59.9493 | -0.0092706 | -0.021969 | -7550.7141 | -3186.2964 | No | No | 59.5 | 0.4493 | 2015
EI_2015-05-21_110450 | 2015-05-21 07:05 | 2015-05-21 07:05 | EDT | 2015-05-21 11:05 | 0 | 59.9991 | 60.0369 | 60.0352 | 0.037776 | 0.036105 |  |  | No | No | 59.5 | 0.5352 | 2015
EI_2015-05-23_062000 | 2015-05-23 02:20 | 2015-05-23 02:20 | EDT | 2015-05-23 06:20 | 856 | 59.9934 | 59.9537 | 59.9499 | -0.039705 | -0.043479 | -2155.9142 | -1968.7573 | Yes | Yes | 59.5 | 0.4499 | 2015
EI_2015-05-23_171141 | 2015-05-23 13:12 | 2015-05-23 13:12 | EDT | 2015-05-23 17:12 | 0 | 59.9992 | 59.9464 | 59.9556 | -0.052807 | -0.043561 |  |  | No | No | 59.5 | 0.4556 | 2015
EI_2015-05-23_214441 | 2015-05-23 17:45 | 2015-05-23 17:45 | EDT | 2015-05-23 21:45 | 663 | 59.9982 | 59.9767 | 59.9629 | -0.021506 | -0.035314 | -3082.8059 | -1877.438 | No | No | 59.5 | 0.4629 | 2015
EI_2015-05-24_075948 | 2015-05-24 04:00 | 2015-05-24 04:00 | EDT | 2015-05-24 08:00 | 0 | 59.9892 | 60.0379 | 60.0403 | 0.048647 | 0.051067 |  |  | No | No | 59.5 | 0.5403 | 2015
EI_2015-05-24_122502 | 2015-05-24 08:25 | 2015-05-24 08:25 | EDT | 2015-05-24 12:25 | 0 | 59.9901 | 60.0398 | 60.0383 | 0.04969 | 0.048156 |  |  | No | No | 59.5 | 0.5383 | 2015
EI_2015-05-24_194918 | 2015-05-24 15:49 | 2015-05-24 15:49 | EDT | 2015-05-24 19:49 | 0 | 59.9907 | 59.9589 | 59.9576 | -0.031782 | -0.033094 |  |  | No | No | 59.5 | 0.4576 | 2015
EI_2015-05-25_165930 | 2015-05-25 13:00 | 2015-05-25 13:00 | EDT | 2015-05-25 17:00 | 630 | 60.006 | 59.9592 | 59.9631 | -0.046825 | -0.042931 | -1345.4232 | -1467.4765 | No | No | 59.5 | 0.4631 | 2015
EI_2015-05-25_212634 | 2015-05-25 17:27 | 2015-05-25 17:27 | EDT | 2015-05-25 21:27 | 975 | 59.9865 | 59.9483 | 59.9471 | -0.03821 | -0.039417 | -2551.7212 | -2473.5502 | Yes | No | 59.5 | 0.4471 | 2015
EI_2015-05-28_031103 | 2015-05-27 23:11 | 2015-05-27 23:11 | EDT | 2015-05-28 03:11 | 0 | 59.989 | 59.9501 | 59.9523 | -0.038826 | -0.036661 |  |  | No | No | 59.5 | 0.4523 | 2015
EI_2015-05-31_130954 | 2015-05-31 09:10 | 2015-05-31 09:10 | EDT | 2015-05-31 13:10 | 0 | 59.9893 | 60.0253 | 60.0267 | 0.035978 | 0.037349 |  |  | No | No | 59.5 | 0.5267 | 2015
EI_2015-05-31_195523 | 2015-05-31 15:55 | 2015-05-31 15:55 | EDT | 2015-05-31 19:55 | 960 | 59.9954 | 59.9542 | 59.9518 | -0.041205 | -0.043611 | -2329.7877 | -2201.289 | Yes | Yes | 59.5 | 0.4518 | 2015
EI_2015-06-01_032008 | 2015-05-31 23:20 | 2015-05-31 23:20 | EDT | 2015-06-01 03:20 | 548 | 60.0236 | 59.9946 | 59.9979 | -0.029001 | -0.025664 | -1889.5657 | -2135.2792 | No | No | 59.5 | 0.4979 | 2015
EI_2015-06-01_121424 | 2015-06-01 08:14 | 2015-06-01 08:14 | EDT | 2015-06-01 12:14 | 0 | 60.0094 | 59.9647 | 59.9732 | -0.044681 | -0.03618 |  |  | No | No | 59.5 | 0.4732 | 2015
EI_2015-06-03_220829 | 2015-06-03 18:08 | 2015-06-03 18:08 | EDT | 2015-06-03 22:08 | 0 | 60.0136 | 59.9595 | 59.9625 | -0.054093 | -0.051054 |  |  | No | No | 59.5 | 0.4625 | 2015
EI_2015-06-04_113107 | 2015-06-04 07:31 | 2015-06-04 07:31 | EDT | 2015-06-04 11:31 | 567 | 60.0024 | 59.9703 | 59.9702 | -0.032097 | -0.032194 | -1766.5369 | -1761.1772 | No | No | 59.5 | 0.4702 | 2015
EI_2015-06-04_192354 | 2015-06-04 15:24 | 2015-06-04 15:24 | EDT | 2015-06-04 19:24 | 0 | 59.9954 | 59.9581 | 59.961 | -0.037256 | -0.034358 |  |  | No | No | 59.5 | 0.461 | 2015
EI_2015-06-06_011332 | 2015-06-05 21:14 | 2015-06-05 21:14 | EDT | 2015-06-06 01:14 | 0 | 59.9791 | 59.9596 | 59.9477 | -0.019465 | -0.031362 |  |  | No | No | 59.5 | 0.4477 | 2015
EI_2015-06-07_123546 | 2015-06-07 08:36 | 2015-06-07 08:36 | EDT | 2015-06-07 12:36 | 556 | 59.9867 | 59.9586 | 59.9567 | -0.028164 | -0.030044 | -1974.1263 | -1850.6142 | No | No | 59.5 | 0.4567 | 2015
EI_2015-06-07_185412 | 2015-06-07 14:54 | 2015-06-07 14:54 | EDT | 2015-06-07 18:54 | 0 | 60.0124 | 60.0456 | 60.0544 | 0.033185 | 0.042014 |  |  | No | No | 59.5 | 0.5544 | 2015
EI_2015-06-07_190014 | 2015-06-07 15:00 | 2015-06-07 15:00 | EDT | 2015-06-07 19:00 | 0 | 59.986 | 59.953 | 59.9493 | -0.032986 | -0.036657 |  |  | No | No | 59.5 | 0.4493 | 2015
EI_2015-06-07_201800 | 2015-06-07 16:18 | 2015-06-07 16:18 | EDT | 2015-06-07 20:18 | 0 | 59.9923 | 59.9655 | 59.9607 | -0.026771 | -0.031606 |  |  | No | No | 59.5 | 0.4607 | 2015
EI_2015-06-08_203849 | 2015-06-08 16:39 | 2015-06-08 16:39 | EDT | 2015-06-08 20:39 | 850 | 60.0132 | 59.979 | 59.9703 | -0.034168 | -0.042914 | -2487.7432 | -1980.6986 | No | No | 59.5 | 0.4703 | 2015
EI_2015-06-09_224948 | 2015-06-09 18:50 | 2015-06-09 18:50 | EDT | 2015-06-09 22:50 | 1260 | 60.0065 | 59.9511 | 59.951 | -0.055412 | -0.055545 | -2273.8936 | -2268.4467 | Yes | Yes | 59.5 | 0.451 | 2015
EI_2015-06-11_220356 | 2015-06-11 18:04 | 2015-06-11 18:04 | EDT | 2015-06-11 22:04 | 705 | 60.0153 | 59.9841 | 59.982 | -0.031259 | -0.033333 | -2255.3566 | -2115.002 | No | No | 59.5 | 0.482 | 2015
EI_2015-06-15_231942 | 2015-06-15 19:20 | 2015-06-15 19:20 | EDT | 2015-06-15 23:20 | 1045 | 59.9856 | 59.9535 | 59.9473 | -0.032088 | -0.038288 | -3256.6972 | -2729.3234 | Yes | No | 59.5 | 0.4473 | 2015
EI_2015-06-16_201343 | 2015-06-16 16:14 | 2015-06-16 16:14 | EDT | 2015-06-16 20:14 | 598 | 59.9809 | 59.9619 | 59.9575 | -0.01904 | -0.023412 | -3140.7361 | -2554.2209 | No | No | 59.5 | 0.4575 | 2015
EI_2015-06-18_160952 | 2015-06-18 12:10 | 2015-06-18 12:10 | EDT | 2015-06-18 16:10 | 792 | 60.0115 | 59.9629 | 59.9718 | -0.048553 | -0.039673 | -1631.191 | -1996.3034 | No | No | 59.5 | 0.4718 | 2015
EI_2015-06-19_062705 | 2015-06-19 02:27 | 2015-06-19 02:27 | EDT | 2015-06-19 06:27 | 1130 | 59.9939 | 59.9729 | 59.9633 | -0.020985 | -0.030601 | -5384.8329 | -3692.6868 | No | No | 59.5 | 0.4633 | 2015
EI_2015-06-21_181648 | 2015-06-21 14:17 | 2015-06-21 14:17 | EDT | 2015-06-21 18:17 | 538 | 60.0011 | 59.9664 | 59.9691 | -0.034724 | -0.032023 | -1549.3398 | -1680.0199 | No | No | 59.5 | 0.4691 | 2015
EI_2015-06-27_123501 | 2015-06-27 08:35 | 2015-06-27 08:35 | EDT | 2015-06-27 12:35 | 0 | 59.975 | 60.0157 | 60.0141 | 0.040688 | 0.039093 |  |  | No | No | 59.5 | 0.5141 | 2015
EI_2015-06-27_212806 | 2015-06-27 17:28 | 2015-06-27 17:28 | EDT | 2015-06-27 21:28 | 0 | 60.0117 | 59.9675 | 59.9735 | -0.044195 | -0.038213 |  |  | No | No | 59.5 | 0.4735 | 2015
EI_2015-07-01_115002 | 2015-07-01 07:50 | 2015-07-01 07:50 | EDT | 2015-07-01 11:50 | 0 | 59.9851 | 60.0197 | 60.0226 | 0.034562 | 0.037485 |  |  | No | No | 59.5 | 0.5226 | 2015
EI_2015-07-08_182720 | 2015-07-08 14:27 | 2015-07-08 14:27 | EDT | 2015-07-08 18:27 | 1041 | 59.9946 | 59.9524 | 59.9647 | -0.042145 | -0.029888 | -2470.0571 | -3482.9854 | No | No | 59.5 | 0.4647 | 2015
EI_2015-07-09_215316 | 2015-07-09 17:53 | 2015-07-09 17:53 | EDT | 2015-07-09 21:53 | 660 | 59.9991 | 59.9742 | 59.9724 | -0.024977 | -0.026742 | -2642.4733 | -2467.9855 | No | No | 59.5 | 0.4724 | 2015
EI_2015-07-10_031755 | 2015-07-09 23:18 | 2015-07-09 23:18 | EDT | 2015-07-10 03:18 | 540 | 60.0155 | 59.9834 | 59.9841 | -0.03211 | -0.031406 | -1681.7294 | -1719.4077 | No | No | 59.5 | 0.4841 | 2015
EI_2015-07-12_202021 | 2015-07-12 16:20 | 2015-07-12 16:20 | EDT | 2015-07-12 20:20 | 522 | 59.9913 | 59.9664 | 59.9609 | -0.024902 | -0.030381 | -2096.2241 | -1718.1542 | No | No | 59.5 | 0.4609 | 2015
EI_2015-07-14_025837 | 2015-07-13 22:59 | 2015-07-13 22:59 | EDT | 2015-07-14 02:59 | 620 | 60.0303 | 60.0112 | 60.0069 | -0.019064 | -0.023412 | -3252.1957 | -2648.2158 | No | No | 59.5 | 0.5069 | 2015
EI_2015-07-20_200930 | 2015-07-20 16:10 | 2015-07-20 16:10 | EDT | 2015-07-20 20:10 | 650 | 59.9881 | 59.9727 | 59.9598 | -0.015423 | -0.02828 | -4214.4903 | -2298.4619 | No | No | 59.5 | 0.4598 | 2015
EI_2015-07-22_215936 | 2015-07-22 18:00 | 2015-07-22 18:00 | EDT | 2015-07-22 22:00 | 790 | 60.0165 | 59.9989 | 59.9931 | -0.017647 | -0.023426 | -4476.6452 | -3372.279 | No | No | 59.5 | 0.4931 | 2015
EI_2015-07-22_225900 | 2015-07-22 18:59 | 2015-07-22 18:59 | EDT | 2015-07-22 22:59 | 700 | 60.03 | 60.0098 | 60.0043 | -0.020118 | -0.025664 | -3479.4352 | -2727.5718 | No | No | 59.5 | 0.5043 | 2015
EI_2015-07-23_071828 | 2015-07-23 03:18 | 2015-07-23 03:18 | EDT | 2015-07-23 07:18 | 850 | 59.9833 | 59.9506 | 59.953 | -0.032749 | -0.030344 | -2595.4897 | -2801.2119 | No | No | 59.5 | 0.453 | 2015
EI_2015-07-24_175329 | 2015-07-24 13:53 | 2015-07-24 13:53 | EDT | 2015-07-24 17:53 | 1130 | 60.0028 | 59.9551 | 59.952 | -0.047748 | -0.050812 | -2366.5797 | -2223.8734 | Yes | Yes | 59.5 | 0.452 | 2015
EI_2015-07-24_192957 | 2015-07-24 15:30 | 2015-07-24 15:30 | EDT | 2015-07-24 19:30 | 0 | 59.9989 | 59.967 | 59.9591 | -0.031989 | -0.039845 |  |  | No | Yes | 59.5 | 0.4591 | 2015
EI_2015-07-27_144226 | 2015-07-27 10:42 | 2015-07-27 10:42 | EDT | 2015-07-27 14:42 | 900 | 59.9849 | 59.9579 | 59.9504 | -0.027017 | -0.034486 | -3331.2233 | -2609.7685 | No | No | 59.5 | 0.4504 | 2015
EI_2015-07-28_100600 | 2015-07-28 06:06 | 2015-07-28 06:06 | EDT | 2015-07-28 10:06 | 1206 | 59.9812 | 59.9511 | 59.9455 | -0.030152 | -0.03575 | -3999.718 | -3373.4574 | No | No | 59.5 | 0.4455 | 2015
EI_2015-07-30_140139 | 2015-07-30 10:02 | 2015-07-30 10:02 | EDT | 2015-07-30 14:02 | 1300 | 60.015 | 59.9753 | 59.9713 | -0.039707 | -0.04374 | -3273.9948 | -2972.138 | No | No | 59.5 | 0.4713 | 2015
EI_2015-07-31_024256 | 2015-07-30 22:43 | 2015-07-30 22:43 | EDT | 2015-07-31 02:43 | 850 | 60.0079 | 59.9798 | 59.9696 | -0.02815 | -0.038343 | -3019.5674 | -2216.8488 | No | No | 59.5 | 0.4696 | 2015
EI_2015-08-05_124454 | 2015-08-05 08:45 | 2015-08-05 08:45 | EDT | 2015-08-05 12:45 | 0 | 59.9779 | 60.014 | 60.0103 | 0.036136 | 0.032394 |  |  | No | No | 59.5 | 0.5103 | 2015
EI_2015-08-05_193855 | 2015-08-05 15:39 | 2015-08-05 15:39 | EDT | 2015-08-05 19:39 | 1198 | 59.9853 | 59.9515 | 59.9421 | -0.033822 | -0.043186 | -3542.0231 | -2774.0657 | Yes | Yes | 59.5 | 0.4421 | 2015
EI_2015-08-06_114720 | 2015-08-06 07:47 | 2015-08-06 07:47 | EDT | 2015-08-06 11:47 | 892 | 60.0146 | 59.9754 | 59.9741 | -0.039127 | -0.040471 | -2279.7807 | -2204.0432 | No | No | 59.5 | 0.4741 | 2015
EI_2015-08-07_133412 | 2015-08-07 09:34 | 2015-08-07 09:34 | EDT | 2015-08-07 13:34 | 626 | 60.0111 | 59.9747 | 59.9774 | -0.0364 | -0.033662 | -1719.7812 | -1859.6856 | No | No | 59.5 | 0.4774 | 2015
EI_2015-08-10_021500 | 2015-08-09 22:15 | 2015-08-09 22:15 | EDT | 2015-08-10 02:15 | 994 | 60.009 | 59.9688 | 59.9727 | -0.0402 | -0.036302 | -2472.6433 | -2738.1524 | No | No | 59.5 | 0.4727 | 2015
EI_2015-08-10_042046 | 2015-08-10 00:21 | 2015-08-10 00:21 | EDT | 2015-08-10 04:21 | 310 | 59.9996 | 59.977 | 59.9711 | -0.022599 | -0.028468 | -1371.7529 | -1088.9278 | No | No | 59.5 | 0.4711 | 2015
EI_2015-08-10_135752 | 2015-08-10 09:58 | 2015-08-10 09:58 | EDT | 2015-08-10 13:58 | 847 | 59.9944 | 59.9602 | 59.9591 | -0.034215 | -0.035276 | -2475.5484 | -2401.0702 | No | No | 59.5 | 0.4591 | 2015
EI_2015-08-11_063950 | 2015-08-11 02:40 | 2015-08-11 02:40 | EDT | 2015-08-11 06:40 | 1240 | 60.0085 | 59.96 | 59.9568 | -0.048508 | -0.051695 | -2556.2561 | -2398.6906 | Yes | Yes | 59.5 | 0.4568 | 2015
EI_2015-08-12_035102 | 2015-08-11 23:51 | 2015-08-11 23:51 | EDT | 2015-08-12 03:51 | 701 | 60.0124 | 59.9805 | 59.9854 | -0.031873 | -0.026981 | -2199.3665 | -2598.1594 | No | No | 59.5 | 0.4854 | 2015
EI_2015-08-21_182854 | 2015-08-21 14:29 | 2015-08-21 14:29 | EDT | 2015-08-21 18:29 | 860 | 59.9992 | 59.9638 | 59.961 | -0.035369 | -0.038195 | -2431.4746 | -2251.5958 | Yes | No | 59.5 | 0.461 | 2015
EI_2015-08-22_202751 | 2015-08-22 16:28 | 2015-08-22 16:28 | EDT | 2015-08-22 20:28 | 685 | 59.9787 | 59.952 | 59.9608 | -0.026717 | -0.017881 | -2563.8747 | -3830.8998 | No | No | 59.5 | 0.4608 | 2015
EI_2015-08-23_203412 | 2015-08-23 16:34 | 2015-08-23 16:34 | EDT | 2015-08-23 20:34 | 761 | 59.979 | 59.9605 | 59.9553 | -0.018524 | -0.023675 | -4108.2649 | -3214.3012 | No | No | 59.5 | 0.4553 | 2015
EI_2015-08-30_230922 | 2015-08-30 19:09 | 2015-08-30 19:09 | EDT | 2015-08-30 23:09 | 726 | 59.9811 | 59.9536 | 59.9493 | -0.027445 | -0.031782 | -2645.3165 | -2284.2839 | No | No | 59.5 | 0.4493 | 2015
EI_2015-09-03_091705 | 2015-09-03 05:17 | 2015-09-03 05:17 | EDT | 2015-09-03 09:17 | 830 | 60.0066 | 59.9863 | 59.976 | -0.020289 | -0.030617 | -4090.8848 | -2710.8701 | No | No | 59.5 | 0.476 | 2015
EI_2015-09-04_204546 | 2015-09-04 16:46 | 2015-09-04 16:46 | EDT | 2015-09-04 20:46 | 742.6 | 59.9977 | 59.9674 | 59.9669 | -0.030346 | -0.030832 | -2447.0952 | -2408.5698 | No | No | 59.5 | 0.4669 | 2015
EI_2015-09-05_010657 | 2015-09-04 21:07 | 2015-09-04 21:07 | EDT | 2015-09-05 01:07 | 1310 | 59.9897 | 59.9387 | 59.9374 | -0.05103 | -0.052293 | -2567.1148 | -2505.1124 | Yes | Yes | 59.5 | 0.4374 | 2015
EI_2015-09-05_095357 | 2015-09-05 05:54 | 2015-09-05 05:54 | EDT | 2015-09-05 09:54 | 0 | 60.0139 | 59.9778 | 59.9769 | -0.036125 | -0.036978 |  |  | No | No | 59.5 | 0.4769 | 2015
EI_2015-09-05_100613 | 2015-09-05 06:06 | 2015-09-05 06:06 | EDT | 2015-09-05 10:06 | 814 | 60.01 | 59.9737 | 59.974 | -0.036285 | -0.035989 | -2243.3819 | -2261.8143 | No | No | 59.5 | 0.474 | 2015
EI_2015-09-06_125833 | 2015-09-06 08:59 | 2015-09-06 08:59 | EDT | 2015-09-06 12:59 | 0 | 59.9818 | 60.0238 | 60.0181 | 0.042052 | 0.036332 |  |  | No | No | 59.5 | 0.5181 | 2015
EI_2015-09-08_111815 | 2015-09-08 07:18 | 2015-09-08 07:18 | EDT | 2015-09-08 11:18 | 720 | 60.009 | 59.9721 | 59.9738 | -0.036944 | -0.035237 | -1948.9029 | -2043.3025 | No | No | 59.5 | 0.4738 | 2015
EI_2015-09-08_124833 | 2015-09-08 08:49 | 2015-09-08 08:49 | EDT | 2015-09-08 12:49 | 614 | 60.0065 | 59.9729 | 59.9795 | -0.033607 | -0.02702 | -1826.9929 | -2272.4328 | No | No | 59.5 | 0.4795 | 2015
EI_2015-09-10_025148 | 2015-09-09 22:52 | 2015-09-09 22:52 | EDT | 2015-09-10 02:52 | 740 | 60.0172 | 59.9735 | 59.9788 | -0.043696 | -0.038385 | -1693.5178 | -1927.8167 | No | No | 59.5 | 0.4788 | 2015
EI_2015-09-10_131257 | 2015-09-10 09:13 | 2015-09-10 09:13 | EDT | 2015-09-10 13:13 | 0 | 60.0195 | 59.9741 | 59.9845 | -0.045422 | -0.035048 |  |  | No | No | 59.5 | 0.4845 | 2015
EI_2015-09-14_030605 | 2015-09-13 23:06 | 2015-09-13 23:06 | EDT | 2015-09-14 03:06 | 1198 | 59.9847 | 59.9538 | 59.9441 | -0.030869 | -0.040606 | -3880.8635 | -2950.284 | Yes | Yes | 59.5 | 0.4441 | 2015
EI_2015-09-14_035953 | 2015-09-14 | 2015-09-14 | EDT | 2015-09-14 04:00 | 0 | 60.0207 | 59.9767 | 59.9895 | -0.043958 | -0.03119 |  |  | No | No | 59.5 | 0.4895 | 2015
EI_2015-09-14_082630 | 2015-09-14 04:26 | 2015-09-14 04:26 | EDT | 2015-09-14 08:26 | 1225 | 60.0018 | 59.9527 | 59.9478 | -0.049149 | -0.054001 | -2492.4203 | -2268.4926 | Yes | Yes | 59.5 | 0.4478 | 2015
EI_2015-09-15_063016 | 2015-09-15 02:30 | 2015-09-15 02:30 | EDT | 2015-09-15 06:30 | -1520 | 60.0009 | 60.0528 | 60.0538 | 0.051897 | 0.052893 | -2928.8817 | -2873.7304 | No | Yes | 59.5 | 0.5538 | 2015
EI_2015-09-16_051731 | 2015-09-16 01:18 | 2015-09-16 01:18 | EDT | 2015-09-16 05:18 | 680 | 60.0098 | 59.9876 | 59.9826 | -0.022172 | -0.027174 | -3066.9628 | -2502.3924 | No | No | 59.5 | 0.4826 | 2015
EI_2015-09-20_202147 | 2015-09-20 16:22 | 2015-09-20 16:22 | EDT | 2015-09-20 20:22 | 0 | 60.0168 | 59.971 | 59.9787 | -0.045846 | -0.038101 |  |  | No | No | 59.5 | 0.4787 | 2015
EI_2015-09-20_205816 | 2015-09-20 16:58 | 2015-09-20 16:58 | EDT | 2015-09-20 20:58 | 695 | 60.0026 | 59.9699 | 59.9688 | -0.032641 | -0.033751 | -2129.2137 | -2059.2121 | No | No | 59.5 | 0.4688 | 2015
EI_2015-09-21_065518 | 2015-09-21 02:55 | 2015-09-21 02:55 | EDT | 2015-09-21 06:55 | 590 | 60.0036 | 59.9704 | 59.9683 | -0.033198 | -0.035344 | -1777.1937 | -1669.3128 | No | No | 59.5 | 0.4683 | 2015
EI_2015-09-29_004613 | 2015-09-28 20:46 | 2015-09-28 20:46 | EDT | 2015-09-29 00:46 | 1238 | 60.01 | 59.9452 | 59.957 | -0.064754 | -0.052987 | -1911.8499 | -2336.4388 | No | No | 59.5 | 0.457 | 2015
EI_2015-09-30_042952 | 2015-09-30 00:30 | 2015-09-30 00:30 | EDT | 2015-09-30 04:30 | 0 | 60.0102 | 59.9715 | 59.976 | -0.038753 | -0.034235 |  |  | No | No | 59.5 | 0.476 | 2015
EI_2015-10-01_050328 | 2015-10-01 01:03 | 2015-10-01 01:03 | EDT | 2015-10-01 05:03 | 587 | 60.0065 | 59.9749 | 59.9716 | -0.031634 | -0.034889 | -1855.6121 | -1682.491 | No | No | 59.5 | 0.4716 | 2015
EI_2015-10-02_130504 | 2015-10-02 09:05 | 2015-10-02 09:05 | EDT | 2015-10-02 13:05 | 0 | 59.9803 | 60.0318 | 60.0209 | 0.051538 | 0.040651 |  |  | No | No | 59.5 | 0.5209 | 2015
EI_2015-10-04_041049 | 2015-10-04 00:11 | 2015-10-04 00:11 | EDT | 2015-10-04 04:11 | 1185 | 60.0081 | 59.9374 | 59.9407 | -0.070694 | -0.067418 | -1676.2302 | -1757.6883 | Yes | Yes | 59.5 | 0.4407 | 2015
EI_2015-10-04_042141 | 2015-10-04 00:22 | 2015-10-04 00:22 | EDT | 2015-10-04 04:22 | 0 | 60.013 | 60.0437 | 60.0484 | 0.030736 | 0.035401 |  |  | No | No | 59.5 | 0.5484 | 2015
EI_2015-10-09_124111 | 2015-10-09 08:41 | 2015-10-09 08:41 | EDT | 2015-10-09 12:41 | 681 | 60.0102 | 59.9744 | 59.9741 | -0.035868 | -0.036145 | -1898.6339 | -1884.0671 | No | No | 59.5 | 0.4741 | 2015
EI_2015-10-09_183222 | 2015-10-09 14:32 | 2015-10-09 14:32 | EDT | 2015-10-09 18:32 | 0 | 60.0089 | 59.9731 | 59.9728 | -0.035828 | -0.036124 |  |  | No | No | 59.5 | 0.4728 | 2015
EI_2015-10-11_121501 | 2015-10-11 08:15 | 2015-10-11 08:15 | EDT | 2015-10-11 12:15 | 0 | 59.986 | 60.0337 | 60.0278 | 0.047737 | 0.04182 |  |  | No | No | 59.5 | 0.5278 | 2015
EI_2015-10-12_060217 | 2015-10-12 02:02 | 2015-10-12 02:02 | EDT | 2015-10-12 06:02 | 630 | 59.9923 | 59.9681 | 59.9597 | -0.024204 | -0.032554 | -2602.849 | -1935.223 | No | No | 59.5 | 0.4597 | 2015
EI_2015-10-13_221536 | 2015-10-13 18:16 | 2015-10-13 18:16 | EDT | 2015-10-13 22:16 | 860 | 59.9875 | 59.9457 | 59.9433 | -0.041738 | -0.04417 | -2060.474 | -1947.0377 | Yes | Yes | 59.5 | 0.4433 | 2015
EI_2015-10-14_114009 | 2015-10-14 07:40 | 2015-10-14 07:40 | EDT | 2015-10-14 11:40 | 620 | 60.0136 | 59.9688 | 59.9749 | -0.044886 | -0.038738 | -1381.2722 | -1600.4853 | No | No | 59.5 | 0.4749 | 2015
EI_2015-10-14_184214 | 2015-10-14 14:42 | 2015-10-14 14:42 | EDT | 2015-10-14 18:42 | 0 | 59.9871 | 59.9655 | 59.9587 | -0.021618 | -0.02842 |  |  | No | No | 59.5 | 0.4587 | 2015
EI_2015-10-14_194701 | 2015-10-14 15:47 | 2015-10-14 15:47 | EDT | 2015-10-14 19:47 | 640 | 59.988 | 59.9586 | 59.953 | -0.029381 | -0.034963 | -2178.2983 | -1830.4872 | No | No | 59.5 | 0.453 | 2015
EI_2015-10-16_131801 | 2015-10-16 09:18 | 2015-10-16 09:18 | EDT | 2015-10-16 13:18 | 0 | 59.9781 | 59.9445 | 59.9421 | -0.033572 | -0.035999 |  |  | No | No | 59.5 | 0.4421 | 2015
EI_2015-10-17_100003 | 2015-10-17 06:00 | 2015-10-17 06:00 | EDT | 2015-10-17 10:00 | 0 | 59.9828 | 60.0277 | 60.0186 | 0.044867 | 0.035794 |  |  | No | No | 59.5 | 0.5186 | 2015
EI_2015-10-18_052912 | 2015-10-18 01:29 | 2015-10-18 01:29 | EDT | 2015-10-18 05:29 | 0 | 59.9933 | 59.9601 | 59.9546 | -0.03328 | -0.038743 |  |  | No | No | 59.5 | 0.4546 | 2015
EI_2015-10-19_140325 | 2015-10-19 10:03 | 2015-10-19 10:03 | EDT | 2015-10-19 14:03 | 0 | 59.9797 | 59.9636 | 59.9495 | -0.016048 | -0.030156 |  |  | No | No | 59.5 | 0.4495 | 2015
EI_2015-10-19_143856 | 2015-10-19 10:39 | 2015-10-19 10:39 | EDT | 2015-10-19 14:39 | 755 | 60.0154 | 59.9728 | 59.9771 | -0.042572 | -0.038263 | -1773.4493 | -1973.2059 | No | No | 59.5 | 0.4771 | 2015
EI_2015-10-19_211336 | 2015-10-19 17:14 | 2015-10-19 17:14 | EDT | 2015-10-19 21:14 | 0 | 59.987 | 59.9595 | 59.9548 | -0.027499 | -0.032157 |  |  | No | No | 59.5 | 0.4548 | 2015
EI_2015-10-20_182149 | 2015-10-20 14:22 | 2015-10-20 14:22 | EDT | 2015-10-20 18:22 | 0 | 60.0186 | 59.9714 | 59.979 | -0.047108 | -0.039557 |  |  | No | No | 59.5 | 0.479 | 2015
EI_2015-10-20_205502 | 2015-10-20 16:55 | 2015-10-20 16:55 | EDT | 2015-10-20 20:55 | 810 | 60.0047 | 59.9552 | 59.9603 | -0.049518 | -0.044399 | -1635.7645 | -1824.3449 | Yes | No | 59.5 | 0.4603 | 2015
EI_2015-10-25_135424 | 2015-10-25 09:54 | 2015-10-25 09:54 | EDT | 2015-10-25 13:54 | 956 | 59.9796 | 59.9429 | 59.9453 | -0.036696 | -0.034338 | -2605.1773 | -2784.1265 | No | No | 59.5 | 0.4453 | 2015
EI_2015-11-02_153500 | 2015-11-02 10:35 | 2015-11-02 10:35 | EST | 2015-11-02 15:35 | 460 | 59.9987 | 59.9743 | 59.9698 | -0.024419 | -0.028932 | -1883.782 | -1589.9298 | No | No | 59.5 | 0.4698 | 2015
EI_2015-11-02_225040 | 2015-11-02 17:51 | 2015-11-02 17:51 | EST | 2015-11-02 22:51 | 460 | 60.0028 | 59.9625 | 59.9673 | -0.040358 | -0.035512 | -1139.7912 | -1295.3205 | No | No | 59.5 | 0.4673 | 2015
EI_2015-11-05_182623 | 2015-11-05 13:26 | 2015-11-05 13:26 | EST | 2015-11-05 18:26 | 470 | 59.9933 | 59.9729 | 59.9629 | -0.020354 | -0.030389 | -2309.1026 | -1546.5965 | No | No | 59.5 | 0.4629 | 2015
EI_2015-11-10_051428 | 2015-11-10 00:14 | 2015-11-10 00:14 | EST | 2015-11-10 05:14 | 0 | 60.0045 | 59.9604 | 59.9807 | -0.04408 | -0.023749 |  |  | No | No | 59.5 | 0.4807 | 2015
EI_2015-11-12_163232 | 2015-11-12 11:33 | 2015-11-12 11:33 | EST | 2015-11-12 16:33 | 1280 | 60.0134 | 59.952 | 59.9574 | -0.061354 | -0.055999 | -2086.2395 | -2285.7534 | Yes | Yes | 59.5 | 0.4574 | 2015
EI_2015-11-14_013236 | 2015-11-13 20:33 | 2015-11-13 20:33 | EST | 2015-11-14 01:33 | 700 | 60.011 | 59.9775 | 59.99 | -0.033514 | -0.021036 | -2088.7004 | -3327.6808 | No | No | 59.5 | 0.49 | 2015
EI_2015-11-16_060247 | 2015-11-16 01:03 | 2015-11-16 01:03 | EST | 2015-11-16 06:03 | 600 | 60.0023 | 59.9761 | 59.9732 | -0.026203 | -0.029135 | -2289.7942 | -2059.3627 | No | No | 59.5 | 0.4732 | 2015
EI_2015-11-18_100116 | 2015-11-18 05:01 | 2015-11-18 05:01 | EST | 2015-11-18 10:01 | 0 | 59.9648 | 60.0126 | 60.0078 | 0.047861 | 0.043013 |  |  | No | No | 59.5 | 0.5078 | 2015
EI_2015-11-21_071504 | 2015-11-21 02:15 | 2015-11-21 02:15 | EST | 2015-11-21 07:15 | 700 | 60.0194 | 59.9631 | 59.9785 | -0.05631 | -0.040862 | -1243.1086 | -1713.0896 | No | No | 59.5 | 0.4785 | 2015
EI_2015-11-21_170808 | 2015-11-21 12:08 | 2015-11-21 12:08 | EST | 2015-11-21 17:08 | 1200 | 59.9864 | 59.9517 | 59.9387 | -0.034727 | -0.047723 | -3455.4955 | -2514.5331 | Yes | Yes | 59.5 | 0.4387 | 2015
EI_2015-11-22_145842 | 2015-11-22 09:59 | 2015-11-22 09:59 | EST | 2015-11-22 14:59 | 600 | 60.0275 | 59.9956 | 59.9949 | -0.031896 | -0.032587 | -1881.1265 | -1841.2221 | No | No | 59.5 | 0.4949 | 2015
EI_2015-11-22_172947 | 2015-11-22 12:30 | 2015-11-22 12:30 | EST | 2015-11-22 17:30 | 0 | 60.0007 | 59.9666 | 59.9601 | -0.034099 | -0.040558 |  |  | No | No | 59.5 | 0.4601 | 2015
EI_2015-11-22_205219 | 2015-11-22 15:52 | 2015-11-22 15:52 | EST | 2015-11-22 20:52 | 0 | 59.9885 | 60.0198 | 60.0279 | 0.031361 | 0.03942 |  |  | No | No | 59.5 | 0.5279 | 2015
EI_2015-11-23_134423 | 2015-11-23 08:44 | 2015-11-23 08:44 | EST | 2015-11-23 13:44 | 1161 | 59.994 | 59.9476 | 59.9481 | -0.046452 | -0.045912 | -2499.337 | -2528.7623 | Yes | Yes | 59.5 | 0.4481 | 2015
EI_2015-11-25_134652 | 2015-11-25 08:47 | 2015-11-25 08:47 | EST | 2015-11-25 13:47 | 620 | 60.0009 | 59.9714 | 59.9702 | -0.029452 | -0.030694 | -2105.1497 | -2019.9069 | No | No | 59.5 | 0.4702 | 2015
EI_2015-11-27_103141 | 2015-11-27 05:32 | 2015-11-27 05:32 | EST | 2015-11-27 10:32 | 1080 | 59.98 | 59.9518 | 59.9492 | -0.028199 | -0.030769 | -3829.869 | -3509.9866 | No | No | 59.5 | 0.4492 | 2015
EI_2015-11-29_011242 | 2015-11-28 20:13 | 2015-11-28 20:13 | EST | 2015-11-29 01:13 | 620 | 59.986 | 59.9657 | 59.9586 | -0.020289 | -0.02742 | -3055.809 | -2261.1 | No | No | 59.5 | 0.4586 | 2015
EI_2015-11-29_171737 | 2015-11-29 12:18 | 2015-11-29 12:18 | EST | 2015-11-29 17:18 | 710 | 60.0057 | 59.9613 | 59.9598 | -0.044418 | -0.045918 | -1598.4471 | -1546.243 | No | No | 59.5 | 0.4598 | 2015
EI_2015-11-30_073543 | 2015-11-30 02:36 | 2015-11-30 02:36 | EST | 2015-11-30 07:36 | 800 | 60.009 | 59.9562 | 59.9657 | -0.052775 | -0.043314 | -1515.856 | -1846.9889 | No | No | 59.5 | 0.4657 | 2015
EI_2015-12-01_003401 | 2015-11-30 19:34 | 2015-11-30 19:34 | EST | 2015-12-01 00:34 | 600 | 60.0031 | 59.9693 | 59.9719 | -0.033854 | -0.031205 | -1772.2997 | -1922.7432 | No | No | 59.5 | 0.4719 | 2015
EI_2015-12-01_232052 | 2015-12-01 18:21 | 2015-12-01 18:21 | EST | 2015-12-01 23:21 | 950 | 60.0067 | 59.9858 | 59.9661 | -0.020946 | -0.040626 | -4535.3649 | -2338.3874 | No | No | 59.5 | 0.4661 | 2016
EI_2015-12-04_204025 | 2015-12-04 15:40 | 2015-12-04 15:40 | EST | 2015-12-04 20:40 |  | 60.0032 | 59.9498 | 59.9612 | -0.053321 | -0.041962 |  |  | No | No | 59.5 | 0.4612 | 2016
EI_2015-12-05_223137 | 2015-12-05 17:32 | 2015-12-05 17:32 | EST | 2015-12-05 22:32 | 1031 | 59.988 | 59.945 | 59.948 | -0.043 | -0.04 | -2397.6744 | -2577.5 | Yes | Yes | 59.5 | 0.448 | 2016
EI_2015-12-05_225254 | 2015-12-05 17:53 | 2015-12-05 17:53 | EST | 2015-12-05 22:53 | 461 | 59.9833 | 59.9599 | 59.9534 | -0.023354 | -0.029857 | -1973.9535 | -1544.006 | No | No | 59.5 | 0.4534 | 2016
EI_2015-12-06_020142 | 2015-12-05 21:02 | 2015-12-05 21:02 | EST | 2015-12-06 02:02 | 566 | 60.0111 | 59.9761 | 59.9768 | -0.035004 | -0.034338 | -1616.9436 | -1648.2969 | No | No | 59.5 | 0.4768 | 2016
EI_2015-12-06_095515 | 2015-12-06 04:55 | 2015-12-06 04:55 | EST | 2015-12-06 09:55 |  | 59.9812 | 60.0231 | 60.0182 | 0.041901 | 0.036963 |  |  | No | No | 59.5 | 0.5182 | 2016
EI_2015-12-08_094458 | 2015-12-08 04:45 | 2015-12-08 04:45 | EST | 2015-12-08 09:45 |  | 59.9764 | 60.025 | 60.0069 | 0.048561 | 0.030501 |  |  | No | No | 59.5 | 0.5069 | 2016
EI_2015-12-09_083803 | 2015-12-09 03:38 | 2015-12-09 03:38 | EST | 2015-12-09 08:38 | 809 | 60.006 | 59.957 | 59.958 | -0.049 | -0.048 | -1651.0204 | -1685.4167 | Yes | Yes | 59.5 | 0.458 | 2016
EI_2015-12-09_160455 | 2015-12-09 11:05 | 2015-12-09 11:05 | EST | 2015-12-09 16:05 | 655 | 59.999 | 59.952 | 59.958 | -0.047 | -0.041 | -1393.617 | -1597.561 | Yes | Yes | 59.5 | 0.458 | 2016
EI_2015-12-11_032524 | 2015-12-10 22:25 | 2015-12-10 22:25 | EST | 2015-12-11 03:25 | 400 | 60.0191 | 60.0352 | 60.0417 | 0.016198 | 0.022648 | 2469.4187 | 1766.1343 | No | No | 59.5 | 0.5417 | 2016
EI_2015-12-11_045949 | 2015-12-11 | 2015-12-11 | EST | 2015-12-11 05:00 | 0 | 60.0147 | 59.9651 | 59.9797 | -0.049526 | -0.034977 |  |  | No | No | 59.5 | 0.4797 | 2016
EI_2015-12-14_131111 | 2015-12-14 08:11 | 2015-12-14 08:11 | EST | 2015-12-14 13:11 |  | 59.9897 | 59.9593 | 59.9584 | -0.030398 | -0.031249 |  |  | No | No | 59.5 | 0.4584 | 2016
EI_2015-12-15_000429 | 2015-12-14 19:04 | 2015-12-14 19:04 | EST | 2015-12-15 00:04 | 1040 | 60.011 | 59.977 | 59.968 | -0.034 | -0.043 | -3058.8235 | -2418.6047 | Yes | No | 59.5 | 0.468 | 2016
EI_2015-12-16_012703 | 2015-12-15 20:27 | 2015-12-15 20:27 | EST | 2015-12-16 01:27 | 840 | 60.016 | 59.965 | 59.959 | -0.051 | -0.057 | -1647.0588 | -1473.6842 | Yes | No | 59.5 | 0.459 | 2016
EI_2015-12-16_060324 | 2015-12-16 01:03 | 2015-12-16 01:03 | EST | 2015-12-16 06:03 | -320 | 59.9941 | 60.0227 | 60.0227 | 0.028512 | 0.028558 | -1122.3429 | -1120.5167 | No | No | 59.5 | 0.5227 | 2016
EI_2015-12-16_165542 | 2015-12-16 11:56 | 2015-12-16 11:56 | EST | 2015-12-16 16:56 | 361.2 | 60.0012 | 59.971 | 59.9694 | -0.030229 | -0.031833 | -1194.8778 | -1134.6654 | No | No | 59.5 | 0.4694 | 2016
EI_2015-12-18_134723 | 2015-12-18 08:47 | 2015-12-18 08:47 | EST | 2015-12-18 13:47 | 560.8 | 60.0051 | 59.9753 | 59.9708 | -0.029818 | -0.034295 | -1880.7723 | -1635.2426 | No | No | 59.5 | 0.4708 | 2016
EI_2015-12-18_184718 | 2015-12-18 13:47 | 2015-12-18 13:47 | EST | 2015-12-18 18:47 | 525 | 60.0125 | 59.9689 | 59.9775 | -0.043613 | -0.034967 | -1203.7625 | -1501.4077 | No | No | 59.5 | 0.4775 | 2016
EI_2015-12-23_112055 | 2015-12-23 06:21 | 2015-12-23 06:21 | EST | 2015-12-23 11:21 |  | 59.9805 | 60.0273 | 60.0232 | 0.046738 | 0.042658 |  |  | No | No | 59.5 | 0.5232 | 2016
EI_2015-12-23_180246 | 2015-12-23 13:03 | 2015-12-23 13:03 | EST | 2015-12-23 18:03 |  | 59.9779 | 59.9445 | 59.9417 | -0.033426 | -0.036181 |  |  | No | No | 59.5 | 0.4417 | 2016
EI_2015-12-27_164750 | 2015-12-27 11:48 | 2015-12-27 11:48 | EST | 2015-12-27 16:48 | 816 | 59.995 | 59.96 | 59.96 | -0.035 | -0.035 | -2331.4286 | -2331.4286 | Yes | No | 59.5 | 0.46 | 2016
EI_2016-01-02_083516 | 2016-01-02 03:35 | 2016-01-02 03:35 | EST | 2016-01-02 08:35 | 587 | 60.0089 | 59.9709 | 59.976 | -0.038006 | -0.032892 | -1544.5073 | -1784.6291 | No | No | 59.5 | 0.476 | 2016
EI_2016-01-04_210016 | 2016-01-04 16:00 | 2016-01-04 16:00 | EST | 2016-01-04 21:00 |  | 60.0221 | 59.9802 | 59.98 | -0.041947 | -0.042126 |  |  | No | No | 59.5 | 0.48 | 2016
EI_2016-01-05_081126 | 2016-01-05 03:11 | 2016-01-05 03:11 | EST | 2016-01-05 08:11 | 575 | 59.9984 | 59.9611 | 59.9636 | -0.037298 | -0.034755 | -1541.6319 | -1654.4159 | No | No | 59.5 | 0.4636 | 2016
EI_2016-01-06_002829 | 2016-01-05 19:28 | 2016-01-05 19:28 | EST | 2016-01-06 00:28 | 400 | 59.9897 | 59.9707 | 59.9583 | -0.019022 | -0.031417 | -2102.8248 | -1273.1811 | No | No | 59.5 | 0.4583 | 2016
EI_2016-01-06_112811 | 2016-01-06 06:28 | 2016-01-06 06:28 | EST | 2016-01-06 11:28 | 844 | 60.0007 | 59.9721 | 59.9696 | -0.028668 | -0.031125 | -2944.0566 | -2711.6821 | No | No | 59.5 | 0.4696 | 2016
EI_2016-01-07_155729 | 2016-01-07 10:57 | 2016-01-07 10:57 | EST | 2016-01-07 15:57 | 595 | 60.0119 | 59.9751 | 59.971 | -0.036799 | -0.040868 | -1616.9109 | -1455.9138 | No | No | 59.5 | 0.471 | 2016
EI_2016-01-09_071356 | 2016-01-09 02:14 | 2016-01-09 02:14 | EST | 2016-01-09 07:14 | 360 | 60.0133 | 59.9788 | 59.9831 | -0.034487 | -0.030193 | -1043.8597 | -1192.3352 | No | No | 59.5 | 0.4831 | 2016
EI_2016-01-09_083701 | 2016-01-09 03:37 | 2016-01-09 03:37 | EST | 2016-01-09 08:37 | 977 | 59.996 | 59.957 | 59.968 | -0.039 | -0.028 | -2505.1282 | -3489.2857 | Yes | No | 59.5 | 0.468 | 2016
EI_2016-01-10_154854 | 2016-01-10 10:49 | 2016-01-10 10:49 | EST | 2016-01-10 15:49 | 395 | 60.0177 | 59.9757 | 59.9853 | -0.041939 | -0.032384 | -941.8407 | -1219.7502 | No | No | 59.5 | 0.4853 | 2016
EI_2016-01-14_042202 | 2016-01-13 23:22 | 2016-01-13 23:22 | EST | 2016-01-14 04:22 | 671 | 60.0162 | 59.9842 | 59.9859 | -0.031989 | -0.030312 | -2097.6176 | -2213.6577 | No | No | 59.5 | 0.4859 | 2016
EI_2016-01-15_014413 | 2016-01-14 20:44 | 2016-01-14 20:44 | EST | 2016-01-15 01:44 |  | 60.0017 | 59.9693 | 59.9643 | -0.032378 | -0.037383 |  |  | No | No | 59.5 | 0.4643 | 2016
EI_2016-01-20_171802 | 2016-01-20 12:18 | 2016-01-20 12:18 | EST | 2016-01-20 17:18 | 729 | 59.9989 | 59.9658 | 59.9665 | -0.033134 | -0.032407 | -2200.17 | -2249.5108 | No | No | 59.5 | 0.4665 | 2016
EI_2016-01-22_212557 | 2016-01-22 16:26 | 2016-01-22 16:26 | EST | 2016-01-22 21:26 | 659 | 60.0071 | 59.9617 | 59.9676 | -0.045417 | -0.039523 | -1451.011 | -1667.3682 | No | No | 59.5 | 0.4676 | 2016
EI_2016-01-24_023911 | 2016-01-23 21:39 | 2016-01-23 21:39 | EST | 2016-01-24 02:39 | 452 | 59.9876 | 59.9644 | 59.9616 | -0.023248 | -0.025998 | -1944.2472 | -1738.5716 | No | No | 59.5 | 0.4616 | 2016
EI_2016-01-25_064704 | 2016-01-25 01:47 | 2016-01-25 01:47 | EST | 2016-01-25 06:47 | 1231 | 60.018 | 59.97 | 59.968 | -0.048 | -0.05 | -2564.5833 | -2462 | Yes | No | 59.5 | 0.468 | 2016
EI_2016-01-28_002157 | 2016-01-27 19:22 | 2016-01-27 19:22 | EST | 2016-01-28 00:22 | 755 | 60.004 | 59.967 | 59.971 | -0.037 | -0.033 | -2040.5405 | -2287.8788 | No | No | 59.5 | 0.471 | 2016
EI_2016-01-28_054430 | 2016-01-28 00:44 | 2016-01-28 00:44 | EST | 2016-01-28 05:44 | 700 | 60 | 59.984 | 59.965 | -0.016 | -0.035 | -4375 | -2000 | No | No | 59.5 | 0.465 | 2016
EI_2016-01-28_220008 | 2016-01-28 17:00 | 2016-01-28 17:00 | EST | 2016-01-28 22:00 |  | 59.9809 | 60.0306 | 60.0242 | 0.049666 | 0.043281 |  |  | No | No | 59.5 | 0.5242 | 2016
EI_2016-01-29_142129 | 2016-01-29 09:21 | 2016-01-29 09:21 | EST | 2016-01-29 14:21 | 434 | 59.9952 | 59.9734 | 59.9719 | -0.021751 | -0.023249 | -1995.3511 | -1866.7158 | No | No | 59.5 | 0.4719 | 2016
EI_2016-01-29_182125 | 2016-01-29 13:21 | 2016-01-29 13:21 | EST | 2016-01-29 18:21 | 915 | 59.995 | 59.971 | 59.954 | -0.024 | -0.041 | -3812.5 | -2231.7073 | Yes | Yes | 59.5 | 0.454 | 2016
EI_2016-01-29_231731 | 2016-01-29 18:18 | 2016-01-29 18:18 | EST | 2016-01-29 23:18 |  | 59.9927 | 60.0305 | 60.0368 | 0.037758 | 0.044101 |  |  | No | No | 59.5 | 0.5368 | 2016
EI_2016-01-30_023858 | 2016-01-29 21:39 | 2016-01-29 21:39 | EST | 2016-01-30 02:39 | 670 | 60.0075 | 59.9599 | 59.9651 | -0.047667 | -0.042432 | -1405.5714 | -1579.0033 | No | No | 59.5 | 0.4651 | 2016
EI_2016-01-31_131204 | 2016-01-31 08:12 | 2016-01-31 08:12 | EST | 2016-01-31 13:12 | 634 | 59.9866 | 59.969 | 59.9682 | -0.017589 | -0.018418 | -3604.5703 | -3442.271 | No | No | 59.5 | 0.4682 | 2016
EI_2016-01-31_230554 | 2016-01-31 18:06 | 2016-01-31 18:06 | EST | 2016-01-31 23:06 |  | 59.9806 | 60.0157 | 60.0179 | 0.035072 | 0.037274 |  |  | No | No | 59.5 | 0.5179 | 2016
EI_2016-02-01_083206 | 2016-02-01 03:32 | 2016-02-01 03:32 | EST | 2016-02-01 08:32 |  | 59.9997 | 60.0343 | 60.033 | 0.034649 | 0.03332 |  |  | No | No | 59.5 | 0.533 | 2016
EI_2016-02-01_150229 | 2016-02-01 10:02 | 2016-02-01 10:02 | EST | 2016-02-01 15:02 | 970 | 59.991 | 59.947 | 59.947 | -0.044 | -0.044 | -2204.5455 | -2204.5455 | Yes | Yes | 59.5 | 0.447 | 2016
EI_2016-02-03_200709 | 2016-02-03 15:07 | 2016-02-03 15:07 | EST | 2016-02-03 20:07 | 566 | 60.0075 | 59.9755 | 59.9732 | -0.031927 | -0.034261 | -1772.8014 | -1652.0017 | No | No | 59.5 | 0.4732 | 2016
EI_2016-02-04_162153 | 2016-02-04 11:22 | 2016-02-04 11:22 | EST | 2016-02-04 16:22 | 880 | 60.02 | 59.962 | 59.966 | -0.058 | -0.054 | -1517.2414 | -1629.6296 | Yes | No | 59.5 | 0.466 | 2016
EI_2016-02-06_212516 | 2016-02-06 16:25 | 2016-02-06 16:25 | EST | 2016-02-06 21:25 |  | 59.9626 | 59.9988 | 59.999 | 0.036191 | 0.036407 |  |  | No | No | 59.5 | 0.499 | 2016
EI_2016-02-07_182525 | 2016-02-07 13:25 | 2016-02-07 13:25 | EST | 2016-02-07 18:25 | 871 | 59.9986 | 59.9798 | 59.9859 | -0.018816 | -0.012712 | -4629.133 | -6852.0496 | No | No | 59.5 | 0.4859 | 2016
EI_2016-02-07_231031 | 2016-02-07 18:11 | 2016-02-07 18:11 | EST | 2016-02-07 23:11 |  | 59.9856 | 60.0156 | 60.0275 | 0.029933 | 0.041876 |  |  | No | No | 59.5 | 0.5275 | 2016
EI_2016-02-08_000054 | 2016-02-07 19:01 | 2016-02-07 19:01 | EST | 2016-02-08 00:01 |  | 60.0207 | 59.9676 | 59.9888 | -0.053116 | -0.031925 |  |  | No | No | 59.5 | 0.4888 | 2016
EI_2016-02-08_002329 | 2016-02-07 19:23 | 2016-02-07 19:23 | EST | 2016-02-08 00:23 |  | 60.0001 | 60.0079 | 60.0372 | 0.007784 | 0.0371 |  |  | No | No | 59.5 | 0.5372 | 2016
EI_2016-02-08_010902 | 2016-02-07 20:09 | 2016-02-07 20:09 | EST | 2016-02-08 01:09 |  | 59.9913 | 60.0215 | 60.0303 | 0.03026 | 0.039038 |  |  | No | No | 59.5 | 0.5303 | 2016
EI_2016-02-08_012156 | 2016-02-07 20:22 | 2016-02-07 20:22 | EST | 2016-02-08 01:22 |  | 59.9967 | 59.9604 | 59.9668 | -0.036341 | -0.029931 |  |  | No | No | 59.5 | 0.4668 | 2016
EI_2016-02-08_021140 | 2016-02-07 21:12 | 2016-02-07 21:12 | EST | 2016-02-08 02:12 |  | 60.0071 | 59.9793 | 59.9708 | -0.027834 | -0.036333 |  |  | No | No | 59.5 | 0.4708 | 2016
EI_2016-02-08_021735 | 2016-02-07 21:18 | 2016-02-07 21:18 | EST | 2016-02-08 02:18 |  | 60.007 | 59.974 | 59.972 | -0.033 | -0.035 |  |  | No | No | 59.5 | 0.472 | 2016
EI_2016-02-08_200356 | 2016-02-08 15:04 | 2016-02-08 15:04 | EST | 2016-02-08 20:04 | 1280 | 59.9736 | 59.9483 | 59.9503 | -0.025289 | -0.023276 | -5061.4008 | -5499.2053 | No | No | 59.5 | 0.4503 | 2016
EI_2016-02-13_205914 | 2016-02-13 15:59 | 2016-02-13 15:59 | EST | 2016-02-13 20:59 | 518 | 59.9955 | 59.9707 | 59.9717 | -0.024771 | -0.023776 | -2091.1174 | -2178.7063 | No | No | 59.5 | 0.4717 | 2016
EI_2016-02-15_015859 | 2016-02-14 20:59 | 2016-02-14 20:59 | EST | 2016-02-15 01:59 | 1237 | 59.992 | 59.9649 | 59.9604 | -0.027114 | -0.031581 | -4562.1724 | -3916.8622 | No | No | 59.5 | 0.4604 | 2016
EI_2016-02-16_133306 | 2016-02-16 08:33 | 2016-02-16 08:33 | EST | 2016-02-16 13:33 | 829 | 60.007 | 59.972 | 59.969 | -0.035 | -0.038 | -2368.5714 | -2181.5789 | Yes | No | 59.5 | 0.469 | 2016
EI_2016-02-19_225541 | 2016-02-19 17:56 | 2016-02-19 17:56 | EST | 2016-02-19 22:56 | 457 |  |  |  | 0 | 0 |  |  | No | No | 59.5 | -59.5 | 2016
EI_2016-02-20_012747 | 2016-02-19 20:28 | 2016-02-19 20:28 | EST | 2016-02-20 01:28 | 373 | 60.0014 | 59.978 | 59.9748 | -0.023344 | -0.026556 | -1597.8462 | -1404.5782 | No | No | 59.5 | 0.4748 | 2016
EI_2016-02-21_030538 | 2016-02-20 22:06 | 2016-02-20 22:06 | EST | 2016-02-21 03:06 | 915 | 59.989 | 59.96 | 59.959 | -0.029 | -0.03 | -3155.1724 | -3050 | Yes | No | 59.5 | 0.459 | 2016
EI_2016-02-22_095957 | 2016-02-22 05:00 | 2016-02-22 05:00 | EST | 2016-02-22 10:00 |  | 59.9953 | 60.028 | 60.035 | 0.032694 | 0.039663 |  |  | No | No | 59.5 | 0.535 | 2016
EI_2016-02-22_160615 | 2016-02-22 11:06 | 2016-02-22 11:06 | EST | 2016-02-22 16:06 | 750 | 59.9892 | 59.965 | 59.9556 | -0.02412 | -0.033549 | -3109.4883 | -2235.5155 | No | No | 59.5 | 0.4556 | 2016
EI_2016-02-22_163243 | 2016-02-22 11:33 | 2016-02-22 11:33 | EST | 2016-02-22 16:33 | 694 | 59.9884 | 59.9577 | 59.9551 | -0.030783 | -0.033342 | -2254.5131 | -2081.4363 | No | No | 59.5 | 0.4551 | 2016
EI_2016-03-01_175556 | 2016-03-01 12:56 | 2016-03-01 12:56 | EST | 2016-03-01 17:56 | 500 | 60.0171 | 59.9645 | 59.9778 | -0.052628 | -0.039339 | -950.0568 | -1271.0012 | No | No | 59.5 | 0.4778 | 2016
EI_2016-03-02_075329 | 2016-03-02 02:53 | 2016-03-02 02:53 | EST | 2016-03-02 07:53 | 1194 | 60.004 | 59.947 | 59.947 | -0.057 | -0.057 | -2094.7368 | -2094.7368 | Yes | Yes | 59.5 | 0.447 | 2016
EI_2016-03-02_171025 | 2016-03-02 12:10 | 2016-03-02 12:10 | EST | 2016-03-02 17:10 | 797 | 60.002 | 59.975 | 59.967 | -0.027 | -0.035 | -2951.8519 | -2277.1429 | No | No | 59.5 | 0.467 | 2016
EI_2016-03-04_162400 | 2016-03-04 11:24 | 2016-03-04 11:24 | EST | 2016-03-04 16:24 | 499 | 60.0036 | 59.9886 | 59.9729 | -0.014976 | -0.030674 | -3332.0888 | -1626.7606 | No | No | 59.5 | 0.4729 | 2016
EI_2016-03-04_211022 | 2016-03-04 16:10 | 2016-03-04 16:10 | EST | 2016-03-04 21:10 | 380 | 59.9976 | 59.9695 | 59.9729 | -0.028124 | -0.024687 | -1351.1654 | -1539.2536 | No | No | 59.5 | 0.4729 | 2016
EI_2016-03-05_225827 | 2016-03-05 17:58 | 2016-03-05 17:58 | EST | 2016-03-05 22:58 |  | 59.96 | 59.9948 | 59.9922 | 0.034777 | 0.03218 |  |  | No | No | 59.5 | 0.4922 | 2016
EI_2016-03-06_201159 | 2016-03-06 15:12 | 2016-03-06 15:12 | EST | 2016-03-06 20:12 | 895 | 59.99 | 59.958 | 59.949 | -0.032 | -0.041 | -2796.875 | -2182.9268 | Yes | Yes | 59.5 | 0.449 | 2016
EI_2016-03-08_035852 | 2016-03-07 22:59 | 2016-03-07 22:59 | EST | 2016-03-08 03:59 |  | 60.014 | 59.962 | 59.979 | -0.052 | -0.035 |  |  | No | No | 59.5 | 0.479 | 2016
EI_2016-03-08_145727 | 2016-03-08 09:57 | 2016-03-08 09:57 | EST | 2016-03-08 14:57 |  | 60.016 | 59.9767 | 59.9711 | -0.039286 | -0.044931 |  |  | No | No | 59.5 | 0.4711 | 2016
EI_2016-03-08_221539 | 2016-03-08 17:16 | 2016-03-08 17:16 | EST | 2016-03-08 22:16 | 679 | 60.0179 | 59.9687 | 59.9812 | -0.049218 | -0.036699 | -1379.5714 | -1850.2078 | No | No | 59.5 | 0.4812 | 2016
EI_2016-03-09_111327 | 2016-03-09 06:13 | 2016-03-09 06:13 | EST | 2016-03-09 11:13 |  | 59.9628 | 60.0165 | 60.0025 | 0.053731 | 0.03973 |  |  | No | No | 59.5 | 0.5025 | 2016
EI_2016-03-10_071010 | 2016-03-10 02:10 | 2016-03-10 02:10 | EST | 2016-03-10 07:10 | 657 | 59.9802 | 59.973 | 59.9492 | -0.0072206 | -0.030982 | -9098.9661 | -2120.6176 | No | No | 59.5 | 0.4492 | 2016
EI_2016-03-11_105548 | 2016-03-11 05:56 | 2016-03-11 05:56 | EST | 2016-03-11 10:56 |  | 60.004 | 60.0419 | 60.042 | 0.037945 | 0.037999 |  |  | No | No | 59.5 | 0.542 | 2016
EI_2016-03-11_142832 | 2016-03-11 09:29 | 2016-03-11 09:29 | EST | 2016-03-11 14:29 | 505 | 59.9963 | 59.9622 | 59.9629 | -0.03418 | -0.033439 | -1477.466 | -1510.1947 | No | No | 59.5 | 0.4629 | 2016
EI_2016-03-11_152258 | 2016-03-11 10:23 | 2016-03-11 10:23 | EST | 2016-03-11 15:23 | 463 | 60.0267 | 59.9909 | 59.9974 | -0.035799 | -0.029295 | -1293.3146 | -1580.4762 | No | No | 59.5 | 0.4974 | 2016
EI_2016-03-12_135535 | 2016-03-12 08:56 | 2016-03-12 08:56 | EST | 2016-03-12 13:56 | 623 | 59.993 | 59.956 | 59.946 | -0.037 | -0.047 | -1683.7838 | -1325.5319 | Yes | Yes | 59.5 | 0.446 | 2016
EI_2016-03-13_073934 | 2016-03-13 03:40 | 2016-03-13 03:40 | EDT | 2016-03-13 07:40 |  | 59.9947 | 60.0378 | 60.0344 | 0.043027 | 0.039676 |  |  | No | No | 59.5 | 0.5344 | 2016
EI_2016-03-13_111518 | 2016-03-13 07:15 | 2016-03-13 07:15 | EDT | 2016-03-13 11:15 |  | 59.9774 | 60.0298 | 60.0257 | 0.052367 | 0.048312 |  |  | No | No | 59.5 | 0.5257 | 2016
EI_2016-03-15_014558 | 2016-03-14 21:46 | 2016-03-14 21:46 | EDT | 2016-03-15 01:46 | 543 | 60.0333 | 60.0134 | 60.0076 | -0.019948 | -0.025707 | -2722.048 | -2112.2254 | No | No | 59.5 | 0.5076 | 2016
EI_2016-03-15_182857 | 2016-03-15 14:29 | 2016-03-15 14:29 | EDT | 2016-03-15 18:29 |  | 59.9725 | 59.9403 | 59.9402 | -0.032163 | -0.03228 |  |  | No | No | 59.5 | 0.4402 | 2016
EI_2016-03-16_101711 | 2016-03-16 06:17 | 2016-03-16 06:17 | EDT | 2016-03-16 10:17 |  | 59.9784 | 60.0298 | 60.0218 | 0.051421 | 0.043407 |  |  | No | No | 59.5 | 0.5218 | 2016
EI_2016-03-16_131914 | 2016-03-16 09:19 | 2016-03-16 09:19 | EDT | 2016-03-16 13:19 | 972 | 60.0057 | 59.9744 | 59.9738 | -0.031264 | -0.031906 | -3108.9869 | -3046.4823 | No | No | 59.5 | 0.4738 | 2016
EI_2016-03-16_174747 | 2016-03-16 13:48 | 2016-03-16 13:48 | EDT | 2016-03-16 17:48 | 889 | 60.009 | 59.96 | 59.963 | -0.049 | -0.046 | -1814.2857 | -1932.6087 | Yes | No | 59.5 | 0.463 | 2016
EI_2016-03-17_015513 | 2016-03-16 21:55 | 2016-03-16 21:55 | EDT | 2016-03-17 01:55 | 527 | 60.0227 | 59.9786 | 59.9871 | -0.044125 | -0.035614 | -1194.3354 | -1479.7447 | No | No | 59.5 | 0.4871 | 2016
EI_2016-03-17_091644 | 2016-03-17 05:17 | 2016-03-17 05:17 | EDT | 2016-03-17 09:17 | 675 | 60.0124 | 59.9681 | 59.9744 | -0.044312 | -0.038 | -1523.2919 | -1776.3108 | No | No | 59.5 | 0.4744 | 2016
EI_2016-03-18_031342 | 2016-03-17 23:14 | 2016-03-17 23:14 | EDT | 2016-03-18 03:14 |  | 60 | 59.965 | 59.97 | -0.035 | -0.03 |  |  | No | No | 59.5 | 0.47 | 2016
EI_2016-03-18_192852 | 2016-03-18 15:29 | 2016-03-18 15:29 | EDT | 2016-03-18 19:29 |  | 60.016 | 59.979 | 59.981 | -0.037 | -0.035 |  |  | No | No | 59.5 | 0.481 | 2016
EI_2016-03-19_100403 | 2016-03-19 06:04 | 2016-03-19 06:04 | EDT | 2016-03-19 10:04 |  | 59.9887 | 60.0361 | 60.0298 | 0.047398 | 0.041113 |  |  | No | No | 59.5 | 0.5298 | 2016
EI_2016-03-22_021446 | 2016-03-21 22:15 | 2016-03-21 22:15 | EDT | 2016-03-22 02:15 | 380 | 59.991 | 59.971 | 59.961 | -0.02 | -0.03 | -1900 | -1266.6667 | No | No | 59.5 | 0.461 | 2016
EI_2016-03-22_021448 | 2016-03-21 22:15 | 2016-03-21 22:15 | EDT | 2016-03-22 02:15 | 380 | 59.9911 | 59.9708 | 59.9619 | -0.020311 | -0.029245 | -1870.9172 | -1299.3507 | No | No | 59.5 | 0.4619 | 2016
EI_2016-03-22_153105 | 2016-03-22 11:31 | 2016-03-22 11:31 | EDT | 2016-03-22 15:31 | 1111 | 59.978 | 59.934 | 59.935 | -0.044 | -0.043 | -2525 | -2583.7209 | Yes | Yes | 59.5 | 0.435 | 2016
EI_2016-03-22_200134 | 2016-03-22 16:02 | 2016-03-22 16:02 | EDT | 2016-03-22 20:02 |  | 60.0214 | 59.9799 | 59.9798 | -0.041491 | -0.041593 |  |  | No | No | 59.5 | 0.4798 | 2016
EI_2016-03-26_172222 | 2016-03-26 13:22 | 2016-03-26 13:22 | EDT | 2016-03-26 17:22 |  | 60.012 | 59.998 | 60.007 | -0.014 | -0.005 |  |  | No | No | 59.5 | 0.507 | 2016
EI_2016-03-26_222229 | 2016-03-26 18:22 | 2016-03-26 18:22 | EDT | 2016-03-26 22:22 |  | 59.9937 | 60.042 | 60.038 | 0.048291 | 0.044286 |  |  | No | No | 59.5 | 0.538 | 2016
EI_2016-03-27_143006 | 2016-03-27 10:30 | 2016-03-27 10:30 | EDT | 2016-03-27 14:30 |  | 60.0197 | 60.0087 | 59.9885 | -0.010942 | -0.031177 |  |  | No | No | 59.5 | 0.4885 | 2016
EI_2016-03-28_114857 | 2016-03-28 07:49 | 2016-03-28 07:49 | EDT | 2016-03-28 11:49 | 1361 | 59.9888 | 59.978 | 59.9713 | -0.010801 | -0.017545 | -12600.7303 | -7756.9917 | No | No | 59.5 | 0.4713 | 2016
EI_2016-03-29_162307 | 2016-03-29 12:23 | 2016-03-29 12:23 | EDT | 2016-03-29 16:23 | 439 | 60.0263 | 59.9843 | 59.9925 | -0.041948 | -0.03375 | -1046.5435 | -1300.7385 | No | No | 59.5 | 0.4925 | 2016
EI_2016-03-30_083506 | 2016-03-30 04:35 | 2016-03-30 04:35 | EDT | 2016-03-30 08:35 |  | 59.9895 | 60.0241 | 60.0329 | 0.034561 | 0.043396 |  |  | No | No | 59.5 | 0.5329 | 2016
EI_2016-04-04_112644 | 2016-04-04 07:27 | 2016-04-04 07:27 | EDT | 2016-04-04 11:27 | 589 | 60.005 | 59.962 | 59.957 | -0.043 | -0.048 | -1369.7674 | -1227.0833 | Yes | Yes | 59.5 | 0.457 | 2016
EI_2016-04-07_085000 | 2016-04-07 04:50 | 2016-04-07 04:50 | EDT | 2016-04-07 08:50 | 682 | 60.011 | 59.983 | 59.971 | -0.028 | -0.04 | -2435.7143 | -1705 | No | No | 59.5 | 0.471 | 2016
EI_2016-04-10_105957 | 2016-04-10 07:00 | 2016-04-10 07:00 | EDT | 2016-04-10 11:00 | 601 | 60.02 | 59.966 | 59.981 | -0.054 | -0.039 | -1112.963 | -1541.0256 | No | No | 59.5 | 0.481 | 2016
EI_2016-04-15_000523 | 2016-04-14 20:05 | 2016-04-14 20:05 | EDT | 2016-04-15 00:05 | 1092 | 59.991 | 59.944 | 59.941 | -0.047 | -0.05 | -2323.4043 | -2184 | Yes | Yes | 59.5 | 0.441 | 2016
EI_2016-04-18_013115 | 2016-04-17 21:31 | 2016-04-17 21:31 | EDT | 2016-04-18 01:31 | 856 | 60.005 | 59.97 | 59.96 | -0.035 | -0.045 | -2445.7143 | -1902.2222 | Yes | Yes | 59.5 | 0.46 | 2016
EI_2016-04-18_023207 | 2016-04-17 22:32 | 2016-04-17 22:32 | EDT | 2016-04-18 02:32 | 0 | 60.019 | 59.972 | 59.993 | -0.047 | -0.026 |  |  | No | No | 59.5 | 0.493 | 2016
EI_2016-04-24_031532 | 2016-04-23 23:16 | 2016-04-23 23:16 | EDT | 2016-04-24 03:16 | 0 | 60.014 | 59.977 | 59.987 | -0.037 | -0.027 |  |  | No | No | 59.5 | 0.487 | 2016
EI_2016-04-24_033256 | 2016-04-23 23:33 | 2016-04-23 23:33 | EDT | 2016-04-24 03:33 | 0 | 60.011 | 59.975 | 59.978 | -0.036 | -0.033 |  |  | No | No | 59.5 | 0.478 | 2016
EI_2016-04-30_023413 | 2016-04-29 22:34 | 2016-04-29 22:34 | EDT | 2016-04-30 02:34 | 0 | 60.021 | 59.982 | 59.992 | -0.039 | -0.029 |  |  | No | No | 59.5 | 0.492 | 2016
EI_2016-05-11_195318 | 2016-05-11 15:53 | 2016-05-11 15:53 | EDT | 2016-05-11 19:53 | 1155 | 60.011 | 59.945 | 59.944 | -0.066 | -0.067 | -1750 | -1723.8806 | Yes | Yes | 59.5 | 0.444 | 2016
EI_2016-05-14_202423 | 2016-05-14 16:24 | 2016-05-14 16:24 | EDT | 2016-05-14 20:24 | 0 | 60.003 | 59.962 | 59.958 | -0.041 | -0.045 |  |  | No | No | 59.5 | 0.458 | 2016
EI_2016-05-15_104433 | 2016-05-15 06:45 | 2016-05-15 06:45 | EDT | 2016-05-15 10:45 | 1155 | 60.023 | 59.966 | 59.97 | -0.057 | -0.053 | -2026.3158 | -2179.2453 | No | No | 59.5 | 0.47 | 2016
EI_2016-05-16_020311 | 2016-05-15 22:03 | 2016-05-15 22:03 | EDT | 2016-05-16 02:03 | 541 | 59.99 | 59.966 | 59.948 | -0.024 | -0.042 | -2254.1667 | -1288.0952 | Yes | Yes | 59.5 | 0.448 | 2016
EI_2016-05-18_142801 | 2016-05-18 10:28 | 2016-05-18 10:28 | EDT | 2016-05-18 14:28 | 660 | 59.986 | 59.952 | 59.947 | -0.034 | -0.039 | -1941.1765 | -1692.3077 | No | No | 59.5 | 0.447 | 2016
EI_2016-05-19_182130 | 2016-05-19 14:22 | 2016-05-19 14:22 | EDT | 2016-05-19 18:22 | 0 | 60.009 | 59.977 | 59.97 | -0.032 | -0.039 |  |  | No | No | 59.5 | 0.47 | 2016
EI_2016-05-20_011719 | 2016-05-19 21:17 | 2016-05-19 21:17 | EDT | 2016-05-20 01:17 | 560 | 60.01 | 59.978 | 59.976 | -0.032 | -0.034 | -1750 | -1647.0588 | No | No | 59.5 | 0.476 | 2016
EI_2016-05-20_221046 | 2016-05-20 18:11 | 2016-05-20 18:11 | EDT | 2016-05-20 22:11 | 0 | 60 | 59.964 | 59.972 | -0.036 | -0.028 |  |  | No | No | 59.5 | 0.472 | 2016
EI_2016-05-25_060603 | 2016-05-25 02:06 | 2016-05-25 02:06 | EDT | 2016-05-25 06:06 | 1221 | 60.014 | 59.958 | 59.952 | -0.056 | -0.062 | -2180.3571 | -1969.3548 | Yes | Yes | 59.5 | 0.452 | 2016
EI_2016-05-29_051101 | 2016-05-29 01:11 | 2016-05-29 01:11 | EDT | 2016-05-29 05:11 | 1011 | 60.022 | 59.967 | 59.982 | -0.055 | -0.04 | -1838.1818 | -2527.5 | No | No | 59.5 | 0.482 | 2016
EI_2016-05-30_182633 | 2016-05-30 14:27 | 2016-05-30 14:27 | EDT | 2016-05-30 18:27 | 945 | 59.987 | 59.95 | 59.948 | -0.037 | -0.039 | -2554.0541 | -2423.0769 | Yes | No | 59.5 | 0.448 | 2016
EI_2016-05-31_202648 | 2016-05-31 16:27 | 2016-05-31 16:27 | EDT | 2016-05-31 20:27 | 934 | 59.997 | 59.953 | 59.953 | -0.044 | -0.044 | -2122.7273 | -2122.7273 | Yes | Yes | 59.5 | 0.453 | 2016
EI_2016-06-03_151649 | 2016-06-03 11:17 | 2016-06-03 11:17 | EDT | 2016-06-03 15:17 | 0 | 59.969 | 59.939 | 59.938 | -0.03 | -0.031 |  |  | No | No | 59.5 | 0.438 | 2016
EI_2016-06-04_023500 | 2016-06-03 22:35 | 2016-06-03 22:35 | EDT | 2016-06-04 02:35 | 0 | 60.007 | 59.967 | 59.972 | -0.04 | -0.035 |  |  | No | No | 59.5 | 0.472 | 2016
EI_2016-06-05_184912 | 2016-06-05 14:49 | 2016-06-05 14:49 | EDT | 2016-06-05 18:49 | 693 | 60 | 59.974 | 59.97 | -0.026 | -0.03 | -2665.3846 | -2310 | No | No | 59.5 | 0.47 | 2016
EI_2016-06-05_211333 | 2016-06-05 17:14 | 2016-06-05 17:14 | EDT | 2016-06-05 21:14 | 918 | 60.001 | 59.964 | 59.958 | -0.037 | -0.043 | -2481.0811 | -2134.8837 | Yes | Yes | 59.5 | 0.458 | 2016
EI_2016-06-08_104317 | 2016-06-08 06:43 | 2016-06-08 06:43 | EDT | 2016-06-08 10:43 | 0 | 60.012 | 59.987 | 59.988 | -0.025 | -0.024 |  |  | No | No | 59.5 | 0.488 | 2016
EI_2016-06-08_200822 | 2016-06-08 16:08 | 2016-06-08 16:08 | EDT | 2016-06-08 20:08 | 0 | 60.006 | 59.975 | 59.974 | -0.031 | -0.032 |  |  | No | No | 59.5 | 0.474 | 2016
EI_2016-06-11_182728 | 2016-06-11 14:27 | 2016-06-11 14:27 | EDT | 2016-06-11 18:27 | 0 | 59.996 | 59.975 | 59.963 | -0.021 | -0.033 |  |  | No | No | 59.5 | 0.463 | 2016
EI_2016-06-13_150554 | 2016-06-13 11:06 | 2016-06-13 11:06 | EDT | 2016-06-13 15:06 | 842 | 60.004 | 59.967 | 59.97 | -0.037 | -0.034 | -2275.6757 | -2476.4706 | No | No | 59.5 | 0.47 | 2016
EI_2016-06-16_024418 | 2016-06-15 22:44 | 2016-06-15 22:44 | EDT | 2016-06-16 02:44 | 0 | 60.033 | 59.994 | 60.003 | -0.039 | -0.03 |  |  | No | No | 59.5 | 0.503 | 2016
EI_2016-06-18_203107 | 2016-06-18 16:31 | 2016-06-18 16:31 | EDT | 2016-06-18 20:31 | 700 | 60.013 | 59.978 | 59.974 | -0.035 | -0.039 | -2000 | -1794.8718 | No | No | 59.5 | 0.474 | 2016
EI_2016-06-19_010142 | 2016-06-18 21:02 | 2016-06-18 21:02 | EDT | 2016-06-19 01:02 | 0 | 60.012 | 59.967 | 59.998 | -0.045 | -0.014 |  |  | No | No | 59.5 | 0.498 | 2016
EI_2016-06-19_201849 | 2016-06-19 16:19 | 2016-06-19 16:19 | EDT | 2016-06-19 20:19 | 0 | 60.015 | 59.987 | 59.977 | -0.028 | -0.038 |  |  | No | No | 59.5 | 0.477 | 2016
EI_2016-06-22_031947 | 2016-06-21 23:20 | 2016-06-21 23:20 | EDT | 2016-06-22 03:20 | 0 | 59.998 | 59.968 | 59.967 | -0.03 | -0.031 |  |  | No | No | 59.5 | 0.467 | 2016
EI_2016-06-24_161500 | 2016-06-24 12:15 | 2016-06-24 12:15 | EDT | 2016-06-24 16:15 | 0 | 59.99 | 59.997 | 59.992 | 0.007 | 0.002 |  |  | No | No | 59.5 | 0.492 | 2016
EI_2016-06-25_190725 | 2016-06-25 15:07 | 2016-06-25 15:07 | EDT | 2016-06-25 19:07 | 1266 | 60.024 | 59.96 | 59.975 | -0.064 | -0.049 | -1978.125 | -2583.6735 | Yes | No | 59.5 | 0.475 | 2016
EI_2016-06-26_165548 | 2016-06-26 12:56 | 2016-06-26 12:56 | EDT | 2016-06-26 16:56 | 0 | 60.005 | 59.969 | 59.976 | -0.036 | -0.029 |  |  | No | No | 59.5 | 0.476 | 2016
EI_2016-06-28_082253 | 2016-06-28 04:23 | 2016-06-28 04:23 | EDT | 2016-06-28 08:23 | 1213 | 59.994 | 59.964 | 59.955 | -0.03 | -0.039 | -4043.3333 | -3110.2564 | Yes | Yes | 59.5 | 0.455 | 2016
EI_2016-07-01_025320 | 2016-06-30 22:53 | 2016-06-30 22:53 | EDT | 2016-07-01 02:53 | 0 | 60.014 | 59.981 | 59.981 | -0.033 | -0.033 |  |  | No | No | 59.5 | 0.481 | 2016
EI_2016-07-05_222533 | 2016-07-05 18:26 | 2016-07-05 18:26 | EDT | 2016-07-05 22:26 | 1299 | 59.97 | 59.935 | 59.933 | -0.035 | -0.037 | -3711.4286 | -3510.8108 | Yes | No | 59.5 | 0.433 | 2016
EI_2016-07-06_133806 | 2016-07-06 09:38 | 2016-07-06 09:38 | EDT | 2016-07-06 13:38 | 994 | 59.978 | 59.941 | 59.942 | -0.037 | -0.036 | -2686.4865 | -2761.1111 | Yes | No | 59.5 | 0.442 | 2016
EI_2016-07-06_163307 | 2016-07-06 12:33 | 2016-07-06 12:33 | EDT | 2016-07-06 16:33 | 457 | 59.998 | 59.96 | 59.963 | -0.038 | -0.035 | -1202.6316 | -1305.7143 | No | No | 59.5 | 0.463 | 2016
EI_2016-07-06_163814 | 2016-07-06 12:38 | 2016-07-06 12:38 | EDT | 2016-07-06 16:38 | 625 | 59.977 | 59.953 | 59.951 | -0.024 | -0.026 | -2604.1667 | -2403.8462 | No | No | 59.5 | 0.451 | 2016
EI_2016-07-07_030111 | 2016-07-06 23:01 | 2016-07-06 23:01 | EDT | 2016-07-07 03:01 | 635 | 60 | 59.959 | 59.965 | -0.041 | -0.035 | -1548.7805 | -1814.2857 | No | No | 59.5 | 0.465 | 2016
EI_2016-07-08_152520 | 2016-07-08 11:25 | 2016-07-08 11:25 | EDT | 2016-07-08 15:25 | 599 | 60.008 | 59.974 | 59.974 | -0.034 | -0.034 | -1761.7647 | -1761.7647 | No | No | 59.5 | 0.474 | 2016
EI_2016-07-09_104745 | 2016-07-09 06:48 | 2016-07-09 06:48 | EDT | 2016-07-09 10:48 | 499 | 60.015 | 59.988 | 59.983 | -0.027 | -0.032 | -1848.1481 | -1559.375 | No | No | 59.5 | 0.483 | 2016
EI_2016-07-12_181312 | 2016-07-12 14:13 | 2016-07-12 14:13 | EDT | 2016-07-12 18:13 | 800 | 59.986 | 59.956 | 59.956 | -0.03 | -0.03 | -2666.6667 | -2666.6667 | Yes | No | 59.5 | 0.456 | 2016
EI_2016-07-13_110101 | 2016-07-13 07:01 | 2016-07-13 07:01 | EDT | 2016-07-13 11:01 | 938 | 59.988 | 59.963 | 59.955 | -0.025 | -0.033 | -3752 | -2842.4242 | Yes | No | 59.5 | 0.455 | 2016
EI_2016-07-18_141332 | 2016-07-18 10:14 | 2016-07-18 10:14 | EDT | 2016-07-18 14:14 | 1000 | 59.974 | 59.946 | 59.949 | -0.028 | -0.025 | -3571.4286 | -4000 | No | No | 59.5 | 0.449 | 2016
EI_2016-07-18_173209 | 2016-07-18 13:32 | 2016-07-18 13:32 | EDT | 2016-07-18 17:32 | 781 | 60.003 | 59.98 | 59.974 | -0.023 | -0.029 | -3395.6522 | -2693.1034 | No | No | 59.5 | 0.474 | 2016
EI_2016-07-23_045406 | 2016-07-23 00:54 | 2016-07-23 00:54 | EDT | 2016-07-23 04:54 | 0 | 60.011 | 59.968 | 59.97 | -0.043 | -0.041 |  |  | No | No | 59.5 | 0.47 | 2016
EI_2016-07-24_202210 | 2016-07-24 16:22 | 2016-07-24 16:22 | EDT | 2016-07-24 20:22 | 1300 | 60 | 59.961 | 59.959 | -0.039 | -0.041 | -3333.3333 | -3170.7317 | Yes | Yes | 59.5 | 0.459 | 2016
EI_2016-07-26_000000 | 2016-07-25 20:00 | 2016-07-25 20:00 | EDT | 2016-07-26 | 1355 | 60.004 | 59.99 | 59.982 | -0.014 | -0.022 | -9678.5714 | -6159.0909 | No | No | 59.5 | 0.482 | 2016
EI_2016-07-28_172741 | 2016-07-28 13:28 | 2016-07-28 13:28 | EDT | 2016-07-28 17:28 | 801 | 59.979 | 59.944 | 59.951 | -0.035 | -0.028 | -2288.5714 | -2860.7143 | Yes | No | 59.5 | 0.451 | 2016
EI_2016-07-31_151457 | 2016-07-31 11:15 | 2016-07-31 11:15 | EDT | 2016-07-31 15:15 | 609 | 59.99 | 59.949 | 59.956 | -0.041 | -0.034 | -1485.3659 | -1791.1765 | No | No | 59.5 | 0.456 | 2016
EI_2016-08-02_004459 | 2016-08-01 20:45 | 2016-08-01 20:45 | EDT | 2016-08-02 00:45 | 675 | 60.008 | 59.981 | 59.976 | -0.027 | -0.032 | -2500 | -2109.375 | No | No | 59.5 | 0.476 | 2016
EI_2016-08-08_150943 | 2016-08-08 11:10 | 2016-08-08 11:10 | EDT | 2016-08-08 15:10 | 680 | 60.006 | 59.971 | 59.966 | -0.035 | -0.04 | -1942.8571 | -1700 | Yes | No | 59.5 | 0.466 | 2016
EI_2016-08-09_064348 | 2016-08-09 02:44 | 2016-08-09 02:44 | EDT | 2016-08-09 06:44 | 893 | 59.983 | 59.947 | 59.944 | -0.036 | -0.039 | -2480.5556 | -2289.7436 | Yes | No | 59.5 | 0.444 | 2016
EI_2016-08-11_135836 | 2016-08-11 09:59 | 2016-08-11 09:59 | EDT | 2016-08-11 13:59 | 0 | 59.993 | 59.954 | 59.958 | -0.039 | -0.035 |  |  | No | No | 59.5 | 0.458 | 2016
EI_2016-08-13_001034 | 2016-08-12 20:11 | 2016-08-12 20:11 | EDT | 2016-08-13 00:11 | 800 | 59.991 | 59.968 | 59.96 | -0.023 | -0.031 | -3478.2609 | -2580.6452 | Yes | No | 59.5 | 0.46 | 2016
EI_2016-08-13_163240 | 2016-08-13 12:33 | 2016-08-13 12:33 | EDT | 2016-08-13 16:33 | 781 | 59.991 | 59.979 | 59.968 | -0.012 | -0.023 | -6508.3333 | -3395.6522 | No | No | 59.5 | 0.468 | 2016
EI_2016-08-17_171816 | 2016-08-17 13:18 | 2016-08-17 13:18 | EDT | 2016-08-17 17:18 | 830 | 59.988 | 59.962 | 59.958 | -0.026 | -0.03 | -3192.3077 | -2766.6667 | Yes | No | 59.5 | 0.458 | 2016
EI_2016-08-24_173850 | 2016-08-24 13:39 | 2016-08-24 13:39 | EDT | 2016-08-24 17:39 | 729 | 59.988 | 59.957 | 59.955 | -0.031 | -0.033 | -2351.6129 | -2209.0909 | No | No | 59.5 | 0.455 | 2016
EI_2016-08-30_122722 | 2016-08-30 08:27 | 2016-08-30 08:27 | EDT | 2016-08-30 12:27 | 775 | 59.986 | 59.973 | 59.964 | -0.013 | -0.022 | -5961.5385 | -3522.7273 | No | No | 59.5 | 0.464 | 2016
EI_2016-08-31_010912 | 2016-08-30 21:09 | 2016-08-30 21:09 | EDT | 2016-08-31 01:09 | 1137 | 60.009 | 59.954 | 59.959 | -0.055 | -0.05 | -2067.2727 | -2274 | Yes | Yes | 59.5 | 0.459 | 2016
EI_2016-08-31_191307 | 2016-08-31 15:13 |  | EDT | 2016-08-31 19:13 | 1202 | 59.994 | 59.958 | 59.952 | -0.036 | -0.042 | -3338.8889 | -2861.9048 | Yes | Yes | 59.5 | 0.452 | 2016
EI_2016-09-02_095355 | 2016-09-02 05:54 | 2016-09-02 05:54 | EDT | 2016-09-02 09:54 | 0 | 60.008 | 59.997 | 60.005 | -0.011 | -0.003 |  |  | No | No | 59.5 | 0.505 | 2016
EI_2016-09-03_120248 | 2016-09-03 08:03 | 2016-09-03 08:03 | EDT | 2016-09-03 12:03 | 855 | 59.994 | 59.953 | 59.957 | -0.041 | -0.037 | -2085.3659 | -2310.8108 | Yes | No | 59.5 | 0.457 | 2016
EI_2016-09-05_024157 | 2016-09-04 22:42 | 2016-09-04 22:42 | EDT | 2016-09-05 02:42 | 0 | 60.024 | 59.972 | 59.98 | -0.052 | -0.044 |  |  | No | No | 59.5 | 0.48 | 2016
EI_2016-09-09_211758 | 2016-09-09 17:18 | 2016-09-09 17:18 | EDT | 2016-09-09 21:18 | 1395 | 59.982 | 59.939 | 59.934 | -0.043 | -0.048 | -3244.186 | -2906.25 | Yes | Yes | 59.5 | 0.434 | 2016
EI_2016-09-10_074331 | 2016-09-10 03:44 | 2016-09-10 03:44 | EDT | 2016-09-10 07:44 | 931 | 59.988 | 59.958 | 59.952 | -0.03 | -0.036 | -3103.3333 | -2586.1111 | Yes | No | 59.5 | 0.452 | 2016
EI_2016-09-11_232803 | 2016-09-11 19:28 | 2016-09-11 19:28 | EDT | 2016-09-11 23:28 | 1270 | 59.983 | 59.948 | 59.941 | -0.035 | -0.042 | -3628.5714 | -3023.8095 | Yes | No | 59.5 | 0.441 | 2016
EI_2016-09-26_185141 | 2016-09-26 14:52 | 2016-09-26 14:52 | EDT | 2016-09-26 18:52 | 845 | 60.007 | 59.964 | 59.967 | -0.043 | -0.04 | -1965.1163 | -2112.5 | No | No | 59.5 | 0.467 | 2016
EI_2016-09-26_202712 | 2016-09-26 16:27 | 2016-09-26 16:27 | EDT | 2016-09-26 20:27 | 978 | 60.004 | 59.96 | 59.958 | -0.044 | -0.046 | -2222.7273 | -2126.087 | Yes | Yes | 59.5 | 0.458 | 2016
EI_2016-09-27_114615 | 2016-09-27 07:46 | 2016-09-27 07:46 | EDT | 2016-09-27 11:46 | 795 | 60.022 | 59.971 | 59.978 | -0.051 | -0.044 | -1558.8235 | -1806.8182 | Yes | No | 59.5 | 0.478 | 2016
EI_2016-10-01_101453 | 2016-10-01 06:15 | 2016-10-01 06:15 | EDT | 2016-10-01 10:15 | 930 | 60.005 | 59.97 | 59.955 | -0.035 | -0.05 | -2657.1429 | -1860 | Yes | Yes | 59.5 | 0.455 | 2016
EI_2016-10-05_032321 | 2016-10-04 23:23 | 2016-10-04 23:23 | EDT | 2016-10-05 03:23 | 0 | 60.019 | 59.975 | 59.986 | -0.044 | -0.033 |  |  | No | No | 59.5 | 0.486 | 2016
EI_2016-10-08_170229 | 2016-10-08 13:02 | 2016-10-08 13:02 | EDT | 2016-10-08 17:02 | 734 | 59.988 | 59.966 | 59.954 | -0.022 | -0.034 | -3336.3636 | -2158.8235 | No | No | 59.5 | 0.454 | 2016
EI_2016-10-09_042338 | 2016-10-09 00:24 | 2016-10-09 00:24 | EDT | 2016-10-09 04:24 | 508 | 60.026 | 59.989 | 59.99 | -0.037 | -0.036 | -1372.973 | -1411.1111 | No | No | 59.5 | 0.49 | 2016
EI_2016-10-09_065405 | 2016-10-09 02:54 | 2016-10-09 02:54 | EDT | 2016-10-09 06:54 | 865 | 60.011 | 59.96 | 59.956 | -0.051 | -0.055 | -1696.0784 | -1572.7273 | Yes | No | 59.5 | 0.456 | 2016
EI_2016-10-09_082725 | 2016-10-09 04:27 | 2016-10-09 04:27 | EDT | 2016-10-09 08:27 | 850 | 59.994 | 59.969 | 59.954 | -0.025 | -0.04 | -3400 | -2125 | Yes | Yes | 59.5 | 0.454 | 2016
EI_2016-10-11_020555 | 2016-10-10 22:06 | 2016-10-10 22:06 | EDT | 2016-10-11 02:06 | 0 | 59.981 | 59.943 | 59.948 | -0.038 | -0.033 |  |  | No | No | 59.5 | 0.448 | 2016
EI_2016-10-11_042507 | 2016-10-11 00:25 | 2016-10-11 00:25 | EDT | 2016-10-11 04:25 | 0 | 60.022 | 59.98 | 59.984 | -0.042 | -0.038 |  |  | No | No | 59.5 | 0.484 | 2016
EI_2016-10-12_121859 | 2016-10-12 08:19 | 2016-10-12 08:19 | EDT | 2016-10-12 12:19 | 1210 | 59.979 | 59.941 | 59.9406 | -0.038 | -0.0384 | -3184.2105 | -3151.0417 |  |  | 59.5 | 0.4406 | 2016
EI_2016-10-12_183852 | 2016-10-12 14:39 | 2016-10-12 14:39 | EDT | 2016-10-12 18:39 | 1163 | 59.969 | 59.942 | 59.93 | -0.027 | -0.039 | -4307.4074 | -2982.0513 | Yes | No | 59.5 | 0.43 | 2016
EI_2016-10-15_024554 | 2016-10-14 22:46 | 2016-10-14 22:46 | EDT | 2016-10-15 02:46 | 595 | 60.022 | 59.98 | 59.983 | -0.042 | -0.039 | -1416.6667 | -1525.641 | Yes | No | 59.5 | 0.483 | 2016
EI_2016-10-16_213201 | 2016-10-16 17:32 | 2016-10-16 17:32 | EDT | 2016-10-16 21:32 | 0 | 60.011 | 59.976 | 59.982 | -0.035 | -0.029 |  |  | No | No | 59.5 | 0.482 | 2016
EI_2016-10-23_023254 | 2016-10-22 22:33 | 2016-10-22 22:33 | EDT | 2016-10-23 02:33 | 0 | 60.02 | 59.977 | 59.989 | -0.043 | -0.031 |  |  | No | No | 59.5 | 0.489 | 2016
EI_2016-10-23_235516 | 2016-10-23 19:55 | 2016-10-23 19:55 | EDT | 2016-10-23 23:55 | 0 | 60.035 | 60.003 | 60.021 | -0.032 | -0.014 |  |  | No | No | 59.5 | 0.521 | 2016
EI_2016-10-24_212806 | 2016-10-24 17:28 | 2016-10-24 17:28 | EDT | 2016-10-24 21:28 | 1133 | 59.973 | 59.945 | 59.933 | -0.028 | -0.04 | -4046.4286 | -2832.5 | Yes | Yes | 59.5 | 0.433 | 2016
EI_2016-10-25_023604 | 2016-10-24 22:36 | 2016-10-24 22:36 | EDT | 2016-10-25 02:36 | 0 | 60.008 | 59.969 | 59.974 | -0.039 | -0.034 |  |  | No | No | 59.5 | 0.474 | 2016
EI_2016-10-26_020156 | 2016-10-25 22:02 | 2016-10-25 22:02 | EDT | 2016-10-26 02:02 | 0 | 60.031 | 59.983 | 59.999 | -0.048 | -0.032 |  |  | No | No | 59.5 | 0.499 | 2016
EI_2016-10-26_124049 | 2016-10-26 08:41 | 2016-10-26 08:41 | EDT | 2016-10-26 12:41 | 0 | 60.009 | 59.981 | 59.978 | -0.028 | -0.031 |  |  | No | No | 59.5 | 0.478 | 2016
EI_2016-10-27_155859 | 2016-10-27 11:59 | 2016-10-27 11:59 | EDT | 2016-10-27 15:59 | 853 | 60.027 | 60.002 | 59.986 | -0.025 | -0.041 | -3412 | -2080.4878 | Yes | No | 59.5 | 0.486 | 2016
EI_2016-11-04_003228 | 2016-11-03 20:32 | 2016-11-03 20:32 | EDT | 2016-11-04 00:32 | 750 | 60.03 | 59.98 | 59.996 | -0.05 | -0.034 | -1500 | -2205.8824 | No | No | 59.5 | 0.496 | 2016
EI_2016-11-04_211112 | 2016-11-04 17:11 | 2016-11-04 17:11 | EDT | 2016-11-04 21:11 | 1167 | 59.994 | 59.946 | 59.939 | -0.048 | -0.055 | -2431.25 | -2121.8182 | No | No | 59.5 | 0.439 | 2016
EI_2016-11-04_220409 | 2016-11-04 18:04 | 2016-11-04 18:04 | EDT | 2016-11-04 22:04 | 0 | 60.025 | 59.984 | 59.994 | -0.041 | -0.031 |  |  | No | No | 59.5 | 0.494 | 2016
EI_2016-11-05_101148 | 2016-11-05 06:12 | 2016-11-05 06:12 | EDT | 2016-11-05 10:12 | 0 | 60.012 | 59.98 | 59.977 | -0.032 | -0.035 |  |  | No | No | 59.5 | 0.477 | 2016
EI_2016-11-06_043820 | 2016-11-05 23:38 | 2016-11-05 23:38 | EST | 2016-11-06 04:38 | 0 | 60.015 | 59.983 | 59.98 | -0.032 | -0.035 |  |  | No | No | 59.5 | 0.48 | 2016
EI_2016-11-06_144357 | 2016-11-06 09:44 | 2016-11-06 09:44 | EST | 2016-11-06 14:44 | 0 | 60.02 | 59.971 | 59.979 | -0.049 | -0.041 |  |  | No | No | 59.5 | 0.479 | 2016
EI_2016-11-09_120120 | 2016-11-09 07:01 | 2016-11-09 07:01 | EST | 2016-11-09 12:01 | 0 | 60.022 | 59.976 | 60.016 | -0.046 | -0.006 |  |  | No | No | 59.5 | 0.516 | 2016
EI_2016-11-11_140713 | 2016-11-11 09:07 | 2016-11-11 09:07 | EST | 2016-11-11 14:07 | 987 | 59.993 | 59.96 | 59.954 | -0.033 | -0.039 | -2990.9091 | -2530.7692 | Yes | No | 59.5 | 0.454 | 2016
EI_2016-11-13_073739 | 2016-11-13 02:38 | 2016-11-13 02:38 | EST | 2016-11-13 07:38 | 0 | 59.991 | 60.024 | 59.989 | 0.033 | -0.002 |  |  | No | No | 59.5 | 0.489 | 2016
EI_2016-11-14_095434 | 2016-11-14 04:55 | 2016-11-14 04:55 | EST | 2016-11-14 09:55 | 851 | 60.002 | 59.961 | 59.956 | -0.041 | -0.046 | -2075.6098 | -1850 | Yes | Yes | 59.5 | 0.456 | 2016
EI_2016-11-14_183556 | 2016-11-14 13:36 | 2016-11-14 13:36 | EST | 2016-11-14 18:36 | 0 | 59.968 | 59.948 | 59.94 | -0.02 | -0.028 |  |  | No | No | 59.5 | 0.44 | 2016
EI_2016-11-16_134835 | 2016-11-16 08:49 | 2016-11-16 08:49 | EST | 2016-11-16 13:49 | 750 | 60.013 | 59.976 | 59.975 | -0.037 | -0.038 | -2027.027 | -1973.6842 | Yes | No | 59.5 | 0.475 | 2016
EI_2016-11-17_060540 | 2016-11-17 01:06 | 2016-11-17 01:06 | EST | 2016-11-17 06:06 | 0 | 60.004 | 59.961 | 59.971 | -0.043 | -0.033 |  |  | No | No | 59.5 | 0.471 | 2016
EI_2016-11-17_132105 | 2016-11-17 08:21 | 2016-11-17 08:21 | EST | 2016-11-17 13:21 | 754 | 60.013 | 59.959 | 59.964 | -0.054 | -0.049 | -1396.2963 | -1538.7755 | Yes | No | 59.5 | 0.464 | 2016
EI_2016-11-17_175313 | 2016-11-17 12:53 | 2016-11-17 12:53 | EST | 2016-11-17 17:53 | 0 | 59.998 | 59.954 | 59.951 | -0.044 | -0.047 |  |  | No | No | 59.5 | 0.451 | 2016
EI_2016-11-18_050410 | 2016-11-18 00:04 | 2016-11-18 00:04 | EST | 2016-11-18 05:04 | 0 | 60.02 | 59.98 | 59.99 | -0.04 | -0.03 |  |  | No | No | 59.5 | 0.49 | 2016
EI_2016-11-20_042207 | 2016-11-19 23:22 | 2016-11-19 23:22 | EST | 2016-11-20 04:22 | 0 | 60.027 | 59.979 | 60.019 | -0.048 | -0.008 |  |  | No | No | 59.5 | 0.519 | 2016
EI_2016-11-20_084243 | 2016-11-20 03:43 | 2016-11-20 03:43 | EST | 2016-11-20 08:43 | 612 | 60.012 | 59.99 | 59.986 | -0.022 | -0.026 | -2781.8182 | -2353.8462 | No | No | 59.5 | 0.486 | 2016
EI_2016-11-20_094845 | 2016-11-20 04:49 | 2016-11-20 04:49 | EST | 2016-11-20 09:49 | 700 | 60.018 | 59.976 | 59.977 | -0.042 | -0.041 | -1666.6667 | -1707.3171 | Yes | No | 59.5 | 0.477 | 2016
EI_2016-11-21_095932 | 2016-11-21 05:00 | 2016-11-21 05:00 | EST | 2016-11-21 10:00 | 0 | 59.988 | 60.038 | 59.983 | 0.05 | -0.005 |  |  | No | No | 59.5 | 0.483 | 2016
EI_2016-11-22_094728 | 2016-11-22 04:47 | 2016-11-22 04:47 | EST | 2016-11-22 09:47 | 0 | 59.974 | 60.017 | 59.973 | 0.043 | -0.001 |  |  | No | No | 59.5 | 0.473 | 2016
EI_2016-11-23_061621 | 2016-11-23 01:16 | 2016-11-23 01:16 | EST | 2016-11-23 06:16 | 0 | 60.01 | 59.979 | 59.984 | -0.031 | -0.026 |  |  | No | No | 59.5 | 0.484 | 2016
EI_2016-11-24_065501 | 2016-11-24 01:55 | 2016-11-24 01:55 | EST | 2016-11-24 06:55 | 0 | 60.006 | 59.957 | 59.971 | -0.049 | -0.035 |  |  | No | No | 59.5 | 0.471 | 2016
EI_2016-11-25_024830 | 2016-11-24 21:48 | 2016-11-24 21:48 | EST | 2016-11-25 02:49 | 0 | 60.006 | 59.97 | 59.973 | -0.036 | -0.033 |  |  | No | No | 59.5 | 0.473 | 2016
EI_2016-11-25_031750 | 2016-11-24 22:18 | 2016-11-24 22:18 | EST | 2016-11-25 03:18 | 0 | 60.024 | 59.996 | 59.996 | -0.028 | -0.028 |  |  | No | No | 59.5 | 0.496 | 2016
EI_2016-11-27_062631 | 2016-11-27 01:27 | 2016-11-27 01:27 | EST | 2016-11-27 06:27 | 980 | 60.005 | 59.95 | 59.95 | -0.055 | -0.055 | -1781.8182 | -1781.8182 | Yes | Yes | 59.5 | 0.45 | 2016
EI_2016-11-27_154645 | 2016-11-27 10:47 | 2016-11-27 10:47 | EST | 2016-11-27 15:47 | 0 | 60.029 | 60 | 60.022 | -0.029 | -0.007 |  |  | No | No | 59.5 | 0.522 | 2016
EI_2016-11-28_231735 | 2016-11-28 18:18 | 2016-11-28 18:18 | EST | 2016-11-28 23:18 | 536 | 60.021 | 59.972 | 59.996 | -0.049 | -0.025 | -1093.8776 | -2144 | No | No | 59.5 | 0.496 | 2016
EI_2016-11-29_110000 | 2016-11-29 06:00 | 2016-11-29 06:00 | EST | 2016-11-29 11:00 | 0 | 60.024 | 59.956 | 59.991 | -0.068 | -0.033 |  |  | No | No | 59.5 | 0.491 | 2016
EI_2016-11-29_161116 | 2016-11-29 11:11 | 2016-11-29 11:11 | EST | 2016-11-29 16:11 | 0 | 59.978 | 60.013 | 59.975 | 0.035 | -0.003 |  |  | No | No | 59.5 | 0.475 | 2016
EI_2016-11-29_163110 | 2016-11-29 11:31 | 2016-11-29 11:31 | EST | 2016-11-29 16:31 | 559 | 60.005 | 59.965 | 59.961 | -0.04 | -0.044 | -1397.5 | -1270.4545 | Yes | No | 59.5 | 0.461 | 2016
EI_2016-11-29_181855 | 2016-11-29 13:19 | 2016-11-29 13:19 | EST | 2016-11-29 18:19 | 0 | 60.01 | 59.976 | 59.986 | -0.034 | -0.024 |  |  | No | No | 59.5 | 0.486 | 2016
EI_2016-12-01_195634 | 2016-12-01 14:57 | 2016-12-01 14:57 | EST | 2016-12-01 19:57 | 800 | 59.997 | 59.966 | 59.96 | -0.031 | -0.037 | -2580.6452 | -2162.1622 | Yes | No | 59.5 | 0.46 | 2017
EI_2016-12-03_100942 | 2016-12-03 05:10 | 2016-12-03 05:10 | EST | 2016-12-03 10:10 |  | 60.015 | 59.978 | 59.9867 | -0.037 | -0.0283 |  |  | No | No | 59.5 | 0.4867 | 2017
EI_2016-12-03_144034 | 2016-12-03 09:41 | 2016-12-03 09:41 | EST | 2016-12-03 14:41 | 637.9 | 59.992 | 59.956 | 59.955 | -0.036 | -0.037 | -1771.9444 | -1724.0541 | Yes | No | 59.5 | 0.455 | 2017
EI_2016-12-04_032407 | 2016-12-03 22:24 | 2016-12-03 22:24 | EST | 2016-12-04 03:24 | 916 | 59.987 | 59.966 | 59.951 | -0.021 | -0.036 | -4361.9048 | -2544.4444 | Yes | No | 59.5 | 0.451 | 2017
EI_2016-12-06_173655 | 2016-12-06 12:37 | 2016-12-06 12:37 | EST | 2016-12-06 17:37 | 723 | 59.983 | 59.955 | 59.9495 | -0.028 | -0.0335 | -2582.1429 | -2158.209 | No | No | 59.5 | 0.4495 | 2017
EI_2016-12-09_091454 | 2016-12-09 04:15 | 2016-12-09 04:15 | EST | 2016-12-09 09:15 | 656.2 | 59.986 | 59.964 | 59.9677 | -0.022 | -0.0183 | -2982.7273 | -3585.7923 | No | No | 59.5 | 0.4677 | 2017
EI_2016-12-10_080054 | 2016-12-10 03:01 | 2016-12-10 03:01 | EST | 2016-12-10 08:01 | 500 | 60.007 | 59.966 | 59.968 | -0.041 | -0.039 | -1219.5122 | -1282.0513 | Yes | No | 59.5 | 0.468 | 2017
EI_2016-12-10_134816 | 2016-12-10 08:48 | 2016-12-10 08:48 | EST | 2016-12-10 13:48 | 630 | 59.994 | 59.975 | 59.9674 | -0.019 | -0.0266 | -3315.7895 | -2368.4211 | No | No | 59.5 | 0.4674 | 2017
EI_2016-12-11_065953 | 2016-12-11 02:00 | 2016-12-11 02:00 | EST | 2016-12-11 07:00 | 573.5 | 60.016 | 59.979 | 59.9889 | -0.037 | -0.0271 | -1550 | -2116.2362 | No | No | 59.5 | 0.4889 | 2017
EI_2016-12-11_203948 | 2016-12-11 15:40 | 2016-12-11 15:40 | EST | 2016-12-11 20:40 | 770 | 59.997 | 59.951 | 59.9622 | -0.046 | -0.0348 | -1673.913 | -2212.6437 | No | No | 59.5 | 0.4622 | 2017
EI_2016-12-13_024406 | 2016-12-12 21:44 | 2016-12-12 21:44 | EST | 2016-12-13 02:44 |  | 60 | 59.982 | 59.9717 | -0.018 | -0.0283 |  |  | No | No | 59.5 | 0.4717 | 2017
EI_2016-12-15_134120 | 2016-12-15 08:41 | 2016-12-15 08:41 | EST | 2016-12-15 13:41 |  | 60.011 | 59.976 | 59.98 | -0.035 | -0.031 |  |  | No | No | 59.5 | 0.48 | 2017
EI_2016-12-16_063345 | 2016-12-16 01:34 | 2016-12-16 01:34 | EST | 2016-12-16 06:34 | 813 | 60.017 | 59.974 | 59.981 | -0.043 | -0.036 | -1890.6977 | -2258.3333 | Yes | No | 59.5 | 0.481 | 2017
EI_2016-12-19_015644 | 2016-12-18 20:57 | 2016-12-18 20:57 | EST | 2016-12-19 01:57 | 800 | 60.006 | 59.981 | 59.975 | -0.025 | -0.031 | -3200 | -2580.6452 | Yes | No | 59.5 | 0.475 | 2017
EI_2016-12-20_135000 | 2016-12-20 08:50 | 2016-12-20 08:50 | EST | 2016-12-20 13:50 | 900 | 60.02 | 59.985 | 59.9935 | -0.035 | -0.0265 | -2571.4286 | -3396.2264 | No | No | 59.5 | 0.4935 | 2017
EI_2016-12-21_071328 | 2016-12-21 02:13 | 2016-12-21 02:13 | EST | 2016-12-21 07:13 | 700 | 60.003 | 59.964 | 59.9691 | -0.039 | -0.0339 | -1794.8718 | -2064.8968 | No | No | 59.5 | 0.4691 | 2017
EI_2016-12-24_162225 | 2016-12-24 11:22 | 2016-12-24 11:22 | EST | 2016-12-24 16:22 |  | 60.003 | 59.973 | 59.9671 | -0.03 | -0.0359 |  |  | No | No | 59.5 | 0.4671 | 2017
EI_2016-12-24_203621 | 2016-12-24 15:36 | 2016-12-24 15:36 | EST | 2016-12-24 20:36 | 850 | 59.987 | 59.958 | 59.953 | -0.029 | -0.034 | -2931.0345 | -2500 | Yes | No | 59.5 | 0.453 | 2017
EI_2016-12-26_051108 | 2016-12-26 00:11 | 2016-12-26 00:11 | EST | 2016-12-26 05:11 | 800 | 60.003 | 59.96 | 59.962 | -0.043 | -0.041 | -1860.4651 | -1951.2195 | Yes | No | 59.5 | 0.462 | 2017
EI_2016-12-26_195612 | 2016-12-26 14:56 | 2016-12-26 14:56 | EST | 2016-12-26 19:56 |  | 60.01 | 59.964 | 59.9701 | -0.046 | -0.0399 |  |  | No | No | 59.5 | 0.4701 | 2017
EI_2016-12-28_225441 | 2016-12-28 17:55 | 2016-12-28 17:55 | EST | 2016-12-28 22:55 |  | 60.017 | 59.979 | 59.9758 | -0.038 | -0.0412 |  |  | No | No | 59.5 | 0.4758 | 2017
EI_2016-12-30_050005 | 2016-12-30 | 2016-12-30 | EST | 2016-12-30 05:00 |  | 60.034 | 59.984 | 59.9963 | -0.05 | -0.0377 |  |  | No | No | 59.5 | 0.4963 | 2017
EI_2016-12-30_111639 | 2016-12-30 06:17 | 2016-12-30 06:17 | EST | 2016-12-30 11:17 | 495 | 60.005 | 59.972 | 59.968 | -0.033 | -0.037 | -1500 | -1337.8378 | Yes | No | 59.5 | 0.468 | 2017
EI_2016-12-31_100729 | 2016-12-31 05:07 | 2016-12-31 05:07 | EST | 2016-12-31 10:07 | 1360 | 60.004 | 59.952 | 59.947 | -0.052 | -0.057 | -2615.3846 | -2385.9649 | Yes | Yes | 59.5 | 0.447 | 2017
EI_2017-01-08_082021 | 2017-01-08 03:20 | 2017-01-08 03:20 | EST | 2017-01-08 08:20 | 998 | 59.984 | 59.962 | 59.953 | -0.022 | -0.031 | -4536.3636 | -3219.3548 | Yes | No | 59.5 | 0.453 | 2017
EI_2017-01-09_032412 | 2017-01-08 22:24 | 2017-01-08 22:24 | EST | 2017-01-09 03:24 | 750 | 60.004 | 59.983 | 59.9732 | -0.021 | -0.0308 | -3571.4286 | -2435.0649 | No | No | 59.5 | 0.4732 | 2017
EI_2017-01-10_002231 | 2017-01-09 19:23 | 2017-01-09 19:23 | EST | 2017-01-10 00:23 | 1325 | 60.005 | 59.958 | 59.952 | -0.047 | -0.053 | -2819.1489 | -2500 | Yes | Yes | 59.5 | 0.452 | 2017
EI_2017-01-10_180318 | 2017-01-10 13:03 | 2017-01-10 13:03 | EST | 2017-01-10 18:03 | 842 | 59.97 | 59.95 | 59.943 | -0.02 | -0.027 | -4210 | -3118.5185 | Yes | No | 59.5 | 0.443 | 2017
EI_2017-01-12_141322 | 2017-01-12 09:13 | 2017-01-12 09:13 | EST | 2017-01-12 14:13 | 1500 | 59.993 | 59.945 | 59.937 | -0.048 | -0.056 | -3125 | -2678.5714 | Yes | Yes | 59.5 | 0.437 | 2017
EI_2017-01-12_182442 | 2017-01-12 13:25 | 2017-01-12 13:25 | EST | 2017-01-12 18:25 | 700 | 60.012 | 59.991 | 59.974 | -0.021 | -0.038 | -3333.3333 | -1842.1053 | Yes | No | 59.5 | 0.474 | 2017
EI_2017-01-21_005232 | 2017-01-20 19:53 | 2017-01-20 19:53 | EST | 2017-01-21 00:53 |  | 59.996 | 59.973 | 59.9697 | -0.023 | -0.0263 |  |  | No | No | 59.5 | 0.4697 | 2017
EI_2017-01-25_201240 | 2017-01-25 15:13 | 2017-01-25 15:13 | EST | 2017-01-25 20:13 | 750 | 60.021 | 59.971 | 59.973 | -0.05 | -0.048 | -1500 | -1562.5 | Yes | No | 59.5 | 0.473 | 2017
EI_2017-01-26_144430 | 2017-01-26 09:44 | 2017-01-26 09:44 | EST | 2017-01-26 14:44 | 1144.3 | 60.006 | 59.957 | 59.954 | -0.049 | -0.052 | -2335.3061 | -2200.5769 | Yes | Yes | 59.5 | 0.454 | 2017
EI_2017-01-28_094353 | 2017-01-28 04:44 | 2017-01-28 04:44 | EST | 2017-01-28 09:44 | 753 | 60.007 | 59.961 | 59.958 | -0.046 | -0.049 | -1636.9565 | -1536.7347 | Yes | Yes | 59.5 | 0.458 | 2017
EI_2017-02-02_232358 | 2017-02-02 18:24 | 2017-02-02 18:24 | EST | 2017-02-02 23:24 | 778 | 59.999 | 59.97 | 59.963 | -0.029 | -0.036 | -2682.7586 | -2161.1111 | Yes | No | 59.5 | 0.463 | 2017
EI_2017-02-06_014650 | 2017-02-05 20:47 | 2017-02-05 20:47 | EST | 2017-02-06 01:47 | 1215 | 60.025 | 59.974 | 60.008 | -0.051 | -0.017 | -2382.3529 | -7147.0588 | No | No | 59.5 | 0.508 | 2017
EI_2017-02-13_101708 | 2017-02-13 05:17 | 2017-02-13 05:17 | EST | 2017-02-13 10:17 |  | 59.999 | 59.976 | 59.962 | -0.023 | -0.037 |  |  | No | No | 59.5 | 0.462 | 2017
EI_2017-02-14_050949 | 2017-02-14 00:10 | 2017-02-14 00:10 | EST | 2017-02-14 05:10 | 1204 | 59.987 | 59.943 | 59.938 | -0.044 | -0.049 | -2736.3636 | -2457.1429 | Yes | Yes | 59.5 | 0.438 | 2017
EI_2017-02-15_032617 | 2017-02-14 22:26 | 2017-02-14 22:26 | EST | 2017-02-15 03:26 | 860 | 59.983 | 59.957 | 59.948 | -0.026 | -0.035 | -3307.6923 | -2457.1429 | Yes | No | 59.5 | 0.448 | 2017
EI_2017-02-17_150739 | 2017-02-17 10:08 | 2017-02-17 10:08 | EST | 2017-02-17 15:08 | 707 | 59.983 | 59.956 | 59.949 | -0.027 | -0.034 | -2618.5185 | -2079.4118 | No | No | 59.5 | 0.449 | 2017
EI_2017-02-18_020050 | 2017-02-17 21:01 | 2017-02-17 21:01 | EST | 2017-02-18 02:01 |  | 60.006 | 59.969 | 59.971 | -0.037 | -0.035 |  |  | No | No | 59.5 | 0.471 | 2017
EI_2017-02-18_020700 | 2017-02-17 21:07 | 2017-02-17 21:07 | EST | 2017-02-18 02:07 |  | 60.014 | 59.983 | 59.987 | -0.031 | -0.027 |  |  | No | No | 59.5 | 0.487 | 2017
EI_2017-02-18_223017 | 2017-02-18 17:30 | 2017-02-18 17:30 | EST | 2017-02-18 22:30 |  | 60.015 | 59.981 | 59.984 | -0.034 | -0.031 |  |  | No | No | 59.5 | 0.484 | 2017
EI_2017-02-20_075629 | 2017-02-20 02:56 | 2017-02-20 02:56 | EST | 2017-02-20 07:56 |  | 60.013 | 59.965 | 59.966 | -0.048 | -0.047 |  |  | No | No | 59.5 | 0.466 | 2017
EI_2017-02-22_033008 | 2017-02-21 22:30 | 2017-02-21 22:30 | EST | 2017-02-22 03:30 | 750 | 60.02 | 59.96 | 59.961 | -0.06 | -0.059 | -1250 | -1271.1864 | Yes | No | 59.5 | 0.461 | 2017
EI_2017-02-22_214157 | 2017-02-22 16:42 | 2017-02-22 16:42 | EST | 2017-02-22 21:42 | 1400 | 60.001 | 59.949 | 59.945 | -0.052 | -0.056 | -2692.3077 | -2500 | Yes | Yes | 59.5 | 0.445 | 2017
EI_2017-02-23_115941 | 2017-02-23 07:00 | 2017-02-23 07:00 | EST | 2017-02-23 12:00 | 685 | 60.01 | 59.965 | 59.974 | -0.045 | -0.036 | -1522.2222 | -1902.7778 | No | No | 59.5 | 0.474 | 2017
EI_2017-02-23_222229 | 2017-02-23 17:22 | 2017-02-23 17:22 | EST | 2017-02-23 22:22 |  | 60.025 | 59.988 | 59.992 | -0.037 | -0.033 |  |  | No | No | 59.5 | 0.492 | 2017
EI_2017-02-24_171335 | 2017-02-24 12:14 | 2017-02-24 12:14 | EST | 2017-02-24 17:14 |  | 60.018 | 59.958 | 59.973 | -0.06 | -0.045 |  |  | No | No | 59.5 | 0.473 | 2017
EI_2017-02-25_035242 | 2017-02-24 22:53 | 2017-02-24 22:53 | EST | 2017-02-25 03:53 | 850 | 60.016 | 59.949 | 59.951 | -0.067 | -0.065 | -1268.6567 | -1307.6923 | Yes | Yes | 59.5 | 0.451 | 2017
EI_2017-02-25_055549 | 2017-02-25 00:56 | 2017-02-25 00:56 | EST | 2017-02-25 05:56 |  | 60.004 | 59.976 | 59.973 | -0.028 | -0.031 |  |  | No | No | 59.5 | 0.473 | 2017
EI_2017-03-01_095506 | 2017-03-01 04:55 | 2017-03-01 04:55 | EST | 2017-03-01 09:55 |  | 59.965 | 60.011 | 59.963 | 0.046 | -0.002 |  |  | No | No | 59.5 | 0.463 | 2017
EI_2017-03-05_112545 | 2017-03-05 06:26 | 2017-03-05 06:26 | EST | 2017-03-05 11:26 |  | 60.011 | 59.981 | 59.974 | -0.03 | -0.037 |  |  | No | No | 59.5 | 0.474 | 2017
EI_2017-03-06_172902 | 2017-03-06 12:29 | 2017-03-06 12:29 | EST | 2017-03-06 17:29 |  | 60.013 | 59.966 | 59.986 | -0.047 | -0.027 |  |  | No | No | 59.5 | 0.486 | 2017
EI_2017-03-06_191711 | 2017-03-06 14:17 | 2017-03-06 14:17 | EST | 2017-03-06 19:17 |  | 59.994 | 59.961 | 59.955 | -0.033 | -0.039 |  |  | No | No | 59.5 | 0.455 | 2017
EI_2017-03-07_095908 | 2017-03-07 04:59 | 2017-03-07 04:59 | EST | 2017-03-07 09:59 |  | 59.974 | 60.03 | 59.977 | 0.056 | 0.003 |  |  | No | No | 59.5 | 0.477 | 2017
EI_2017-03-07_100543 | 2017-03-07 05:06 | 2017-03-07 05:06 | EST | 2017-03-07 10:06 |  | 59.974 | 60.025 | 59.977 | 0.051 | 0.003 |  |  | No | No | 59.5 | 0.477 | 2017
EI_2017-03-07_135345 | 2017-03-07 08:54 | 2017-03-07 08:54 | EST | 2017-03-07 13:54 | 1085.5 | 60.006 | 59.954 | 59.949 | -0.052 | -0.057 | -2087.5 | -1904.386 | Yes | Yes | 59.5 | 0.449 | 2017
EI_2017-03-08_100850 | 2017-03-08 05:09 | 2017-03-08 05:09 | EST | 2017-03-08 10:09 |  | 59.98 | 60.033 | 59.982 | 0.053 | 0.002 |  |  | No | No | 59.5 | 0.482 | 2017
EI_2017-03-08_150006 | 2017-03-08 10:00 | 2017-03-08 10:00 | EST | 2017-03-08 15:00 |  | 60.009 | 59.968 | 59.969 | -0.041 | -0.04 |  |  | No | No | 59.5 | 0.469 | 2017
EI_2017-03-08_190035 | 2017-03-08 14:01 | 2017-03-08 14:01 | EST | 2017-03-08 19:01 | 544 | 59.998 | 59.966 | 59.956 | -0.032 | -0.042 | -1700 | -1295.2381 | Yes | No | 59.5 | 0.456 | 2017
EI_2017-03-08_232932 | 2017-03-08 18:30 | 2017-03-08 18:30 | EST | 2017-03-08 23:30 | 700 | 59.976 | 59.954 | 59.942 | -0.022 | -0.034 | -3181.8182 | -2058.8235 | No | No | 59.5 | 0.442 | 2017
EI_2017-03-09_162236 | 2017-03-09 11:23 | 2017-03-09 11:23 | EST | 2017-03-09 16:23 | 663 | 59.988 | 59.952 | 59.948 | -0.036 | -0.04 | -1841.6667 | -1657.5 | Yes | No | 59.5 | 0.448 | 2017
EI_2017-03-15_144016 | 2017-03-15 10:40 | 2017-03-15 10:40 | EDT | 2017-03-15 14:40 |  | 60 | 59.964 | 59.963 | -0.036 | -0.037 |  |  | No | No | 59.5 | 0.463 | 2017
EI_2017-03-16_161145 | 2017-03-16 12:12 | 2017-03-16 12:12 | EDT | 2017-03-16 16:12 |  | 59.975 | 59.94 | 59.934 | -0.035 | -0.041 |  |  | No | No | 59.5 | 0.434 | 2017
EI_2017-03-18_150612 | 2017-03-18 11:06 | 2017-03-18 11:06 | EDT | 2017-03-18 15:06 |  | 60.018 | 59.959 | 59.968 | -0.059 | -0.05 |  |  | No | No | 59.5 | 0.468 | 2017
EI_2017-03-19_210250 | 2017-03-19 17:03 | 2017-03-19 17:03 | EDT | 2017-03-19 21:03 |  | 59.975 | 60.026 | 59.977 | 0.051 | 0.002 |  |  | No | No | 59.5 | 0.477 | 2017
EI_2017-03-20_001332 | 2017-03-19 20:14 | 2017-03-19 20:14 | EDT | 2017-03-20 00:14 |  | 59.973 | 60.019 | 59.97 | 0.046 | -0.003 |  |  | No | No | 59.5 | 0.47 | 2017
EI_2017-03-20_121313 | 2017-03-20 08:13 | 2017-03-20 08:13 | EDT | 2017-03-20 12:13 | 1150 | 59.989 | 59.953 | 59.944 | -0.036 | -0.045 | -3194.4444 | -2555.5556 | Yes | Yes | 59.5 | 0.444 | 2017
EI_2017-03-20_121754 | 2017-03-20 08:18 | 2017-03-20 08:18 | EDT | 2017-03-20 12:18 |  | 59.979 | 60.016 | 59.983 | 0.037 | 0.004 |  |  | No | No | 59.5 | 0.483 | 2017
EI_2017-03-23_153450 | 2017-03-23 11:35 | 2017-03-23 11:35 | EDT | 2017-03-23 15:35 |  | 60.018 | 59.964 | 59.953 | -0.054 | -0.065 |  |  | No | No | 59.5 | 0.453 | 2017
EI_2017-03-24_090017 | 2017-03-24 05:00 | 2017-03-24 05:00 | EDT | 2017-03-24 09:00 |  | 59.986 | 60.037 | 59.982 | 0.051 | -0.004 |  |  | No | No | 59.5 | 0.482 | 2017
EI_2017-03-26_125503 | 2017-03-26 08:55 | 2017-03-26 08:55 | EDT | 2017-03-26 12:55 |  | 59.992 | 60.032 | 59.994 | 0.04 | 0.002 |  |  | No | No | 59.5 | 0.494 | 2017
EI_2017-03-28_080109 | 2017-03-28 04:01 | 2017-03-28 04:01 | EDT | 2017-03-28 08:01 |  | 59.987 | 60.031 | 59.992 | 0.044 | 0.005 |  |  | No | No | 59.5 | 0.492 | 2017
EI_2017-03-29_055456 | 2017-03-29 01:55 | 2017-03-29 01:55 | EDT | 2017-03-29 05:55 | 471 | 60.011 | 59.967 | 59.962 | -0.044 | -0.049 | -1070.4545 | -961.2245 | Yes | No | 59.5 | 0.462 | 2017
EI_2017-03-29_104945 | 2017-03-29 06:50 | 2017-03-29 06:50 | EDT | 2017-03-29 10:50 |  | 59.994 | 60.042 | 59.993 | 0.048 | -0.001 |  |  | No | No | 59.5 | 0.493 | 2017
EI_2017-03-30_100329 | 2017-03-30 06:03 | 2017-03-30 06:03 | EDT | 2017-03-30 10:03 |  | 59.977 | 60.038 | 59.981 | 0.061 | 0.004 |  |  | No | No | 59.5 | 0.481 | 2017
EI_2017-04-04_050916 | 2017-04-04 01:09 | 2017-04-04 01:09 | EDT | 2017-04-04 05:09 | 1413 | 60.015 | 59.958 | 59.972 | -0.057 | -0.043 | -2478.9474 | -3286.0465 | Yes | No | 59.5 | 0.472 | 2017
EI_2017-04-05_005928 | 2017-04-04 20:59 | 2017-04-04 20:59 | EDT | 2017-04-05 00:59 |  | 59.982 | 59.938 | 59.939 | -0.044 | -0.043 |  |  | No | No | 59.5 | 0.439 | 2017
EI_2017-04-05_010543 | 2017-04-04 21:06 | 2017-04-04 21:06 | EDT | 2017-04-05 01:06 | 850 | 60.015 | 59.978 | 59.992 | -0.037 | -0.023 | -2297.2973 | -3695.6522 | No | No | 59.5 | 0.492 | 2017
EI_2017-04-07_102506 | 2017-04-07 06:25 | 2017-04-07 06:25 | EDT | 2017-04-07 10:25 |  | 59.989 | 60.04 | 59.995 | 0.051 | 0.006 |  |  | No | No | 59.5 | 0.495 | 2017
EI_2017-04-07_194648 | 2017-04-07 15:47 | 2017-04-07 15:47 | EDT | 2017-04-07 19:47 |  | 60.008 | 59.965 | 59.983 | -0.043 | -0.025 |  |  | No | No | 59.5 | 0.483 | 2017
EI_2017-04-08_054504 | 2017-04-08 01:45 | 2017-04-08 01:45 | EDT | 2017-04-08 05:45 |  | 60.016 | 59.981 | 59.988 | -0.035 | -0.028 |  |  | No | No | 59.5 | 0.488 | 2017
EI_2017-04-08_155247 | 2017-04-08 11:53 | 2017-04-08 11:53 | EDT | 2017-04-08 15:53 | 1195 | 60.02 | 59.948 | 59.944 | -0.072 | -0.076 | -1659.7222 | -1572.3684 | Yes | Yes | 59.5 | 0.444 | 2017
EI_2017-04-08_214427 | 2017-04-08 17:44 | 2017-04-08 17:44 | EDT | 2017-04-08 21:44 |  | 59.988 | 60.03 | 59.992 | 0.042 | 0.004 |  |  | No | No | 59.5 | 0.492 | 2017
EI_2017-04-09_031633 | 2017-04-08 23:17 | 2017-04-08 23:17 | EDT | 2017-04-09 03:17 |  | 60.02 | 59.973 | 59.988 | -0.047 | -0.032 |  |  | No | No | 59.5 | 0.488 | 2017
EI_2017-04-09_192517 | 2017-04-09 15:25 | 2017-04-09 15:25 | EDT | 2017-04-09 19:25 |  | 59.985 | 59.959 | 59.949 | -0.026 | -0.036 |  |  | No | No | 59.5 | 0.449 | 2017
EI_2017-04-10_024835 | 2017-04-09 22:49 | 2017-04-09 22:49 | EDT | 2017-04-10 02:49 |  | 60.008 | 59.974 | 59.97 | -0.034 | -0.038 |  |  | No | No | 59.5 | 0.47 | 2017
EI_2017-04-10_223656 | 2017-04-10 18:37 | 2017-04-10 18:37 | EDT | 2017-04-10 22:37 |  | 60.01 | 59.968 | 59.97 | -0.042 | -0.04 |  |  | No | No | 59.5 | 0.47 | 2017
EI_2017-04-11_161312 | 2017-04-11 12:13 | 2017-04-11 12:13 | EDT | 2017-04-11 16:13 | 755.6 | 60.001 | 59.961 | 59.954 | -0.04 | -0.047 | -1889 | -1607.6596 | Yes | Yes | 59.5 | 0.454 | 2017
EI_2017-04-13_030154 | 2017-04-12 23:02 | 2017-04-12 23:02 | EDT | 2017-04-13 03:02 |  | 60.033 | 59.975 | 60.018 | -0.058 | -0.015 |  |  | No | No | 59.5 | 0.518 | 2017
EI_2017-04-13_041528 | 2017-04-13 00:15 | 2017-04-13 00:15 | EDT | 2017-04-13 04:15 |  | 60.006 | 59.965 | 59.966 | -0.041 | -0.04 |  |  | No | No | 59.5 | 0.466 | 2017
EI_2017-04-17_043709 | 2017-04-17 00:37 | 2017-04-17 00:37 | EDT | 2017-04-17 04:37 |  | 59.989 | 60.023 | 59.994 | 0.034 | 0.005 |  |  | No | No | 59.5 | 0.494 | 2017
EI_2017-04-19_034149 | 2017-04-18 23:42 | 2017-04-18 23:42 | EDT | 2017-04-19 03:42 |  | 60.018 | 59.963 | 59.983 | -0.055 | -0.035 |  |  | No | No | 59.5 | 0.483 | 2017
EI_2017-04-20_220908 | 2017-04-20 18:09 | 2017-04-20 18:09 | EDT | 2017-04-20 22:09 | 605 | 60.025 | 59.986 | 59.985 | -0.039 | -0.04 | -1551.2821 | -1512.5 | Yes | No | 59.5 | 0.485 | 2017
EI_2017-04-21_132732 | 2017-04-21 09:28 | 2017-04-21 09:28 | EDT | 2017-04-21 13:28 |  | 59.979 | 60.019 | 59.984 | 0.04 | 0.005 |  |  | No | No | 59.5 | 0.484 | 2017
EI_2017-04-22_010044 | 2017-04-21 21:01 | 2017-04-21 21:01 | EDT | 2017-04-22 01:01 |  | 60.028 | 59.97 | 60.01 | -0.058 | -0.018 |  |  | No | No | 59.5 | 0.51 | 2017
EI_2017-04-22_040804 | 2017-04-22 00:08 | 2017-04-22 00:08 | EDT | 2017-04-22 04:08 |  | 59.993 | 59.955 | 59.96 | -0.038 | -0.033 |  |  | No | No | 59.5 | 0.46 | 2017
EI_2017-04-23_040427 | 2017-04-23 00:04 | 2017-04-23 00:04 | EDT | 2017-04-23 04:04 |  | 60.009 | 59.961 | 59.971 | -0.048 | -0.038 |  |  | No | No | 59.5 | 0.471 | 2017
EI_2017-04-26_150234 | 2017-04-26 11:03 | 2017-04-26 11:03 | EDT | 2017-04-26 15:03 | 839.1 | 60 | 59.949 | 59.954 | -0.051 | -0.046 | -1645.2941 | -1824.1304 | Yes | Yes | 59.5 | 0.454 | 2017
EI_2017-04-26_162612 | 2017-04-26 12:26 | 2017-04-26 12:26 | EDT | 2017-04-26 16:26 | 665 | 59.979 | 59.962 | 59.955 | -0.017 | -0.024 | -3911.7647 | -2770.8333 | No | No | 59.5 | 0.455 | 2017
EI_2017-04-27_101045 | 2017-04-27 06:11 | 2017-04-27 06:11 | EDT | 2017-04-27 10:11 |  | 60.022 | 60 | 60.024 | -0.022 | 0.002 |  |  | No | No | 59.5 | 0.524 | 2017
EI_2017-04-29_044737 | 2017-04-29 00:48 | 2017-04-29 00:48 | EDT | 2017-04-29 04:48 |  | 60.011 | 59.971 | 59.972 | -0.04 | -0.039 |  |  | No | No | 59.5 | 0.472 | 2017
EI_2017-04-29_052944 | 2017-04-29 01:30 | 2017-04-29 01:30 | EDT | 2017-04-29 05:30 | 678 | 60.01 | 59.962 | 59.962 | -0.048 | -0.048 | -1412.5 | -1412.5 | Yes | No | 59.5 | 0.462 | 2017
EI_2017-04-29_211353 | 2017-04-29 17:14 | 2017-04-29 17:14 | EDT | 2017-04-29 21:14 |  | 60.01 | 59.975 | 59.972 | -0.035 | -0.038 |  |  | No | No | 59.5 | 0.472 | 2017
EI_2017-05-02_025714 | 2017-05-01 22:57 | 2017-05-01 22:57 | EDT | 2017-05-02 02:57 |  | 60.021 | 59.955 | 59.984 | -0.066 | -0.037 |  |  | No | No | 59.5 | 0.484 | 2017
EI_2017-05-02_135429 | 2017-05-02 09:54 | 2017-05-02 09:54 | EDT | 2017-05-02 13:54 |  | 60.003 | 59.972 | 59.967 | -0.031 | -0.036 |  |  | No | No | 59.5 | 0.467 | 2017
EI_2017-05-03_163905 | 2017-05-03 12:39 | 2017-05-03 12:39 | EDT | 2017-05-03 16:39 |  | 60.009 | 59.968 | 59.97 | -0.041 | -0.039 |  |  | No | No | 59.5 | 0.47 | 2017
EI_2017-05-06_003219 | 2017-05-05 20:32 | 2017-05-05 20:32 | EDT | 2017-05-06 00:32 | 585 | 60.004 | 59.968 | 59.965 | -0.036 | -0.039 | -1625 | -1500 | Yes | No | 59.5 | 0.465 | 2017
EI_2017-05-08_081529 | 2017-05-08 04:15 | 2017-05-08 04:15 | EDT | 2017-05-08 08:15 | 1047 | 59.975 | 59.952 | 59.944 | -0.023 | -0.031 | -4552.1739 | -3377.4194 | No | No | 59.5 | 0.444 | 2017
EI_2017-05-12_040743 | 2017-05-12 00:08 | 2017-05-12 00:08 | EDT | 2017-05-12 04:08 |  | 60.013 | 59.972 | 59.983 | -0.041 | -0.03 |  |  | No | No | 59.5 | 0.483 | 2017
EI_2017-05-15_053956 | 2017-05-15 01:40 | 2017-05-15 01:40 | EDT | 2017-05-15 05:40 |  | 60.019 | 59.979 | 59.987 | -0.04 | -0.032 |  |  | No | No | 59.5 | 0.487 | 2017
EI_2017-05-15_164910 | 2017-05-15 12:49 | 2017-05-15 12:49 | EDT | 2017-05-15 16:49 | 587.4 | 59.995 | 59.972 | 59.96 | -0.023 | -0.035 | -2553.913 | -1678.2857 | No | No | 59.5 | 0.46 | 2017
EI_2017-05-18_120925 | 2017-05-18 08:09 | 2017-05-18 08:09 | EDT | 2017-05-18 12:09 | 825 | 60.01 | 59.951 | 59.957 | -0.059 | -0.053 | -1398.3051 | -1556.6038 | Yes | Yes | 59.5 | 0.457 | 2017
EI_2017-05-19_024132 | 2017-05-18 22:42 | 2017-05-18 22:42 | EDT | 2017-05-19 02:42 | 613 | 60.008 | 59.98 | 59.966 | -0.028 | -0.042 | -2189.2857 | -1459.5238 | Yes | No | 59.5 | 0.466 | 2017
EI_2017-05-19_103024 | 2017-05-19 06:30 | 2017-05-19 06:30 | EDT | 2017-05-19 10:30 |  | 60.009 | 59.968 | 59.969 | -0.041 | -0.04 |  |  | No | No | 59.5 | 0.469 | 2017
EI_2017-05-19_131650 | 2017-05-19 09:17 | 2017-05-19 09:17 | EDT | 2017-05-19 13:17 | 666 | 59.996 | 59.967 | 59.963 | -0.029 | -0.033 | -2296.5517 | -2018.1818 | No | No | 59.5 | 0.463 | 2017
EI_2017-05-20_082548 | 2017-05-20 04:26 | 2017-05-20 04:26 | EDT | 2017-05-20 08:26 |  | 60.001 | 59.973 | 59.964 | -0.028 | -0.037 |  |  | No | No | 59.5 | 0.464 | 2017
EI_2017-05-21_211644 | 2017-05-21 17:17 | 2017-05-21 17:17 | EDT | 2017-05-21 21:17 |  | 59.989 | 59.958 | 59.945 | -0.031 | -0.044 |  |  | No | No | 59.5 | 0.445 | 2017
EI_2017-05-22_233704 | 2017-05-22 19:37 | 2017-05-22 19:37 | EDT | 2017-05-22 23:37 | 730 | 59.997 | 59.972 | 59.957 | -0.025 | -0.04 | -2920 | -1825 | Yes | Yes | 59.5 | 0.457 | 2017
EI_2017-05-24_171813 | 2017-05-24 13:18 | 2017-05-24 13:18 | EDT | 2017-05-24 17:18 | 1500 | 59.989 | 59.949 | 59.937 | -0.04 | -0.052 | -3750 | -2884.6154 | No | No | 59.5 | 0.437 | 2017
EI_2017-05-28_013800 | 2017-05-27 21:38 | 2017-05-27 21:38 | EDT | 2017-05-28 01:38 |  | 60.019 | 59.976 | 59.978 | -0.043 | -0.041 |  |  | No | No | 59.5 | 0.478 | 2017
EI_2017-05-28_043058 | 2017-05-28 00:31 | 2017-05-28 00:31 | EDT | 2017-05-28 04:31 |  | 60.011 | 59.975 | 59.967 | -0.036 | -0.044 |  |  | No | No | 59.5 | 0.467 | 2017
EI_2017-05-29_152619 | 2017-05-29 11:26 | 2017-05-29 11:26 | EDT | 2017-05-29 15:26 | 896 | 60.008 | 59.958 | 59.956 | -0.05 | -0.052 | -1792 | -1723.0769 | Yes | No | 59.5 | 0.456 | 2017
EI_2017-05-30_162323 | 2017-05-30 12:23 | 2017-05-30 12:23 | EDT | 2017-05-30 16:23 | 599 | 59.997 | 59.96 | 59.959 | -0.037 | -0.038 | -1618.9189 | -1576.3158 | Yes | No | 59.5 | 0.459 | 2017
EI_2017-06-03_053022 | 2017-06-03 01:30 | 2017-06-03 01:30 | EDT | 2017-06-03 05:30 |  | 60.01 | 59.962 | 59.965 | -0.048 | -0.045 |  |  | No | No | 59.5 | 0.465 | 2017
EI_2017-06-05_185334 | 2017-06-05 14:54 | 2017-06-05 14:54 | EDT | 2017-06-05 18:54 | 960 | 60.019 | 59.986 | 59.985 | -0.033 | -0.034 | -2909.0909 | -2823.5294 | No | No | 59.5 | 0.485 | 2017
EI_2017-06-06_032917 | 2017-06-05 23:29 | 2017-06-05 23:29 | EDT | 2017-06-06 03:29 |  | 60.018 | 59.974 | 59.979 | -0.044 | -0.039 |  |  | No | No | 59.5 | 0.479 | 2017
EI_2017-06-07_174745 | 2017-06-07 13:48 | 2017-06-07 13:48 | EDT | 2017-06-07 17:48 | 701.5 | 59.981 | 59.962 | 59.957 | -0.019 | -0.024 | -3692.1053 | -2922.9167 | No | No | 59.5 | 0.457 | 2017
EI_2017-06-08_192700 | 2017-06-08 15:27 | 2017-06-08 15:27 | EDT | 2017-06-08 19:27 | 1325 | 60 | 59.94 | 59.935 | -0.06 | -0.065 | -2208.3333 | -2038.4615 | Yes | Yes | 59.5 | 0.435 | 2017
EI_2017-06-10_002018 | 2017-06-09 20:20 | 2017-06-09 20:20 | EDT | 2017-06-10 00:20 |  | 60.021 | 59.972 | 59.982 | -0.049 | -0.039 |  |  | No | No | 59.5 | 0.482 | 2017
EI_2017-06-11_040600 | 2017-06-11 00:06 | 2017-06-11 00:06 | EDT | 2017-06-11 04:06 | 917.6 | 60.004 | 59.961 | 59.967 | -0.043 | -0.037 | -2133.9535 | -2480 | Yes | No | 59.5 | 0.467 | 2017
EI_2017-06-15_145143 | 2017-06-15 10:52 | 2017-06-15 10:52 | EDT | 2017-06-15 14:52 | 820 | 60.021 | 59.986 | 59.984 | -0.035 | -0.037 | -2342.8571 | -2216.2162 | Yes | No | 59.5 | 0.484 | 2017
EI_2017-06-19_011054 | 2017-06-18 21:11 | 2017-06-18 21:11 | EDT | 2017-06-19 01:11 | 750 | 59.996 | 59.961 | 59.955 | -0.035 | -0.041 | -2142.8571 | -1829.2683 | Yes | Yes | 59.5 | 0.455 | 2017
EI_2017-06-19_181147 | 2017-06-19 14:12 | 2017-06-19 14:12 | EDT | 2017-06-19 18:12 | 700 | 60 | 59.976 | 59.974 | -0.024 | -0.026 | -2916.6667 | -2692.3077 | No | No | 59.5 | 0.474 | 2017
EI_2017-06-20_031617 | 2017-06-19 23:16 | 2017-06-19 23:16 | EDT | 2017-06-20 03:16 |  | 60.01 | 59.969 | 59.975 | -0.041 | -0.035 |  |  | No | No | 59.5 | 0.475 | 2017
EI_2017-06-21_132200 | 2017-06-21 09:22 | 2017-06-21 09:22 | EDT | 2017-06-21 13:22 | 830 | 60.017 | 59.997 | 59.99 | -0.02 | -0.027 | -4150 | -3074.0741 | Yes | No | 59.5 | 0.49 | 2017
EI_2017-06-23_202030 | 2017-06-23 16:20 | 2017-06-23 16:20 | EDT | 2017-06-23 20:20 | 442 | 59.99 | 59.976 | 59.969 | -0.014 | -0.021 | -3157.1429 | -2104.7619 | No | No | 59.5 | 0.469 | 2017
EI_2017-06-24_011855 | 2017-06-23 21:19 | 2017-06-23 21:19 | EDT | 2017-06-24 01:19 | 1019 | 59.986 | 59.946 | 59.944 | -0.04 | -0.042 | -2547.5 | -2426.1905 | Yes | Yes | 59.5 | 0.444 | 2017
EI_2017-06-24_133228 | 2017-06-24 09:32 | 2017-06-24 09:32 | EDT | 2017-06-24 13:32 | -1 | 59.976 | 59.995 | 60.004 | 0.019 | 0.028 | -5.2632 | -3.5714 | No | No | 59.5 | 0.504 | 2017
EI_2017-06-26_054032 | 2017-06-26 01:41 | 2017-06-26 01:41 | EDT | 2017-06-26 05:41 |  | 59.995 | 59.986 | 59.971 | -0.009 | -0.024 |  |  | No | No | 59.5 | 0.471 | 2017
EI_2017-06-28_114112 | 2017-06-28 07:41 | 2017-06-28 07:41 | EDT | 2017-06-28 11:41 | -1 | 59.992 | 60.028 | 60.026 | 0.036 | 0.034 | -2.7778 | -2.9412 | No | No | 59.5 | 0.526 | 2017
EI_2017-06-29_125725 | 2017-06-29 08:57 | 2017-06-29 08:57 | EDT | 2017-06-29 12:57 | 1021 | 59.992 | 59.966 | 59.957 | -0.026 | -0.035 | -3926.9231 | -2917.1429 | Yes | No | 59.5 | 0.457 | 2017
EI_2017-06-29_192108 | 2017-06-29 15:21 | 2017-06-29 15:21 | EDT | 2017-06-29 19:21 | 778 | 59.99 | 59.956 | 59.953 | -0.034 | -0.037 | -2288.2353 | -2102.7027 | Yes | No | 59.5 | 0.453 | 2017
EI_2017-07-01_135648 | 2017-07-01 09:57 | 2017-07-01 09:57 | EDT | 2017-07-01 13:57 | -1 | 59.999 | 60.039 | 60.036 | 0.04 | 0.037 | -2.5 | -2.7027 | No | No | 59.5 | 0.536 | 2017
EI_2017-07-06_125513 | 2017-07-06 08:55 | 2017-07-06 08:55 | EDT | 2017-07-06 12:55 | -1 | 59.979 | 60.017 | 60.025 | 0.038 | 0.046 | -2.6316 | -2.1739 | No | No | 59.5 | 0.525 | 2017
EI_2017-07-10_162649 | 2017-07-10 12:27 | 2017-07-10 12:27 | EDT | 2017-07-10 16:27 | 0 | 60.031 | 59.969 | 59.973 | -0.062 | -0.058 |  |  | No | No | 59.5 | 0.473 | 2017
EI_2017-07-17_120505 | 2017-07-17 08:05 | 2017-07-17 08:05 | EDT | 2017-07-17 12:05 | 464 | 60.011 | 59.976 | 59.972 | -0.035 | -0.039 | -1325.7143 | -1189.7436 | Yes | No | 59.5 | 0.472 | 2017
EI_2017-07-17_210533 | 2017-07-17 17:06 | 2017-07-17 17:06 | EDT | 2017-07-17 21:06 | 1222 | 59.999 | 59.96 | 59.951 | -0.039 | -0.048 | -3133.3333 | -2545.8333 | Yes | Yes | 59.5 | 0.451 | 2017
EI_2017-07-21_152740 | 2017-07-21 11:28 | 2017-07-21 11:28 | EDT | 2017-07-21 15:28 | 370 | 60.001 | 59.96 | 59.964 | -0.041 | -0.037 | -902.439 | -1000 | No | No | 59.5 | 0.464 | 2017
EI_2017-07-21_170556 | 2017-07-21 13:06 | 2017-07-21 13:06 | EDT | 2017-07-21 17:06 | 1661 | 59.999 | 59.956 | 59.953 | -0.043 | -0.046 | -3862.7907 | -3610.8696 | Yes | Yes | 59.5 | 0.453 | 2017
EI_2017-07-24_203854 | 2017-07-24 16:39 | 2017-07-24 16:39 | EDT | 2017-07-24 20:39 | 893 | 59.995 | 59.963 | 59.959 | -0.032 | -0.036 | -2790.625 | -2480.5556 | Yes | No | 59.5 | 0.459 | 2017
EI_2017-07-25_120004 | 2017-07-25 08:00 | 2017-07-25 08:00 | EDT | 2017-07-25 12:00 | -1 | 59.98 | 60.013 | 60.016 | 0.033 | 0.036 | -3.0303 | -2.7778 | No | No | 59.5 | 0.516 | 2017
EI_2017-07-27_120111 | 2017-07-27 08:01 | 2017-07-27 08:01 | EDT | 2017-07-27 12:01 | -1 | 59.989 | 60.033 | 60.027 | 0.044 | 0.038 | -2.2727 | -2.6316 | No | No | 59.5 | 0.527 | 2017
EI_2017-07-27_193048 | 2017-07-27 15:31 | 2017-07-27 15:31 | EDT | 2017-07-27 19:31 | 569 | 60.019 | 59.968 | 59.974 | -0.051 | -0.045 | -1115.6863 | -1264.4444 | Yes | No | 59.5 | 0.474 | 2017
EI_2017-08-04_151031 | 2017-08-04 11:11 | 2017-08-04 11:11 | EDT | 2017-08-04 15:11 | 0 | 60.024 | 59.959 | 59.977 | -0.065 | -0.047 |  |  | No | No | 59.5 | 0.477 | 2017
EI_2017-08-06_023438 | 2017-08-05 22:35 | 2017-08-05 22:35 | EDT | 2017-08-06 02:35 | 940 | 59.997 | 59.952 | 59.955 | -0.045 | -0.042 | -2088.8889 | -2238.0952 | Yes | No | 59.5 | 0.455 | 2017
EI_2017-08-06_191322 | 2017-08-06 15:13 | 2017-08-06 15:13 | EDT | 2017-08-06 19:13 | 586 | 60 | 59.973 | 59.967 | -0.027 | -0.033 | -2170.3704 | -1775.7576 | No | No | 59.5 | 0.467 | 2017
EI_2017-08-16_151133 | 2017-08-16 11:12 | 2017-08-16 11:12 | EDT | 2017-08-16 15:12 | 700 | 59.978 | 59.953 | 59.952 | -0.025 | -0.026 | -2800 | -2692.3077 | No | No | 59.5 | 0.452 | 2017
EI_2017-08-19_015535 | 2017-08-18 21:56 | 2017-08-18 21:56 | EDT | 2017-08-19 01:56 | 1010 | 60.011 | 59.976 | 59.968 | -0.035 | -0.043 | -2885.7143 | -2348.8372 | No | No | 59.5 | 0.468 | 2017
EI_2017-08-24_123912 | 2017-08-24 08:39 | 2017-08-24 08:39 | EDT | 2017-08-24 12:39 | 300 | 59.987 | 59.97 | 59.961 | -0.017 | -0.026 | -1764.7059 | -1153.8462 | No | No | 59.5 | 0.461 | 2017
EI_2017-08-24_233123 | 2017-08-24 19:31 | 2017-08-24 19:31 | EDT | 2017-08-24 23:31 | 800 | 59.993 | 59.959 | 59.957 | -0.034 | -0.036 | -2352.9412 | -2222.2222 | No | No | 59.5 | 0.457 | 2017
EI_2017-08-27_004106 | 2017-08-26 20:41 | 2017-08-26 20:41 | EDT | 2017-08-27 00:41 | 652 | 60.017 | 59.965 | 59.974 | -0.052 | -0.043 | -1253.8462 | -1516.2791 | Yes | No | 59.5 | 0.474 | 2017
EI_2017-08-27_035240 | 2017-08-26 23:53 | 2017-08-26 23:53 | EDT | 2017-08-27 03:53 | 762 | 59.999 | 59.969 | 59.958 | -0.03 | -0.041 | -2540 | -1858.5366 | Yes | Yes | 59.5 | 0.458 | 2017
EI_2017-08-28_123630 | 2017-08-28 08:37 | 2017-08-28 08:37 | EDT | 2017-08-28 12:36 | 978 | 60.007 | 59.962 | 59.954 | -0.045 | -0.053 | -2173.3333 | -1845.283 | Yes | Yes | 59.5 | 0.454 | 2017
EI_2017-08-30_215216 | 2017-08-30 17:52 | 2017-08-30 17:52 | EDT | 2017-08-30 21:52 | 630 | 60.012 | 59.972 | 59.97 | -0.04 | -0.042 | -1575 | -1500 | Yes | No | 59.5 | 0.47 | 2017
EI_2017-09-01_211425 | 2017-09-01 17:14 | 2017-09-01 17:14 | EDT | 2017-09-01 21:14 |  | 60.01 | 59.962 | 59.965 | -0.048 | -0.045 |  |  | No | No | 59.5 | 0.465 | 2017
EI_2017-09-02_043402 | 2017-09-02 00:34 | 2017-09-02 00:34 | EDT | 2017-09-02 04:34 | 950 | 59.999 | 59.958 | 59.955 | -0.041 | -0.044 | -2317.0732 | -2159.0909 | Yes | Yes | 59.5 | 0.455 | 2017
EI_2017-09-04_210958 | 2017-09-04 17:10 | 2017-09-04 17:10 | EDT | 2017-09-04 21:10 | 661 | 59.996 | 59.969 | 59.959 | -0.027 | -0.037 | -2448.1481 | -1786.4865 | Yes | No | 59.5 | 0.459 | 2017
EI_2017-09-06_163212 | 2017-09-06 12:32 | 2017-09-06 12:32 | EDT | 2017-09-06 16:32 | 560 | 60.006 | 59.966 | 59.968 | -0.04 | -0.038 | -1400 | -1473.6842 | Yes | No | 59.5 | 0.468 | 2017
EI_2017-09-07_131430 | 2017-09-07 09:15 | 2017-09-07 09:15 | EDT | 2017-09-07 13:14 | 908 | 59.985 | 59.957 | 59.95 | -0.028 | -0.035 | -3242.8571 | -2594.2857 | Yes | No | 59.5 | 0.45 | 2017
EI_2017-09-07_195217 | 2017-09-07 15:52 | 2017-09-07 15:52 | EDT | 2017-09-07 19:52 | 675 | 59.997 | 59.96 | 59.958 | -0.037 | -0.039 | -1824.3243 | -1730.7692 | Yes | No | 59.5 | 0.458 | 2017
EI_2017-09-08_095940 | 2017-09-08 06:00 | 2017-09-08 06:00 | EDT | 2017-09-08 10:00 | -1 | 59.973 | 60.021 | 60.015 | 0.048 | 0.042 | -2.0833 | -2.381 | No | No | 59.5 | 0.515 | 2017
EI_2017-09-08_173131 | 2017-09-08 13:32 | 2017-09-08 13:32 | EDT | 2017-09-08 17:32 | 757 | 59.983 | 59.964 | 59.957 | -0.019 | -0.026 | -3984.2105 | -2911.5385 | No | No | 59.5 | 0.457 | 2017
EI_2017-09-09_054455 | 2017-09-09 01:45 | 2017-09-09 01:45 | EDT | 2017-09-09 05:45 |  | 60.019 | 59.964 | 59.982 | -0.055 | -0.037 |  |  | No | No | 59.5 | 0.482 | 2017
EI_2017-09-10_225519 | 2017-09-10 18:55 | 2017-09-10 18:55 | EDT | 2017-09-10 22:55 | 770 | 59.99 | 59.964 | 59.956 | -0.026 | -0.034 | -2961.5385 | -2264.7059 | No | No | 59.5 | 0.456 | 2017
EI_2017-09-11_010814 | 2017-09-10 21:08 | 2017-09-10 21:08 | EDT | 2017-09-11 01:08 |  | 60.009 | 59.974 | 59.973 | -0.035 | -0.036 |  |  | No | No | 59.5 | 0.473 | 2017
EI_2017-09-21_174556 | 2017-09-21 13:46 | 2017-09-21 13:46 | EDT | 2017-09-21 17:46 |  | 60.026 | 59.984 | 59.986 | -0.042 | -0.04 |  |  | No | No | 59.5 | 0.486 | 2017
EI_2017-09-22_175916 | 2017-09-22 13:59 | 2017-09-22 13:59 | EDT | 2017-09-22 17:59 | 700 | 60.015 | 59.987 | 59.98 | -0.028 | -0.035 | -2500 | -2000 | No | No | 59.5 | 0.48 | 2017
EI_2017-09-27_104622 | 2017-09-27 06:46 | 2017-09-27 06:46 | EDT | 2017-09-27 10:46 | 825 | 59.997 | 59.966 | 59.967 | -0.031 | -0.03 | -2661.2903 | -2750 | Yes | No | 59.5 | 0.467 | 2017
EI_2017-10-03_184428 | 2017-10-03 14:44 | 2017-10-03 14:44 | EDT | 2017-10-03 18:44 | 724 | 59.989 | 59.957 | 59.952 | -0.032 | -0.037 | -2262.5 | -1956.7568 | Yes | No | 59.5 | 0.452 | 2017
EI_2017-10-08_170802 | 2017-10-08 13:08 | 2017-10-08 13:08 | EDT | 2017-10-08 17:08 | 657 | 60.003 | 59.955 | 59.955 | -0.048 | -0.048 | -1368.75 | -1368.75 | Yes | Yes | 59.5 | 0.455 | 2017
EI_2017-10-11_120600 | 2017-10-11 08:06 | 2017-10-11 08:06 | EDT | 2017-10-11 12:06 | 850 | 59.978 | 59.985 | 59.964 | 0.007 | -0.014 | 12142.8571 | -6071.4286 | No | No | 59.5 | 0.464 | 2017
EI_2017-10-14_003923 | 2017-10-13 20:39 | 2017-10-13 20:39 | EDT | 2017-10-14 00:39 | 600 | 60.017 | 59.987 | 59.978 | -0.03 | -0.039 | -2000 | -1538.4615 | Yes | No | 59.5 | 0.478 | 2017
EI_2017-10-24_194713 | 2017-10-24 15:47 | 2017-10-24 15:47 | EDT | 2017-10-24 19:47 | 736 | 60.002 | 59.976 | 59.962 | -0.026 | -0.04 | -2830.7692 | -1840 | Yes | No | 59.5 | 0.462 | 2017
EI_2017-10-25_090010 | 2017-10-25 05:00 | 2017-10-25 05:00 | EDT | 2017-10-25 09:00 |  | 60.017 | 59.969 | 59.978 | -0.048 | -0.039 |  |  | No | No | 59.5 | 0.478 | 2017
EI_2017-10-25_093025 | 2017-10-25 05:30 | 2017-10-25 05:30 | EDT | 2017-10-25 09:30 | -1 | 59.983 | 60.012 | 60.018 | 0.029 | 0.035 | -3.4483 | -2.8571 | No | No | 59.5 | 0.518 | 2017
EI_2017-10-26_061255 | 2017-10-26 02:13 | 2017-10-26 02:13 | EDT | 2017-10-26 06:13 | 1010 | 60.019 | 59.959 | 59.954 | -0.06 | -0.065 | -1683.3333 | -1553.8462 | Yes | Yes | 59.5 | 0.454 | 2017
EI_2017-10-27_042343 | 2017-10-27 00:24 | 2017-10-27 00:24 | EDT | 2017-10-27 04:24 |  | 60.009 | 59.971 | 59.975 | -0.038 | -0.034 |  |  | No | No | 59.5 | 0.475 | 2017
EI_2017-10-27_201743 | 2017-10-27 16:18 | 2017-10-27 16:18 | EDT | 2017-10-27 20:18 |  | 60.008 | 59.967 | 59.968 | -0.041 | -0.04 |  |  | No | No | 59.5 | 0.468 | 2017
EI_2017-10-30_171147 | 2017-10-30 13:12 | 2017-10-30 13:12 | EDT | 2017-10-30 17:12 | 551 | 60.006 | 59.967 | 59.961 | -0.039 | -0.045 | -1412.8205 | -1224.4444 | Yes | No | 59.5 | 0.461 | 2017
EI_2017-10-31_195217 | 2017-10-31 15:52 | 2017-10-31 15:52 | EDT | 2017-10-31 19:52 |  | 59.997 | 59.96 | 59.958 | -0.037 | -0.039 |  |  | No | No | 59.5 | 0.458 | 2017
EI_2017-11-01_153800 | 2017-11-01 11:38 | 2017-11-01 11:38 | EDT | 2017-11-01 15:38 | 765 | 60 | 59.987 | 59.984 | -0.013 | -0.016 | -5884.6154 | -4781.25 | No | No | 59.5 | 0.484 | 2017
EI_2017-11-04_002149 | 2017-11-03 20:22 | 2017-11-03 20:22 | EDT | 2017-11-04 00:22 | 1050 | 60.024 | 59.971 | 59.964 | -0.053 | -0.06 | -1981.1321 | -1750 | Yes | No | 59.5 | 0.464 | 2017
EI_2017-11-04_064922 | 2017-11-04 02:49 | 2017-11-04 02:49 | EDT | 2017-11-04 06:49 |  | 60.018 | 59.983 | 59.98 | -0.035 | -0.038 |  |  | No | No | 59.5 | 0.48 | 2017
EI_2017-11-07_060719 | 2017-11-07 01:07 | 2017-11-07 01:07 | EST | 2017-11-07 06:07 | 650 | 60.004 | 59.964 | 59.959 | -0.04 | -0.045 | -1625 | -1444.4444 | Yes | Yes | 59.5 | 0.459 | 2017
EI_2017-11-07_071455 | 2017-11-07 02:15 | 2017-11-07 02:15 | EST | 2017-11-07 07:15 | 522 | 59.991 | 59.955 | 59.952 | -0.036 | -0.039 | -1450 | -1338.4615 | Yes | No | 59.5 | 0.452 | 2017
EI_2017-11-07_100400 | 2017-11-07 05:04 | 2017-11-07 05:04 | EST | 2017-11-07 10:04 | 943 | 59.991 | 59.964 | 59.952 | -0.027 | -0.039 | -3492.5926 | -2417.9487 | Yes | No | 59.5 | 0.452 | 2017
EI_2017-11-07_172823 | 2017-11-07 12:28 | 2017-11-07 12:28 | EST | 2017-11-07 17:28 | 1120 | 60.009 | 59.96 | 59.956 | -0.049 | -0.053 | -2285.7143 | -2113.2075 | Yes | Yes | 59.5 | 0.456 | 2017
EI_2017-11-08_005643 | 2017-11-07 19:57 | 2017-11-07 19:57 | EST | 2017-11-08 00:57 | 989 | 59.998 | 59.958 | 59.949 | -0.04 | -0.049 | -2472.5 | -2018.3673 | Yes | Yes | 59.5 | 0.449 | 2017
EI_2017-11-08_085334 | 2017-11-08 03:54 | 2017-11-08 03:54 | EST | 2017-11-08 08:54 | 511 | 60.014 | 59.965 | 59.972 | -0.049 | -0.042 | -1042.8571 | -1216.6667 | Yes | No | 59.5 | 0.472 | 2017
EI_2017-11-09_061324 | 2017-11-09 01:13 | 2017-11-09 01:13 | EST | 2017-11-09 06:13 |  | 60.029 | 59.982 | 59.989 | -0.047 | -0.04 |  |  | No | No | 59.5 | 0.489 | 2017
EI_2017-11-11_172902 | 2017-11-11 12:29 | 2017-11-11 12:29 | EST | 2017-11-11 17:29 |  | 60.017 | 59.982 | 59.976 | -0.035 | -0.041 |  |  | No | No | 59.5 | 0.476 | 2017
EI_2017-11-13_111329 | 2017-11-13 06:13 | 2017-11-13 06:13 | EST | 2017-11-13 11:13 | 604 | 59.981 | 59.957 | 59.955 | -0.024 | -0.026 | -2516.6667 | -2323.0769 | No | No | 59.5 | 0.455 | 2017
EI_2017-11-15_064631 | 2017-11-15 01:47 | 2017-11-15 01:47 | EST | 2017-11-15 06:47 | 866 | 60.01 | 59.975 | 59.969 | -0.035 | -0.041 | -2474.2857 | -2112.1951 | Yes | No | 59.5 | 0.469 | 2017
EI_2017-11-17_095959 | 2017-11-17 05:00 | 2017-11-17 05:00 | EST | 2017-11-17 10:00 | -1 | 60.013 | 60.042 | 60.052 | 0.029 | 0.039 | -3.4483 | -2.5641 | No | No | 59.5 | 0.552 | 2017
EI_2017-11-20_211215 | 2017-11-20 16:12 | 2017-11-20 16:12 | EST | 2017-11-20 21:12 | 852 | 59.998 | 59.951 | 59.946 | -0.047 | -0.052 | -1812.766 | -1638.4615 | Yes | Yes | 59.5 | 0.446 | 2017
EI_2017-12-01_181024 | 2017-12-01 13:10 | 2017-12-01 13:10 | EST | 2017-12-01 18:10 | 582 | 60.001 | 59.95 | 59.955 | -0.051 | -0.046 | -1141.1765 | -1265.2174 | Yes | No | 59.5 | 0.455 | 2018
EI_2017-12-02_060843 | 2017-12-02 01:09 | 2017-12-02 01:09 | EST | 2017-12-02 06:09 |  | 60.01 | 59.965 | 59.973 | -0.045 | -0.037 |  |  | No | No | 59.5 | 0.473 | 2018
EI_2017-12-03_034348 | 2017-12-02 22:44 | 2017-12-02 22:44 | EST | 2017-12-03 03:44 | 486 | 60.008 | 59.973 | 59.963 | -0.035 | -0.045 | -1388.5714 | -1080 | Yes | No | 59.5 | 0.463 | 2018
EI_2017-12-05_221852 | 2017-12-05 17:19 | 2017-12-05 17:19 | EST | 2017-12-05 22:19 | 648 | 59.996 | 59.957 | 59.954 | -0.039 | -0.042 | -1661.5385 | -1542.8571 | Yes | Yes | 59.5 | 0.454 | 2018
EI_2017-12-06_154423 | 2017-12-06 10:44 | 2017-12-06 10:44 | EST | 2017-12-06 15:44 | 514 | 60.016 | 59.98 | 59.977 | -0.036 | -0.039 | -1427.7778 | -1317.9487 | Yes | No | 59.5 | 0.477 | 2018
EI_2017-12-06_232712 | 2017-12-06 18:27 | 2017-12-06 18:27 | EST | 2017-12-06 23:27 | 895 | 60.006 | 59.958 | 59.959 | -0.048 | -0.047 | -1864.5833 | -1904.2553 | Yes | Yes | 59.5 | 0.459 | 2018
EI_2017-12-09_041703 | 2017-12-08 23:17 | 2017-12-08 23:17 | EST | 2017-12-09 04:17 |  | 59.993 | 59.969 | 59.954 | -0.024 | -0.039 |  |  | No | No | 59.5 | 0.454 | 2018
EI_2017-12-11_135857 | 2017-12-11 08:59 | 2017-12-11 08:59 | EST | 2017-12-11 13:59 | 1150 | 60.015 | 59.963 | 59.958 | -0.052 | -0.057 | -2211.5385 | -2017.5439 | Yes | Yes | 59.5 | 0.458 | 2018
EI_2017-12-16_135830 | 2017-12-16 08:58 | 2017-12-16 08:58 | EST | 2017-12-16 13:58 |  | 60.01 | 59.975 | 59.974 | -0.035 | -0.036 |  |  | No | No | 59.5 | 0.474 | 2018
EI_2017-12-16_142317 | 2017-12-16 09:23 | 2017-12-16 09:23 | EST | 2017-12-16 14:23 | 601.3 | 60.014 | 59.966 | 59.973 | -0.048 | -0.041 | -1252.7083 | -1466.5854 | Yes | No | 59.5 | 0.473 | 2018
EI_2017-12-21_225255 | 2017-12-21 17:53 | 2017-12-21 17:53 | EST | 2017-12-21 22:53 | 425.1 | 59.985 | 59.962 | 59.957 | -0.023 | -0.028 | -1848.2609 | -1518.2143 | No | No | 59.5 | 0.457 | 2018
EI_2017-12-24_054039 | 2017-12-24 00:41 | 2017-12-24 00:41 | EST | 2017-12-24 05:41 |  | 60.006 | 59.973 | 59.974 | -0.033 | -0.032 |  |  | No | No | 59.5 | 0.474 | 2018
EI_2017-12-27_033405 | 2017-12-26 22:34 | 2017-12-26 22:34 | EST | 2017-12-27 03:34 | 930 | 60.011 | 59.963 | 59.962 | -0.048 | -0.049 | -1937.5 | -1897.9592 | Yes | No | 59.5 | 0.462 | 2018
EI_2017-12-28_190457 | 2017-12-28 14:05 | 2017-12-28 14:05 | EST | 2017-12-28 19:05 |  | 60.007 | 59.974 | 59.967 | -0.033 | -0.04 |  |  | No | No | 59.5 | 0.467 | 2018
EI_2017-12-29_001444 | 2017-12-28 19:15 | 2017-12-28 19:15 | EST | 2017-12-29 00:15 |  | 59.998 | 59.972 | 59.962 | -0.026 | -0.036 |  |  | No | No | 59.5 | 0.462 | 2018
EI_2018-01-01_054542 | 2018-01-01 00:46 | 2018-01-01 00:46 | EST | 2018-01-01 05:46 | 540 | 60.014 | 59.967 | 59.976 | -0.047 | -0.038 | -1148.9362 | -1421.0526 | Yes | No | 59.5 | 0.476 | 2018
EI_2018-01-01_073852 | 2018-01-01 02:39 | 2018-01-01 02:39 | EST | 2018-01-01 07:39 | 642 | 59.988 | 59.954 | 59.952 | -0.034 | -0.036 | -1888.2353 | -1783.3333 | No | No | 59.5 | 0.452 | 2018
EI_2018-01-01_233423 | 2018-01-01 18:34 | 2018-01-01 18:34 | EST | 2018-01-01 23:34 | 1234 | 59.992 | 59.958 | 59.955 | -0.034 | -0.037 | -3629.4118 | -3335.1351 | Yes | No | 59.5 | 0.455 | 2018
EI_2018-01-03_075940 | 2018-01-03 03:00 | 2018-01-03 03:00 | EST | 2018-01-03 08:00 | 1350 | 59.997 | 59.941 | 59.943 | -0.056 | -0.054 | -2410.7143 | -2500 | Yes | Yes | 59.5 | 0.443 | 2018
EI_2018-01-07_114239 | 2018-01-07 06:43 | 2018-01-07 06:43 | EST | 2018-01-07 11:43 | 965 | 60.009 | 59.961 | 59.965 | -0.048 | -0.044 | -2010.4167 | -2193.1818 | Yes | No | 59.5 | 0.465 | 2018
EI_2018-01-09_100404 | 2018-01-09 05:04 | 2018-01-09 05:04 | EST | 2018-01-09 10:04 | -1 | 59.989 | 60.032 | 60.032 | 0.043 | 0.043 | -2.3256 | -2.3256 | No | No | 59.5 | 0.532 | 2018
EI_2018-01-10_100035 | 2018-01-10 05:01 | 2018-01-10 05:01 | EST | 2018-01-10 10:01 | -1 | 60.002 | 60.038 | 60.043 | 0.036 | 0.041 | -2.7778 | -2.439 | No | No | 59.5 | 0.543 | 2018
EI_2018-01-11_111432 | 2018-01-11 06:15 | 2018-01-11 06:15 | EST | 2018-01-11 11:15 | -1 | 59.981 | 60.027 | 60.017 | 0.046 | 0.036 | -2.1739 | -2.7778 | No | No | 59.5 | 0.517 | 2018
EI_2018-01-11_114511 | 2018-01-11 06:45 | 2018-01-11 06:45 | EST | 2018-01-11 11:45 | -1 | 59.984 | 60.023 | 60.022 | 0.039 | 0.038 | -2.5641 | -2.6316 | No | No | 59.5 | 0.522 | 2018
EI_2018-01-12_215310 | 2018-01-12 16:53 | 2018-01-12 16:53 | EST | 2018-01-12 21:53 | 640 | 59.998 | 59.97 | 59.962 | -0.028 | -0.036 | -2285.7143 | -1777.7778 | No | No | 59.5 | 0.462 | 2018
EI_2018-01-16_044958 | 2018-01-15 23:50 | 2018-01-15 23:50 | EST | 2018-01-16 04:50 | 561 | 60.017 | 59.983 | 59.981 | -0.034 | -0.036 | -1650 | -1558.3333 | Yes | No | 59.5 | 0.481 | 2018
EI_2018-01-19_204638 | 2018-01-19 15:47 | 2018-01-19 15:47 | EST | 2018-01-19 20:47 | 1000 | 59.985 | 59.96 | 59.954 | -0.025 | -0.031 | -4000 | -3225.8065 | Yes | No | 59.5 | 0.454 | 2018
EI_2018-01-21_220009 | 2018-01-21 17:00 | 2018-01-21 17:00 | EST | 2018-01-21 22:00 | -1 | 59.991 | 60.036 | 60.031 | 0.045 | 0.04 | -2.2222 | -2.5 | No | No | 59.5 | 0.531 | 2018
EI_2018-01-24_095458 | 2018-01-24 04:55 | 2018-01-24 04:55 | EST | 2018-01-24 09:55 | 549 | 59.989 | 59.969 | 59.956 | -0.02 | -0.033 | -2745 | -1663.6364 | No | No | 59.5 | 0.456 | 2018
EI_2018-01-25_024748 | 2018-01-24 21:48 | 2018-01-24 21:48 | EST | 2018-01-25 02:48 | 370 | 60.006 | 59.97 | 59.992 | -0.036 | -0.014 | -1027.7778 | -2642.8571 | No | No | 59.5 | 0.492 | 2018
EI_2018-01-27_211741 | 2018-01-27 16:18 | 2018-01-27 16:18 | EST | 2018-01-27 21:18 | 845 | 59.992 | 59.948 | 59.946 | -0.044 | -0.046 | -1920.4545 | -1836.9565 | Yes | Yes | 59.5 | 0.446 | 2018
EI_2018-01-31_002243 | 2018-01-30 19:23 | 2018-01-30 19:23 | EST | 2018-01-31 00:23 | 1293.5 | 60.006 | 59.953 | 59.965 | -0.053 | -0.041 | -2440.566 | -3154.878 | Yes | No | 59.5 | 0.465 | 2018
EI_2018-02-03_133519 | 2018-02-03 08:35 | 2018-02-03 08:35 | EST | 2018-02-03 13:35 | 1302 | 60.003 | 59.951 | 59.953 | -0.052 | -0.05 | -2503.8462 | -2604 | Yes | Yes | 59.5 | 0.453 | 2018
EI_2018-02-05_003808 | 2018-02-04 19:38 | 2018-02-04 19:38 | EST | 2018-02-05 00:38 |  | 60.051 | 59.986 | 60.015 | -0.065 | -0.036 |  |  | No | No | 59.5 | 0.515 | 2018
EI_2018-02-10_090947 | 2018-02-10 04:10 | 2018-02-10 04:10 | EST | 2018-02-10 09:10 | 800 | 60.014 | 59.978 | 59.977 | -0.036 | -0.037 | -2222.2222 | -2162.1622 | Yes | No | 59.5 | 0.477 | 2018
EI_2018-02-16_032945 | 2018-02-15 22:30 | 2018-02-15 22:30 | EST | 2018-02-16 03:30 |  | 60.019 | 59.986 | 59.984 | -0.033 | -0.035 |  |  | No | No | 59.5 | 0.484 | 2018
EI_2018-02-16_070125 | 2018-02-16 02:01 | 2018-02-16 02:01 | EST | 2018-02-16 07:01 | 1000 | 59.995 | 59.956 | 59.95 | -0.039 | -0.045 | -2564.1026 | -2222.2222 | Yes | No | 59.5 | 0.45 | 2018
EI_2018-02-16_151421 | 2018-02-16 10:14 | 2018-02-16 10:14 | EST | 2018-02-16 15:14 | 1237 | 59.996 | 59.946 | 59.941 | -0.05 | -0.055 | -2474 | -2249.0909 | Yes | Yes | 59.5 | 0.441 | 2018
EI_2018-02-21_001740 | 2018-02-20 19:18 | 2018-02-20 19:18 | EST | 2018-02-21 00:18 | 636 | 59.998 | 59.964 | 59.947 | -0.034 | -0.051 | -1870.5882 | -1247.0588 | Yes | Yes | 59.5 | 0.447 | 2018
EI_2018-02-22_100019 | 2018-02-22 05:00 | 2018-02-22 05:00 | EST | 2018-02-22 10:00 |  | 60.013 | 59.965 | 59.968 | -0.048 | -0.045 |  |  | No | No | 59.5 | 0.468 | 2018
EI_2018-02-24_231359 | 2018-02-24 18:14 | 2018-02-24 18:14 | EST | 2018-02-24 23:14 | 561.8 | 60.005 | 59.966 | 59.959 | -0.039 | -0.046 | -1440.5128 | -1221.3043 | Yes | No | 59.5 | 0.459 | 2018
EI_2018-02-25_035459 | 2018-02-24 22:55 | 2018-02-24 22:55 | EST | 2018-02-25 03:55 |  | 60.012 | 59.974 | 59.972 | -0.038 | -0.04 |  |  | No | No | 59.5 | 0.472 | 2018
EI_2018-03-03_091159 | 2018-03-03 04:12 | 2018-03-03 04:12 | EST | 2018-03-03 09:12 | -1 | 59.988 | 60.007 | 60.029 | 0.019 | 0.041 | -5.2632 | -2.439 | No | No | 59.5 | 0.529 | 2018
EI_2018-03-03_094230 | 2018-03-03 04:42 | 2018-03-03 04:42 | EST | 2018-03-03 09:42 | -1 | 59.984 | 60.031 | 60.028 | 0.047 | 0.044 | -2.1277 | -2.2727 | No | No | 59.5 | 0.528 | 2018
EI_2018-03-03_095415 | 2018-03-03 04:54 | 2018-03-03 04:54 | EST | 2018-03-03 09:54 | -1 | 59.976 | 60.019 | 60.013 | 0.043 | 0.037 | -2.3256 | -2.7027 | No | No | 59.5 | 0.513 | 2018
EI_2018-03-04_023857 | 2018-03-03 21:39 | 2018-03-03 21:39 | EST | 2018-03-04 02:39 |  | 60.02 | 59.974 | 59.996 | -0.046 | -0.024 |  |  | No | No | 59.5 | 0.496 | 2018
EI_2018-03-05_204126 | 2018-03-05 15:41 | 2018-03-05 15:41 | EST | 2018-03-05 20:41 | 750 | 59.998 | 59.971 | 59.959 | -0.027 | -0.039 | -2777.7778 | -1923.0769 | No | No | 59.5 | 0.459 | 2018
EI_2018-03-05_222914 | 2018-03-05 17:29 | 2018-03-05 17:29 | EST | 2018-03-05 22:29 | -1 | 59.981 | 60.019 | 60.02 | 0.038 | 0.039 | -2.6316 | -2.5641 | No | No | 59.5 | 0.52 | 2018
EI_2018-03-06_195347 | 2018-03-06 14:54 | 2018-03-06 14:54 | EST | 2018-03-06 19:54 | 677 | 59.989 | 59.967 | 59.954 | -0.022 | -0.035 | -3077.2727 | -1934.2857 | Yes | No | 59.5 | 0.454 | 2018
EI_2018-03-08_051550 | 2018-03-08 00:16 | 2018-03-08 00:16 | EST | 2018-03-08 05:16 | 1600 | 60.008 | 59.951 | 59.939 | -0.057 | -0.069 | -2807.0175 | -2318.8406 | Yes | Yes | 59.5 | 0.439 | 2018
EI_2018-03-09_085509 | 2018-03-09 03:55 | 2018-03-09 03:55 | EST | 2018-03-09 08:55 | -1 | 59.988 | 60.034 | 60.025 | 0.046 | 0.037 | -2.1739 | -2.7027 | No | No | 59.5 | 0.525 | 2018
EI_2018-03-09_174924 | 2018-03-09 12:49 | 2018-03-09 12:49 | EST | 2018-03-09 17:49 | 600 | 60.009 | 59.97 | 59.969 | -0.039 | -0.04 | -1538.4615 | -1500 | No | No | 59.5 | 0.469 | 2018
EI_2018-03-10_101024 | 2018-03-10 05:10 | 2018-03-10 05:10 | EST | 2018-03-10 10:10 | -1 | 59.981 | 60.026 | 60.021 | 0.045 | 0.04 | -2.2222 | -2.5 | No | No | 59.5 | 0.521 | 2018
EI_2018-03-12_020609 | 2018-03-11 22:06 | 2018-03-11 22:06 | EDT | 2018-03-12 02:06 |  | 60.015 | 59.956 | 59.983 | -0.059 | -0.032 |  |  | No | No | 59.5 | 0.483 | 2018
EI_2018-03-13_080001 | 2018-03-13 04:00 | 2018-03-13 04:00 | EDT | 2018-03-13 08:00 | -1 | 59.97 | 60.014 | 60.011 | 0.044 | 0.041 | -2.2727 | -2.439 | No | No | 59.5 | 0.511 | 2018
EI_2018-03-14_123810 | 2018-03-14 08:38 | 2018-03-14 08:38 | EDT | 2018-03-14 12:38 | 2006 | 59.998 | 59.952 | 59.94 | -0.046 | -0.058 | -4360.8696 | -3458.6207 | Yes | Yes | 59.5 | 0.44 | 2018
EI_2018-03-14_175958 | 2018-03-14 14:00 | 2018-03-14 14:00 | EDT | 2018-03-14 18:00 |  | 60.016 | 59.985 | 59.982 | -0.031 | -0.034 |  |  | No | No | 59.5 | 0.482 | 2018
EI_2018-03-15_174410 | 2018-03-15 13:44 | 2018-03-15 13:44 | EDT | 2018-03-15 17:44 |  | 60.005 | 59.979 | 59.969 | -0.026 | -0.036 |  |  | No | No | 59.5 | 0.469 | 2018
EI_2018-03-16_083001 | 2018-03-16 04:30 | 2018-03-16 04:30 | EDT | 2018-03-16 08:30 | -1 | 59.979 | 60.027 | 60.026 | 0.048 | 0.047 | -2.0833 | -2.1277 | No | No | 59.5 | 0.526 | 2018
EI_2018-03-17_160842 | 2018-03-17 12:09 | 2018-03-17 12:09 | EDT | 2018-03-17 16:09 | 661 | 60.025 | 59.972 | 59.981 | -0.053 | -0.044 | -1247.1698 | -1502.2727 | No | No | 59.5 | 0.481 | 2018
EI_2018-03-18_025224 | 2018-03-17 22:52 | 2018-03-17 22:52 | EDT | 2018-03-18 02:52 |  | 60.015 | 59.971 | 60.01 | -0.044 | -0.005 |  |  | No | No | 59.5 | 0.51 | 2018
EI_2018-03-18_165910 | 2018-03-18 12:59 | 2018-03-18 12:59 | EDT | 2018-03-18 16:59 | 1105 | 59.992 | 59.946 | 59.947 | -0.046 | -0.045 | -2402.1739 | -2455.5556 | Yes | Yes | 59.5 | 0.447 | 2018
EI_2018-03-18_215510 | 2018-03-18 17:55 | 2018-03-18 17:55 | EDT | 2018-03-18 21:55 | -1 | 59.995 | 60.024 | 60.031 | 0.029 | 0.036 | -3.4483 | -2.7778 | No | No | 59.5 | 0.531 | 2018
EI_2018-03-19_073115 | 2018-03-19 03:31 | 2018-03-19 03:31 | EDT | 2018-03-19 07:31 | -1 | 59.989 | 60.022 | 60.024 | 0.033 | 0.035 | -3.0303 | -2.8571 | No | No | 59.5 | 0.524 | 2018
EI_2018-03-20_162001 | 2018-03-20 12:20 | 2018-03-20 12:20 | EDT | 2018-03-20 16:20 |  | 60.01 | 59.974 | 59.972 | -0.036 | -0.038 |  |  | No | No | 59.5 | 0.472 | 2018
EI_2018-03-24_191301 | 2018-03-24 15:13 | 2018-03-24 15:13 | EDT | 2018-03-24 19:13 |  | 60.006 | 59.979 | 59.986 | -0.027 | -0.02 |  |  | No | No | 59.5 | 0.486 | 2018
EI_2018-03-30_005953 | 2018-03-29 21:00 | 2018-03-29 21:00 | EDT | 2018-03-30 01:00 |  | 60.003 | 59.967 | 59.959 | -0.036 | -0.044 |  |  | No | No | 59.5 | 0.459 | 2018
EI_2018-03-30_090000 | 2018-03-30 05:00 | 2018-03-30 05:00 | EDT | 2018-03-30 09:00 | -1 | 59.984 | 60.01 | 60.017 | 0.026 | 0.033 | -3.8462 | -3.0303 | No | No | 59.5 | 0.517 | 2018
EI_2018-03-31_181228 | 2018-03-31 14:12 | 2018-03-31 14:12 | EDT | 2018-03-31 18:12 | 660 | 60.005 | 59.963 | 59.966 | -0.042 | -0.039 | -1571.4286 | -1692.3077 | Yes | No | 59.5 | 0.466 | 2018
EI_2018-03-31_220103 | 2018-03-31 18:01 | 2018-03-31 18:01 | EDT | 2018-03-31 22:01 | -1 | 59.979 | 60.045 | 60.023 | 0.066 | 0.044 | -1.5152 | -2.2727 | No | No | 59.5 | 0.523 | 2018
EI_2018-04-01_234321 | 2018-04-01 19:43 | 2018-04-01 19:43 | EDT | 2018-04-01 23:43 | 607 | 60.003 | 59.962 | 59.959 | -0.041 | -0.044 | -1480.4878 | -1379.5455 | Yes | No | 59.5 | 0.459 | 2018
EI_2018-04-02_192113 | 2018-04-02 15:21 | 2018-04-02 15:21 | EDT | 2018-04-02 19:21 | 1350 | 59.965 | 59.949 | 59.93 | -0.016 | -0.035 | -8437.5 | -3857.1429 | Yes | No | 59.5 | 0.43 | 2018
EI_2018-04-04_025416 | 2018-04-03 22:54 | 2018-04-03 22:54 | EDT | 2018-04-04 02:54 | 1019.8 | 60.01 | 59.96 | 59.966 | -0.05 | -0.044 | -2039.6 | -2317.7273 | Yes | No | 59.5 | 0.466 | 2018
EI_2018-04-05_095455 | 2018-04-05 05:55 | 2018-04-05 05:55 | EDT | 2018-04-05 09:55 | 850 | 60.012 | 59.982 | 59.972 | -0.03 | -0.04 | -2833.3333 | -2125 | Yes | No | 59.5 | 0.472 | 2018
EI_2018-04-07_082752 | 2018-04-07 04:28 | 2018-04-07 04:28 | EDT | 2018-04-07 08:28 |  | 60.015 | 59.991 | 59.98 | -0.024 | -0.035 |  |  | No | No | 59.5 | 0.48 | 2018
EI_2018-04-07_123600 | 2018-04-07 08:36 | 2018-04-07 08:36 | EDT | 2018-04-07 12:36 | 987 | 60.007 | 59.951 | 59.953 | -0.056 | -0.054 | -1762.5 | -1827.7778 | Yes | Yes | 59.5 | 0.453 | 2018
EI_2018-04-12_132224 | 2018-04-12 09:22 | 2018-04-12 09:22 | EDT | 2018-04-12 13:22 | 1199 | 59.985 | 59.953 | 59.938 | -0.032 | -0.047 | -3746.875 | -2551.0638 | Yes | No | 59.5 | 0.438 | 2018
EI_2018-04-12_172613 | 2018-04-12 13:26 | 2018-04-12 13:26 | EDT | 2018-04-12 17:26 | 1250 | 59.975 | 59.944 | 59.933 | -0.031 | -0.042 | -4032.2581 | -2976.1905 | Yes | Yes | 59.5 | 0.433 | 2018
EI_2018-04-13_031358 | 2018-04-12 23:14 | 2018-04-12 23:14 | EDT | 2018-04-13 03:14 | 1045 | 59.983 | 59.952 | 59.945 | -0.031 | -0.038 | -3370.9677 | -2750 | Yes | No | 59.5 | 0.445 | 2018
EI_2018-04-13_035021 | 2018-04-12 23:50 | 2018-04-12 23:50 | EDT | 2018-04-13 03:50 | 900 | 60.013 | 59.98 | 59.955 | -0.033 | -0.058 | -2727.2727 | -1551.7241 | No | No | 59.5 | 0.455 | 2018
EI_2018-04-13_035109 | 2018-04-12 23:51 | 2018-04-12 23:51 | EDT | 2018-04-13 03:51 | 900 | 59.988 | 59.956 | 59.946 | -0.032 | -0.042 | -2812.5 | -2142.8571 | No | No | 59.5 | 0.446 | 2018
EI_2018-04-14_085415 | 2018-04-14 04:54 | 2018-04-14 04:54 | EDT | 2018-04-14 08:54 | 503 | 60.003 | 59.956 | 59.955 | -0.047 | -0.048 | -1070.2128 | -1047.9167 | No | No | 59.5 | 0.455 | 2018
EI_2018-04-15_040623 | 2018-04-15 00:06 | 2018-04-15 00:06 | EDT | 2018-04-15 04:06 |  | 60.013 | 59.966 | 59.972 | -0.047 | -0.041 |  |  | No | No | 59.5 | 0.472 | 2018
EI_2018-04-18_190931 | 2018-04-18 15:10 | 2018-04-18 15:10 | EDT | 2018-04-18 19:10 | 900 | 60.009 | 59.96 | 59.962 | -0.049 | -0.047 | -1836.7347 | -1914.8936 | Yes | No | 59.5 | 0.462 | 2018
EI_2018-04-22_021458 | 2018-04-21 22:15 | 2018-04-21 22:15 | EDT | 2018-04-22 02:15 |  | 60.027 | 59.983 | 59.989 | -0.044 | -0.038 |  |  | No | No | 59.5 | 0.489 | 2018
EI_2018-04-24_111855 | 2018-04-24 07:19 | 2018-04-24 07:19 | EDT | 2018-04-24 11:19 | 700 | 59.978 | 59.954 | 59.946 | -0.024 | -0.032 | -2916.6667 | -2187.5 | No | No | 59.5 | 0.446 | 2018
EI_2018-04-29_103700 | 2018-04-29 06:37 | 2018-04-29 06:37 | EDT | 2018-04-29 10:37 | -1 | 59.993 | 60.03 | 60.039 | 0.037 | 0.046 | -2.7027 | -2.1739 | No | No | 59.5 | 0.539 | 2018
EI_2018-04-30_162320 | 2018-04-30 12:23 | 2018-04-30 12:23 | EDT | 2018-04-30 16:23 | 600 | 60.014 | 59.982 | 59.974 | -0.032 | -0.04 | -1875 | -1500 | No | No | 59.5 | 0.474 | 2018
EI_2018-05-01_091620 | 2018-05-01 05:16 | 2018-05-01 05:16 | EDT | 2018-05-01 09:16 | -1 | 59.986 | 60.026 | 60.028 | 0.04 | 0.042 | -2.5 | -2.381 | No | No | 59.5 | 0.528 | 2018
EI_2018-05-02_140954 | 2018-05-02 10:10 | 2018-05-02 10:10 | EDT | 2018-05-02 14:10 | -1 | 59.99 | 60.02 | 60.02 | 0.03 | 0.03 | -3.3333 | -3.3333 | No | No | 59.5 | 0.52 | 2018
EI_2018-05-03_122951 | 2018-05-03 08:30 | 2018-05-03 08:30 | EDT | 2018-05-03 12:30 | 850 | 60.013 | 59.964 | 59.96 | -0.049 | -0.053 | -1734.6939 | -1603.7736 | Yes | No | 59.5 | 0.46 | 2018
EI_2018-05-04_040156 | 2018-05-04 00:02 | 2018-05-04 00:02 | EDT | 2018-05-04 04:02 |  | 60.017 | 59.971 | 59.997 | -0.046 | -0.02 |  |  | No | No | 59.5 | 0.497 | 2018
EI_2018-05-06_044356 | 2018-05-06 00:44 | 2018-05-06 00:44 | EDT | 2018-05-06 04:44 | -1 | 59.988 | 60.032 | 60.022 | 0.044 | 0.034 | -2.2727 | -2.9412 | No | No | 59.5 | 0.522 | 2018
EI_2018-05-06_060038 | 2018-05-06 02:01 | 2018-05-06 02:01 | EDT | 2018-05-06 06:01 | 341 | 60.02 | 59.98 | 59.984 | -0.04 | -0.036 | -852.5 | -947.2222 | No | No | 59.5 | 0.484 | 2018
EI_2018-05-06_091412 | 2018-05-06 05:14 | 2018-05-06 05:14 | EDT | 2018-05-06 09:14 | -1 | 59.986 | 60.033 | 60.022 | 0.047 | 0.036 | -2.1277 | -2.7778 | No | No | 59.5 | 0.522 | 2018
EI_2018-05-06_120256 | 2018-05-06 08:03 | 2018-05-06 08:03 | EDT | 2018-05-06 12:03 | -1 | 59.99 | 60.03 | 60.032 | 0.04 | 0.042 | -2.5 | -2.381 | No | No | 59.5 | 0.532 | 2018
EI_2018-05-07_072557 | 2018-05-07 03:26 | 2018-05-07 03:26 | EDT | 2018-05-07 07:26 | 1090 | 59.975 | 59.947 | 59.933 | -0.028 | -0.042 | -3892.8571 | -2595.2381 | Yes | No | 59.5 | 0.433 | 2018
EI_2018-05-07_103224 | 2018-05-07 06:32 | 2018-05-07 06:32 | EDT | 2018-05-07 10:32 | -1 | 59.96 | 60.021 | 60 | 0.061 | 0.04 | -1.6393 | -2.5 | No | No | 59.5 | 0.5 | 2018
EI_2018-05-07_213927 | 2018-05-07 17:39 | 2018-05-07 17:39 | EDT | 2018-05-07 21:39 | 769 | 59.998 | 59.963 | 59.961 | -0.035 | -0.037 | -2197.1429 | -2078.3784 | Yes | No | 59.5 | 0.461 | 2018
EI_2018-05-09_150148 | 2018-05-09 11:02 | 2018-05-09 11:02 | EDT | 2018-05-09 15:02 | -1 | 59.973 | 60.019 | 60.009 | 0.046 | 0.036 | -2.1739 | -2.7778 | No | No | 59.5 | 0.509 | 2018
EI_2018-05-10_093509 | 2018-05-10 05:35 | 2018-05-10 05:35 | EDT | 2018-05-10 09:35 | -1 | 59.978 | 60.034 | 60.014 | 0.056 | 0.036 | -1.7857 | -2.7778 | No | No | 59.5 | 0.514 | 2018
EI_2018-05-11_135111 | 2018-05-11 09:51 | 2018-05-11 09:51 | EDT | 2018-05-11 13:51 | -1 | 59.981 | 60.012 | 60.016 | 0.031 | 0.035 | -3.2258 | -2.8571 | No | No | 59.5 | 0.516 | 2018
EI_2018-05-14_220501 | 2018-05-14 18:05 | 2018-05-14 18:05 | EDT | 2018-05-14 22:05 |  | 60.006 | 59.971 | 59.973 | -0.035 | -0.033 |  |  | No | No | 59.5 | 0.473 | 2018
EI_2018-05-18_115103 | 2018-05-18 07:51 | 2018-05-18 07:51 | EDT | 2018-05-18 11:51 | -1 | 59.995 | 60.031 | 60.035 | 0.036 | 0.04 | -2.7778 | -2.5 | No | No | 59.5 | 0.535 | 2018
EI_2018-05-18_170652 | 2018-05-18 13:07 | 2018-05-18 13:07 | EDT | 2018-05-18 17:07 | 1490 | 60.007 | 59.959 | 59.973 | -0.048 | -0.034 | -3104.1667 | -4382.3529 | No | No | 59.5 | 0.473 | 2018
EI_2018-05-19_070903 | 2018-05-19 03:09 | 2018-05-19 03:09 | EDT | 2018-05-19 07:09 | -1 | 59.986 | 60.026 | 60.016 | 0.04 | 0.03 | -2.5 | -3.3333 | No | No | 59.5 | 0.516 | 2018
EI_2018-05-19_110322 | 2018-05-19 07:03 | 2018-05-19 07:03 | EDT | 2018-05-19 11:03 | -1 | 59.985 | 60.031 | 60.016 | 0.046 | 0.031 | -2.1739 | -3.2258 | No | No | 59.5 | 0.516 | 2018
EI_2018-05-19_121930 | 2018-05-19 08:20 | 2018-05-19 08:20 | EDT | 2018-05-19 12:20 | -1 | 59.981 | 60.033 | 60 | 0.052 | 0.019 | -1.9231 | -5.2632 | No | No | 59.5 | 0.5 | 2018
EI_2018-05-19_131533 | 2018-05-19 09:16 | 2018-05-19 09:16 | EDT | 2018-05-19 13:16 | -1 | 59.99 | 60.026 | 60.028 | 0.036 | 0.038 | -2.7778 | -2.6316 | No | No | 59.5 | 0.528 | 2018
EI_2018-05-22_174318 | 2018-05-22 13:43 | 2018-05-22 13:43 | EDT | 2018-05-22 17:43 | 757 | 60.001 | 59.972 | 59.971 | -0.029 | -0.03 | -2610.3448 | -2523.3333 | No | No | 59.5 | 0.471 | 2018
EI_2018-05-23_141050 | 2018-05-23 10:11 | 2018-05-23 10:11 | EDT | 2018-05-23 14:11 | -1 | 59.984 | 60.023 | 60.012 | 0.039 | 0.028 | -2.5641 | -3.5714 | No | No | 59.5 | 0.512 | 2018
EI_2018-05-26_032608 | 2018-05-25 23:26 | 2018-05-25 23:26 | EDT | 2018-05-26 03:26 |  | 60.015 | 59.962 | 59.978 | -0.053 | -0.037 |  |  | No | No | 59.5 | 0.478 | 2018
EI_2018-05-29_014658 | 2018-05-28 21:47 | 2018-05-28 21:47 | EDT | 2018-05-29 01:47 |  | 60.011 | 59.978 | 59.976 | -0.033 | -0.035 |  |  | No | No | 59.5 | 0.476 | 2018
EI_2018-05-30_035227 | 2018-05-29 23:52 | 2018-05-29 23:52 | EDT | 2018-05-30 03:52 | 669 | 60.024 | 59.973 | 59.978 | -0.051 | -0.046 | -1311.7647 | -1454.3478 | No | No | 59.5 | 0.478 | 2018
EI_2018-06-03_045157 | 2018-06-03 00:52 | 2018-06-03 00:52 | EDT | 2018-06-03 04:52 | 810 | 60.022 | 59.994 | 59.995 | -0.028 | -0.027 | -2892.8571 | -3000 | Yes | No | 59.5 | 0.495 | 2018
EI_2018-06-03_132256 | 2018-06-03 09:23 | 2018-06-03 09:23 | EDT | 2018-06-03 13:23 | -1 | 59.989 | 60.029 | 60.008 | 0.04 | 0.019 | -2.5 | -5.2632 | No | No | 59.5 | 0.508 | 2018
EI_2018-06-04_141959 | 2018-06-04 10:20 | 2018-06-04 10:20 | EDT | 2018-06-04 14:20 | 1210 | 59.992 | 59.959 | 59.957 | -0.033 | -0.035 | -3666.6667 | -3457.1429 | Yes | No | 59.5 | 0.457 | 2018
EI_2018-06-05_094344 | 2018-06-05 05:44 | 2018-06-05 05:44 | EDT | 2018-06-05 09:44 | -1 | 59.99 | 60.021 | 60.034 | 0.031 | 0.044 | -3.2258 | -2.2727 | No | No | 59.5 | 0.534 | 2018
EI_2018-06-05_162000 | 2018-06-05 12:20 | 2018-06-05 12:20 | EDT | 2018-06-05 16:20 | 1027 | 59.977 | 59.95 | 59.944 | -0.027 | -0.033 | -3803.7037 | -3112.1212 | Yes | No | 59.5 | 0.444 | 2018
EI_2018-06-06_051932 | 2018-06-06 01:20 | 2018-06-06 01:20 | EDT | 2018-06-06 05:20 | 0 | 60.015 | 59.978 | 59.98 | -0.037 | -0.035 |  |  | No | No | 59.5 | 0.48 | 2018
EI_2018-06-12_193926 | 2018-06-12 15:39 | 2018-06-12 15:39 | EDT | 2018-06-12 19:39 | 1074 | 59.977 | 59.943 | 59.937 | -0.034 | -0.04 | -3158.8235 | -2685 | Yes | Yes | 59.5 | 0.437 | 2018
EI_2018-06-19_202030 | 2018-06-19 16:20 | 2018-06-19 16:20 | EDT | 2018-06-19 20:20 | 0 | 60.014 | 59.974 | 59.975 | -0.04 | -0.039 |  |  | No | No | 59.5 | 0.475 | 2018
EI_2018-06-22_124120 | 2018-06-22 08:41 | 2018-06-22 08:41 | EDT | 2018-06-22 12:41 | 1077 | 59.988 | 59.954 | 59.944 | -0.034 | -0.044 | -3167.6471 | -2447.7273 | Yes | Yes | 59.5 | 0.444 | 2018
EI_2018-06-23_131119 | 2018-06-23 09:11 | 2018-06-23 09:11 | EDT | 2018-06-23 13:11 | -1 | 59.984 | 60.021 | 60.022 | 0.037 | 0.038 | -2.7027 | -2.6316 | No | No | 59.5 | 0.522 | 2018
EI_2018-06-30_134457 | 2018-06-30 09:45 | 2018-06-30 09:45 | EDT | 2018-06-30 13:45 | 1293 | 59.986 | 59.948 | 59.944 | -0.038 | -0.042 | -3402.6316 | -3078.5714 | Yes | Yes | 59.5 | 0.444 | 2018
EI_2018-07-02_130745 | 2018-07-02 09:08 | 2018-07-02 09:08 | EDT | 2018-07-02 13:08 | 582 | 60.012 | 59.981 | 59.974 | -0.031 | -0.038 | -1877.4194 | -1531.5789 | Yes | No | 59.5 | 0.474 | 2018
EI_2018-07-03_135334 | 2018-07-03 09:54 | 2018-07-03 09:54 | EDT | 2018-07-03 13:54 | 1205 | 60.018 | 59.971 | 59.974 | -0.047 | -0.044 | -2563.8298 | -2738.6364 | Yes | No | 59.5 | 0.474 | 2018
EI_2018-07-05_122420 | 2018-07-05 08:24 | 2018-07-05 08:24 | EDT | 2018-07-05 12:24 | 690 | 60.017 | 59.977 | 59.981 | -0.04 | -0.036 | -1725 | -1916.6667 | Yes | No | 59.5 | 0.481 | 2018
EI_2018-07-06_115933 | 2018-07-06 08:00 | 2018-07-06 08:00 | EDT | 2018-07-06 12:00 | -1 | 59.97 | 60.01 | 60.006 | 0.04 | 0.036 | -2.5 | -2.7778 | No | No | 59.5 | 0.506 | 2018
EI_2018-07-07_130453 | 2018-07-07 09:05 | 2018-07-07 09:05 | EDT | 2018-07-07 13:05 | -1 | 59.993 | 60.028 | 60.035 | 0.035 | 0.042 | -2.8571 | -2.381 | No | No | 59.5 | 0.535 | 2018
EI_2018-07-09_111450 | 2018-07-09 07:15 | 2018-07-09 07:15 | EDT | 2018-07-09 11:15 | -1 | 59.994 | 60.014 | 60.028 | 0.02 | 0.034 | -5 | -2.9412 | No | No | 59.5 | 0.528 | 2018
EI_2018-07-10_194634 | 2018-07-10 15:47 | 2018-07-10 15:47 | EDT | 2018-07-10 19:47 | 800 | 59.927 | 59.902 | 59.904 | -0.025 | -0.023 | -3200 | -3478.2609 | Yes | No | 59.5 | 0.404 | 2018
EI_2018-07-11_184439 | 2018-07-11 14:45 | 2018-07-11 14:45 | EDT | 2018-07-11 18:45 | 710 | 60.005 | 59.972 | 59.968 | -0.033 | -0.037 | -2151.5152 | -1918.9189 | Yes | No | 59.5 | 0.468 | 2018
EI_2018-07-17_105637 | 2018-07-17 06:57 | 2018-07-17 06:57 | EDT | 2018-07-17 10:57 | -1 | 59.991 | 60.035 | 60.028 | 0.044 | 0.037 | -2.2727 | -2.7027 | No | No | 59.5 | 0.528 | 2018
EI_2018-07-17_214140 | 2018-07-17 17:42 | 2018-07-17 17:42 | EDT | 2018-07-17 21:42 | 844 | 59.992 | 59.977 | 59.964 | -0.015 | -0.028 | -5626.6667 | -3014.2857 | No | No | 59.5 | 0.464 | 2018
EI_2018-07-23_125136 | 2018-07-23 08:52 | 2018-07-23 08:52 | EDT | 2018-07-23 12:52 | 695 | 60.017 | 59.985 | 59.981 | -0.032 | -0.036 | -2171.875 | -1930.5556 | Yes | No | 59.5 | 0.481 | 2018
EI_2018-07-24_085904 | 2018-07-24 04:59 | 2018-07-24 04:59 | EDT | 2018-07-24 08:59 | -1 | 59.984 | 60.019 | 60.02 | 0.035 | 0.036 | -2.8571 | -2.7778 | No | No | 59.5 | 0.52 | 2018
EI_2018-07-27_153316 | 2018-07-27 11:33 | 2018-07-27 11:33 | EDT | 2018-07-27 15:33 | 906 | 59.992 | 59.963 | 59.972 | -0.029 | -0.02 | -3124.1379 | -4530 | No | No | 59.5 | 0.472 | 2018
EI_2018-07-28_121743 | 2018-07-28 08:18 | 2018-07-28 08:18 | EDT | 2018-07-28 12:18 | -1 | 59.994 | 60.022 | 60.027 | 0.028 | 0.033 | -3.5714 | -3.0303 | No | No | 59.5 | 0.527 | 2018
EI_2018-08-06_161835 | 2018-08-06 12:19 | 2018-08-06 12:19 | EDT | 2018-08-06 16:19 | 820 | 59.993 | 59.967 | 59.962 | -0.026 | -0.031 | -3153.8462 | -2645.1613 | Yes | No | 59.5 | 0.462 | 2018
EI_2018-08-10_020624 | 2018-08-09 22:06 | 2018-08-09 22:06 | EDT | 2018-08-10 02:06 | 1159.9 | 60.029 | 59.967 | 59.975 | -0.062 | -0.054 | -1870.8065 | -2147.963 | Yes | No | 59.5 | 0.475 | 2018
EI_2018-08-10_135459 | 2018-08-10 09:55 | 2018-08-10 09:55 | EDT | 2018-08-10 13:55 | 0 | 59.995 | 59.963 | 59.956 | -0.032 | -0.039 |  |  | No | No | 59.5 | 0.456 | 2018
EI_2018-08-11_060811 | 2018-08-11 02:08 | 2018-08-11 02:08 | EDT | 2018-08-11 06:08 | 0 | 60.006 | 59.961 | 59.963 | -0.045 | -0.043 |  |  | No | No | 59.5 | 0.463 | 2018
EI_2018-08-12_142830 | 2018-08-12 10:29 | 2018-08-12 10:29 | EDT | 2018-08-12 14:28 | 798.5 | 59.995 | 59.964 | 59.955 | -0.031 | -0.04 | -2575.8065 | -1996.25 | Yes | Yes | 59.5 | 0.455 | 2018
EI_2018-08-12_150514 | 2018-08-12 11:05 | 2018-08-12 11:05 | EDT | 2018-08-12 15:05 | 850 | 59.991 | 59.962 | 59.963 | -0.029 | -0.028 | -2931.0345 | -3035.7143 | Yes | No | 59.5 | 0.463 | 2018
EI_2018-08-15_151350 | 2018-08-15 11:14 | 2018-08-15 11:14 | EDT | 2018-08-15 15:14 | 792.5 | 59.992 | 59.96 | 59.96 | -0.032 | -0.032 | -2476.5625 | -2476.5625 | No | No | 59.5 | 0.46 | 2018
EI_2018-08-22_134534 | 2018-08-22 09:46 | 2018-08-22 09:46 | EDT | 2018-08-22 13:46 | 1151 | 60.014 | 59.965 | 59.956 | -0.049 | -0.058 | -2348.9796 | -1984.4828 | Yes | Yes | 59.5 | 0.456 | 2018
EI_2018-08-23_025958 | 2018-08-22 23:00 | 2018-08-22 23:00 | EDT | 2018-08-23 03:00 | 0 | 60.005 | 59.963 | 59.972 | -0.042 | -0.033 |  |  | No | No | 59.5 | 0.472 | 2018
EI_2018-08-24_110004 | 2018-08-24 07:00 | 2018-08-24 07:00 | EDT | 2018-08-24 11:00 | 0 | 60.006 | 59.97 | 59.974 | -0.036 | -0.032 |  |  | No | No | 59.5 | 0.474 | 2018
EI_2018-08-26_145834 | 2018-08-26 10:59 | 2018-08-26 10:59 | EDT | 2018-08-26 14:59 | 994 | 60.025 | 59.978 | 59.974 | -0.047 | -0.051 | -2114.8936 | -1949.0196 | Yes | No | 59.5 | 0.474 | 2018
EI_2018-08-27_043315 | 2018-08-27 00:33 | 2018-08-27 00:33 | EDT | 2018-08-27 04:33 | 1270 | 59.979 | 59.943 | 59.934 | -0.036 | -0.045 | -3527.7778 | -2822.2222 | Yes | Yes | 59.5 | 0.434 | 2018
EI_2018-08-27_215734 | 2018-08-27 17:58 | 2018-08-27 17:58 | EDT | 2018-08-27 21:58 | 610.5 | 60.013 | 59.976 | 59.98 | -0.037 | -0.033 | -1650 | -1850 | No | No | 59.5 | 0.48 | 2018
EI_2018-08-29_151643 | 2018-08-29 11:17 | 2018-08-29 11:17 | EDT | 2018-08-29 15:17 | 827.8 | 60.022 | 59.979 | 59.977 | -0.043 | -0.045 | -1925.1163 | -1839.5556 | Yes | No | 59.5 | 0.477 | 2018
EI_2018-08-30_134435 | 2018-08-30 09:45 | 2018-08-30 09:45 | EDT | 2018-08-30 13:45 | 699 | 60.018 | 59.979 | 59.984 | -0.039 | -0.034 | -1792.3077 | -2055.8824 | No | No | 59.5 | 0.484 | 2018
EI_2018-09-01_100506 | 2018-09-01 06:05 | 2018-09-01 06:05 | EDT | 2018-09-01 10:05 | -1 | 59.993 | 60.024 | 60.013 | 0.031 | 0.02 | -3.2258 | -5 | No | No | 59.5 | 0.513 | 2018
EI_2018-09-02_113455 | 2018-09-02 07:35 | 2018-09-02 07:35 | EDT | 2018-09-02 11:35 | 0 | 60.014 | 59.991 | 60.003 | -0.023 | -0.011 |  |  | No | No | 59.5 | 0.503 | 2018
EI_2018-09-03_131005 | 2018-09-03 09:10 | 2018-09-03 09:10 | EDT | 2018-09-03 13:10 | -1 | 59.989 | 60.026 | 60.016 | 0.037 | 0.027 | -2.7027 | -3.7037 | No | No | 59.5 | 0.516 | 2018
EI_2018-09-06_132648 | 2018-09-06 09:27 | 2018-09-06 09:27 | EDT | 2018-09-06 13:27 | -1 | 59.986 | 60.016 | 60.017 | 0.03 | 0.031 | -3.3333 | -3.2258 | No | No | 59.5 | 0.517 | 2018
EI_2018-09-07_085706 | 2018-09-07 04:57 | 2018-09-07 04:57 | EDT | 2018-09-07 08:57 | -1 | 59.981 | 60.012 | 60.009 | 0.031 | 0.028 | -3.2258 | -3.5714 | No | No | 59.5 | 0.509 | 2018
EI_2018-09-07_145511 | 2018-09-07 10:55 | 2018-09-07 10:55 | EDT | 2018-09-07 14:55 | 0 | 60.021 | 59.982 | 59.993 | -0.039 | -0.028 |  |  | No | No | 59.5 | 0.493 | 2018
EI_2018-09-08_101110 | 2018-09-08 06:11 | 2018-09-08 06:11 | EDT | 2018-09-08 10:11 | -1 | 59.993 | 60.027 | 60.028 | 0.034 | 0.035 | -2.9412 | -2.8571 | No | No | 59.5 | 0.528 | 2018
EI_2018-09-08_131214 | 2018-09-08 09:12 | 2018-09-08 09:12 | EDT | 2018-09-08 13:12 | -1 | 59.986 | 60.016 | 60.009 | 0.03 | 0.023 | -3.3333 | -4.3478 | No | No | 59.5 | 0.509 | 2018
EI_2018-09-08_215528 | 2018-09-08 17:55 | 2018-09-08 17:55 | EDT | 2018-09-08 21:55 | -1 | 59.984 | 60.029 | 59.996 | 0.045 | 0.012 | -2.2222 | -8.3333 | No | No | 59.5 | 0.496 | 2018
EI_2018-09-09_125846 | 2018-09-09 08:59 | 2018-09-09 08:59 | EDT | 2018-09-09 12:59 | -1 | 59.978 | 60.016 | 60.01 | 0.038 | 0.032 | -2.6316 | -3.125 | No | No | 59.5 | 0.51 | 2018
EI_2018-09-10_095928 | 2018-09-10 05:59 | 2018-09-10 05:59 | EDT | 2018-09-10 09:59 | -1 | 59.982 | 60.03 | 60.029 | 0.048 | 0.047 | -2.0833 | -2.1277 | No | No | 59.5 | 0.529 | 2018
EI_2018-09-11_093012 | 2018-09-11 05:30 | 2018-09-11 05:30 | EDT | 2018-09-11 09:30 | -1 | 59.988 | 60.017 | 60.019 | 0.029 | 0.031 | -3.4483 | -3.2258 | No | No | 59.5 | 0.519 | 2018
EI_2018-09-11_103402 | 2018-09-11 06:34 | 2018-09-11 06:34 | EDT | 2018-09-11 10:34 | -1 | 59.98 | 60.014 | 60.014 | 0.034 | 0.034 | -2.9412 | -2.9412 | No | No | 59.5 | 0.514 | 2018
EI_2018-09-11_112917 | 2018-09-11 07:29 | 2018-09-11 07:29 | EDT | 2018-09-11 11:29 | -1 | 59.99 | 60.027 | 60.024 | 0.037 | 0.034 | -2.7027 | -2.9412 | No | No | 59.5 | 0.524 | 2018
EI_2018-09-13_100405 | 2018-09-13 06:04 | 2018-09-13 06:04 | EDT | 2018-09-13 10:04 | -1 | 59.965 | 60.01 | 60.001 | 0.045 | 0.036 | -2.2222 | -2.7778 | No | No | 59.5 | 0.501 | 2018
EI_2018-09-13_113450 | 2018-09-13 07:35 | 2018-09-13 07:35 | EDT | 2018-09-13 11:35 | -1 | 59.981 | 60.02 | 60.008 | 0.039 | 0.027 | -2.5641 | -3.7037 | No | No | 59.5 | 0.508 | 2018
EI_2018-09-13_134614 | 2018-09-13 09:46 | 2018-09-13 09:46 | EDT | 2018-09-13 13:46 | 1300 | 59.982 | 59.934 | 59.93 | -0.048 | -0.052 | -2708.3333 | -2500 | Yes | No | 59.5 | 0.43 | 2018
EI_2018-09-13_154815 | 2018-09-13 11:48 | 2018-09-13 11:48 | EDT | 2018-09-13 15:48 | 0 | 60.002 | 59.97 | 59.971 | -0.032 | -0.031 |  |  | No | No | 59.5 | 0.471 | 2018
EI_2018-09-14_100432 | 2018-09-14 06:05 | 2018-09-14 06:05 | EDT | 2018-09-14 10:05 | 530 | 60.009 | 59.974 | 59.974 | -0.035 | -0.035 | -1514.2857 | -1514.2857 | No | No | 59.5 | 0.474 | 2018
EI_2018-09-14_172347 | 2018-09-14 13:24 | 2018-09-14 13:24 | EDT | 2018-09-14 17:24 | 1224 | 60.02 | 59.966 | 59.97 | -0.054 | -0.05 | -2266.6667 | -2448 | Yes | No | 59.5 | 0.47 | 2018
EI_2018-09-14_214427 | 2018-09-14 17:44 | 2018-09-14 17:44 | EDT | 2018-09-14 21:44 | 1387.6 | 60.004 | 59.96 | 59.964 | -0.044 | -0.04 | -3153.6364 | -3469 | Yes | No | 59.5 | 0.464 | 2018
EI_2018-09-16_115915 | 2018-09-16 07:59 | 2018-09-16 07:59 | EDT | 2018-09-16 11:59 | -1 | 59.986 | 60.023 | 60.023 | 0.037 | 0.037 | -2.7027 | -2.7027 | No | No | 59.5 | 0.523 | 2018
EI_2018-09-18_055214 | 2018-09-18 01:52 | 2018-09-18 01:52 | EDT | 2018-09-18 05:52 | -1 | 59.988 | 60.019 | 60.025 | 0.031 | 0.037 | -3.2258 | -2.7027 | No | No | 59.5 | 0.525 | 2018
EI_2018-09-18_085906 | 2018-09-18 04:59 | 2018-09-18 04:59 | EDT | 2018-09-18 08:59 | -1 | 59.989 | 60.016 | 60.014 | 0.027 | 0.025 | -3.7037 | -4 | No | No | 59.5 | 0.514 | 2018
EI_2018-09-18_092453 | 2018-09-18 05:25 | 2018-09-18 05:25 | EDT | 2018-09-18 09:25 | 1000 | 60.023 | 59.959 | 59.958 | -0.064 | -0.065 | -1562.5 | -1538.4615 | Yes | Yes | 59.5 | 0.458 | 2018
EI_2018-09-19_130620 | 2018-09-19 09:06 | 2018-09-19 09:06 | EDT | 2018-09-19 13:06 | -1 | 59.993 | 60.024 | 60.026 | 0.031 | 0.033 | -3.2258 | -3.0303 | No | No | 59.5 | 0.526 | 2018
EI_2018-09-20_000402 | 2018-09-19 20:04 | 2018-09-19 20:04 | EDT | 2018-09-20 00:04 | 395 | 59.999 | 59.968 | 59.97 | -0.031 | -0.029 | -1274.1935 | -1362.069 | No | No | 59.5 | 0.47 | 2018
EI_2018-09-20_100418 | 2018-09-20 06:04 | 2018-09-20 06:04 | EDT | 2018-09-20 10:04 | -1 | 59.969 | 60.022 | 59.987 | 0.053 | 0.018 | -1.8868 | -5.5556 | No | No | 59.5 | 0.487 | 2018
EI_2018-09-20_105430 | 2018-09-20 06:54 | 2018-09-20 06:54 | EDT | 2018-09-20 10:54 | -1 | 59.979 | 60.013 | 60.003 | 0.034 | 0.024 | -2.9412 | -4.1667 | No | No | 59.5 | 0.503 | 2018
EI_2018-09-20_124149 | 2018-09-20 08:42 | 2018-09-20 08:42 | EDT | 2018-09-20 12:42 | 1250 | 60.007 | 59.959 | 59.949 | -0.048 | -0.058 | -2604.1667 | -2155.1724 | Yes | Yes | 59.5 | 0.449 | 2018
EI_2018-09-21_101947 | 2018-09-21 06:20 | 2018-09-21 06:20 | EDT | 2018-09-21 10:20 | -1 | 59.977 | 60.019 | 60.012 | 0.042 | 0.035 | -2.381 | -2.8571 | No | No | 59.5 | 0.512 | 2018
EI_2018-09-21_121304 | 2018-09-21 08:13 | 2018-09-21 08:13 | EDT | 2018-09-21 12:13 | 0 | 60.018 | 59.984 | 59.981 | -0.034 | -0.037 |  |  | No | No | 59.5 | 0.481 | 2018
EI_2018-09-21_142210 | 2018-09-21 10:22 | 2018-09-21 10:22 | EDT | 2018-09-21 14:22 | -1 | 59.982 | 60.022 | 60.016 | 0.04 | 0.034 | -2.5 | -2.9412 | No | No | 59.5 | 0.516 | 2018
EI_2018-09-22_024527 | 2018-09-21 22:45 | 2018-09-21 22:45 | EDT | 2018-09-22 02:45 | 0 | 60.009 | 59.961 | 59.977 | -0.048 | -0.032 |  |  | No | No | 59.5 | 0.477 | 2018
EI_2018-09-22_093741 | 2018-09-22 05:38 | 2018-09-22 05:38 | EDT | 2018-09-22 09:38 | -1 | 59.99 | 60.03 | 60.014 | 0.04 | 0.024 | -2.5 | -4.1667 | No | No | 59.5 | 0.514 | 2018
EI_2018-09-22_135430 | 2018-09-22 09:54 | 2018-09-22 09:54 | EDT | 2018-09-22 13:54 | -1 | 59.969 | 60.005 | 59.996 | 0.036 | 0.027 | -2.7778 | -3.7037 | No | No | 59.5 | 0.496 | 2018
EI_2018-09-22_142429 | 2018-09-22 10:24 | 2018-09-22 10:24 | EDT | 2018-09-22 14:24 | -1 | 59.987 | 60.028 | 60.022 | 0.041 | 0.035 | -2.439 | -2.8571 | No | No | 59.5 | 0.522 | 2018
EI_2018-09-22_142923 | 2018-09-22 10:29 | 2018-09-22 10:29 | EDT | 2018-09-22 14:29 | -1 | 59.973 | 60.01 | 60 | 0.037 | 0.027 | -2.7027 | -3.7037 | No | No | 59.5 | 0.5 | 2018
EI_2018-09-22_211030 | 2018-09-22 17:11 | 2018-09-22 17:11 | EDT | 2018-09-22 21:10 | -1 | 60 | 60.033 | 60.038 | 0.033 | 0.038 | -3.0303 | -2.6316 | No | No | 59.5 | 0.538 | 2018
EI_2018-09-23_042217 | 2018-09-23 00:22 | 2018-09-23 00:22 | EDT | 2018-09-23 04:22 | 0 | 60.019 | 59.979 | 59.984 | -0.04 | -0.035 |  |  | No | No | 59.5 | 0.484 | 2018
EI_2018-09-23_110203 | 2018-09-23 07:02 | 2018-09-23 07:02 | EDT | 2018-09-23 11:02 | -1 | 59.985 | 60.021 | 60.013 | 0.036 | 0.028 | -2.7778 | -3.5714 | No | No | 59.5 | 0.513 | 2018
EI_2018-09-24_080205 | 2018-09-24 04:02 | 2018-09-24 04:02 | EDT | 2018-09-24 08:02 | -1 | 59.976 | 60.02 | 60.004 | 0.044 | 0.028 | -2.2727 | -3.5714 | No | No | 59.5 | 0.504 | 2018
EI_2018-09-24_110245 | 2018-09-24 07:03 | 2018-09-24 07:03 | EDT | 2018-09-24 11:03 | 0 | 59.985 | 60.023 | 59.991 | 0.038 | 0.006 |  |  | No | No | 59.5 | 0.491 | 2018
EI_2018-09-25_103618 | 2018-09-25 06:36 | 2018-09-25 06:36 | EDT | 2018-09-25 10:36 | -1 | 59.965 | 60.015 | 59.987 | 0.05 | 0.022 | -2 | -4.5455 | No | No | 59.5 | 0.487 | 2018
EI_2018-09-25_111116 | 2018-09-25 07:11 | 2018-09-25 07:11 | EDT | 2018-09-25 11:11 | -1 | 59.985 | 60.028 | 60.016 | 0.043 | 0.031 | -2.3256 | -3.2258 | No | No | 59.5 | 0.516 | 2018
EI_2018-09-26_095324 | 2018-09-26 05:53 | 2018-09-26 05:53 | EDT | 2018-09-26 09:53 | -1 | 59.979 | 60.014 | 60.002 | 0.035 | 0.023 | -2.8571 | -4.3478 | No | No | 59.5 | 0.502 | 2018
EI_2018-09-26_101511 | 2018-09-26 06:15 | 2018-09-26 06:15 | EDT | 2018-09-26 10:15 | -1 | 59.98 | 60.015 | 60.014 | 0.035 | 0.034 | -2.8571 | -2.9412 | No | No | 59.5 | 0.514 | 2018
EI_2018-09-27_000803 | 2018-09-26 20:08 | 2018-09-26 20:08 | EDT | 2018-09-27 00:08 | 925 | 59.989 | 59.955 | 59.95 | -0.034 | -0.039 | -2720.5882 | -2371.7949 | Yes | No | 59.5 | 0.45 | 2018
EI_2018-09-27_102619 | 2018-09-27 06:26 | 2018-09-27 06:26 | EDT | 2018-09-27 10:26 | -1 | 59.992 | 60.026 | 60.028 | 0.034 | 0.036 | -2.9412 | -2.7778 | No | No | 59.5 | 0.528 | 2018
EI_2018-09-28_024051 | 2018-09-27 22:41 | 2018-09-27 22:41 | EDT | 2018-09-28 02:41 | 0 | 59.998 | 59.961 | 59.969 | -0.037 | -0.029 |  |  | No | No | 59.5 | 0.469 | 2018
EI_2018-09-28_034936 | 2018-09-27 23:50 | 2018-09-27 23:50 | EDT | 2018-09-28 03:50 | 0 | 60.006 | 59.963 | 59.968 | -0.043 | -0.038 |  |  | No | No | 59.5 | 0.468 | 2018
EI_2018-09-28_050750 | 2018-09-28 01:08 | 2018-09-28 01:08 | EDT | 2018-09-28 05:08 | -1 | 59.979 | 60.019 | 60.005 | 0.04 | 0.026 | -2.5 | -3.8462 | No | No | 59.5 | 0.505 | 2018
EI_2018-09-28_122100 | 2018-09-28 08:21 | 2018-09-28 08:21 | EDT | 2018-09-28 12:21 | -1 | 59.991 | 60.03 | 60.032 | 0.039 | 0.041 | -2.5641 | -2.439 | No | No | 59.5 | 0.532 | 2018
EI_2018-09-28_154634 | 2018-09-28 11:47 | 2018-09-28 11:47 | EDT | 2018-09-28 15:47 | 680 | 59.985 | 59.952 | 59.95 | -0.033 | -0.035 | -2060.6061 | -1942.8571 | No | No | 59.5 | 0.45 | 2018
EI_2018-09-29_110459 | 2018-09-29 07:05 | 2018-09-29 07:05 | EDT | 2018-09-29 11:05 | -1 | 59.987 | 60.018 | 60.022 | 0.031 | 0.035 | -3.2258 | -2.8571 | No | No | 59.5 | 0.522 | 2018
EI_2018-09-29_124512 | 2018-09-29 08:45 | 2018-09-29 08:45 | EDT | 2018-09-29 12:45 | -1 | 59.979 | 60.005 | 60.005 | 0.026 | 0.026 | -3.8462 | -3.8462 | No | No | 59.5 | 0.505 | 2018
EI_2018-09-30_133433 | 2018-09-30 09:35 | 2018-09-30 09:35 | EDT | 2018-09-30 13:35 | -1 | 59.991 | 60.025 | 60.026 | 0.034 | 0.035 | -2.9412 | -2.8571 | No | No | 59.5 | 0.526 | 2018
EI_2018-09-30_144224 | 2018-09-30 10:42 | 2018-09-30 10:42 | EDT | 2018-09-30 14:42 | 870.5 | 60.006 | 59.967 | 59.953 | -0.039 | -0.053 | -2232.0513 | -1642.4528 | Yes | Yes | 59.5 | 0.453 | 2018
EI_2018-09-30_152852 | 2018-09-30 11:29 | 2018-09-30 11:29 | EDT | 2018-09-30 15:29 | 1320 | 60.009 | 59.962 | 59.97 | -0.047 | -0.039 | -2808.5106 | -3384.6154 | Yes | No | 59.5 | 0.47 | 2018
EI_2018-10-01_111051 | 2018-10-01 07:11 | 2018-10-01 07:11 | EDT | 2018-10-01 11:11 | -1 | 59.985 | 60.027 | 60.015 | 0.042 | 0.03 | -2.381 | -3.3333 | No | No | 59.5 | 0.515 | 2018
EI_2018-10-01_115923 | 2018-10-01 07:59 | 2018-10-01 07:59 | EDT | 2018-10-01 11:59 | -1 | 59.981 | 60.015 | 60.014 | 0.034 | 0.033 | -2.9412 | -3.0303 | No | No | 59.5 | 0.514 | 2018
EI_2018-10-01_120311 | 2018-10-01 08:03 | 2018-10-01 08:03 | EDT | 2018-10-01 12:03 | -1 | 59.985 | 60.014 | 60.01 | 0.029 | 0.025 | -3.4483 | -4 | No | No | 59.5 | 0.51 | 2018
EI_2018-10-02_085218 | 2018-10-02 04:52 | 2018-10-02 04:52 | EDT | 2018-10-02 08:52 | -1 | 59.986 | 60.022 | 60.015 | 0.036 | 0.029 | -2.7778 | -3.4483 | No | No | 59.5 | 0.515 | 2018
EI_2018-10-02_102913 | 2018-10-02 06:29 | 2018-10-02 06:29 | EDT | 2018-10-02 10:29 | -1 | 59.982 | 60.025 | 60.019 | 0.043 | 0.037 | -2.3256 | -2.7027 | No | No | 59.5 | 0.519 | 2018
EI_2018-10-04_111052 | 2018-10-04 07:11 | 2018-10-04 07:11 | EDT | 2018-10-04 11:11 | -1 | 59.989 | 60.032 | 60.027 | 0.043 | 0.038 | -2.3256 | -2.6316 | No | No | 59.5 | 0.527 | 2018
EI_2018-10-05_074810 | 2018-10-05 03:48 | 2018-10-05 03:48 | EDT | 2018-10-05 07:48 | 0 | 60.011 | 59.976 | 59.98 | -0.035 | -0.031 |  |  | No | No | 59.5 | 0.48 | 2018
EI_2018-10-05_101420 | 2018-10-05 06:14 | 2018-10-05 06:14 | EDT | 2018-10-05 10:14 | -1 | 59.98 | 60.019 | 60.012 | 0.039 | 0.032 | -2.5641 | -3.125 | No | No | 59.5 | 0.512 | 2018
EI_2018-10-06_034043 | 2018-10-05 23:41 | 2018-10-05 23:41 | EDT | 2018-10-06 03:41 | -1 | 59.98 | 60.021 | 60.006 | 0.041 | 0.026 | -2.439 | -3.8462 | No | No | 59.5 | 0.506 | 2018
EI_2018-10-06_104909 | 2018-10-06 06:49 | 2018-10-06 06:49 | EDT | 2018-10-06 10:49 | -1 | 59.984 | 60.012 | 60.012 | 0.028 | 0.028 | -3.5714 | -3.5714 | No | No | 59.5 | 0.512 | 2018
EI_2018-10-06_110115 | 2018-10-06 07:01 | 2018-10-06 07:01 | EDT | 2018-10-06 11:01 | -1 | 59.976 | 60.026 | 60.008 | 0.05 | 0.032 | -2 | -3.125 | No | No | 59.5 | 0.508 | 2018
EI_2018-10-06_112918 | 2018-10-06 07:29 | 2018-10-06 07:29 | EDT | 2018-10-06 11:29 | -1 | 59.988 | 60.018 | 60.028 | 0.03 | 0.04 | -3.3333 | -2.5 | No | No | 59.5 | 0.528 | 2018
EI_2018-10-06_130621 | 2018-10-06 09:06 | 2018-10-06 09:06 | EDT | 2018-10-06 13:06 | -1 | 60 | 60.032 | 60.026 | 0.032 | 0.026 | -3.125 | -3.8462 | No | No | 59.5 | 0.526 | 2018
EI_2018-10-06_135219 | 2018-10-06 09:52 | 2018-10-06 09:52 | EDT | 2018-10-06 13:52 | -1 | 59.991 | 60.013 | 60.026 | 0.022 | 0.035 | -4.5455 | -2.8571 | No | No | 59.5 | 0.526 | 2018
EI_2018-10-07_163805 | 2018-10-07 12:38 | 2018-10-07 12:38 | EDT | 2018-10-07 16:38 | 0 | 59.998 | 59.968 | 59.958 | -0.03 | -0.04 |  |  | No | No | 59.5 | 0.458 | 2018
EI_2018-10-08_220935 | 2018-10-08 18:10 | 2018-10-08 18:10 | EDT | 2018-10-08 22:10 | 633 | 60.005 | 59.969 | 59.965 | -0.036 | -0.04 | -1758.3333 | -1582.5 | Yes | No | 59.5 | 0.465 | 2018
EI_2018-10-10_083053 | 2018-10-10 04:31 | 2018-10-10 04:31 | EDT | 2018-10-10 08:31 | -1 | 59.985 | 60.024 | 60.016 | 0.039 | 0.031 | -2.5641 | -3.2258 | No | No | 59.5 | 0.516 | 2018
EI_2018-10-10_120008 | 2018-10-10 08:00 | 2018-10-10 08:00 | EDT | 2018-10-10 12:00 | -1 | 59.983 | 60.024 | 60.012 | 0.041 | 0.029 | -2.439 | -3.4483 | No | No | 59.5 | 0.512 | 2018
EI_2018-10-12_080611 | 2018-10-12 04:06 | 2018-10-12 04:06 | EDT | 2018-10-12 08:06 | -1 | 59.991 | 60.02 | 60.02 | 0.029 | 0.029 | -3.4483 | -3.4483 | No | No | 59.5 | 0.52 | 2018
EI_2018-10-12_175324 | 2018-10-12 13:53 | 2018-10-12 13:53 | EDT | 2018-10-12 17:53 | 994 | 59.992 | 59.952 | 59.948 | -0.04 | -0.044 | -2485 | -2259.0909 | Yes | Yes | 59.5 | 0.448 | 2018
EI_2018-10-13_111942 | 2018-10-13 07:20 | 2018-10-13 07:20 | EDT | 2018-10-13 11:20 | 411 | 60.018 | 59.973 | 59.982 | -0.045 | -0.036 | -913.3333 | -1141.6667 | No | No | 59.5 | 0.482 | 2018
EI_2018-10-13_120845 | 2018-10-13 08:09 | 2018-10-13 08:09 | EDT | 2018-10-13 12:09 | -1 | 59.988 | 60.022 | 60.025 | 0.034 | 0.037 | -2.9412 | -2.7027 | No | No | 59.5 | 0.525 | 2018
EI_2018-10-13_162814 | 2018-10-13 12:28 | 2018-10-13 12:28 | EDT | 2018-10-13 16:28 | 0 | 60.009 | 59.967 | 59.98 | -0.042 | -0.029 |  |  | No | No | 59.5 | 0.48 | 2018
EI_2018-10-14_043112 | 2018-10-14 00:31 | 2018-10-14 00:31 | EDT | 2018-10-14 04:31 | -1 | 59.976 | 60.012 | 60.005 | 0.036 | 0.029 | -2.7778 | -3.4483 | No | No | 59.5 | 0.505 | 2018
EI_2018-10-14_050652 | 2018-10-14 01:07 | 2018-10-14 01:07 | EDT | 2018-10-14 05:07 | -1 | 59.99 | 60.034 | 60.023 | 0.044 | 0.033 | -2.2727 | -3.0303 | No | No | 59.5 | 0.523 | 2018
EI_2018-10-14_100438 | 2018-10-14 06:05 | 2018-10-14 06:05 | EDT | 2018-10-14 10:05 | -1 | 59.977 | 60.021 | 60.022 | 0.044 | 0.045 | -2.2727 | -2.2222 | No | No | 59.5 | 0.522 | 2018
EI_2018-10-14_103306 | 2018-10-14 06:33 | 2018-10-14 06:33 | EDT | 2018-10-14 10:33 | -1 | 59.986 | 60.028 | 60.022 | 0.042 | 0.036 | -2.381 | -2.7778 | No | No | 59.5 | 0.522 | 2018
EI_2018-10-15_034107 | 2018-10-14 23:41 | 2018-10-14 23:41 | EDT | 2018-10-15 03:41 | -1 | 59.973 | 60.007 | 59.998 | 0.034 | 0.025 | -2.9412 | -4 | No | No | 59.5 | 0.498 | 2018
EI_2018-10-15_052942 | 2018-10-15 01:30 | 2018-10-15 01:30 | EDT | 2018-10-15 05:30 | -1 | 59.992 | 60.019 | 60.029 | 0.027 | 0.037 | -3.7037 | -2.7027 | No | No | 59.5 | 0.529 | 2018
EI_2018-10-15_084942 | 2018-10-15 04:50 | 2018-10-15 04:50 | EDT | 2018-10-15 08:50 | -1 | 59.993 | 60.031 | 60.032 | 0.038 | 0.039 | -2.6316 | -2.5641 | No | No | 59.5 | 0.532 | 2018
EI_2018-10-15_090957 | 2018-10-15 05:10 | 2018-10-15 05:10 | EDT | 2018-10-15 09:10 | -1 | 59.983 | 60.03 | 60.03 | 0.047 | 0.047 | -2.1277 | -2.1277 | No | No | 59.5 | 0.53 | 2018
EI_2018-10-15_094214 | 2018-10-15 05:42 | 2018-10-15 05:42 | EDT | 2018-10-15 09:42 | -1 | 59.997 | 60.028 | 60.028 | 0.031 | 0.031 | -3.2258 | -3.2258 | No | No | 59.5 | 0.528 | 2018
EI_2018-10-16_092648 | 2018-10-16 05:27 | 2018-10-16 05:27 | EDT | 2018-10-16 09:27 | -1 | 59.992 | 60.027 | 60.029 | 0.035 | 0.037 | -2.8571 | -2.7027 | No | No | 59.5 | 0.529 | 2018
EI_2018-10-16_165045 | 2018-10-16 12:51 | 2018-10-16 12:51 | EDT | 2018-10-16 16:51 | 0 | 60.009 | 59.962 | 59.966 | -0.047 | -0.043 |  |  | No | No | 59.5 | 0.466 | 2018
EI_2018-10-17_092933 | 2018-10-17 05:30 | 2018-10-17 05:30 | EDT | 2018-10-17 09:30 | -1 | 59.988 | 60.013 | 60.014 | 0.025 | 0.026 | -4 | -3.8462 | No | No | 59.5 | 0.514 | 2018
EI_2018-10-17_110514 | 2018-10-17 07:05 | 2018-10-17 07:05 | EDT | 2018-10-17 11:05 | -1 | 59.969 | 60.013 | 59.998 | 0.044 | 0.029 | -2.2727 | -3.4483 | No | No | 59.5 | 0.498 | 2018
EI_2018-10-17_185505 | 2018-10-17 14:55 | 2018-10-17 14:55 | EDT | 2018-10-17 18:55 | -1 | 59.993 | 60.025 | 60.015 | 0.032 | 0.022 | -3.125 | -4.5455 | No | No | 59.5 | 0.515 | 2018
EI_2018-10-18_085913 | 2018-10-18 04:59 | 2018-10-18 04:59 | EDT | 2018-10-18 08:59 | -1 | 59.995 | 60.027 | 60.024 | 0.032 | 0.029 | -3.125 | -3.4483 | No | No | 59.5 | 0.524 | 2018
EI_2018-10-18_090711 | 2018-10-18 05:07 | 2018-10-18 05:07 | EDT | 2018-10-18 09:07 | 0 | 59.988 | 60.022 | 59.973 | 0.034 | -0.015 |  |  | No | No | 59.5 | 0.473 | 2018
EI_2018-10-18_092110 | 2018-10-18 05:21 | 2018-10-18 05:21 | EDT | 2018-10-18 09:21 | -1 | 59.987 | 60.035 | 60.031 | 0.048 | 0.044 | -2.0833 | -2.2727 | No | No | 59.5 | 0.531 | 2018
EI_2018-10-18_111541 | 2018-10-18 07:16 | 2018-10-18 07:16 | EDT | 2018-10-18 11:16 | -1 | 59.982 | 60.026 | 60.018 | 0.044 | 0.036 | -2.2727 | -2.7778 | No | No | 59.5 | 0.518 | 2018
EI_2018-10-19_091054 | 2018-10-19 05:11 | 2018-10-19 05:11 | EDT | 2018-10-19 09:11 | -1 | 59.991 | 60.02 | 60.022 | 0.029 | 0.031 | -3.4483 | -3.2258 | No | No | 59.5 | 0.522 | 2018
EI_2018-10-19_112413 | 2018-10-19 07:24 | 2018-10-19 07:24 | EDT | 2018-10-19 11:24 | -1 | 59.985 | 60.029 | 60.022 | 0.044 | 0.037 | -2.2727 | -2.7027 | No | No | 59.5 | 0.522 | 2018
EI_2018-10-19_152336 | 2018-10-19 11:24 | 2018-10-19 11:24 | EDT | 2018-10-19 15:24 | 0 | 60.034 | 60 | 60.006 | -0.034 | -0.028 |  |  | No | No | 59.5 | 0.506 | 2018
EI_2018-10-19_195924 | 2018-10-19 15:59 | 2018-10-19 15:59 | EDT | 2018-10-19 19:59 | -1 | 59.982 | 60.035 | 60.02 | 0.053 | 0.038 | -1.8868 | -2.6316 | No | No | 59.5 | 0.52 | 2018
EI_2018-10-20_101746 | 2018-10-20 06:18 | 2018-10-20 06:18 | EDT | 2018-10-20 10:18 | -1 | 59.982 | 60.023 | 60.021 | 0.041 | 0.039 | -2.439 | -2.5641 | No | No | 59.5 | 0.521 | 2018
EI_2018-10-21_034235 | 2018-10-20 23:43 | 2018-10-20 23:43 | EDT | 2018-10-21 03:43 | -1 | 59.992 | 60.023 | 60.028 | 0.031 | 0.036 | -3.2258 | -2.7778 | No | No | 59.5 | 0.528 | 2018
EI_2018-10-21_073133 | 2018-10-21 03:32 | 2018-10-21 03:32 | EDT | 2018-10-21 07:32 | 0 | 60.029 | 59.989 | 60.003 | -0.04 | -0.026 |  |  | No | No | 59.5 | 0.503 | 2018
EI_2018-10-21_095335 | 2018-10-21 05:54 | 2018-10-21 05:54 | EDT | 2018-10-21 09:54 | -1 | 59.986 | 60.023 | 60.02 | 0.037 | 0.034 | -2.7027 | -2.9412 | No | No | 59.5 | 0.52 | 2018
EI_2018-10-21_101117 | 2018-10-21 06:11 | 2018-10-21 06:11 | EDT | 2018-10-21 10:11 | -1 | 59.982 | 60.026 | 60.019 | 0.044 | 0.037 | -2.2727 | -2.7027 | No | No | 59.5 | 0.519 | 2018
EI_2018-10-21_130418 | 2018-10-21 09:04 | 2018-10-21 09:04 | EDT | 2018-10-21 13:04 | -1 | 59.985 | 60.02 | 60.018 | 0.035 | 0.033 | -2.8571 | -3.0303 | No | No | 59.5 | 0.518 | 2018
EI_2018-10-22_210010 | 2018-10-22 17:00 | 2018-10-22 17:00 | EDT | 2018-10-22 21:00 | -1 | 59.983 | 60.018 | 60.01 | 0.035 | 0.027 | -2.8571 | -3.7037 | No | No | 59.5 | 0.51 | 2018
EI_2018-10-23_021220 | 2018-10-22 22:12 | 2018-10-22 22:12 | EDT | 2018-10-23 02:12 | 0 | 59.998 | 59.974 | 59.971 | -0.024 | -0.027 |  |  | No | No | 59.5 | 0.471 | 2018
EI_2018-10-23_140029 | 2018-10-23 10:00 | 2018-10-23 10:00 | EDT | 2018-10-23 14:00 | 0 | 60.012 | 59.974 | 59.985 | -0.038 | -0.027 |  |  | No | No | 59.5 | 0.485 | 2018
EI_2018-10-23_163950 | 2018-10-23 12:40 | 2018-10-23 12:40 | EDT | 2018-10-23 16:40 | 0 | 60.014 | 59.975 | 59.977 | -0.039 | -0.037 |  |  | No | No | 59.5 | 0.477 | 2018
EI_2018-10-23_221825 | 2018-10-23 18:18 | 2018-10-23 18:18 | EDT | 2018-10-23 22:18 | -1 | 59.976 | 60.013 | 60.011 | 0.037 | 0.035 | -2.7027 | -2.8571 | No | No | 59.5 | 0.511 | 2018
EI_2018-10-23_225350 | 2018-10-23 18:54 | 2018-10-23 18:54 | EDT | 2018-10-23 22:54 | -1 | 59.989 | 60.019 | 60.022 | 0.03 | 0.033 | -3.3333 | -3.0303 | No | No | 59.5 | 0.522 | 2018
EI_2018-10-24_091427 | 2018-10-24 05:14 | 2018-10-24 05:14 | EDT | 2018-10-24 09:14 | -1 | 59.975 | 60.015 | 60.004 | 0.04 | 0.029 | -2.5 | -3.4483 | No | No | 59.5 | 0.504 | 2018
EI_2018-10-24_093757 | 2018-10-24 05:38 | 2018-10-24 05:38 | EDT | 2018-10-24 09:38 | -1 | 59.998 | 60.03 | 60.023 | 0.032 | 0.025 | -3.125 | -4 | No | No | 59.5 | 0.523 | 2018
EI_2018-10-24_095908 | 2018-10-24 05:59 | 2018-10-24 05:59 | EDT | 2018-10-24 09:59 | -1 | 59.984 | 60.022 | 60.02 | 0.038 | 0.036 | -2.6316 | -2.7778 | No | No | 59.5 | 0.52 | 2018
EI_2018-10-24_101659 | 2018-10-24 06:17 | 2018-10-24 06:17 | EDT | 2018-10-24 10:17 | -1 | 60.002 | 60.037 | 60.032 | 0.035 | 0.03 | -2.8571 | -3.3333 | No | No | 59.5 | 0.532 | 2018
EI_2018-10-25_211638 | 2018-10-25 17:17 | 2018-10-25 17:17 | EDT | 2018-10-25 21:17 | -1 | 59.989 | 60.019 | 60.028 | 0.03 | 0.039 | -3.3333 | -2.5641 | No | No | 59.5 | 0.528 | 2018
EI_2018-10-26_040327 | 2018-10-26 00:03 | 2018-10-26 00:03 | EDT | 2018-10-26 04:03 | 0 | 60.012 | 59.967 | 59.974 | -0.045 | -0.038 |  |  | No | No | 59.5 | 0.474 | 2018
EI_2018-10-27_100703 | 2018-10-27 06:07 | 2018-10-27 06:07 | EDT | 2018-10-27 10:07 | -1 | 60.011 | 60.043 | 60.044 | 0.032 | 0.033 | -3.125 | -3.0303 | No | No | 59.5 | 0.544 | 2018
EI_2018-10-27_112028 | 2018-10-27 07:20 | 2018-10-27 07:20 | EDT | 2018-10-27 11:20 | -1 | 59.966 | 60.018 | 59.997 | 0.052 | 0.031 | -1.9231 | -3.2258 | No | No | 59.5 | 0.497 | 2018
EI_2018-10-27_172624 | 2018-10-27 13:26 | 2018-10-27 13:26 | EDT | 2018-10-27 17:26 | 0 | 60.019 | 59.98 | 59.987 | -0.039 | -0.032 |  |  | No | No | 59.5 | 0.487 | 2018
EI_2018-10-28_012436 | 2018-10-27 21:25 | 2018-10-27 21:25 | EDT | 2018-10-28 01:25 | 0 | 60.011 | 59.979 | 59.975 | -0.032 | -0.036 |  |  | No | No | 59.5 | 0.475 | 2018
EI_2018-10-28_085956 | 2018-10-28 05:00 | 2018-10-28 05:00 | EDT | 2018-10-28 09:00 | -1 | 59.985 | 60.017 | 60.01 | 0.032 | 0.025 | -3.125 | -4 | No | No | 59.5 | 0.51 | 2018
EI_2018-10-28_104720 | 2018-10-28 06:47 | 2018-10-28 06:47 | EDT | 2018-10-28 10:47 | -1 | 59.981 | 60.019 | 60.007 | 0.038 | 0.026 | -2.6316 | -3.8462 | No | No | 59.5 | 0.507 | 2018
EI_2018-10-28_230333 | 2018-10-28 19:04 | 2018-10-28 19:04 | EDT | 2018-10-28 23:04 | -1 | 59.972 | 60.004 | 60.005 | 0.032 | 0.033 | -3.125 | -3.0303 | No | No | 59.5 | 0.505 | 2018
EI_2018-10-29_092913 | 2018-10-29 05:29 | 2018-10-29 05:29 | EDT | 2018-10-29 09:29 | -1 | 59.984 | 60.019 | 60.014 | 0.035 | 0.03 | -2.8571 | -3.3333 | No | No | 59.5 | 0.514 | 2018
EI_2018-10-29_171619 | 2018-10-29 13:16 | 2018-10-29 13:16 | EDT | 2018-10-29 17:16 | 971 | 60.01 | 59.949 | 59.952 | -0.061 | -0.058 | -1591.8033 | -1674.1379 | Yes | Yes | 59.5 | 0.452 | 2018
EI_2018-10-29_201341 | 2018-10-29 16:14 | 2018-10-29 16:14 | EDT | 2018-10-29 20:14 | 0 | 59.989 | 59.958 | 59.953 | -0.031 | -0.036 |  |  | No | No | 59.5 | 0.453 | 2018
EI_2018-10-30_040730 | 2018-10-30 00:08 | 2018-10-30 00:08 | EDT | 2018-10-30 04:08 | 1218 | 60.022 | 59.942 | 59.945 | -0.08 | -0.077 | -1522.5 | -1581.8182 | Yes | No | 59.5 | 0.445 | 2018
EI_2018-10-30_085515 | 2018-10-30 04:55 | 2018-10-30 04:55 | EDT | 2018-10-30 08:55 | -1 | 59.982 | 60.02 | 60.021 | 0.038 | 0.039 | -2.6316 | -2.5641 | No | No | 59.5 | 0.521 | 2018
EI_2018-10-30_085907 | 2018-10-30 04:59 | 2018-10-30 04:59 | EDT | 2018-10-30 08:59 | -1 | 59.985 | 60.03 | 60.02 | 0.045 | 0.035 | -2.2222 | -2.8571 | No | No | 59.5 | 0.52 | 2018
EI_2018-10-30_095927 | 2018-10-30 05:59 | 2018-10-30 05:59 | EDT | 2018-10-30 09:59 | -1 | 59.991 | 60.02 | 60.028 | 0.029 | 0.037 | -3.4483 | -2.7027 | No | No | 59.5 | 0.528 | 2018
EI_2018-10-30_161917 | 2018-10-30 12:19 | 2018-10-30 12:19 | EDT | 2018-10-30 16:19 | 0 | 60.022 | 59.98 | 59.992 | -0.042 | -0.03 |  |  | No | No | 59.5 | 0.492 | 2018
EI_2018-10-31_083113 | 2018-10-31 04:31 | 2018-10-31 04:31 | EDT | 2018-10-31 08:31 | -1 | 59.979 | 60.022 | 60.012 | 0.043 | 0.033 | -2.3256 | -3.0303 | No | No | 59.5 | 0.512 | 2018
EI_2018-10-31_193157 | 2018-10-31 15:32 | 2018-10-31 15:32 | EDT | 2018-10-31 19:32 | 0 | 60.01 | 59.975 | 59.983 | -0.035 | -0.027 |  |  | No | No | 59.5 | 0.483 | 2018
EI_2018-10-31_195537 | 2018-10-31 15:56 | 2018-10-31 15:56 | EDT | 2018-10-31 19:56 | -1 | 59.994 | 60.024 | 60.02 | 0.03 | 0.026 | -3.3333 | -3.8462 | No | No | 59.5 | 0.52 | 2018
EI_2018-10-31_204634 | 2018-10-31 16:47 | 2018-10-31 16:47 | EDT | 2018-10-31 20:47 | -1 | 59.971 | 60.015 | 60.002 | 0.044 | 0.031 | -2.2727 | -3.2258 | No | No | 59.5 | 0.502 | 2018
EI_2018-11-01_054219 | 2018-11-01 01:42 | 2018-11-01 01:42 | EDT | 2018-11-01 05:42 | 755 | 59.994 | 59.972 | 59.962 | -0.022 | -0.032 | -3431.8182 | -2359.375 | No | No | 59.5 | 0.462 | 2018
EI_2018-11-02_081913 | 2018-11-02 04:19 | 2018-11-02 04:19 | EDT | 2018-11-02 08:19 | 0 | 60.009 | 59.983 | 59.98 | -0.026 | -0.029 |  |  | No | No | 59.5 | 0.48 | 2018
EI_2018-11-03_100937 | 2018-11-03 06:10 | 2018-11-03 06:10 | EDT | 2018-11-03 10:10 | -1 | 59.985 | 60.028 | 60.038 | 0.043 | 0.053 | -2.3256 | -1.8868 | No | No | 59.5 | 0.538 | 2018
EI_2018-11-04_191219 | 2018-11-04 14:12 | 2018-11-04 14:12 | EST | 2018-11-04 19:12 | 684 | 59.997 | 59.963 | 59.965 | -0.034 | -0.032 | -2011.7647 | -2137.5 | No | No | 59.5 | 0.465 | 2018
EI_2018-11-05_052700 | 2018-11-05 00:27 | 2018-11-05 00:27 | EST | 2018-11-05 05:27 | 0 | 59.998 | 59.964 | 59.971 | -0.034 | -0.027 |  |  | No | No | 59.5 | 0.471 | 2018
EI_2018-11-05_110004 | 2018-11-05 06:00 | 2018-11-05 06:00 | EST | 2018-11-05 11:00 | 0 | 60.024 | 59.977 | 60.004 | -0.047 | -0.02 |  |  | No | No | 59.5 | 0.504 | 2018
EI_2018-11-05_151101 | 2018-11-05 10:11 | 2018-11-05 10:11 | EST | 2018-11-05 15:11 | 0 | 60.013 | 59.975 | 59.972 | -0.038 | -0.041 |  |  | No | No | 59.5 | 0.472 | 2018
EI_2018-11-07_045551 | 2018-11-06 23:56 | 2018-11-06 23:56 | EST | 2018-11-07 04:56 | 0 | 60.011 | 59.976 | 59.972 | -0.035 | -0.039 |  |  | No | No | 59.5 | 0.472 | 2018
EI_2018-11-08_081152 | 2018-11-08 03:12 | 2018-11-08 03:12 | EST | 2018-11-08 08:12 | 0 | 59.995 | 59.964 | 59.968 | -0.031 | -0.027 |  |  | No | No | 59.5 | 0.468 | 2018
EI_2018-11-10_064644 | 2018-11-10 01:47 | 2018-11-10 01:47 | EST | 2018-11-10 06:47 | 0 | 59.995 | 59.954 | 59.962 | -0.041 | -0.033 |  |  | No | No | 59.5 | 0.462 | 2018
EI_2018-11-11_071542 | 2018-11-11 02:16 | 2018-11-11 02:16 | EST | 2018-11-11 07:16 | 470 | 60.002 | 59.972 | 59.966 | -0.03 | -0.036 | -1566.6667 | -1305.5556 | Yes | No | 59.5 | 0.466 | 2018
EI_2018-11-11_181241 | 2018-11-11 13:13 | 2018-11-11 13:13 | EST | 2018-11-11 18:13 | 0 | 60.01 | 59.974 | 59.98 | -0.036 | -0.03 |  |  | No | No | 59.5 | 0.48 | 2018
EI_2018-11-12_041037 | 2018-11-11 23:11 | 2018-11-11 23:11 | EST | 2018-11-12 04:11 | 0 | 60.012 | 59.959 | 59.972 | -0.053 | -0.04 |  |  | No | No | 59.5 | 0.472 | 2018
EI_2018-11-12_044734 | 2018-11-11 23:48 | 2018-11-11 23:48 | EST | 2018-11-12 04:48 | 0 | 60.023 | 59.975 | 59.992 | -0.048 | -0.031 |  |  | No | No | 59.5 | 0.492 | 2018
EI_2018-11-12_110004 | 2018-11-12 06:00 | 2018-11-12 06:00 | EST | 2018-11-12 11:00 | 0 | 60.013 | 59.972 | 59.979 | -0.041 | -0.034 |  |  | No | No | 59.5 | 0.479 | 2018
EI_2018-11-13_033007 | 2018-11-12 22:30 | 2018-11-12 22:30 | EST | 2018-11-13 03:30 | 0 | 60.017 | 59.968 | 59.975 | -0.049 | -0.042 |  |  | No | No | 59.5 | 0.475 | 2018
EI_2018-11-15_183046 | 2018-11-15 13:31 | 2018-11-15 13:31 | EST | 2018-11-15 18:31 | 0 | 60.028 | 59.974 | 59.982 | -0.054 | -0.046 |  |  | No | No | 59.5 | 0.482 | 2018
EI_2018-11-15_222816 | 2018-11-15 17:28 | 2018-11-15 17:28 | EST | 2018-11-15 22:28 | 964 | 60.005 | 59.989 | 59.969 | -0.016 | -0.036 | -6025 | -2677.7778 | Yes | No | 59.5 | 0.469 | 2018
EI_2018-11-17_015629 | 2018-11-16 20:56 | 2018-11-16 20:56 | EST | 2018-11-17 01:56 | 0 | 60.006 | 59.974 | 59.962 | -0.032 | -0.044 |  |  | No | No | 59.5 | 0.462 | 2018
EI_2018-11-17_174259 | 2018-11-17 12:43 | 2018-11-17 12:43 | EST | 2018-11-17 17:43 | 800 | 60.015 | 59.971 | 59.967 | -0.044 | -0.048 | -1818.1818 | -1666.6667 | Yes | No | 59.5 | 0.467 | 2018
EI_2018-11-17_184541 | 2018-11-17 13:46 | 2018-11-17 13:46 | EST | 2018-11-17 18:46 | 0 | 60.012 | 59.961 | 59.971 | -0.051 | -0.041 |  |  | No | No | 59.5 | 0.471 | 2018
EI_2018-11-22_135630 | 2018-11-22 08:56 | 2018-11-22 08:56 | EST | 2018-11-22 13:56 | 510 | 59.987 | 59.956 | 59.959 | -0.031 | -0.028 | -1645.1613 | -1821.4286 | No | No | 59.5 | 0.459 | 2018
EI_2018-11-24_072927 | 2018-11-24 02:29 | 2018-11-24 02:29 | EST | 2018-11-24 07:29 | 0 | 60.014 | 59.985 | 59.978 | -0.029 | -0.036 |  |  | No | No | 59.5 | 0.478 | 2018
EI_2018-11-24_110254 | 2018-11-24 06:03 | 2018-11-24 06:03 | EST | 2018-11-24 11:03 | -1 | 59.988 | 60.038 | 60.015 | 0.05 | 0.027 | -2 | -3.7037 | No | No | 59.5 | 0.515 | 2018
EI_2018-11-26_031132 | 2018-11-25 22:12 | 2018-11-25 22:12 | EST | 2018-11-26 03:12 | 0 | 60.016 | 59.983 | 59.974 | -0.033 | -0.042 |  |  | No | No | 59.5 | 0.474 | 2018
EI_2018-11-26_140746 | 2018-11-26 09:08 | 2018-11-26 09:08 | EST | 2018-11-26 14:08 | 594 | 60.01 | 59.968 | 59.972 | -0.042 | -0.038 | -1414.2857 | -1563.1579 | Yes | No | 59.5 | 0.472 | 2018
EI_2018-11-27_180044 | 2018-11-27 13:01 | 2018-11-27 13:01 | EST | 2018-11-27 18:01 | 0 | 60.02 | 59.975 | 59.982 | -0.045 | -0.038 |  |  | No | No | 59.5 | 0.482 | 2018
EI_2018-11-27_181658 | 2018-11-27 13:17 | 2018-11-27 13:17 | EST | 2018-11-27 18:17 | 981 | 59.987 | 59.96 | 59.961 | -0.027 | -0.026 | -3633.3333 | -3773.0769 | Yes | No | 59.5 | 0.461 | 2018
EI_2018-11-28_061810 | 2018-11-28 01:18 | 2018-11-28 01:18 | EST | 2018-11-28 06:18 | 0 | 60.025 | 59.98 | 59.998 | -0.045 | -0.027 |  |  | No | No | 59.5 | 0.498 | 2018
EI_2018-11-28_162835 | 2018-11-28 11:29 | 2018-11-28 11:29 | EST | 2018-11-28 16:29 | 0 | 60.011 | 59.979 | 59.978 | -0.032 | -0.033 |  |  | No | No | 59.5 | 0.478 | 2018
EI_2018-11-28_173214 | 2018-11-28 12:32 | 2018-11-28 12:32 | EST | 2018-11-28 17:32 | 0 | 60.01 | 59.968 | 59.972 | -0.042 | -0.038 |  |  | No | No | 59.5 | 0.472 | 2018
EI_2018-11-29_105350 | 2018-11-29 05:54 | 2018-11-29 05:54 | EST | 2018-11-29 10:54 | -1 | 59.983 | 60.02 | 60.013 | 0.037 | 0.03 | -2.7027 | -3.3333 | No | No | 59.5 | 0.513 | 2018
EI_2018-12-01_063851 | 2018-12-01 01:39 | 2018-12-01 01:39 | EST | 2018-12-01 06:39 | 0 | 60.011 | 59.977 | 59.972 | -0.034 | -0.039 |  |  | No | No | 59.5 | 0.472 | 2019
EI_2018-12-01_071331 | 2018-12-01 02:14 | 2018-12-01 02:14 | EST | 2018-12-01 07:14 | 0 | 60.012 | 59.967 | 59.98 | -0.045 | -0.032 |  |  | No | No | 59.5 | 0.48 | 2019
EI_2018-12-02_083817 | 2018-12-02 03:38 | 2018-12-02 03:38 | EST | 2018-12-02 08:38 | 937 | 60.019 | 59.951 | 59.979 | -0.068 | -0.04 | -1377.9412 | -2342.5 | Yes | No | 59.5 | 0.479 | 2019
EI_2018-12-02_110000 | 2018-12-02 06:00 | 2018-12-02 06:00 | EST | 2018-12-02 11:00 | 0 | 60.019 | 59.963 | 59.988 | -0.056 | -0.031 |  |  | No | No | 59.5 | 0.488 | 2019
EI_2018-12-02_120808 | 2018-12-02 07:08 | 2018-12-02 07:08 | EST | 2018-12-02 12:08 | 838 | 60.011 | 59.961 | 59.961 | -0.05 | -0.05 | -1676 | -1676 | Yes | No | 59.5 | 0.461 | 2019
EI_2018-12-05_051744 | 2018-12-05 00:18 | 2018-12-05 00:18 | EST | 2018-12-05 05:18 | 0 | 60.014 | 59.974 | 59.989 | -0.04 | -0.025 |  |  | No | No | 59.5 | 0.489 | 2019
EI_2018-12-09_112957 | 2018-12-09 06:30 | 2018-12-09 06:30 | EST | 2018-12-09 11:30 | 0 | 60.013 | 59.97 | 59.99 | -0.043 | -0.023 |  |  | No | No | 59.5 | 0.49 | 2019
EI_2018-12-15_062957 | 2018-12-15 01:30 | 2018-12-15 01:30 | EST | 2018-12-15 06:30 | 0 | 60.012 | 59.974 | 59.979 | -0.038 | -0.033 |  |  | No | No | 59.5 | 0.479 | 2019
EI_2018-12-16_142720 | 2018-12-16 09:27 | 2018-12-16 09:27 | EST | 2018-12-16 14:27 | 0 | 60.006 | 59.973 | 59.969 | -0.033 | -0.037 |  |  | No | No | 59.5 | 0.469 | 2019
EI_2018-12-16_174158 | 2018-12-16 12:42 | 2018-12-16 12:42 | EST | 2018-12-16 17:42 | 0 | 60.004 | 59.972 | 59.972 | -0.032 | -0.032 |  |  | No | No | 59.5 | 0.472 | 2019
EI_2018-12-16_180412 | 2018-12-16 13:04 | 2018-12-16 13:04 | EST | 2018-12-16 18:04 | 0 | 60.01 | 59.976 | 59.974 | -0.034 | -0.036 |  |  | No | No | 59.5 | 0.474 | 2019
EI_2018-12-17_234542 | 2018-12-17 18:46 | 2018-12-17 18:46 | EST | 2018-12-17 23:46 | 0 | 60.017 | 59.967 | 59.965 | -0.05 | -0.052 |  |  | No | No | 59.5 | 0.465 | 2019
EI_2018-12-18_172647 | 2018-12-18 12:27 | 2018-12-18 12:27 | EST | 2018-12-18 17:27 | 1000.2 | 59.998 | 59.964 | 59.958 | -0.034 | -0.04 | -2941.7647 | -2500.5 | Yes | Yes | 59.5 | 0.458 | 2019
EI_2018-12-24_114514 | 2018-12-24 06:45 | 2018-12-24 06:45 | EST | 2018-12-24 11:45 | 0 | 60.006 | 59.982 | 59.97 | -0.024 | -0.036 |  |  | No | No | 59.5 | 0.47 | 2019
EI_2018-12-25_183201 | 2018-12-25 13:32 | 2018-12-25 13:32 | EST | 2018-12-25 18:32 | 0 | 60.009 | 59.982 | 59.979 | -0.027 | -0.03 |  |  | No | No | 59.5 | 0.479 | 2019
EI_2018-12-26_060151 | 2018-12-26 01:02 | 2018-12-26 01:02 | EST | 2018-12-26 06:02 | 0 | 60.02 | 59.979 | 59.985 | -0.041 | -0.035 |  |  | No | No | 59.5 | 0.485 | 2019
EI_2018-12-26_134624 | 2018-12-26 08:46 | 2018-12-26 08:46 | EST | 2018-12-26 13:46 | 705 | 60.015 | 59.993 | 59.984 | -0.022 | -0.031 | -3204.5455 | -2274.1935 | No | No | 59.5 | 0.484 | 2019
EI_2018-12-30_020309 | 2018-12-29 21:03 | 2018-12-29 21:03 | EST | 2018-12-30 02:03 | 0 | 60.001 | 59.974 | 59.969 | -0.027 | -0.032 |  |  | No | No | 59.5 | 0.469 | 2019
EI_2018-12-30_070625 | 2018-12-30 02:06 | 2018-12-30 02:06 | EST | 2018-12-30 07:06 | 0 | 60.011 | 59.975 | 59.97 | -0.036 | -0.041 |  |  | No | No | 59.5 | 0.47 | 2019
EI_2018-12-31_123259 | 2018-12-31 07:33 | 2018-12-31 07:33 | EST | 2018-12-31 12:33 | 0 | 60.006 | 59.975 | 59.974 | -0.031 | -0.032 |  |  | No | No | 59.5 | 0.474 | 2019
EI_2018-12-31_144459 | 2018-12-31 09:45 | 2018-12-31 09:45 | EST | 2018-12-31 14:45 | 0 | 60.011 | 59.964 | 59.964 | -0.047 | -0.047 |  |  | No | No | 59.5 | 0.464 | 2019
EI_2019-01-01_193136 | 2019-01-01 14:32 | 2019-01-01 14:32 | EST | 2019-01-01 19:32 | 0 | 60.018 | 59.986 | 59.983 | -0.032 | -0.035 |  |  | No | No | 59.5 | 0.483 | 2019
EI_2019-01-04_012804 | 2019-01-03 20:28 | 2019-01-03 20:28 | EST | 2019-01-04 01:28 | 0 | 60.018 | 59.981 | 59.974 | -0.037 | -0.044 |  |  | No | No | 59.5 | 0.474 | 2019
EI_2019-01-09_111058 | 2019-01-09 06:11 | 2019-01-09 06:11 | EST | 2019-01-09 11:11 | 0 | 60.004 | 59.965 | 59.964 | -0.039 | -0.04 |  |  | No | No | 59.5 | 0.464 | 2019
EI_2019-01-11_042531 | 2019-01-10 23:26 | 2019-01-10 23:26 | EST | 2019-01-11 04:26 | 863.8 | 59.991 | 59.959 | 59.957 | -0.032 | -0.034 | -2699.375 | -2540.5882 | Yes | No | 59.5 | 0.457 | 2019
EI_2019-01-17_081400 | 2019-01-17 03:14 | 2019-01-17 03:14 | EST | 2019-01-17 08:14 | 0 | 60 | 59.963 | 59.971 | -0.037 | -0.029 |  |  | No | No | 59.5 | 0.471 | 2019
EI_2019-01-21_005540 | 2019-01-20 19:56 | 2019-01-20 19:56 | EST | 2019-01-21 00:56 | 850 | 59.983 | 59.956 | 59.953 | -0.027 | -0.03 | -3148.1481 | -2833.3333 | Yes | No | 59.5 | 0.453 | 2019
EI_2019-01-22_050538 | 2019-01-22 00:06 | 2019-01-22 00:06 | EST | 2019-01-22 05:06 | 540 | 59.997 | 59.959 | 59.964 | -0.038 | -0.033 | -1421.0526 | -1636.3636 | No | No | 59.5 | 0.464 | 2019
EI_2019-01-23_032800 | 2019-01-22 22:28 | 2019-01-22 22:28 | EST | 2019-01-23 03:28 | 1285 | 59.972 | 59.957 | 59.947 | -0.015 | -0.025 | -8566.6667 | -5140 | No | No | 59.5 | 0.447 | 2019
EI_2019-01-30_172220 | 2019-01-30 12:22 | 2019-01-30 12:22 | EST | 2019-01-30 17:22 | 1078 | 60.015 | 59.981 | 59.972 | -0.034 | -0.043 | -3170.5882 | -2506.9767 | Yes | No | 59.5 | 0.472 | 2019
EI_2019-01-31_062529 | 2019-01-31 01:25 | 2019-01-31 01:25 | EST | 2019-01-31 06:25 | 1107 | 60 | 59.963 | 59.96 | -0.037 | -0.04 | -2991.8919 | -2767.5 | Yes | Yes | 59.5 | 0.46 | 2019
EI_2019-01-31_080113 | 2019-01-31 03:01 | 2019-01-31 03:01 | EST | 2019-01-31 08:01 | 1170 | 60.005 | 59.972 | 59.968 | -0.033 | -0.037 | -3545.4545 | -3162.1622 | Yes | No | 59.5 | 0.468 | 2019
EI_2019-01-31_142444 | 2019-01-31 09:25 | 2019-01-31 09:25 | EST | 2019-01-31 14:25 | 1530 | 60.016 | 59.97 | 59.97 | -0.046 | -0.046 | -3326.087 | -3326.087 | Yes | No | 59.5 | 0.47 | 2019
EI_2019-02-01_064802 | 2019-02-01 01:48 | 2019-02-01 01:48 | EST | 2019-02-01 06:48 | 0 | 60.019 | 59.979 | 59.983 | -0.04 | -0.036 |  |  | No | No | 59.5 | 0.483 | 2019
EI_2019-02-04_020630 | 2019-02-03 21:06 | 2019-02-03 21:06 | EST | 2019-02-04 02:06 | 0 | 60.019 | 59.961 | 59.979 | -0.058 | -0.04 |  |  | No | No | 59.5 | 0.479 | 2019
EI_2019-02-04_022044 | 2019-02-03 21:21 | 2019-02-03 21:21 | EST | 2019-02-04 02:21 | 0 | 60.031 | 59.978 | 59.998 | -0.053 | -0.033 |  |  | No | No | 59.5 | 0.498 | 2019
EI_2019-02-04_062047 | 2019-02-04 01:21 | 2019-02-04 01:21 | EST | 2019-02-04 06:21 | 0 | 60.006 | 59.964 | 59.966 | -0.042 | -0.04 |  |  | No | No | 59.5 | 0.466 | 2019
EI_2019-02-04_151154 | 2019-02-04 10:12 | 2019-02-04 10:12 | EST | 2019-02-04 15:12 | 700 | 60.011 | 59.978 | 59.988 | -0.033 | -0.023 | -2121.2121 | -3043.4783 | No | No | 59.5 | 0.488 | 2019
EI_2019-02-12_190431 | 2019-02-12 14:05 | 2019-02-12 14:05 | EST | 2019-02-12 19:05 | 749 | 60.02 | 59.971 | 59.985 | -0.049 | -0.035 | -1528.5714 | -2140 | No | No | 59.5 | 0.485 | 2019
EI_2019-02-20_231719 | 2019-02-20 18:17 | 2019-02-20 18:17 | EST | 2019-02-20 23:17 | 0 | 60.012 | 59.967 | 59.972 | -0.045 | -0.04 |  |  | No | No | 59.5 | 0.472 | 2019
EI_2019-02-23_205652 | 2019-02-23 15:57 | 2019-02-23 15:57 | EST | 2019-02-23 20:57 | 1423 | 60.011 | 59.939 | 59.936 | -0.072 | -0.075 | -1976.3889 | -1897.3333 | Yes | Yes | 59.5 | 0.436 | 2019
EI_2019-02-25_052421 | 2019-02-25 00:24 | 2019-02-25 00:24 | EST | 2019-02-25 05:24 | 830 | 60.006 | 59.958 | 59.96 | -0.048 | -0.046 | -1729.1667 | -1804.3478 | Yes | Yes | 59.5 | 0.46 | 2019
EI_2019-02-28_132520 | 2019-02-28 08:25 | 2019-02-28 08:25 | EST | 2019-02-28 13:25 | 0 | 60.018 | 59.982 | 59.979 | -0.036 | -0.039 |  |  | No | No | 59.5 | 0.479 | 2019
EI_2019-03-03_172950 | 2019-03-03 12:30 | 2019-03-03 12:30 | EST | 2019-03-03 17:30 | 1338 | 60.013 | 59.956 | 59.946 | -0.057 | -0.067 | -2347.3684 | -1997.0149 | Yes | No | 59.5 | 0.446 | 2019
EI_2019-03-03_202938 | 2019-03-03 15:30 | 2019-03-03 15:30 | EST | 2019-03-03 20:30 | 571 | 60.008 | 59.974 | 59.973 | -0.034 | -0.035 | -1679.4118 | -1631.4286 | No | No | 59.5 | 0.473 | 2019
EI_2019-03-07_030450 | 2019-03-06 22:05 | 2019-03-06 22:05 | EST | 2019-03-07 03:05 | 1600 | 59.988 | 59.951 | 59.945 | -0.037 | -0.043 | -4324.3243 | -3720.9302 | Yes | Yes | 59.5 | 0.445 | 2019
EI_2019-03-10_050145 | 2019-03-10 00:02 | 2019-03-10 00:02 | EST | 2019-03-10 05:02 | 1239 | 59.997 | 59.953 | 59.945 | -0.044 | -0.052 | -2815.9091 | -2382.6923 | Yes | Yes | 59.5 | 0.445 | 2019
EI_2019-03-11_192135 | 2019-03-11 15:22 | 2019-03-11 15:22 | EDT | 2019-03-11 19:22 | 0 | 60.017 | 59.976 | 59.979 | -0.041 | -0.038 |  |  | No | No | 59.5 | 0.479 | 2019
EI_2019-03-15_170010 | 2019-03-15 13:00 | 2019-03-15 13:00 | EDT | 2019-03-15 17:00 | 1000 | 59.996 | 59.96 | 59.947 | -0.036 | -0.049 | -2777.7778 | -2040.8163 | Yes | No | 59.5 | 0.447 | 2019
EI_2019-03-16_003902 | 2019-03-15 20:39 | 2019-03-15 20:39 | EDT | 2019-03-16 00:39 | 850 | 60.001 | 59.952 | 59.949 | -0.049 | -0.052 | -1734.6939 | -1634.6154 | Yes | Yes | 59.5 | 0.449 | 2019
EI_2019-03-16_164620 | 2019-03-16 12:46 | 2019-03-16 12:46 | EDT | 2019-03-16 16:46 | 0 | 60.016 | 59.966 | 59.972 | -0.05 | -0.044 |  |  | No | No | 59.5 | 0.472 | 2019
EI_2019-03-18_235856 | 2019-03-18 19:59 | 2019-03-18 19:59 | EDT | 2019-03-18 23:59 | 540 | 60.016 | 59.981 | 59.977 | -0.035 | -0.039 | -1542.8571 | -1384.6154 | Yes | No | 59.5 | 0.477 | 2019
EI_2019-03-24_184504 | 2019-03-24 14:45 | 2019-03-24 14:45 | EDT | 2019-03-24 18:45 | 0 | 59.987 | 59.946 | 59.938 | -0.041 | -0.049 |  |  | No | No | 59.5 | 0.438 | 2019
EI_2019-03-29_161531 | 2019-03-29 12:16 | 2019-03-29 12:16 | EDT | 2019-03-29 16:16 | 732 | 59.996 | 59.966 | 59.958 | -0.03 | -0.038 | -2440 | -1926.3158 | Yes | No | 59.5 | 0.458 | 2019
EI_2019-03-30_003527 | 2019-03-29 20:35 | 2019-03-29 20:35 | EDT | 2019-03-30 00:35 | 511 | 60.012 | 59.97 | 59.984 | -0.042 | -0.028 | -1216.6667 | -1825 | No | No | 59.5 | 0.484 | 2019
EI_2019-04-03_152846 | 2019-04-03 11:29 | 2019-04-03 11:29 | EDT | 2019-04-03 15:29 | 0 | 60.02 | 59.977 | 59.991 | -0.043 | -0.029 |  |  | No | No | 59.5 | 0.491 | 2019
EI_2019-04-05_184038 | 2019-04-05 14:41 | 2019-04-05 14:41 | EDT | 2019-04-05 18:41 | 0 | 60.016 | 59.955 | 59.994 | -0.061 | -0.022 |  |  | No | No | 59.5 | 0.494 | 2019
EI_2019-04-06_035956 | 2019-04-06 | 2019-04-06 | EDT | 2019-04-06 04:00 | 0 | 60.022 | 59.964 | 59.997 | -0.058 | -0.025 |  |  | No | No | 59.5 | 0.497 | 2019
EI_2019-04-10_025854 | 2019-04-09 22:59 | 2019-04-09 22:59 | EDT | 2019-04-10 02:59 | 0 | 59.993 | 59.958 | 59.971 | -0.035 | -0.022 |  |  | No | No | 59.5 | 0.471 | 2019
EI_2019-04-10_032600 | 2019-04-09 23:26 | 2019-04-09 23:26 | EDT | 2019-04-10 03:26 | 0 | 60.018 | 59.971 | 59.988 | -0.047 | -0.03 |  |  | No | No | 59.5 | 0.488 | 2019
EI_2019-04-11_173414 | 2019-04-11 13:34 | 2019-04-11 13:34 | EDT | 2019-04-11 17:34 | 0 | 60.023 | 59.964 | 59.975 | -0.059 | -0.048 |  |  | No | No | 59.5 | 0.475 | 2019
EI_2019-04-14_185254 | 2019-04-14 14:53 | 2019-04-14 14:53 | EDT | 2019-04-14 18:53 | 0 | 60.016 | 59.971 | 59.989 | -0.045 | -0.027 |  |  | No | No | 59.5 | 0.489 | 2019
EI_2019-04-14_231904 | 2019-04-14 19:19 | 2019-04-14 19:19 | EDT | 2019-04-14 23:19 | 817 | 60.001 | 59.958 | 59.953 | -0.043 | -0.048 | -1900 | -1702.0833 | Yes | Yes | 59.5 | 0.453 | 2019
EI_2019-04-15_172546 | 2019-04-15 13:26 | 2019-04-15 13:26 | EDT | 2019-04-15 17:26 | 0 | 60.008 | 59.962 | 59.974 | -0.046 | -0.034 |  |  | No | No | 59.5 | 0.474 | 2019
EI_2019-04-17_133006 | 2019-04-17 09:30 | 2019-04-17 09:30 | EDT | 2019-04-17 13:30 | 0 | 60.003 | 59.965 | 59.972 | -0.038 | -0.031 |  |  | No | No | 59.5 | 0.472 | 2019
EI_2019-04-20_032126 | 2019-04-19 23:21 | 2019-04-19 23:21 | EDT | 2019-04-20 03:21 | 0 | 60.016 | 59.977 | 59.984 | -0.039 | -0.032 |  |  | No | No | 59.5 | 0.484 | 2019
EI_2019-04-21_040926 | 2019-04-21 00:09 | 2019-04-21 00:09 | EDT | 2019-04-21 04:09 | 0 | 60.011 | 59.975 | 59.977 | -0.036 | -0.034 |  |  | No | No | 59.5 | 0.477 | 2019
EI_2019-04-21_052218 | 2019-04-21 01:22 | 2019-04-21 01:22 | EDT | 2019-04-21 05:22 | 0 | 60.004 | 59.961 | 59.96 | -0.043 | -0.044 |  |  | No | No | 59.5 | 0.46 | 2019
EI_2019-04-21_175809 | 2019-04-21 13:58 | 2019-04-21 13:58 | EDT | 2019-04-21 17:58 | 944.1 | 60.011 | 59.958 | 59.953 | -0.053 | -0.058 | -1781.3208 | -1627.7586 | Yes | Yes | 59.5 | 0.453 | 2019
EI_2019-04-22_030700 | 2019-04-21 23:07 | 2019-04-21 23:07 | EDT | 2019-04-22 03:07 | 0 | 59.979 | 59.95 | 59.94 | -0.029 | -0.039 |  |  | No | No | 59.5 | 0.44 | 2019
EI_2019-04-23_040410 | 2019-04-23 00:04 | 2019-04-23 00:04 | EDT | 2019-04-23 04:04 | 0 | 60.015 | 59.976 | 59.978 | -0.039 | -0.037 |  |  | No | No | 59.5 | 0.478 | 2019
EI_2019-04-23_231610 | 2019-04-23 19:16 | 2019-04-23 19:16 | EDT | 2019-04-23 23:16 | 0 | 60.022 | 59.975 | 59.975 | -0.047 | -0.047 |  |  | No | No | 59.5 | 0.475 | 2019
EI_2019-04-24_065200 | 2019-04-24 02:52 | 2019-04-24 02:52 | EDT | 2019-04-24 06:52 | 691.2 | 60.019 | 59.969 | 59.964 | -0.05 | -0.055 | -1382.4 | -1256.7273 | Yes | No | 59.5 | 0.464 | 2019
EI_2019-04-24_182930 | 2019-04-24 14:30 | 2019-04-24 14:30 | EDT | 2019-04-24 18:30 | 987 | 60.002 | 59.959 | 59.963 | -0.043 | -0.039 | -2295.3488 | -2530.7692 | No | No | 59.5 | 0.463 | 2019
EI_2019-04-25_131843 | 2019-04-25 09:19 | 2019-04-25 09:19 | EDT | 2019-04-25 13:19 | 1000 | 60.011 | 59.96 | 59.949 | -0.051 | -0.062 | -1960.7843 | -1612.9032 | Yes | Yes | 59.5 | 0.449 | 2019
EI_2019-05-03_084232 | 2019-05-03 04:43 | 2019-05-03 04:43 | EDT | 2019-05-03 08:43 | 760 | 60.009 | 59.967 | 59.962 | -0.042 | -0.047 | -1809.5238 | -1617.0213 | Yes | No | 59.5 | 0.462 | 2019
EI_2019-05-03_195408 | 2019-05-03 15:54 | 2019-05-03 15:54 | EDT | 2019-05-03 19:54 | 1224 | 60.003 | 59.953 | 59.948 | -0.05 | -0.055 | -2448 | -2225.4545 | Yes | Yes | 59.5 | 0.448 | 2019
EI_2019-05-09_084812 | 2019-05-09 04:48 | 2019-05-09 04:48 | EDT | 2019-05-09 08:48 | 956 | 59.996 | 59.962 | 59.945 | -0.034 | -0.051 | -2811.7647 | -1874.5098 | Yes | Yes | 59.5 | 0.445 | 2019
EI_2019-05-22_063333 | 2019-05-22 02:34 | 2019-05-22 02:34 | EDT | 2019-05-22 06:34 | 1082 | 60.029 | 59.964 | 59.966 | -0.065 | -0.063 | -1664.6154 | -1717.4603 | Yes | No | 59.5 | 0.466 | 2019
EI_2019-05-26_003813 | 2019-05-25 20:38 | 2019-05-25 20:38 | EDT | 2019-05-26 00:38 | 845 | 60.004 | 59.963 | 59.954 | -0.041 | -0.05 | -2060.9756 | -1690 | Yes | Yes | 59.5 | 0.454 | 2019
EI_2019-05-26_101230 | 2019-05-26 06:12 | 2019-05-26 06:12 | EDT | 2019-05-26 10:12 | 1020.2 | 59.986 | 59.962 | 59.953 | -0.024 | -0.033 | -4250.8333 | -3091.5152 | Yes | No | 59.5 | 0.453 | 2019
EI_2019-05-31_202940 | 2019-05-31 16:30 | 2019-05-31 16:30 | EDT | 2019-05-31 20:30 | 587 | 59.994 | 59.959 | 59.955 | -0.035 | -0.039 | -1677.1429 | -1505.1282 | Yes | No | 59.5 | 0.455 | 2019
EI_2019-06-01_025223 | 2019-05-31 22:52 | 2019-05-31 22:52 | EDT | 2019-06-01 02:52 | 0 | 60.015 | 59.969 | 59.984 | -0.046 | -0.031 |  |  | No | No | 59.5 | 0.484 | 2019
EI_2019-06-02_190747 | 2019-06-02 15:08 | 2019-06-02 15:08 | EDT | 2019-06-02 19:08 | 716 | 60.031 | 59.977 | 59.982 | -0.054 | -0.049 | -1325.9259 | -1461.2245 | Yes | No | 59.5 | 0.482 | 2019
EI_2019-06-03_042440 | 2019-06-03 00:25 | 2019-06-03 00:25 | EDT | 2019-06-03 04:25 | 0 | 60.028 | 59.98 | 60.02 | -0.048 | -0.008 |  |  | No | No | 59.5 | 0.52 | 2019
EI_2019-06-04_054451 | 2019-06-04 01:45 | 2019-06-04 01:45 | EDT | 2019-06-04 05:45 | 1180 | 60.029 | 59.997 | 60.008 | -0.032 | -0.021 | -3687.5 | -5619.0476 | No | No | 59.5 | 0.508 | 2019
EI_2019-06-06_044335 | 2019-06-06 00:44 | 2019-06-06 00:44 | EDT | 2019-06-06 04:44 | 846 | 60.013 | 59.976 | 59.98 | -0.037 | -0.033 | -2286.4865 | -2563.6364 | No | No | 59.5 | 0.48 | 2019
EI_2019-06-11_132840 | 2019-06-11 09:29 | 2019-06-11 09:29 | EDT | 2019-06-11 13:29 | 850 | 59.992 | 59.964 | 59.957 | -0.028 | -0.035 | -3035.7143 | -2428.5714 | Yes | No | 59.5 | 0.457 | 2019
EI_2019-06-17_114234 | 2019-06-17 07:43 | 2019-06-17 07:43 | EDT | 2019-06-17 11:43 | 652.3 | 60.006 | 59.965 | 59.961 | -0.041 | -0.045 | -1590.9756 | -1449.5556 | Yes | No | 59.5 | 0.461 | 2019
EI_2019-06-19_154140 | 2019-06-19 11:42 | 2019-06-19 11:42 | EDT | 2019-06-19 15:42 | 704.3 | 60.009 | 59.972 | 59.972 | -0.037 | -0.037 | -1903.5135 | -1903.5135 | No | No | 59.5 | 0.472 | 2019
EI_2019-06-22_005304 | 2019-06-21 20:53 | 2019-06-21 20:53 | EDT | 2019-06-22 00:53 | 0 | 60.02 | 59.978 | 59.978 | -0.042 | -0.042 |  |  | No | No | 59.5 | 0.478 | 2019
EI_2019-07-03_200132 | 2019-07-03 16:02 | 2019-07-03 16:02 | EDT | 2019-07-03 20:02 | 848.6 | 59.978 | 59.962 | 59.958 | -0.016 | -0.02 | -5303.75 | -4243 | No | No | 59.5 | 0.458 | 2019
EI_2019-07-05_200030 | 2019-07-05 16:01 | 2019-07-05 16:01 | EDT | 2019-07-05 20:01 | 850 | 60.006 | 59.975 | 59.976 | -0.031 | -0.03 | -2741.9355 | -2833.3333 | Yes | No | 59.5 | 0.476 | 2019
EI_2019-07-08_155557 | 2019-07-08 11:56 | 2019-07-08 11:56 | EDT | 2019-07-08 15:56 | 525.3 | 60.012 | 59.969 | 59.972 | -0.043 | -0.04 | -1221.6279 | -1313.25 | Yes | No | 59.5 | 0.472 | 2019
EI_2019-07-11_154904 | 2019-07-11 11:49 | 2019-07-11 11:49 | EDT | 2019-07-11 15:49 | 825 | 60.01 | 59.969 | 59.964 | -0.041 | -0.046 | -2012.1951 | -1793.4783 | Yes | No | 59.5 | 0.464 | 2019
EI_2019-07-11_180557 | 2019-07-11 14:06 | 2019-07-11 14:06 | EDT | 2019-07-11 18:06 | 915.2 | 60.003 | 59.979 | 59.972 | -0.024 | -0.031 | -3813.3333 | -2952.2581 | Yes | No | 59.5 | 0.472 | 2019
EI_2019-07-12_004514 | 2019-07-11 20:45 | 2019-07-11 20:45 | EDT | 2019-07-12 00:45 | 1493 | 59.999 | 59.948 | 59.946 | -0.051 | -0.053 | -2927.451 | -2816.9811 | Yes | Yes | 59.5 | 0.446 | 2019
EI_2019-07-19_134539 | 2019-07-19 09:46 | 2019-07-19 09:46 | EDT | 2019-07-19 13:46 | 1211 | 60.01 | 59.957 | 59.955 | -0.053 | -0.055 | -2284.9057 | -2201.8182 | Yes | Yes | 59.5 | 0.455 | 2019
EI_2019-07-25_130430 | 2019-07-25 09:05 | 2019-07-25 09:05 | EDT | 2019-07-25 13:04 | 0 | 60.008 | 59.968 | 59.967 | -0.04 | -0.041 |  |  | No | No | 59.5 | 0.467 | 2019
EI_2019-07-26_221105 | 2019-07-26 18:11 | 2019-07-26 18:11 | EDT | 2019-07-26 22:11 | 0 | 59.987 | 59.956 | 59.943 | -0.031 | -0.044 |  |  | No | No | 59.5 | 0.443 | 2019
EI_2019-07-27_233004 | 2019-07-27 19:30 | 2019-07-27 19:30 | EDT | 2019-07-27 23:30 | 1249 | 60.004 | 59.961 | 59.956 | -0.043 | -0.048 | -2904.6512 | -2602.0833 | Yes | Yes | 59.5 | 0.456 | 2019
EI_2019-07-31_180557 | 2019-07-31 14:06 | 2019-07-31 14:06 | EDT | 2019-07-31 18:06 | 511.7 | 60.02 | 59.974 | 59.985 | -0.046 | -0.035 | -1112.3913 | -1462 | No | No | 59.5 | 0.485 | 2019
EI_2019-08-03_072710 | 2019-08-03 03:27 | 2019-08-03 03:27 | EDT | 2019-08-03 07:27 | 1070.6 | 60.017 | 59.961 | 59.975 | -0.056 | -0.042 | -1911.7857 | -2549.0476 | Yes | No | 59.5 | 0.475 | 2019
EI_2019-08-03_151219 | 2019-08-03 11:12 | 2019-08-03 11:12 | EDT | 2019-08-03 15:12 | 785 | 60.01 | 59.966 | 59.967 | -0.044 | -0.043 | -1784.0909 | -1825.5814 | Yes | No | 59.5 | 0.467 | 2019
EI_2019-08-11_121322 | 2019-08-11 08:13 | 2019-08-11 08:13 | EDT | 2019-08-11 12:13 | 645 | 60.006 | 59.955 | 59.966 | -0.051 | -0.04 | -1264.7059 | -1612.5 | Yes | No | 59.5 | 0.466 | 2019
EI_2019-08-11_121358 | 2019-08-11 08:14 | 2019-08-11 08:14 | EDT | 2019-08-11 12:14 | 950 | 59.965 | 59.949 | 59.937 | -0.016 | -0.028 | -5937.5 | -3392.8571 | No | No | 59.5 | 0.437 | 2019
EI_2019-08-12_165559 | 2019-08-12 12:56 | 2019-08-12 12:56 | EDT | 2019-08-12 16:56 | 434.8 | 60.01 | 59.973 | 59.978 | -0.037 | -0.032 | -1175.1351 | -1358.75 | No | No | 59.5 | 0.478 | 2019
EI_2019-08-20_164845 | 2019-08-20 12:49 | 2019-08-20 12:49 | EDT | 2019-08-20 16:49 | 852 | 60.026 | 60.005 | 59.997 | -0.021 | -0.029 | -4057.1429 | -2937.931 | No | No | 59.5 | 0.497 | 2019
EI_2019-08-21_122939 | 2019-08-21 08:30 | 2019-08-21 08:30 | EDT | 2019-08-21 12:30 | 486 | 59.999 | 59.967 | 59.966 | -0.032 | -0.033 | -1518.75 | -1472.7273 | No | No | 59.5 | 0.466 | 2019
EI_2019-08-25_160401 | 2019-08-25 12:04 | 2019-08-25 12:04 | EDT | 2019-08-25 16:04 | 915 | 60.006 | 59.957 | 59.956 | -0.049 | -0.05 | -1867.3469 | -1830 | Yes | Yes | 59.5 | 0.456 | 2019
EI_2019-08-26_141550 | 2019-08-26 10:16 | 2019-08-26 10:16 | EDT | 2019-08-26 14:16 | 689 | 60.028 | 59.97 | 59.983 | -0.058 | -0.045 | -1187.931 | -1531.1111 | Yes | No | 59.5 | 0.483 | 2019
EI_2019-08-27_051029 | 2019-08-27 01:10 | 2019-08-27 01:10 | EDT | 2019-08-27 05:10 | 1125 | 59.974 | 59.944 | 59.934 | -0.03 | -0.04 | -3750 | -2812.5 | Yes | Yes | 59.5 | 0.434 | 2019
EI_2019-08-29_100532 | 2019-08-29 06:06 | 2019-08-29 06:06 | EDT | 2019-08-29 10:06 | -1 | 59.997 | 60.05 | 60.041 | 0.053 | 0.044 | -1.8868 | -2.2727 | No | No | 59.5 | 0.541 | 2019
EI_2019-08-31_161055 | 2019-08-31 12:11 | 2019-08-31 12:11 | EDT | 2019-08-31 16:11 | 0 | 59.995 | 59.946 | 59.966 | -0.049 | -0.029 |  |  | No | No | 59.5 | 0.466 | 2019
EI_2019-09-01_005544 | 2019-08-31 20:56 | 2019-08-31 20:56 | EDT | 2019-09-01 00:56 | 1146 | 60.008 | 59.964 | 59.953 | -0.044 | -0.055 | -2604.5455 | -2083.6364 | Yes | Yes | 59.5 | 0.453 | 2019
EI_2019-09-02_050005 | 2019-09-02 01:00 | 2019-09-02 01:00 | EDT | 2019-09-02 05:00 | 0 | 59.996 | 59.956 | 59.974 | -0.04 | -0.022 |  |  | No | No | 59.5 | 0.474 | 2019
EI_2019-09-03_133529 | 2019-09-03 09:35 | 2019-09-03 09:35 | EDT | 2019-09-03 13:35 | 1208 | 59.98 | 59.95 | 59.94 | -0.03 | -0.04 | -4026.6667 | -3020 | Yes | Yes | 59.5 | 0.44 | 2019
EI_2019-09-04_040821 | 2019-09-04 00:08 | 2019-09-04 00:08 | EDT | 2019-09-04 04:08 | 0 | 60.018 | 59.981 | 59.98 | -0.037 | -0.038 |  |  | No | No | 59.5 | 0.48 | 2019
EI_2019-09-11_053932 | 2019-09-11 01:40 | 2019-09-11 01:40 | EDT | 2019-09-11 05:40 | 0 | 60.016 | 59.968 | 59.963 | -0.048 | -0.053 |  |  | No | No | 59.5 | 0.463 | 2019
EI_2019-09-12_160048 | 2019-09-12 12:01 | 2019-09-12 12:01 | EDT | 2019-09-12 16:01 | 0 | 59.993 | 59.966 | 59.954 | -0.027 | -0.039 |  |  | No | No | 59.5 | 0.454 | 2019
EI_2019-09-16_022055 | 2019-09-15 22:21 | 2019-09-15 22:21 | EDT | 2019-09-16 02:21 | 0 | 60.02 | 59.966 | 59.99 | -0.054 | -0.03 |  |  | No | No | 59.5 | 0.49 | 2019
EI_2019-09-21_130019 | 2019-09-21 09:00 | 2019-09-21 09:00 | EDT | 2019-09-21 13:00 | 930 | 60.003 | 59.957 | 59.951 | -0.046 | -0.052 | -2021.7391 | -1788.4615 | Yes | Yes | 59.5 | 0.451 | 2019
EI_2019-09-21_223258 | 2019-09-21 18:33 | 2019-09-21 18:33 | EDT | 2019-09-21 22:33 | 714 | 60.01 | 59.977 | 59.967 | -0.033 | -0.043 | -2163.6364 | -1660.4651 | Yes | No | 59.5 | 0.467 | 2019
EI_2019-09-23_160602 | 2019-09-23 12:06 | 2019-09-23 12:06 | EDT | 2019-09-23 16:06 | 1250 | 59.985 | 59.947 | 59.937 | -0.038 | -0.048 | -3289.4737 | -2604.1667 | Yes | Yes | 59.5 | 0.437 | 2019
EI_2019-10-07_022048 | 2019-10-06 22:21 | 2019-10-06 22:21 | EDT | 2019-10-07 02:21 | 501 | 60.011 | 59.981 | 59.976 | -0.03 | -0.035 | -1670 | -1431.4286 | No | No | 59.5 | 0.476 | 2019
EI_2019-10-10_103941 | 2019-10-10 06:40 | 2019-10-10 06:40 | EDT | 2019-10-10 10:40 | 703.6 | 59.993 | 59.962 | 59.959 | -0.031 | -0.034 | -2269.6774 | -2069.4118 | No | No | 59.5 | 0.459 | 2019
EI_2019-10-10_192833 | 2019-10-10 15:29 | 2019-10-10 15:29 | EDT | 2019-10-10 19:29 | 630 | 59.999 | 59.961 | 59.962 | -0.038 | -0.037 | -1657.8947 | -1702.7027 | Yes | No | 59.5 | 0.462 | 2019
EI_2019-10-14_232147 | 2019-10-14 19:22 | 2019-10-14 19:22 | EDT | 2019-10-14 23:22 | 779 | 59.985 | 59.952 | 59.943 | -0.033 | -0.042 | -2360.6061 | -1854.7619 | Yes | Yes | 59.5 | 0.443 | 2019
EI_2019-10-16_053504 | 2019-10-16 01:35 | 2019-10-16 01:35 | EDT | 2019-10-16 05:35 | 0 | 59.999 | 59.962 | 59.97 | -0.037 | -0.029 |  |  | No | No | 59.5 | 0.47 | 2019
EI_2019-10-18_112712 | 2019-10-18 07:27 | 2019-10-18 07:27 | EDT | 2019-10-18 11:27 | -1 | 59.984 | 60.032 | 59.993 | 0.048 | 0.009 | -2.0833 | -11.1111 | No | No | 59.5 | 0.493 | 2019
EI_2019-10-19_045958 | 2019-10-19 01:00 | 2019-10-19 01:00 | EDT | 2019-10-19 05:00 | 0 | 60.005 | 59.961 | 59.968 | -0.044 | -0.037 |  |  | No | No | 59.5 | 0.468 | 2019
EI_2019-10-19_164241 | 2019-10-19 12:43 | 2019-10-19 12:43 | EDT | 2019-10-19 16:43 | 535.9 | 59.995 | 59.972 | 59.958 | -0.023 | -0.037 | -2330 | -1448.3784 | Yes | No | 59.5 | 0.458 | 2019
EI_2019-10-19_192243 | 2019-10-19 15:23 | 2019-10-19 15:23 | EDT | 2019-10-19 19:23 | 0 | 60.014 | 59.964 | 59.968 | -0.05 | -0.046 |  |  | No | No | 59.5 | 0.468 | 2019
EI_2019-10-19_215917 | 2019-10-19 17:59 | 2019-10-19 17:59 | EDT | 2019-10-19 21:59 | 493.2 | 60.011 | 59.978 | 59.969 | -0.033 | -0.042 | -1494.5455 | -1174.2857 | Yes | No | 59.5 | 0.469 | 2019
EI_2019-10-20_114957 | 2019-10-20 07:50 | 2019-10-20 07:50 | EDT | 2019-10-20 11:50 | -1 | 60.004 | 60.041 | 60.051 | 0.037 | 0.047 | -2.7027 | -2.1277 | No | No | 59.5 | 0.551 | 2019
EI_2019-10-23_050947 | 2019-10-23 01:10 | 2019-10-23 01:10 | EDT | 2019-10-23 05:10 | 334 | 60.017 | 59.968 | 59.974 | -0.049 | -0.043 | -681.6327 | -776.7442 | No | No | 59.5 | 0.474 | 2019
EI_2019-10-26_125758 | 2019-10-26 08:58 | 2019-10-26 08:58 | EDT | 2019-10-26 12:58 | 0 | 60.018 | 59.976 | 59.97 | -0.042 | -0.048 |  |  | No | No | 59.5 | 0.47 | 2019
EI_2019-11-03_043053 | 2019-11-02 23:31 | 2019-11-02 23:31 | EST | 2019-11-03 04:31 | 497 | 60.021 | 59.977 | 59.983 | -0.044 | -0.038 | -1129.5455 | -1307.8947 | No | No | 59.5 | 0.483 | 2019
EI_2019-11-04_041730 | 2019-11-03 23:18 | 2019-11-03 23:18 | EST | 2019-11-04 04:18 | 0 | 60.002 | 59.96 | 59.963 | -0.042 | -0.039 |  |  | No | No | 59.5 | 0.463 | 2019
EI_2019-11-08_212734 | 2019-11-08 16:28 | 2019-11-08 16:28 | EST | 2019-11-08 21:28 | 0 | 60.007 | 59.96 | 59.972 | -0.047 | -0.035 |  |  | No | No | 59.5 | 0.472 | 2019
EI_2019-11-24_015612 | 2019-11-23 20:56 | 2019-11-23 20:56 | EST | 2019-11-24 01:56 | 0 | 60.014 | 59.965 | 59.966 | -0.049 | -0.048 |  |  | No | No | 59.5 | 0.466 | 2019
EI_2019-11-25_102956 | 2019-11-25 05:30 | 2019-11-25 05:30 | EST | 2019-11-25 10:30 | 90 | 60.004 | 59.966 | 59.964 | -0.038 | -0.04 | -236.8421 | -225 | No | No | 59.5 | 0.464 | 2019
EI_2019-11-26_130904 | 2019-11-26 08:09 | 2019-11-26 08:09 | EST | 2019-11-26 13:09 | 720 | 60.022 | 59.977 | 59.983 | -0.045 | -0.039 | -1600 | -1846.1538 | Yes | No | 59.5 | 0.483 | 2019
EI_2019-11-30_123855 | 2019-11-30 07:39 | 2019-11-30 07:39 | EST | 2019-11-30 12:39 | 844.5 | 59.99 | 59.957 | 59.954 | -0.033 | -0.036 | -2559.0909 | -2345.8333 | Yes | No | 59.5 | 0.454 | 2019
EI_2019-12-03_090026 | 2019-12-03 04:00 | 2019-12-03 04:00 | EST | 2019-12-03 09:00 | 0 | 60.019 | 59.966 | 59.988 | -0.053 | -0.031 |  |  | No | No | 59.5 | 0.488 | 2020
EI_2019-12-03_152201 | 2019-12-03 10:22 | 2019-12-03 10:22 | EST | 2019-12-03 15:22 | 540 | 60.015 | 59.973 | 59.974 | -0.042 | -0.041 | -1285.7143 | -1317.0732 | No | No | 59.5 | 0.474 | 2020
EI_2019-12-07_100019 | 2019-12-07 05:00 | 2019-12-07 05:00 | EST | 2019-12-07 10:00 | 550 | 60.025 | 59.971 | 59.985 | -0.054 | -0.04 | -1018.5185 | -1375 | No | No | 59.5 | 0.485 | 2020
EI_2019-12-07_163435 | 2019-12-07 11:35 | 2019-12-07 11:35 | EST | 2019-12-07 16:35 | 805 | 60.015 | 59.982 | 59.971 | -0.033 | -0.044 | -2439.3939 | -1829.5455 | Yes | No | 59.5 | 0.471 | 2020
EI_2019-12-09_123935 | 2019-12-09 07:40 | 2019-12-09 07:40 | EST | 2019-12-09 12:40 | 511 | 60.019 | 59.983 | 59.974 | -0.036 | -0.045 | -1419.4444 | -1135.5556 | Yes | No | 59.5 | 0.474 | 2020
EI_2019-12-11_030132 | 2019-12-10 22:02 | 2019-12-10 22:02 | EST | 2019-12-11 03:02 | 400 | 60.016 | 59.979 | 59.977 | -0.037 | -0.039 | -1081.0811 | -1025.641 | No | No | 59.5 | 0.477 | 2020
EI_2019-12-11_210442 | 2019-12-11 16:05 | 2019-12-11 16:05 | EST | 2019-12-11 21:05 | 1283 | 60.016 | 59.959 | 59.953 | -0.057 | -0.063 | -2250.8772 | -2036.5079 | Yes | Yes | 59.5 | 0.453 | 2020
EI_2019-12-12_093359 | 2019-12-12 04:34 | 2019-12-12 04:34 | EST | 2019-12-12 09:34 | 1200 | 59.978 | 59.952 | 59.952 | -0.026 | -0.026 | -4615.3846 | -4615.3846 | Yes | No | 59.5 | 0.452 | 2020
EI_2019-12-19_044658 | 2019-12-18 23:47 | 2019-12-18 23:47 | EST | 2019-12-19 04:47 | 886 | 60 | 59.967 | 59.971 | -0.033 | -0.029 | -2684.8485 | -3055.1724 | Yes | No | 59.5 | 0.471 | 2020
EI_2019-12-19_181323 | 2019-12-19 13:13 | 2019-12-19 13:13 | EST | 2019-12-19 18:13 | 500 | 60.021 | 59.994 | 59.992 | -0.027 | -0.029 | -1851.8519 | -1724.1379 | No | No | 59.5 | 0.492 | 2020
EI_2019-12-23_040530 | 2019-12-22 23:06 | 2019-12-22 23:06 | EST | 2019-12-23 04:06 | 0 | 60.013 | 59.965 | 59.978 | -0.048 | -0.035 |  |  | No | No | 59.5 | 0.478 | 2020
EI_2019-12-27_002058 | 2019-12-26 19:21 | 2019-12-26 19:21 | EST | 2019-12-27 00:21 | 486 | 60.013 | 59.976 | 59.978 | -0.037 | -0.035 | -1313.5135 | -1388.5714 | No | No | 59.5 | 0.478 | 2020
EI_2019-12-27_120447 | 2019-12-27 07:05 | 2019-12-27 07:05 | EST | 2019-12-27 12:05 | 0 | 60.008 | 59.967 | 59.955 | -0.041 | -0.053 |  |  | No | No | 59.5 | 0.455 | 2020
EI_2020-01-04_200130 | 2020-01-04 15:01 | 2020-01-04 15:01 | EST | 2020-01-04 20:02 | 384 | 60.01 | 59.977 | 59.974 | -0.033 | -0.036 | -1163.6364 | -1066.6667 | No | No | 59.5 | 0.474 | 2020
EI_2020-01-09_060013 | 2020-01-09 01:00 | 2020-01-09 01:00 | EST | 2020-01-09 06:00 | 707.2 | 59.98 | 59.968 | 59.959 | -0.012 | -0.021 | -5893.3333 | -3367.619 | No | No | 59.5 | 0.459 | 2020
EI_2020-01-10_192803 | 2020-01-10 14:28 | 2020-01-10 14:28 | EST | 2020-01-10 19:28 | 540 | 60.028 | 59.993 | 59.993 | -0.035 | -0.035 | -1542.8571 | -1542.8571 | No | No | 59.5 | 0.493 | 2020
EI_2020-01-16_194626 | 2020-01-16 14:46 | 2020-01-16 14:46 | EST | 2020-01-16 19:46 | 533 | 60.016 | 59.969 | 59.976 | -0.047 | -0.04 | -1134.0426 | -1332.5 | No | No | 59.5 | 0.476 | 2020
EI_2020-01-20_000129 | 2020-01-19 19:01 | 2020-01-19 19:01 | EST | 2020-01-20 00:01 | 716.8 | 60.025 | 59.984 | 59.988 | -0.041 | -0.037 | -1748.2927 | -1937.2973 | No | No | 59.5 | 0.488 | 2020
EI_2020-01-20_140451 | 2020-01-20 09:05 | 2020-01-20 09:05 | EST | 2020-01-20 14:05 | 1090 | 59.989 | 59.958 | 59.948 | -0.031 | -0.041 | -3516.129 | -2658.5366 | Yes | Yes | 59.5 | 0.448 | 2020
EI_2020-01-21_174659 | 2020-01-21 12:47 | 2020-01-21 12:47 | EST | 2020-01-21 17:47 | 0 | 60.012 | 59.968 | 59.975 | -0.044 | -0.037 |  |  | No | No | 59.5 | 0.475 | 2020
EI_2020-01-27_090011 | 2020-01-27 04:00 | 2020-01-27 04:00 | EST | 2020-01-27 09:00 | -1 | 59.99 | 60.034 | 59.998 | 0.044 | 0.008 | -2.2727 | -12.5 | No | No | 59.5 | 0.498 | 2020
EI_2020-01-28_161933 | 2020-01-28 11:20 | 2020-01-28 11:20 | EST | 2020-01-28 16:20 | 0 | 60.01 | 59.964 | 59.969 | -0.046 | -0.041 |  |  | No | No | 59.5 | 0.469 | 2020
EI_2020-01-29_050024 | 2020-01-29 | 2020-01-29 | EST | 2020-01-29 05:00 | 0 | 60.014 | 59.97 | 59.974 | -0.044 | -0.04 |  |  | No | No | 59.5 | 0.474 | 2020
EI_2020-02-05_091601 | 2020-02-05 04:16 | 2020-02-05 04:16 | EST | 2020-02-05 09:16 | 857 | 59.987 | 59.955 | 59.951 | -0.032 | -0.036 | -2678.125 | -2380.5556 | Yes | No | 59.5 | 0.451 | 2020
EI_2020-02-08_034207 | 2020-02-07 22:42 | 2020-02-07 22:42 | EST | 2020-02-08 03:42 | 1450 | 59.99 | 59.949 | 59.936 | -0.041 | -0.054 | -3536.5854 | -2685.1852 | Yes | Yes | 59.5 | 0.436 | 2020
EI_2020-02-09_075854 | 2020-02-09 02:59 | 2020-02-09 02:59 | EST | 2020-02-09 07:59 | 419.3 | 60.013 | 59.97 | 59.976 | -0.043 | -0.037 | -975.1163 | -1133.2432 | No | No | 59.5 | 0.476 | 2020
EI_2020-02-10_183113 | 2020-02-10 13:31 | 2020-02-10 13:31 | EST | 2020-02-10 18:31 | 1600 | 59.999 | 59.942 | 59.932 | -0.057 | -0.067 | -2807.0175 | -2388.0597 | Yes | Yes | 59.5 | 0.432 | 2020
EI_2020-02-10_201414 | 2020-02-10 15:14 | 2020-02-10 15:14 | EST | 2020-02-10 20:14 | 900 | 60.008 | 59.952 | 59.955 | -0.056 | -0.053 | -1607.1429 | -1698.1132 | Yes | Yes | 59.5 | 0.455 | 2020
EI_2020-02-12_230012 | 2020-02-12 18:00 | 2020-02-12 18:00 | EST | 2020-02-12 23:00 | 1239 | 60.003 | 59.944 | 59.951 | -0.059 | -0.052 | -2100 | -2382.6923 | Yes | Yes | 59.5 | 0.451 | 2020
EI_2020-02-17_171112 | 2020-02-17 12:11 | 2020-02-17 12:11 | EST | 2020-02-17 17:11 | 694 | 60.021 | 59.96 | 59.998 | -0.061 | -0.023 | -1137.7049 | -3017.3913 | No | No | 59.5 | 0.498 | 2020
EI_2020-02-18_111558 | 2020-02-18 06:16 | 2020-02-18 06:16 | EST | 2020-02-18 11:16 | 1136 | 59.996 | 59.966 | 59.952 | -0.03 | -0.044 | -3786.6667 | -2581.8182 | Yes | Yes | 59.5 | 0.452 | 2020
EI_2020-02-19_105901 | 2020-02-19 05:59 | 2020-02-19 05:59 | EST | 2020-02-19 10:59 | 856.3 | 60.038 | 60.023 | 60.02 | -0.015 | -0.018 | -5708.6667 | -4757.2222 | No | No | 59.5 | 0.52 | 2020
EI_2020-02-19_143607 | 2020-02-19 09:36 | 2020-02-19 09:36 | EST | 2020-02-19 14:36 | 1180 | 60 | 59.961 | 59.948 | -0.039 | -0.052 | -3025.641 | -2269.2308 | Yes | Yes | 59.5 | 0.448 | 2020
EI_2020-02-25_165307 | 2020-02-25 11:53 | 2020-02-25 11:53 | EST | 2020-02-25 16:53 | 737 | 60.006 | 59.973 | 59.963 | -0.033 | -0.043 | -2233.3333 | -1713.9535 | Yes | No | 59.5 | 0.463 | 2020
EI_2020-03-02_034053 | 2020-03-01 22:41 | 2020-03-01 22:41 | EST | 2020-03-02 03:41 | 0 | 60.013 | 59.972 | 59.972 | -0.041 | -0.041 |  |  | No | No | 59.5 | 0.472 | 2020
EI_2020-03-03_023404 | 2020-03-02 21:34 | 2020-03-02 21:34 | EST | 2020-03-03 02:34 | 818 | 59.999 | 59.967 | 59.954 | -0.032 | -0.045 | -2556.25 | -1817.7778 | Yes | Yes | 59.5 | 0.454 | 2020
EI_2020-03-04_025502 | 2020-03-03 21:55 | 2020-03-03 21:55 | EST | 2020-03-04 02:55 | 0 | 60.015 | 59.974 | 59.977 | -0.041 | -0.038 |  |  | No | No | 59.5 | 0.477 | 2020
EI_2020-03-04_170515 | 2020-03-04 12:05 | 2020-03-04 12:05 | EST | 2020-03-04 17:05 | 0 | 59.977 | 59.953 | 59.944 | -0.024 | -0.033 |  |  | No | No | 59.5 | 0.444 | 2020
EI_2020-03-08_050028 | 2020-03-08 01:00 | 2020-03-08 01:00 | EDT | 2020-03-08 05:00 | 0 | 60.012 | 59.959 | 59.988 | -0.053 | -0.024 |  |  | No | No | 59.5 | 0.488 | 2020
EI_2020-03-09_132906 | 2020-03-09 09:29 | 2020-03-09 09:29 | EDT | 2020-03-09 13:29 | 0 | 60.016 | 59.978 | 59.991 | -0.038 | -0.025 |  |  | No | No | 59.5 | 0.491 | 2020
EI_2020-03-19_183914 | 2020-03-19 14:39 | 2020-03-19 14:39 | EDT | 2020-03-19 18:39 | 0 | 60.017 | 59.966 | 59.979 | -0.051 | -0.038 |  |  | No | No | 59.5 | 0.479 | 2020
EI_2020-03-23_141206 | 2020-03-23 10:12 | 2020-03-23 10:12 | EDT | 2020-03-23 14:12 | 1106 | 60.025 | 59.948 | 59.952 | -0.077 | -0.073 | -1436.3636 | -1515.0685 | Yes | Yes | 59.5 | 0.452 | 2020
EI_2020-03-25_123515 | 2020-03-25 08:35 | 2020-03-25 08:35 | EDT | 2020-03-25 12:35 | 0 | 60.025 | 59.968 | 59.971 | -0.057 | -0.054 |  |  | No | No | 59.5 | 0.471 | 2020
EI_2020-03-27_231709 | 2020-03-27 19:17 | 2020-03-27 19:17 | EDT | 2020-03-27 23:17 | 0 | 60.002 | 59.963 | 59.952 | -0.039 | -0.05 |  |  | No | Yes | 59.5 | 0.452 | 2020
EI_2020-04-01_202444 | 2020-04-01 16:25 | 2020-04-01 16:25 | EDT | 2020-04-01 20:25 | 1229 | 59.976 | 59.945 | 59.933 | -0.031 | -0.043 | -3964.5161 | -2858.1395 | Yes | Yes | 59.5 | 0.433 | 2020
EI_2020-04-04_061649 | 2020-04-04 02:17 | 2020-04-04 02:17 | EDT | 2020-04-04 06:17 | 1306 | 60.005 | 59.941 | 59.937 | -0.064 | -0.068 | -2040.625 | -1920.5882 | Yes | Yes | 59.5 | 0.437 | 2020
EI_2020-04-04_172244 | 2020-04-04 13:23 | 2020-04-04 13:23 | EDT | 2020-04-04 17:23 | 0 | 59.984 | 59.957 | 59.952 | -0.027 | -0.032 |  |  | No | No | 59.5 | 0.452 | 2020
EI_2020-04-06_023702 | 2020-04-05 22:37 | 2020-04-05 22:37 | EDT | 2020-04-06 02:37 | 0 | 60.022 | 59.992 | 59.984 | -0.03 | -0.038 |  |  | No | No | 59.5 | 0.484 | 2020
EI_2020-04-06_162216 | 2020-04-06 12:22 | 2020-04-06 12:22 | EDT | 2020-04-06 16:22 | 0 | 60.009 | 59.975 | 59.962 | -0.034 | -0.047 |  |  | No | No | 59.5 | 0.462 | 2020
EI_2020-04-13_194952 | 2020-04-13 15:50 | 2020-04-13 15:50 | EDT | 2020-04-13 19:50 | 0 | 60 | 59.949 | 59.949 | -0.051 | -0.051 |  |  | No | Yes | 59.5 | 0.449 | 2020
EI_2020-04-15_150224 | 2020-04-15 11:02 | 2020-04-15 11:02 | EDT | 2020-04-15 15:02 | 533 | 59.984 | 59.959 | 59.953 | -0.025 | -0.031 | -2132 | -1719.3548 | No | No | 59.5 | 0.453 | 2020
EI_2020-04-23_150100 | 2020-04-23 11:01 | 2020-04-23 11:01 | EDT | 2020-04-23 15:01 | 650 | 60.003 | 59.96 | 59.949 | -0.043 | -0.054 | -1511.6279 | -1203.7037 | Yes | Yes | 59.5 | 0.449 | 2020
EI_2020-04-24_192024 | 2020-04-24 15:20 | 2020-04-24 15:20 | EDT | 2020-04-24 19:20 | 0 | 60.005 | 59.971 | 59.96 | -0.034 | -0.045 |  |  | No | No | 59.5 | 0.46 | 2020
EI_2020-04-27_052455 | 2020-04-27 01:25 | 2020-04-27 01:25 | EDT | 2020-04-27 05:25 | 0 | 60.011 | 59.956 | 59.941 | -0.055 | -0.07 |  |  | No | No | 59.5 | 0.441 | 2020
EI_2020-04-28_010451 | 2020-04-27 21:05 | 2020-04-27 21:05 | EDT | 2020-04-28 01:05 | 647 | 59.999 | 59.963 | 59.959 | -0.036 | -0.04 | -1797.2222 | -1617.5 | Yes | Yes | 59.5 | 0.459 | 2020
EI_2020-04-30_211344 | 2020-04-30 17:14 | 2020-04-30 17:14 | EDT | 2020-04-30 21:14 | 0 | 60.016 | 59.973 | 59.96 | -0.043 | -0.056 |  |  | No | No | 59.5 | 0.46 | 2020
EI_2020-04-30_211636 | 2020-04-30 17:17 | 2020-04-30 17:17 | EDT | 2020-04-30 21:17 | 0 | 59.986 | 59.965 | 59.953 | -0.021 | -0.033 |  |  | No | No | 59.5 | 0.453 | 2020
EI_2020-05-03_122134 | 2020-05-03 08:22 | 2020-05-03 08:22 | EDT | 2020-05-03 12:22 | 0 | 60.01 | 59.967 | 59.955 | -0.043 | -0.055 |  |  | No | Yes | 59.5 | 0.455 | 2020
EI_2020-05-05_095946 | 2020-05-05 06:00 | 2020-05-05 06:00 | EDT | 2020-05-05 10:00 | -1 | 60.006 | 60.033 | 60.046 | 0.027 | 0.04 | -3.7037 | -2.5 | No | No | 59.5 | 0.546 | 2020
EI_2020-05-09_134939 | 2020-05-09 09:50 | 2020-05-09 09:50 | EDT | 2020-05-09 13:50 | 0 | 60.018 | 59.966 | 59.969 | -0.052 | -0.049 |  |  | No | No | 59.5 | 0.469 | 2020
EI_2020-05-11_060144 | 2020-05-11 02:02 | 2020-05-11 02:02 | EDT | 2020-05-11 06:02 | 0 | 60.013 | 59.97 | 59.973 | -0.043 | -0.04 |  |  | No | No | 59.5 | 0.473 | 2020
EI_2020-05-17_121923 | 2020-05-17 08:19 | 2020-05-17 08:19 | EDT | 2020-05-17 12:19 | 0 | 60.002 | 59.96 | 59.956 | -0.042 | -0.046 |  |  | No | Yes | 59.5 | 0.456 | 2020
EI_2020-05-25_093320 | 2020-05-25 05:33 | 2020-05-25 05:33 | EDT | 2020-05-25 09:33 | 0 | 59.986 | 59.955 | 59.947 | -0.031 | -0.039 |  |  | No | No | 59.5 | 0.447 | 2020
EI_2020-05-27_184746 | 2020-05-27 14:48 | 2020-05-27 14:48 | EDT | 2020-05-27 18:48 | 1980 | 60.013 | 59.933 | 59.953 | -0.08 | -0.06 | -2475 | -3300 | No | No | 59.5 | 0.453 | 2020
EI_2020-05-28_050929 | 2020-05-28 01:09 | 2020-05-28 01:09 | EDT | 2020-05-28 05:09 | 0 | 60.001 | 59.969 | 59.961 | -0.032 | -0.04 |  |  | No | No | 59.5 | 0.461 | 2020
EI_2020-05-29_003005 | 2020-05-28 20:30 | 2020-05-28 20:30 | EDT | 2020-05-29 00:30 | 0 | 60.009 | 59.967 | 59.977 | -0.042 | -0.032 |  |  | No | No | 59.5 | 0.477 | 2020
EI_2020-05-29_180344 | 2020-05-29 14:04 | 2020-05-29 14:04 | EDT | 2020-05-29 18:04 | 0 | 60.015 | 59.948 | 59.948 | -0.067 | -0.067 |  |  | No | Yes | 59.5 | 0.448 | 2020
EI_2020-05-30_002334 | 2020-05-29 20:24 | 2020-05-29 20:24 | EDT | 2020-05-30 00:24 | 660 | 60.006 | 59.964 | 59.966 | -0.042 | -0.04 | -1571.4286 | -1650 | Yes | No | 59.5 | 0.466 | 2020
EI_2020-06-05_203125 | 2020-06-05 16:31 | 2020-06-05 16:31 | EDT | 2020-06-05 20:31 | 615 | 60.005 | 59.975 | 59.964 | -0.03 | -0.041 | -2050 | -1500 | Yes | No | 59.5 | 0.464 | 2020
EI_2020-06-06_132040 | 2020-06-06 09:21 | 2020-06-06 09:21 | EDT | 2020-06-06 13:21 | 1200 | 59.984 | 59.948 | 59.944 | -0.036 | -0.04 | -3333.3333 | -3000 | Yes | Yes | 59.5 | 0.444 | 2020
EI_2020-06-09_152448 | 2020-06-09 11:25 | 2020-06-09 11:25 | EDT | 2020-06-09 15:25 | 839.5 | 60.008 | 59.969 | 59.967 | -0.039 | -0.041 | -2152.5641 | -2047.561 | No | No | 59.5 | 0.467 | 2020
EI_2020-06-23_155306 | 2020-06-23 11:53 | 2020-06-23 11:53 | EDT | 2020-06-23 15:53 | 670.6 | 60.01 | 59.964 | 59.959 | -0.046 | -0.051 | -1457.8261 | -1314.902 | Yes | Yes | 59.5 | 0.459 | 2020
EI_2020-06-24_180415 | 2020-06-24 14:04 | 2020-06-24 14:04 | EDT | 2020-06-24 18:04 | 670 | 60.005 | 59.968 | 59.965 | -0.037 | -0.04 | -1810.8108 | -1675 | No | No | 59.5 | 0.465 | 2020
EI_2020-06-28_234646 | 2020-06-28 19:47 | 2020-06-28 19:47 | EDT | 2020-06-28 23:47 | 835 | 60.017 | 59.971 | 59.967 | -0.046 | -0.05 | -1815.2174 | -1670 | No | No | 59.5 | 0.467 | 2020
EI_2020-07-06_012050 | 2020-07-05 21:21 | 2020-07-05 21:21 | EDT | 2020-07-06 01:21 | 738 | 60.001 | 59.968 | 59.962 | -0.033 | -0.039 | -2236.3636 | -1892.3077 | Yes | No | 59.5 | 0.462 | 2020
EI_2020-07-06_212013 | 2020-07-06 17:20 | 2020-07-06 17:20 | EDT | 2020-07-06 21:20 | 947 | 59.992 | 59.965 | 59.965 | -0.027 | -0.027 | -3507.4074 | -3507.4074 | No | No | 59.5 | 0.465 | 2020
EI_2020-07-09_130455 | 2020-07-09 09:05 | 2020-07-09 09:05 | EDT | 2020-07-09 13:05 | 850 | 60.005 | 59.964 | 59.967 | -0.041 | -0.038 | -2073.1707 | -2236.8421 | No | No | 59.5 | 0.467 | 2020
EI_2020-07-21_063408 | 2020-07-21 02:34 | 2020-07-21 02:34 | EDT | 2020-07-21 06:34 | 721 | 60.005 | 59.98 | 59.968 | -0.025 | -0.037 | -2884 | -1948.6486 | No | No | 59.5 | 0.468 | 2020
EI_2020-07-24_010216 | 2020-07-23 21:02 | 2020-07-23 21:02 | EDT | 2020-07-24 01:02 | 850 | 59.963 | 59.939 | 59.943 | -0.024 | -0.02 | -3541.6667 | -4250 | Yes | No | 59.5 | 0.443 | 2020
EI_2020-08-02_022447 | 2020-08-01 22:25 | 2020-08-01 22:25 | EDT | 2020-08-02 02:25 | 1000 | 60 | 59.96 | 59.951 | -0.04 | -0.049 | -2500 | -2040.8163 | Yes | Yes | 59.5 | 0.451 | 2020
EI_2020-08-02_033430 | 2020-08-01 23:34 | 2020-08-01 23:34 | EDT | 2020-08-02 03:34 | 393.1 | 60.018 | 59.974 | 59.99 | -0.044 | -0.028 | -893.4091 | -1403.9286 | No | No | 59.5 | 0.49 | 2020
EI_2020-08-04_120320 | 2020-08-04 08:03 | 2020-08-04 08:03 | EDT | 2020-08-04 12:03 | 720 | 60.018 | 59.967 | 59.982 | -0.051 | -0.036 | -1411.7647 | -2000 | No | No | 59.5 | 0.482 | 2020
EI_2020-08-08_062709 | 2020-08-08 02:27 | 2020-08-08 02:27 | EDT | 2020-08-08 06:27 | 970.4 | 60.011 | 59.958 | 59.972 | -0.053 | -0.039 | -1830.9434 | -2488.2051 | No | No | 59.5 | 0.472 | 2020
EI_2020-08-12_111737 | 2020-08-12 07:18 | 2020-08-12 07:18 | EDT | 2020-08-12 11:18 | 708 | 60.003 | 59.965 | 59.964 | -0.038 | -0.039 | -1863.1579 | -1815.3846 | Yes | No | 59.5 | 0.464 | 2020
EI_2020-08-13_133845 | 2020-08-13 09:39 | 2020-08-13 09:39 | EDT | 2020-08-13 13:39 | 951 | 60.001 | 59.966 | 59.959 | -0.035 | -0.042 | -2717.1429 | -2264.2857 | Yes | Yes | 59.5 | 0.459 | 2020
EI_2020-08-18_011049 | 2020-08-17 21:11 | 2020-08-17 21:11 | EDT | 2020-08-18 01:11 | 738 | 60.01 | 59.975 | 59.962 | -0.035 | -0.048 | -2108.5714 | -1537.5 | Yes | No | 59.5 | 0.462 | 2020
EI_2020-08-21_110005 | 2020-08-21 07:00 | 2020-08-21 07:00 | EDT | 2020-08-21 11:00 | -1 | 59.998 | 60.034 | 60.025 | 0.036 | 0.027 | -2.7778 | -3.7037 | No | No | 59.5 | 0.525 | 2020
EI_2020-08-24_005553 | 2020-08-23 20:56 | 2020-08-23 20:56 | EDT | 2020-08-24 00:56 | 689 | 60.007 | 59.976 | 59.968 | -0.031 | -0.039 | -2222.5806 | -1766.6667 | Yes | No | 59.5 | 0.468 | 2020
EI_2020-08-25_175450 | 2020-08-25 13:55 | 2020-08-25 13:55 | EDT | 2020-08-25 17:55 | 830 | 60.019 | 59.987 | 59.978 | -0.032 | -0.041 | -2593.75 | -2024.3902 | No | No | 59.5 | 0.478 | 2020
EI_2020-09-03_195747 | 2020-09-03 15:58 | 2020-09-03 15:58 | EDT | 2020-09-03 19:58 | 0 | 59.983 | 59.951 | 59.943 | -0.032 | -0.04 |  |  | No | Yes | 59.5 | 0.443 | 2020
EI_2020-09-08_132527 | 2020-09-08 09:25 | 2020-09-08 09:25 | EDT | 2020-09-08 13:25 | 0 | 59.986 | 59.948 | 59.943 | -0.038 | -0.043 |  |  | No | Yes | 59.5 | 0.443 | 2020
EI_2020-09-19_103507 | 2020-09-19 06:35 | 2020-09-19 06:35 | EDT | 2020-09-19 10:35 | -1 | 60.004 | 60.03 | 60.035 | 0.026 | 0.031 | -3.8462 | -3.2258 | No | No | 59.5 | 0.535 | 2020
EI_2020-09-24_105130 | 2020-09-24 06:52 | 2020-09-24 06:52 | EDT | 2020-09-24 10:52 | -1 | 59.994 | 60.023 | 60.032 | 0.029 | 0.038 | -3.4483 | -2.6316 | No | No | 59.5 | 0.532 | 2020
EI_2020-09-27_070337 | 2020-09-27 03:04 | 2020-09-27 03:04 | EDT | 2020-09-27 07:04 | 1209 | 60 | 59.943 | 59.939 | -0.057 | -0.061 | -2121.0526 | -1981.9672 | Yes | Yes | 59.5 | 0.439 | 2020
EI_2020-10-09_165747 | 2020-10-09 12:58 | 2020-10-09 12:58 | EDT | 2020-10-09 16:58 | -1 | 60 | 60.038 | 60.06 | 0.038 | 0.06 | -2.6316 | -1.6667 | No | No | 59.5 | 0.56 | 2020
EI_2020-10-12_042626 | 2020-10-12 00:26 | 2020-10-12 00:26 | EDT | 2020-10-12 04:26 | 1160 | 60.004 | 59.954 | 59.94 | -0.05 | -0.064 | -2320 | -1812.5 | Yes | Yes | 59.5 | 0.44 | 2020
EI_2020-10-16_080840 | 2020-10-16 04:09 | 2020-10-16 04:09 | EDT | 2020-10-16 08:09 | 613 | 60.001 | 59.966 | 59.961 | -0.035 | -0.04 | -1751.4286 | -1532.5 | No | No | 59.5 | 0.461 | 2020
EI_2020-10-20_163411 | 2020-10-20 12:34 | 2020-10-20 12:34 | EDT | 2020-10-20 16:34 | 803 | 59.984 | 59.964 | 59.95 | -0.02 | -0.034 | -4015 | -2361.7647 | No | No | 59.5 | 0.45 | 2020
EI_2020-10-25_201039 | 2020-10-25 16:11 | 2020-10-25 16:11 | EDT | 2020-10-25 20:11 | -1 | 59.977 | 60.026 | 59.995 | 0.049 | 0.018 | -2.0408 | -5.5556 | No | No | 59.5 | 0.495 | 2020
EI_2020-11-06_084001 | 2020-11-06 03:40 | 2020-11-06 03:40 | EST | 2020-11-06 08:40 | 1208.9 | 59.981 | 59.956 | 59.935 | -0.025 | -0.046 | -4835.6 | -2628.0435 | Yes | Yes | 59.5 | 0.435 | 2020
EI_2020-11-10_235958 | 2020-11-10 19:00 | 2020-11-10 19:00 | EST | 2020-11-11 | 595 | 60.015 | 59.961 | 59.979 | -0.054 | -0.036 | -1101.8519 | -1652.7778 | No | No | 59.5 | 0.479 | 2020
EI_2020-11-12_223214 | 2020-11-12 17:32 | 2020-11-12 17:32 | EST | 2020-11-12 22:32 | 1228 | 59.965 | 59.93 | 59.928 | -0.035 | -0.037 | -3508.5714 | -3318.9189 | Yes | No | 59.5 | 0.428 | 2020
EI_2020-11-21_161245 | 2020-11-21 11:13 | 2020-11-21 11:13 | EST | 2020-11-21 16:13 | -1 | 59.98 | 60.019 | 60.01 | 0.039 | 0.03 | -2.5641 | -3.3333 | No | No | 59.5 | 0.51 | 2020
EI_2020-11-26_122707 | 2020-11-26 07:27 | 2020-11-26 07:27 | EST | 2020-11-26 12:27 | -1 | 59.997 | 60.033 | 60.031 | 0.036 | 0.034 | -2.7778 | -2.9412 | No | No | 59.5 | 0.531 | 2020
EI_2020-11-29_140540 | 2020-11-29 09:06 | 2020-11-29 09:06 | EST | 2020-11-29 14:06 | 0 | 60.014 | 59.975 | 59.987 | -0.039 | -0.027 |  |  | No | No | 59.5 | 0.487 | 2020
EI_2020-12-09_213511 | 2020-12-09 16:35 | 2020-12-09 16:35 | EST | 2020-12-09 21:35 | -1 | 59.977 | 60.023 | 60.021 | 0.046 | 0.044 | -2.1739 | -2.2727 | No | No | 59.5 | 0.521 | 2021
EI_2020-12-10_220951 | 2020-12-10 17:10 | 2020-12-10 17:10 | EST | 2020-12-10 22:10 | 1074.6 | 60.018 | 59.976 | 59.963 | -0.042 | -0.055 | -2558.5714 | -1953.8182 | Yes | No | 59.5 | 0.463 | 2021
EI_2020-12-11_180401 | 2020-12-11 13:04 | 2020-12-11 13:04 | EST | 2020-12-11 18:04 | 1443.4 | 59.976 | 59.935 | 59.924 | -0.041 | -0.052 | -3520.4878 | -2775.7692 | Yes | Yes | 59.5 | 0.424 | 2021
EI_2020-12-18_093455 | 2020-12-18 04:35 | 2020-12-18 04:35 | EST | 2020-12-18 09:35 | -1 | 59.986 | 60.024 | 60.024 | 0.038 | 0.038 | -2.6316 | -2.6316 | No | No | 59.5 | 0.524 | 2021
EI_2020-12-23_200426 | 2020-12-23 15:04 | 2020-12-23 15:04 | EST | 2020-12-23 20:04 | 636 | 60.004 | 59.963 | 59.967 | -0.041 | -0.037 | -1551.2195 | -1718.9189 | Yes | No | 59.5 | 0.467 | 2021
EI_2020-12-24_050016 | 2020-12-24 | 2020-12-24 | EST | 2020-12-24 05:00 | -1 | 59.992 | 60.036 | 60.028 | 0.044 | 0.036 | -2.2727 | -2.7778 | No | No | 59.5 | 0.528 | 2021
EI_2020-12-27_210014 | 2020-12-27 16:00 | 2020-12-27 16:00 | EST | 2020-12-27 21:00 | -1 | 59.979 | 60.023 | 59.993 | 0.044 | 0.014 | -2.2727 | -7.1429 | No | No | 59.5 | 0.493 | 2021
EI_2020-12-30_091355 | 2020-12-30 04:14 | 2020-12-30 04:14 | EST | 2020-12-30 09:14 | 642 | 59.999 | 59.953 | 59.947 | -0.046 | -0.052 | -1395.6522 | -1234.6154 | Yes | No | 59.5 | 0.447 | 2021
EI_2021-01-01_100428 | 2021-01-01 05:04 | 2021-01-01 05:04 | EST | 2021-01-01 10:04 | -1 | 59.978 | 60.004 | 60.013 | 0.026 | 0.035 | -3.8462 | -2.8571 | No | No | 59.5 | 0.513 | 2021
EI_2021-01-11_090616 | 2021-01-11 04:06 | 2021-01-11 04:06 | EST | 2021-01-11 09:06 | -1 | 59.987 | 60.023 | 60.03 | 0.036 | 0.043 | -2.7778 | -2.3256 | No | No | 59.5 | 0.53 | 2021
EI_2021-01-25_032958 | 2021-01-24 22:30 | 2021-01-24 22:30 | EST | 2021-01-25 03:30 | 1500 | 60.014 | 59.944 | 59.932 | -0.07 | -0.082 | -2142.8571 | -1829.2683 | Yes | Yes | 59.5 | 0.432 | 2021
EI_2021-01-26_102815 | 2021-01-26 05:28 | 2021-01-26 05:28 | EST | 2021-01-26 10:28 | -1 | 59.989 | 60.034 | 60.034 | 0.045 | 0.045 | -2.2222 | -2.2222 | No | No | 59.5 | 0.534 | 2021
EI_2021-02-01_202852 | 2021-02-01 15:29 | 2021-02-01 15:29 | EST | 2021-02-01 20:29 | 864.9 | 59.988 | 59.961 | 59.955 | -0.027 | -0.033 | -3203.3333 | -2620.9091 | No | No | 59.5 | 0.455 | 2021
EI_2021-02-05_051807 | 2021-02-05 00:18 | 2021-02-05 00:18 | EST | 2021-02-05 05:18 | 856.1 | 60.001 | 59.969 | 59.968 | -0.032 | -0.033 | -2675.3125 | -2594.2424 | No | No | 59.5 | 0.468 | 2021
EI_2021-02-07_152122 | 2021-02-07 10:21 | 2021-02-07 10:21 | EST | 2021-02-07 15:21 | 0 | 60.027 | 60.004 | 59.988 | -0.023 | -0.039 |  |  | No | No | 59.5 | 0.488 | 2021
EI_2021-02-09_195612 | 2021-02-09 14:56 | 2021-02-09 14:56 | EST | 2021-02-09 19:56 | 0 | 60.013 | 59.986 | 59.983 | -0.027 | -0.03 |  |  | No | No | 59.5 | 0.483 | 2021
EI_2021-02-14_112832 | 2021-02-14 06:29 | 2021-02-14 06:29 | EST | 2021-02-14 11:29 | 500 | 60.003 | 59.968 | 59.968 | -0.035 | -0.035 | -1428.5714 | -1428.5714 | No | No | 59.5 | 0.468 | 2021
EI_2021-02-16_235918 | 2021-02-16 18:59 | 2021-02-16 18:59 | EST | 2021-02-16 23:59 | 1103 | 60.019 | 59.966 | 59.969 | -0.053 | -0.05 | -2081.1321 | -2206 | Yes | No | 59.5 | 0.469 | 2021
EI_2021-02-18_075000 | 2021-02-18 02:50 | 2021-02-18 02:50 | EST | 2021-02-18 07:50 | 617 | 60.004 | 59.973 | 59.963 | -0.031 | -0.041 | -1990.3226 | -1504.878 | Yes | No | 59.5 | 0.463 | 2021
Note on N1275: Brad Gordon: Selected as M4 despite Fa-c=35mHz

## WI
Initial Start Time
(From Fnet)
UTC Initial t0
Event ID (From UTC Initial t0) | Local Date / Time (MM/DD/YY HH:MM:SS) | Day | Time Zone | Date / Time (MM/DD/YY HH:MM:SS) | NERC Confirmed MW Loss | A Value Hz | B Value Hz | Point C Hz | B-A Delta Hz | C-A Delta Hz | A to B IFRM | A to C IFRM | FWG Sel. M-4 | FWG Sel. BAL-003 | 1st Step UFLS Hz | C - UFLS Margin Hz | Oper Year (Local)
AESO_2017-10-16_224521 | 2017-10-16 15:45 | 2017-10-16 15:45 | PDT | 2017-10-16 22:45 | -1378 | 60.007 | 60.214 | 60.337 | 0.207 | 0.33 | -665.7005 | -417.5758 | No | No | 59.5 | 0.837 | 2017
WI_2011-12-04_203018 | 2011-12-04 12:30 | 2011-12-04 12:30 | PST | 2011-12-04 20:30 |  | 60.0162 | 59.9663 | 59.944 | -0.049942 | -0.072193 |  |  | No | No | 59.5 | 0.444 | 2012
WI_2011-12-06_182734 | 2011-12-06 10:28 | 2011-12-06 10:28 | PST | 2011-12-06 18:28 |  | 59.9983 | 59.9543 | 59.9168 | -0.044025 | -0.081479 |  |  | No | No | 59.5 | 0.4168 | 2012
WI_2011-12-10_101612 | 2011-12-10 02:16 | 2011-12-10 02:16 | PST | 2011-12-10 10:16 |  | 60.0157 | 59.9314 | 59.9172 | -0.084322 | -0.098496 |  |  | No | No | 59.5 | 0.4172 | 2012
WI_2011-12-28_194045 | 2011-12-28 11:41 | 2011-12-28 11:41 | PST | 2011-12-28 19:41 |  | 59.9979 | 59.9246 | 59.893 | -0.07335 | -0.10491 |  |  | No | No | 59.5 | 0.393 | 2012
WI_2012-01-04_174124 | 2012-01-04 09:41 | 2012-01-04 09:41 | PST | 2012-01-04 17:41 |  | 60.011 | 59.9737 | 59.9412 | -0.037321 | -0.069818 |  |  | No | No | 59.5 | 0.4412 | 2012
WI_2012-01-10_193752 | 2012-01-10 11:38 | 2012-01-10 11:38 | PST | 2012-01-10 19:38 |  | 60.0177 | 59.979 | 59.9444 | -0.038734 | -0.073318 |  |  | No | No | 59.5 | 0.4444 | 2012
WI_2012-01-11_000214 | 2012-01-10 16:02 | 2012-01-10 16:02 | PST | 2012-01-11 00:02 |  | 60.0047 | 59.9693 | 59.9354 | -0.035412 | -0.069296 |  |  | No | No | 59.5 | 0.4354 | 2012
WI_2012-01-11_205910 | 2012-01-11 12:59 | 2012-01-11 12:59 | PST | 2012-01-11 20:59 |  | 60.0032 | 59.9578 | 59.9309 | -0.045427 | -0.072281 |  |  | No | No | 59.5 | 0.4309 | 2012
WI_2012-01-20_054547 | 2012-01-19 21:46 | 2012-01-19 21:46 | PST | 2012-01-20 05:46 |  | 60.0249 | 59.9731 | 59.9506 | -0.05184 | -0.074332 |  |  | No | No | 59.5 | 0.4506 | 2012
WI_2012-01-27_012502 | 2012-01-26 17:25 | 2012-01-26 17:25 | PST | 2012-01-27 01:25 |  | 60.0048 | 59.9859 | 59.9305 | -0.01887 | -0.074319 |  |  | No | No | 59.5 | 0.4305 | 2012
WI_2012-02-15_004418 | 2012-02-14 16:44 | 2012-02-14 16:44 | PST | 2012-02-15 00:44 |  | 59.9987 | 59.9304 | 59.8998 | -0.068285 | -0.098913 |  |  | No | No | 59.5 | 0.3998 | 2012
WI_2012-02-18_083104 | 2012-02-18 00:31 | 2012-02-18 00:31 | PST | 2012-02-18 08:31 |  | 60.0139 | 59.952 | 59.9358 | -0.061939 | -0.078102 |  |  | No | No | 59.5 | 0.4358 | 2012
WI_2012-02-23_005718 | 2012-02-22 16:57 | 2012-02-22 16:57 | PST | 2012-02-23 00:57 |  | 60.0215 | 59.9567 | 59.9255 | -0.06481 | -0.095995 |  |  | No | No | 59.5 | 0.4255 | 2012
WI_2012-02-23_025015 | 2012-02-22 18:50 | 2012-02-22 18:50 | PST | 2012-02-23 02:50 |  | 60.0188 | 59.9806 | 59.9484 | -0.038145 | -0.070364 |  |  | No | No | 59.5 | 0.4484 | 2012
WI_2012-02-29_054008 | 2012-02-28 21:40 | 2012-02-28 21:40 | PST | 2012-02-29 05:40 |  | 60.0223 | 59.9513 | 59.93 | -0.070984 | -0.092268 |  |  | No | No | 59.5 | 0.43 | 2012
WI_2012-03-01_045340 | 2012-02-29 20:54 | 2012-02-29 20:54 | PST | 2012-03-01 04:54 | 755 | 60.0099 | 59.9462 | 59.9189 | -0.063759 | -0.091038 | -1184.1425 | -829.3198 | Yes | Yes | 59.5 | 0.4189 | 2012
WI_2012-03-14_162649 | 2012-03-14 09:27 | 2012-03-14 09:27 | PDT | 2012-03-14 16:27 |  | 60.0238 | 59.9853 | 59.9432 | -0.038482 | -0.080582 |  |  | No | No | 59.5 | 0.4432 | 2012
WI_2012-03-15_014417 | 2012-03-14 18:44 | 2012-03-14 18:44 | PDT | 2012-03-15 01:44 |  | 59.9855 | 59.947 | 59.9148 | -0.038496 | -0.070676 |  |  | No | No | 59.5 | 0.4148 | 2012
WI_2012-03-24_223658 | 2012-03-24 15:37 | 2012-03-24 15:37 | PDT | 2012-03-24 22:37 |  | 59.9858 | 60.0353 | 60.0669 | 0.049482 | 0.081092 |  |  | No | No | 59.5 | 0.5669 | 2012
WI_2012-03-28_121858 | 2012-03-28 05:19 | 2012-03-28 05:19 | PDT | 2012-03-28 12:19 |  | 59.9871 | 59.9472 | 59.8976 | -0.039893 | -0.089489 |  |  | No | No | 59.5 | 0.3976 | 2012
WI_2012-03-30_172017 | 2012-03-30 10:20 | 2012-03-30 10:20 | PDT | 2012-03-30 17:20 |  | 60.015 | 59.9005 | 59.802 | -0.1145 | -0.21296 |  |  | No | No | 59.5 | 0.302 | 2012
WI_2012-03-30_230403 | 2012-03-30 16:04 | 2012-03-30 16:04 | PDT | 2012-03-30 23:04 | 930 | 59.972 | 59.9176 | 59.8691 | -0.054326 | -0.10286 | -1711.8923 | -904.1648 | No | No | 59.5 | 0.3691 | 2012
WI_2012-04-03_172601 | 2012-04-03 10:26 | 2012-04-03 10:26 | PDT | 2012-04-03 17:26 |  | 59.9821 | 59.9463 | 59.9167 | -0.035717 | -0.065364 |  |  | No | No | 59.5 | 0.4167 | 2012
WI_2012-04-04_162509 | 2012-04-04 09:25 | 2012-04-04 09:25 | PDT | 2012-04-04 16:25 | 789 | 60.0152 | 59.9529 | 59.9202 | -0.062273 | -0.095018 | -1266.9989 | -830.3656 | Yes | Yes | 59.5 | 0.4202 | 2012
WI_2012-04-06_163818 | 2012-04-06 09:38 | 2012-04-06 09:38 | PDT | 2012-04-06 16:38 | 1400 | 60.025 | 59.9298 | 59.8696 | -0.095138 | -0.15536 | -1471.5457 | -901.1094 | No | No | 59.5 | 0.3696 | 2012
WI_2012-04-11_145444 | 2012-04-11 07:55 | 2012-04-11 07:55 | PDT | 2012-04-11 14:55 |  | 59.9731 | 59.9357 | 59.9112 | -0.037437 | -0.061911 |  |  | No | No | 59.5 | 0.4112 | 2012
WI_2012-04-12_140834 | 2012-04-12 07:09 | 2012-04-12 07:09 | PDT | 2012-04-12 14:09 |  | 60.0133 | 59.9655 | 59.9449 | -0.047796 | -0.068444 |  |  | No | No | 59.5 | 0.4449 | 2012
WI_2012-04-20_223651 | 2012-04-20 15:37 | 2012-04-20 15:37 | PDT | 2012-04-20 22:37 |  | 60.0387 | 59.9118 | 60.0412 | -0.12687 | 0.0025108 |  |  | No | No | 59.5 | 0.5412 | 2012
WI_2012-04-21_181104 | 2012-04-21 11:11 | 2012-04-21 11:11 | PDT | 2012-04-21 18:11 |  | 59.1997 | 59.9863 | 59.9868 | 0.78665 | 0.78712 |  |  | No | No | 59.5 | 0.4868 | 2012
WI_2012-05-02_205158 | 2012-05-02 13:52 | 2012-05-02 13:52 | PDT | 2012-05-02 20:52 |  | 60.015 | 59.9578 | 59.923 | -0.057286 | -0.092037 |  |  | No | No | 59.5 | 0.423 | 2012
WI_2012-05-03_151801 | 2012-05-03 08:18 | 2012-05-03 08:18 | PDT | 2012-05-03 15:18 |  | 60.0086 | 59.9613 | 59.9403 | -0.047276 | -0.068319 |  |  | No | No | 59.5 | 0.4403 | 2012
WI_2012-05-05_130953 | 2012-05-05 06:10 | 2012-05-05 06:10 | PDT | 2012-05-05 13:10 | 630 | 60.0079 | 59.9489 | 59.9133 | -0.058954 | -0.094575 | -1068.6363 | -666.1368 | No | No | 59.5 | 0.4133 | 2012
WI_2012-05-09_155217 | 2012-05-09 08:52 | 2012-05-09 08:52 | PDT | 2012-05-09 15:52 | 590 | 59.975 | 59.9241 | 59.8956 | -0.050898 | -0.079413 | -1159.1899 | -742.952 | No | No | 59.5 | 0.3956 | 2012
WI_2012-05-10_174755 | 2012-05-10 10:48 | 2012-05-10 10:48 | PDT | 2012-05-10 17:48 | 490 | 60.0111 | 59.9778 | 59.9409 | -0.033263 | -0.070158 | -1473.1055 | -698.4235 | No | No | 59.5 | 0.4409 | 2012
WI_2012-05-10_181048 | 2012-05-10 11:11 | 2012-05-10 11:11 | PDT | 2012-05-10 18:11 | 630 | 60.0191 | 59.9657 | 59.9321 | -0.053345 | -0.086983 | -1180.9846 | -724.2778 | No | Yes | 59.5 | 0.4321 | 2012
WI_2012-05-10_183309 | 2012-05-10 11:33 | 2012-05-10 11:33 | PDT | 2012-05-10 18:33 | 460 | 59.9994 | 59.9779 | 59.929 | -0.021505 | -0.070355 | -2139.0861 | -653.8254 | No | No | 59.5 | 0.429 | 2012
WI_2012-05-15_020159 | 2012-05-14 19:02 | 2012-05-14 19:02 | PDT | 2012-05-15 02:02 | 633 | 60.0065 | 59.9354 | 59.8954 | -0.071161 | -0.11112 | -889.5267 | -569.6643 | No | No | 59.5 | 0.3954 | 2012
WI_2012-05-22_202122 | 2012-05-22 13:21 | 2012-05-22 13:21 | PDT | 2012-05-22 20:21 | 634 | 59.9871 | 59.9567 | 59.9077 | -0.030375 | -0.079394 | -2087.2271 | -798.5528 | No | No | 59.5 | 0.4077 | 2012
WI_2012-05-26_170949 | 2012-05-26 10:10 | 2012-05-26 10:10 | PDT | 2012-05-26 17:10 |  | 60.0183 | 59.9847 | 59.9454 | -0.03363 | -0.072881 |  |  | No | No | 59.5 | 0.4454 | 2012
WI_2012-06-08_230622 | 2012-06-08 16:06 | 2012-06-08 16:06 | PDT | 2012-06-08 23:06 | 746 | 60.01 | 59.9503 | 59.9138 | -0.059731 | -0.096238 | -1248.9249 | -775.1586 | Yes | Yes | 59.5 | 0.4138 | 2012
WI_2012-06-17_051201 | 2012-06-16 22:12 | 2012-06-16 22:12 | PDT | 2012-06-17 05:12 |  | 59.9312 | 59.9949 | 60.0048 | 0.063699 | 0.073643 |  |  | No | No | 59.5 | 0.5048 | 2012
WI_2012-06-25_162947 | 2012-06-25 09:30 | 2012-06-25 09:30 | PDT | 2012-06-25 16:30 | 929 | 59.9918 | 59.9215 | 59.8978 | -0.070308 | -0.093987 | -1321.3203 | -988.4372 | Yes | Yes | 59.5 | 0.3978 | 2012
WI_2012-06-26_135808 | 2012-06-26 06:58 | 2012-06-26 06:58 | PDT | 2012-06-26 13:58 |  | 59.9827 | 59.931 | 59.9078 | -0.051761 | -0.074914 |  |  | No | No | 59.5 | 0.4078 | 2012
WI_2012-06-28_154032 | 2012-06-28 08:41 | 2012-06-28 08:41 | PDT | 2012-06-28 15:41 |  | 59.9829 | 59.9336 | 59.9043 | -0.04926 | -0.078568 |  |  | No | No | 59.5 | 0.4043 | 2012
WI_2012-07-04_142040 | 2012-07-04 07:21 | 2012-07-04 07:21 | PDT | 2012-07-04 14:21 |  | 59.998 | 59.9451 | 59.9181 | -0.05283 | -0.079877 |  |  | No | No | 59.5 | 0.4181 | 2012
WI_2012-07-10_102819 | 2012-07-10 03:28 | 2012-07-10 03:28 | PDT | 2012-07-10 10:28 | 1860 | 60.022 | 59.925 | 59.88 | -0.097 | -0.142 | -1917.5258 | -1309.8592 | Yes | Yes | 59.5 | 0.38 | 2012
WI_2012-07-12_125158 | 2012-07-12 05:52 | 2012-07-12 05:52 | PDT | 2012-07-12 12:52 |  | 60.0074 | 59.9706 | 59.9304 | -0.036772 | -0.076956 |  |  | No | No | 59.5 | 0.4304 | 2012
WI_2012-07-12_215036 | 2012-07-12 14:51 | 2012-07-12 14:51 | PDT | 2012-07-12 21:51 |  | 60.0352 | 59.961 | 59.9434 | -0.074198 | -0.091842 |  |  | No | No | 59.5 | 0.4434 | 2012
WI_2012-07-13_230826 | 2012-07-13 16:08 | 2012-07-13 16:08 | PDT | 2012-07-13 23:08 |  | 60.0103 | 59.9381 | 59.9224 | -0.072145 | -0.087886 |  |  | No | No | 59.5 | 0.4224 | 2012
WI_2012-07-15_052243 | 2012-07-14 22:23 | 2012-07-14 22:23 | PDT | 2012-07-15 05:23 | 1038 | 60.0085 | 59.9436 | 59.8974 | -0.064878 | -0.1111 | -1599.9185 | -934.2958 | No | No | 59.5 | 0.3974 | 2012
WI_2012-07-15_055209 | 2012-07-14 22:52 | 2012-07-14 22:52 | PDT | 2012-07-15 05:52 | 784 | 60.0018 | 59.9509 | 59.9212 | -0.050917 | -0.080575 | -1539.7646 | -973.0066 | No | No | 59.5 | 0.4212 | 2012
WI_2012-07-23_002258 | 2012-07-22 17:23 | 2012-07-22 17:23 | PDT | 2012-07-23 00:23 |  | 60.0197 | 59.9724 | 59.9327 | -0.047279 | -0.086999 |  |  | No | No | 59.5 | 0.4327 | 2012
WI_2012-07-23_123638 | 2012-07-23 05:37 | 2012-07-23 05:37 | PDT | 2012-07-23 12:37 |  | 59.9651 | 59.9346 | 59.891 | -0.030555 | -0.07412 |  |  | No | No | 59.5 | 0.391 | 2012
WI_2012-07-24_102800 | 2012-07-24 03:28 | 2012-07-24 03:28 | PDT | 2012-07-24 10:28 |  | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.5 | -59.5 | 2012
WI_2012-08-09_011202 | 2012-08-08 18:12 | 2012-08-08 18:12 | PDT | 2012-08-09 01:12 |  | 60.0064 | 59.9657 | 59.9311 | -0.040728 | -0.07532 |  |  | No | No | 59.5 | 0.4311 | 2012
WI_2012-08-16_023148 | 2012-08-15 19:32 | 2012-08-15 19:32 | PDT | 2012-08-16 02:32 |  | 59.8999 | 59.9871 | 59.993 | 0.087218 | 0.0931 |  |  | No | No | 59.5 | 0.493 | 2012
WI_2012-08-23_185839 | 2012-08-23 11:59 | 2012-08-23 11:59 | PDT | 2012-08-23 18:59 |  | 60.0137 | 59.9664 | 59.94 | -0.047253 | -0.073664 |  |  | No | No | 59.5 | 0.44 | 2012
WI_2012-08-30_181455 | 2012-08-30 11:15 | 2012-08-30 11:15 | PDT | 2012-08-30 18:15 |  | 60.0067 | 59.9584 | 59.9202 | -0.048349 | -0.086513 |  |  | No | No | 59.5 | 0.4202 | 2012
WI_2012-08-30_212602 | 2012-08-30 14:26 | 2012-08-30 14:26 | PDT | 2012-08-30 21:26 |  | 60.001 | 59.9661 | 59.9304 | -0.034983 | -0.070649 |  |  | No | No | 59.5 | 0.4304 | 2012
WI_2012-08-31_185602 | 2012-08-31 11:56 | 2012-08-31 11:56 | PDT | 2012-08-31 18:56 |  | 59.9915 | 59.9079 | 59.8817 | -0.083648 | -0.10981 |  |  | No | No | 59.5 | 0.3817 | 2012
WI_2012-09-17_133238 | 2012-09-17 06:33 | 2012-09-17 06:33 | PDT | 2012-09-17 13:33 |  | 59.9726 | 60.0307 | 60.0481 | 0.058089 | 0.075525 |  |  | No | No | 59.5 | 0.5481 | 2012
WI_2012-09-20_052109 | 2012-09-19 22:21 | 2012-09-19 22:21 | PDT | 2012-09-20 05:21 |  | 60.0459 | 60.0004 | 59.9766 | -0.045497 | -0.069287 |  |  | No | No | 59.5 | 0.4766 | 2012
WI_2012-10-01_082833 | 2012-10-01 01:29 | 2012-10-01 01:29 | PDT | 2012-10-01 08:29 |  | 59.9778 | 59.9246 | 59.8981 | -0.053111 | -0.079654 |  |  | No | No | 59.5 | 0.3981 | 2012
WI_2012-10-11_190848 | 2012-10-11 12:09 | 2012-10-11 12:09 | PDT | 2012-10-11 19:09 | 1119 | 60.0157 | 59.9158 | 59.8781 | -0.099866 | -0.13757 | -1120.5053 | -813.3835 | No | No | 59.5 | 0.3781 | 2012
WI_2012-10-17_031655 | 2012-10-16 20:17 | 2012-10-16 20:17 | PDT | 2012-10-17 03:17 |  | 59.9913 | 59.9352 | 59.917 | -0.056084 | -0.074281 |  |  | No | No | 59.5 | 0.417 | 2012
WI_2012-10-17_043959 | 2012-10-16 21:40 | 2012-10-16 21:40 | PDT | 2012-10-17 04:40 |  | 60.0227 | 59.9628 | 59.9527 | -0.059902 | -0.069961 |  |  | No | No | 59.5 | 0.4527 | 2012
WI_2012-10-18_235520 | 2012-10-18 16:55 | 2012-10-18 16:55 | PDT | 2012-10-18 23:55 | 520 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.5 | -59.5 | 2012
WI_2012-10-19_093320 | 2012-10-19 02:33 | 2012-10-19 02:33 | PDT | 2012-10-19 09:33 |  | 59.9678 | 59.9167 | 59.895 | -0.051134 | -0.072825 |  |  | No | No | 59.5 | 0.395 | 2012
WI_2012-10-28_153438 | 2012-10-28 08:35 | 2012-10-28 08:35 | PDT | 2012-10-28 15:35 |  | 59.9526 | 59.9962 | 60.0233 | 0.043695 | 0.07075 |  |  | No | No | 59.5 | 0.5233 | 2012
WI_2012-10-30_033128 | 2012-10-29 20:31 | 2012-10-29 20:31 | PDT | 2012-10-30 03:31 |  | 60.0395 | 59.9755 | 59.9453 | -0.064064 | -0.094236 |  |  | No | No | 59.5 | 0.4453 | 2012
WI_2012-11-07_153045 | 2012-11-07 07:31 | 2012-11-07 07:31 | PST | 2012-11-07 15:31 |  | 60.0274 | 59.9954 | 59.9571 | -0.031993 | -0.070269 |  |  | No | No | 59.5 | 0.4571 | 2012
WI_2012-11-13_102656 | 2012-11-13 02:27 | 2012-11-13 02:27 | PST | 2012-11-13 10:27 | 599 | 60.0125 | 59.9524 | 59.9264 | -0.060083 | -0.086132 | -996.9582 | -695.4419 | No | Yes | 59.5 | 0.4264 | 2012
WI_2012-11-25_063049 | 2012-11-24 22:31 | 2012-11-24 22:31 | PST | 2012-11-25 06:31 |  | 60.02 | 59.974 | 59.941 | -0.046034 | -0.079017 |  |  | No | No | 59.5 | 0.441 | 2012
WI_2012-11-28_160901 | 2012-11-28 08:09 | 2012-11-28 08:09 | PST | 2012-11-28 16:09 |  | 60.0081 | 59.9487 | 59.9255 | -0.05936 | -0.082557 |  |  | No | No | 59.5 | 0.4255 | 2012
WI_2012-11-28_200307 | 2012-11-28 12:03 | 2012-11-28 12:03 | PST | 2012-11-28 20:03 |  | 59.9952 | 59.9378 | 59.9202 | -0.057405 | -0.074974 |  |  | No | No | 59.5 | 0.4202 | 2012
WI_2012-12-10_030451 | 2012-12-09 19:05 | 2012-12-09 19:05 | PST | 2012-12-10 03:05 |  | 59.9907 | 59.9379 | 59.9064 | -0.052837 | -0.084314 |  |  | No | No | 59.5 | 0.4064 | 2013
WI_2012-12-12_164135 | 2012-12-12 08:42 | 2012-12-12 08:42 | PST | 2012-12-12 16:42 |  | 59.9996 | 59.9474 | 59.9173 | -0.052176 | -0.082306 |  |  | No | No | 59.5 | 0.4173 | 2013
WI_2013-01-17_211158 | 2013-01-17 13:12 | 2013-01-17 13:12 | PST | 2013-01-17 21:12 |  | 59.9928 | 59.9513 | 59.916 | -0.041445 | -0.076787 |  |  | No | No | 59.5 | 0.416 | 2013
WI_2013-01-28_071803 | 2013-01-27 23:18 | 2013-01-27 23:18 | PST | 2013-01-28 07:18 |  | 60.0013 | 59.9529 | 59.9342 | -0.048383 | -0.067112 |  |  | No | No | 59.5 | 0.4342 | 2013
WI_2013-01-31_171859 | 2013-01-31 09:19 | 2013-01-31 09:19 | PST | 2013-01-31 17:19 |  | 59.9913 | 59.9379 | 59.9073 | -0.053353 | -0.083963 |  |  | No | No | 59.5 | 0.4073 | 2013
WI_2013-02-04_180614 | 2013-02-04 10:06 | 2013-02-04 10:06 | PST | 2013-02-04 18:06 |  | 60.0023 | 59.9406 | 59.9208 | -0.061728 | -0.081532 |  |  | No | No | 59.5 | 0.4208 | 2013
WI_2013-02-06_194618 | 2013-02-06 11:46 | 2013-02-06 11:46 | PST | 2013-02-06 19:46 |  | 60.0087 | 59.963 | 59.941 | -0.045693 | -0.067686 |  |  | No | No | 59.5 | 0.441 | 2013
WI_2013-02-13_153244 | 2013-02-13 07:33 | 2013-02-13 07:33 | PST | 2013-02-13 15:33 |  | 60.0177 | 59.9654 | 59.9381 | -0.052254 | -0.079576 |  |  | No | No | 59.5 | 0.4381 | 2013
WI_2013-03-02_210127 | 2013-03-02 13:01 | 2013-03-02 13:01 | PST | 2013-03-02 21:01 | 788 | 60.0251 | 59.955 | 59.9241 | -0.070128 | -0.101 | -1123.6671 | -780.1883 | No | No | 59.5 | 0.4241 | 2013
WI_2013-03-05_180837 | 2013-03-05 10:09 | 2013-03-05 10:09 | PST | 2013-03-05 18:09 |  | 59.9908 | 59.9391 | 59.9128 | -0.051626 | -0.077956 |  |  | No | No | 59.5 | 0.4128 | 2013
WI_2013-03-06_062907 | 2013-03-05 22:29 | 2013-03-05 22:29 | PST | 2013-03-06 06:29 | 750 | 60.0278 | 59.9802 | 59.9541 | -0.047627 | -0.073686 | -1574.7332 | -1017.8307 | No | No | 59.5 | 0.4541 | 2013
WI_2013-03-06_114133 | 2013-03-06 03:42 | 2013-03-06 03:42 | PST | 2013-03-06 11:42 |  | 60.0108 | 59.9559 | 59.9438 | -0.054917 | -0.067043 |  |  | No | No | 59.5 | 0.4438 | 2013
WI_2013-03-15_001443 | 2013-03-14 17:15 | 2013-03-14 17:15 | PDT | 2013-03-15 00:15 |  | 59.9802 | 59.9324 | 59.89 | -0.047773 | -0.0902 |  |  | No | No | 59.5 | 0.39 | 2013
WI_2013-03-17_114907 | 2013-03-17 04:49 | 2013-03-17 04:49 | PDT | 2013-03-17 11:49 |  | 60.0278 | 59.9578 | 59.9521 | -0.069994 | -0.075682 |  |  | No | No | 59.5 | 0.4521 | 2013
WI_2013-03-20_125152 | 2013-03-20 05:52 | 2013-03-20 05:52 | PDT | 2013-03-20 12:52 | 780 | 59.9934 | 59.9297 | 59.8997 | -0.063672 | -0.093657 | -1225.0309 | -832.8303 | Yes | Yes | 59.5 | 0.3997 | 2013
WI_2013-03-28_210128 | 2013-03-28 14:01 | 2013-03-28 14:01 | PDT | 2013-03-28 21:01 | 655 | 60.0148 | 59.9771 | 59.9243 | -0.037722 | -0.09053 | -1736.3748 | -723.5139 | No | No | 59.5 | 0.4243 | 2013
WI_2013-03-30_115935 | 2013-03-30 05:00 | 2013-03-30 05:00 | PDT | 2013-03-30 12:00 |  | 59.9659 | 60.0357 | 60.0459 | 0.069849 | 0.080024 |  |  | No | No | 59.5 | 0.5459 | 2013
WI_2013-04-01_010533 | 2013-03-31 18:06 | 2013-03-31 18:06 | PDT | 2013-04-01 01:06 | 740 | 59.9952 | 59.9479 | 59.8997 | -0.047226 | -0.095456 | -1566.9461 | -775.2292 | Yes | Yes | 59.5 | 0.3997 | 2013
WI_2013-04-01_150753 | 2013-04-01 08:08 | 2013-04-01 08:08 | PDT | 2013-04-01 15:08 | 1400 | 59.9951 | 59.9064 | 59.8426 | -0.088676 | -0.15252 | -1578.7744 | -917.9314 | Yes | Yes | 59.5 | 0.3426 | 2013
WI_2013-04-09_003901 | 2013-04-08 17:39 | 2013-04-08 17:39 | PDT | 2013-04-09 00:39 |  | 60.0167 | 59.965 | 59.9357 | -0.051721 | -0.081006 |  |  | No | No | 59.5 | 0.4357 | 2013
WI_2013-04-15_201453 | 2013-04-15 13:15 | 2013-04-15 13:15 | PDT | 2013-04-15 20:15 | 759 | 59.971 | 59.9305 | 59.9001 | -0.040497 | -0.070905 | -1874.2026 | -1070.4396 | No | No | 59.5 | 0.4001 | 2013
WI_2013-04-27_020102 | 2013-04-26 19:01 | 2013-04-26 19:01 | PDT | 2013-04-27 02:01 |  | 60.004 | 59.9427 | 59.9158 | -0.061318 | -0.088177 |  |  | No | No | 59.5 | 0.4158 | 2013
WI_2013-04-29_174829 | 2013-04-29 10:48 | 2013-04-29 10:48 | PDT | 2013-04-29 17:48 | 880 | 59.9938 | 59.9135 | 59.8588 | -0.080278 | -0.135 | -1096.1851 | -651.8484 | Yes | Yes | 59.5 | 0.3588 | 2013
WI_2013-05-01_071458 | 2013-05-01 00:15 | 2013-05-01 00:15 | PDT | 2013-05-01 07:15 | 774 | 60.0159 | 59.952 | 59.9127 | -0.063921 | -0.10318 | -1210.8707 | -750.1389 | No | No | 59.5 | 0.4127 | 2013
WI_2013-05-07_173647 | 2013-05-07 10:37 | 2013-05-07 10:37 | PDT | 2013-05-07 17:37 | 719 | 60.0043 | 59.9168 | 59.8882 | -0.087485 | -0.11612 | -821.8529 | -619.1878 | Yes | Yes | 59.5 | 0.3882 | 2013
WI_2013-05-15_181640 | 2013-05-15 11:17 | 2013-05-15 11:17 | PDT | 2013-05-15 18:17 |  | 60.0267 | 59.9634 | 59.9349 | -0.063387 | -0.09184 |  |  | No | No | 59.5 | 0.4349 | 2013
WI_2013-05-21_153557 | 2013-05-21 08:36 | 2013-05-21 08:36 | PDT | 2013-05-21 15:36 |  | 60.0012 | 59.9355 | 59.9165 | -0.065691 | -0.084706 |  |  | No | No | 59.5 | 0.4165 | 2013
WI_2013-05-22_222059 | 2013-05-22 15:21 | 2013-05-22 15:21 | PDT | 2013-05-22 22:21 | 1300 | 59.9987 | 59.9195 | 59.8802 | -0.079152 | -0.11849 | -1642.4111 | -1097.095 | Yes | Yes | 59.5 | 0.3802 | 2013
WI_2013-05-26_064105 | 2013-05-25 23:41 | 2013-05-25 23:41 | PDT | 2013-05-26 06:41 |  | 60.0307 | 59.9805 | 59.9331 | -0.050154 | -0.097586 |  |  | No | No | 59.5 | 0.4331 | 2013
WI_2013-05-29_180752 | 2013-05-29 11:08 | 2013-05-29 11:08 | PDT | 2013-05-29 18:08 | 751 | 59.9984 | 59.9497 | 59.9147 | -0.048777 | -0.083739 | -1539.6498 | -896.8389 | No | No | 59.5 | 0.4147 | 2013
WI_2013-05-30_225912 | 2013-05-30 15:59 | 2013-05-30 15:59 | PDT | 2013-05-30 22:59 |  | 59.9791 | 59.8063 | 59.7061 | -0.17282 | -0.27301 |  |  | No | No | 59.5 | 0.2061 | 2013
WI_2013-05-31_084841 | 2013-05-31 01:49 | 2013-05-31 01:49 | PDT | 2013-05-31 08:49 |  | 60.0168 | 59.9542 | 59.9254 | -0.062615 | -0.091376 |  |  | No | No | 59.5 | 0.4254 | 2013
WI_2013-06-12_003243 | 2013-06-11 17:33 | 2013-06-11 17:33 | PDT | 2013-06-12 00:33 |  | 60.0136 | 59.9701 | 59.9296 | -0.043567 | -0.084031 |  |  | No | No | 59.5 | 0.4296 | 2013
WI_2013-06-18_154948 | 2013-06-18 08:50 | 2013-06-18 08:50 | PDT | 2013-06-18 15:50 |  | 59.998 | 60.0461 | 60.0699 | 0.04802 | 0.071851 |  |  | No | No | 59.5 | 0.5699 | 2013
WI_2013-06-20_090230 | 2013-06-20 02:02 | 2013-06-20 02:02 | PDT | 2013-06-20 09:02 |  | 59.9867 | 59.9412 | 59.9258 | -0.045496 | -0.060899 |  |  | No | No | 59.5 | 0.4258 | 2013
WI_2013-06-29_104958 | 2013-06-29 03:50 | 2013-06-29 03:50 | PDT | 2013-06-29 10:50 | 1554 | 60.0211 | 59.9666 | 59.9458 | -0.054507 | -0.075349 | -2850.9932 | -2062.4004 | No | No | 59.5 | 0.4458 | 2013
WI_2013-06-29_172757 | 2013-06-29 10:28 | 2013-06-29 10:28 | PDT | 2013-06-29 17:28 | 1500 | 59.9907 | 59.8818 | 59.8497 | -0.10892 | -0.14101 | -1377.1789 | -1063.7432 | No | No | 59.5 | 0.3497 | 2013
WI_2013-07-06_194114 | 2013-07-06 12:41 | 2013-07-06 12:41 | PDT | 2013-07-06 19:41 | 783 | 59.9813 | 59.9314 | 59.9064 | -0.04998 | -0.074932 | -1566.6358 | -1044.9427 | Yes | Yes | 59.5 | 0.4064 | 2013
WI_2013-07-10_164941 | 2013-07-10 09:50 | 2013-07-10 09:50 | PDT | 2013-07-10 16:50 | 1130 | 59.9889 | 59.9052 | 59.8759 | -0.083714 | -0.11297 | -1349.8285 | -1000.2793 | Yes | Yes | 59.5 | 0.3759 | 2013
WI_2013-07-25_175006 | 2013-07-25 10:50 | 2013-07-25 10:50 | PDT | 2013-07-25 17:50 | 1150 | 59.9759 | 59.9059 | 59.868 | -0.06991 | -0.10786 | -1644.9619 | -1066.2361 | Yes | Yes | 59.5 | 0.368 | 2013
WI_2013-07-25_205214 | 2013-07-25 13:52 | 2013-07-25 13:52 | PDT | 2013-07-25 20:52 | 1000 | 59.9929 | 59.9249 | 59.9029 | -0.068018 | -0.089981 | -1470.204 | -1111.3506 | Yes | Yes | 59.5 | 0.4029 | 2013
WI_2013-07-30_215214 | 2013-07-30 14:52 | 2013-07-30 14:52 | PDT | 2013-07-30 21:52 |  | 60.0303 | 59.9751 | 59.9505 | -0.055199 | -0.079799 |  |  | No | No | 59.5 | 0.4505 | 2013
WI_2013-08-03_095046 | 2013-08-03 02:51 | 2013-08-03 02:51 | PDT | 2013-08-03 09:51 | 800 | 59.9851 | 59.9131 | 59.892 | -0.071979 | -0.093095 | -1111.4408 | -859.3344 | Yes | Yes | 59.5 | 0.392 | 2013
WI_2013-08-04_034544 | 2013-08-03 20:46 | 2013-08-03 20:46 | PDT | 2013-08-04 03:46 | 825 | 60.0109 | 59.9741 | 59.9186 | -0.036835 | -0.092346 | -2239.7287 | -893.382 | No | No | 59.5 | 0.4186 | 2013
WI_2013-08-04_075913 | 2013-08-04 00:59 | 2013-08-04 00:59 | PDT | 2013-08-04 07:59 |  | 59.9829 | 59.921 | 59.9031 | -0.061888 | -0.079807 |  |  | No | No | 59.5 | 0.4031 | 2013
WI_2013-08-07_222302 | 2013-08-07 15:23 | 2013-08-07 15:23 | PDT | 2013-08-07 22:23 |  | 60.0102 | 59.9559 | 59.9441 | -0.05428 | -0.066087 |  |  | No | No | 59.5 | 0.4441 | 2013
WI_2013-08-09_015350 | 2013-08-08 18:54 | 2013-08-08 18:54 | PDT | 2013-08-09 01:54 |  | 60.0038 | 59.9191 | 59.8694 | -0.084727 | -0.13438 |  |  | No | No | 59.5 | 0.3694 | 2013
WI_2013-08-10_234607 | 2013-08-10 16:46 | 2013-08-10 16:46 | PDT | 2013-08-10 23:46 |  | 59.9976 | 59.9237 | 59.9041 | -0.073845 | -0.093483 |  |  | No | No | 59.5 | 0.4041 | 2013
WI_2013-08-12_004006 | 2013-08-11 17:40 | 2013-08-11 17:40 | PDT | 2013-08-12 00:40 | 750 | 60.0002 | 59.9434 | 59.9049 | -0.05687 | -0.095331 | -1318.7884 | -786.729 | Yes | Yes | 59.5 | 0.4049 | 2013
WI_2013-08-13_223011 | 2013-08-13 15:30 | 2013-08-13 15:30 | PDT | 2013-08-13 22:30 |  | 59.9906 | 59.9512 | 59.9066 | -0.039404 | -0.084024 |  |  | No | No | 59.5 | 0.4066 | 2013
WI_2013-08-13_225605 | 2013-08-13 15:56 | 2013-08-13 15:56 | PDT | 2013-08-13 22:56 |  | 60.0078 | 59.97 | 59.9326 | -0.037834 | -0.075196 |  |  | No | No | 59.5 | 0.4326 | 2013
WI_2013-08-18_230350 | 2013-08-18 16:04 | 2013-08-18 16:04 | PDT | 2013-08-18 23:04 | 1800 | 59.9971 | 59.8898 | 59.8327 | -0.1073 | -0.16443 | -1677.5772 | -1094.6771 | No | No | 59.5 | 0.3327 | 2013
WI_2013-09-03_011601 | 2013-09-02 18:16 | 2013-09-02 18:16 | PDT | 2013-09-03 01:16 |  | 60.0113 | 59.9507 | 59.9152 | -0.060622 | -0.096132 |  |  | No | No | 59.5 | 0.4152 | 2013
WI_2013-09-07_073543 | 2013-09-07 00:36 | 2013-09-07 00:36 | PDT | 2013-09-07 07:36 |  | 60.0171 | 59.9703 | 59.946 | -0.046786 | -0.071108 |  |  | No | No | 59.5 | 0.446 | 2013
WI_2013-09-12_171007 | 2013-09-12 10:10 | 2013-09-12 10:10 | PDT | 2013-09-12 17:10 | 495 | 59.9949 | 59.9541 | 59.9303 | -0.040786 | -0.064611 | -1213.6627 | -766.1239 | No | No | 59.5 | 0.4303 | 2013
WI_2013-09-15_161111 | 2013-09-15 09:11 | 2013-09-15 09:11 | PDT | 2013-09-15 16:11 |  | 60.0129 | 59.9496 | 59.9424 | -0.063383 | -0.070536 |  |  | No | No | 59.5 | 0.4424 | 2013
WI_2013-09-15_161718 | 2013-09-15 09:17 | 2013-09-15 09:17 | PDT | 2013-09-15 16:17 |  | 60.005 | 59.9341 | 59.9264 | -0.070891 | -0.078613 |  |  | No | No | 59.5 | 0.4264 | 2013
WI_2013-09-15_233540 | 2013-09-15 16:36 | 2013-09-15 16:36 | PDT | 2013-09-15 23:36 |  | 59.9956 | 59.9547 | 59.9252 | -0.040908 | -0.070442 |  |  | No | No | 59.5 | 0.4252 | 2013
WI_2013-09-26_160000 | 2013-09-26 09:00 | 2013-09-26 09:00 | PDT | 2013-09-26 16:00 |  | 60.0225 | 59.982 | 59.9448 | -0.040483 | -0.07773 |  |  | No | No | 59.5 | 0.4448 | 2013
WI_2013-10-11_011407 | 2013-10-10 18:14 | 2013-10-10 18:14 | PDT | 2013-10-11 01:14 | 850 | 60.0066 | 59.9485 | 59.9058 | -0.058095 | -0.10084 | -1463.1113 | -842.8848 | Yes | Yes | 59.5 | 0.4058 | 2013
WI_2013-10-17_153600 | 2013-10-17 08:36 | 2013-10-17 08:36 | PDT | 2013-10-17 15:36 | 600 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.5 | -59.5 | 2013
WI_2013-10-19_174319 | 2013-10-19 10:43 | 2013-10-19 10:43 | PDT | 2013-10-19 17:43 |  | 60.0091 | 59.9551 | 59.9349 | -0.053951 | -0.07417 |  |  | No | No | 59.5 | 0.4349 | 2013
WI_2013-10-26_130010 | 2013-10-26 06:00 | 2013-10-26 06:00 | PDT | 2013-10-26 13:00 |  | 59.9786 | 60.0449 | 60.0556 | 0.066235 | 0.076949 |  |  | No | No | 59.5 | 0.5556 | 2013
WI_2013-11-13_130131 | 2013-11-13 05:02 | 2013-11-13 05:02 | PST | 2013-11-13 13:02 | 462 | 59.964 | 59.9204 | 59.9137 | -0.043568 | -0.050256 | -1060.4019 | -919.293 | No | No | 59.5 | 0.4137 | 2013
WI_2013-11-16_174251 | 2013-11-16 09:43 | 2013-11-16 09:43 | PST | 2013-11-16 17:43 |  | 60.0046 | 59.9355 | 59.9143 | -0.069189 | -0.09035 |  |  | No | No | 59.5 | 0.4143 | 2013
WI_2013-12-03_005842 | 2013-12-02 16:59 | 2013-12-02 16:59 | PST | 2013-12-03 00:59 | 1342 | 60.0066 | 59.9124 | 59.8714 | -0.094228 | -0.13521 | -1424.2089 | -992.5474 | Yes | Yes | 59.5 | 0.3714 | 2014
WI_2013-12-09_173829 | 2013-12-09 09:38 | 2013-12-09 09:38 | PST | 2013-12-09 17:38 | 400 | 59.9995 | 59.9784 | 59.9535 | -0.021065 | -0.045963 | -1898.8541 | -870.2598 | No | No | 59.5 | 0.4535 | 2014
WI_2013-12-11_230713 | 2013-12-11 15:07 | 2013-12-11 15:07 | PST | 2013-12-11 23:07 | 778 | 60.0153 | 59.9443 | 59.9243 | -0.071019 | -0.091043 | -1095.477 | -854.5458 | No | No | 59.5 | 0.4243 | 2014
WI_2014-01-13_133813 | 2014-01-13 05:38 | 2014-01-13 05:38 | PST | 2014-01-13 13:38 | 500 | 59.9521 | 59.9168 | 59.9037 | -0.035293 | -0.048367 | -1416.7019 | -1033.7673 | No | No | 59.5 | 0.4037 | 2014
WI_2014-01-15_151956 | 2014-01-15 07:20 | 2014-01-15 07:20 | PST | 2014-01-15 15:20 |  | 59.9682 | 59.9207 | 59.9444 | -0.047475 | -0.02378 |  |  | No | No | 59.5 | 0.4444 | 2014
WI_2014-01-25_024930 | 2014-01-24 18:49 | 2014-01-24 18:49 | PST | 2014-01-25 02:50 |  | 60.0208 | 59.9754 | 59.9442 | -0.045353 | -0.076558 |  |  | No | No | 59.5 | 0.4442 | 2014
WI_2014-01-26_181543 | 2014-01-26 10:16 | 2014-01-26 10:16 | PST | 2014-01-26 18:16 |  | 60.0084 | 59.9427 | 59.9679 | -0.065627 | -0.040464 |  |  | No | No | 59.5 | 0.4679 | 2014
WI_2014-01-29_144635 | 2014-01-29 06:47 | 2014-01-29 06:47 | PST | 2014-01-29 14:47 | 2200 | 59.991 | 59.8004 | 59.7508 | -0.1906 | -0.24018 | -1154.2711 | -915.9787 | No | No | 59.5 | 0.2508 | 2014
WI_2014-01-29_150327 | 2014-01-29 07:03 | 2014-01-29 07:03 | PST | 2014-01-29 15:03 | 1884 | 60.0069 | 59.8504 | 59.7799 | -0.15652 | -0.22698 | -1203.6515 | -830.024 | No | No | 59.5 | 0.2799 | 2014
WI_2014-02-02_192902 | 2014-02-02 11:29 | 2014-02-02 11:29 | PST | 2014-02-02 19:29 | 1450 | 60.0083 | 59.9088 | 59.8728 | -0.099492 | -0.13551 | -1457.4078 | -1070.0019 | Yes | Yes | 59.5 | 0.3728 | 2014
WI_2014-02-21_181346 | 2014-02-21 10:14 | 2014-02-21 10:14 | PST | 2014-02-21 18:14 | 939 | 59.9904 | 59.9151 | 59.8864 | -0.075312 | -0.104 | -1246.8054 | -902.8652 | Yes | Yes | 59.5 | 0.3864 | 2014
WI_2014-02-24_102611 | 2014-02-24 02:26 | 2014-02-24 02:26 | PST | 2014-02-24 10:26 | 740 | 60.0176 | 59.9382 | 59.9167 | -0.079351 | -0.10089 | -932.5675 | -733.4831 | No | No | 59.5 | 0.4167 | 2014
WI_2014-02-27_165352 | 2014-02-27 08:54 | 2014-02-27 08:54 | PST | 2014-02-27 16:54 | 877 | 59.9901 | 59.9208 | 59.8865 | -0.069293 | -0.10359 | -1265.6429 | -846.6457 | Yes | Yes | 59.5 | 0.3865 | 2014
WI_2014-03-02_202100 | 2014-03-02 12:21 | 2014-03-02 12:21 | PST | 2014-03-02 20:21 | 395 | 60.0204 | 59.9716 | 59.9466 | -0.048802 | -0.073755 | -809.3866 | -535.5585 | No | No | 59.5 | 0.4466 | 2014
WI_2014-03-13_165829 | 2014-03-13 09:58 | 2014-03-13 09:58 | PDT | 2014-03-13 16:58 | 365 | 60.0155 | 59.959 | 59.9225 | -0.056492 | -0.093018 | -646.1146 | -392.3959 | No | No | 59.5 | 0.4225 | 2014
WI_2014-03-23_194055 | 2014-03-23 12:41 | 2014-03-23 12:41 | PDT | 2014-03-23 19:41 | 496 | 60.01 | 59.9746 | 59.9388 | -0.035348 | -0.071175 | -1403.1809 | -696.8776 | No | No | 59.5 | 0.4388 | 2014
WI_2014-03-26_203644 | 2014-03-26 13:37 | 2014-03-26 13:37 | PDT | 2014-03-26 20:37 |  | 59.9775 | 60.0338 | 60.0478 | 0.056313 | 0.070336 |  |  | No | No | 59.5 | 0.5478 | 2014
WI_2014-03-31_160140 | 2014-03-31 09:02 | 2014-03-31 09:02 | PDT | 2014-03-31 16:02 | 560 | 59.9739 | 59.9343 | 59.9082 | -0.03956 | -0.065694 | -1415.569 | -852.4358 | No | No | 59.5 | 0.4082 | 2014
WI_2014-04-07_101549 | 2014-04-07 03:16 | 2014-04-07 03:16 | PDT | 2014-04-07 10:16 | 455 | 59.9944 | 59.9511 | 59.9273 | -0.043244 | -0.067069 | -1052.1645 | -678.4053 | No | No | 59.5 | 0.4273 | 2014
WI_2014-04-10_003257 | 2014-04-09 17:33 | 2014-04-09 17:33 | PDT | 2014-04-10 00:33 | 750 | 60.0162 | 59.9495 | 59.9188 | -0.066665 | -0.097356 | -1125.0266 | -770.3717 | No | No | 59.5 | 0.4188 | 2014
WI_2014-04-15_124532 | 2014-04-15 05:46 | 2014-04-15 05:46 | PDT | 2014-04-15 12:46 | 800 | 59.9936 | 59.9255 | 59.891 | -0.068103 | -0.10259 | -1174.6915 | -779.8115 | Yes | Yes | 59.5 | 0.391 | 2014
WI_2014-04-15_214242 | 2014-04-15 14:43 | 2014-04-15 14:43 | PDT | 2014-04-15 21:43 | 1509 | 60.0096 | 59.8956 | 59.8581 | -0.11399 | -0.15152 | -1323.7789 | -995.8798 | Yes | Yes | 59.5 | 0.3581 | 2014
WI_2014-04-21_174114 | 2014-04-21 10:41 | 2014-04-21 10:41 | PDT | 2014-04-21 17:41 | 1039 | 60.0082 | 59.9218 | 59.8749 | -0.086474 | -0.13334 | -1201.5116 | -779.2257 | Yes | Yes | 59.5 | 0.3749 | 2014
WI_2014-04-27_203353 | 2014-04-27 13:34 | 2014-04-27 13:34 | PDT | 2014-04-27 20:34 | 467 | 60.0076 | 59.9762 | 59.9337 | -0.031437 | -0.073906 | -1485.5087 | -631.8822 | No | No | 59.5 | 0.4337 | 2014
WI_2014-04-29_122257 | 2014-04-29 05:23 | 2014-04-29 05:23 | PDT | 2014-04-29 12:23 | 739 | 59.9826 | 59.919 | 59.8956 | -0.063652 | -0.087032 | -1161.0043 | -849.1168 | Yes | Yes | 59.5 | 0.3956 | 2014
WI_2014-05-12_173128 | 2014-05-12 10:31 | 2014-05-12 10:31 | PDT | 2014-05-12 17:31 | 747 | 60.0245 | 59.9445 | 59.9201 | -0.079987 | -0.10437 | -933.896 | -715.6959 | No | No | 59.5 | 0.4201 | 2014
WI_2014-05-17_061754 | 2014-05-16 23:18 | 2014-05-16 23:18 | PDT | 2014-05-17 06:18 | 3200 | 60.0091 | 59.8257 | 59.7505 | -0.18339 | -0.25857 | -1744.8877 | -1237.5795 | No | No | 59.5 | 0.2505 | 2014
WI_2014-05-26_193129 | 2014-05-26 12:31 | 2014-05-26 12:31 | PDT | 2014-05-26 19:31 | 1300 | 60.0018 | 59.8909 | 59.8161 | -0.11087 | -0.18565 | -1172.5298 | -700.2456 | No | No | 59.5 | 0.3161 | 2014
WI_2014-05-27_003132 | 2014-05-26 17:32 | 2014-05-26 17:32 | PDT | 2014-05-27 00:32 | 2826 | 59.9842 | 59.8044 | 59.6708 | -0.17974 | -0.31338 | -1572.2545 | -901.7929 | Yes | Yes | 59.5 | 0.1708 | 2014
WI_2014-06-02_160316 | 2014-06-02 09:03 | 2014-06-02 09:03 | PDT | 2014-06-02 16:03 | 662 | 60.0024 | 59.9457 | 59.9216 | -0.056699 | -0.080844 | -1167.5719 | -818.8594 | No | No | 59.5 | 0.4216 | 2014
WI_2014-06-05_065023 | 2014-06-04 23:50 | 2014-06-04 23:50 | PDT | 2014-06-05 06:50 | 792 | 60.0168 | 59.9347 | 59.9123 | -0.082133 | -0.1045 | -964.2845 | -757.8961 | No | No | 59.5 | 0.4123 | 2014
WI_2014-06-06_103711 | 2014-06-06 03:37 | 2014-06-06 03:37 | PDT | 2014-06-06 10:37 | 725 | 59.9919 | 59.9164 | 59.8852 | -0.075543 | -0.10671 | -959.7226 | -679.4011 | Yes | Yes | 59.5 | 0.3852 | 2014
WI_2014-06-13_010726 | 2014-06-12 18:07 | 2014-06-12 18:07 | PDT | 2014-06-13 01:07 | 1800 | 60.0234 | 59.9015 | 59.8418 | -0.1219 | -0.18164 | -1476.5764 | -990.9899 | No | No | 59.5 | 0.3418 | 2014
WI_2014-06-14_182145 | 2014-06-14 11:22 | 2014-06-14 11:22 | PDT | 2014-06-14 18:22 | 765 | 59.9786 | 59.926 | 59.9017 | -0.052576 | -0.076901 | -1455.0455 | -994.786 | No | No | 59.5 | 0.4017 | 2014
WI_2014-06-16_162800 | 2014-06-16 09:28 | 2014-06-16 09:28 | PDT | 2014-06-16 16:28 | 787 | 59.997 | 59.9426 | 59.9148 | -0.054422 | -0.082239 | -1446.0996 | -956.9679 | Yes | Yes | 59.5 | 0.4148 | 2014
WI_2014-06-30_202412 | 2014-06-30 13:24 | 2014-06-30 13:24 | PDT | 2014-06-30 20:24 | 694 | 59.9807 | 59.9332 | 59.9081 | -0.047429 | -0.07255 | -1463.2361 | -956.5809 | No | No | 59.5 | 0.4081 | 2014
WI_2014-07-02_214654 | 2014-07-02 14:47 | 2014-07-02 14:47 | PDT | 2014-07-02 21:47 | 1125 | 59.9661 | 59.902 | 59.8634 | -0.064109 | -0.1027 | -1754.823 | -1095.4185 | No | No | 59.5 | 0.3634 | 2014
WI_2014-07-04_101403 | 2014-07-04 03:14 | 2014-07-04 03:14 | PDT | 2014-07-04 10:14 | 725 | 59.9784 | 59.9354 | 59.9032 | -0.043043 | -0.075245 | -1684.3588 | -963.5174 | No | No | 59.5 | 0.4032 | 2014
WI_2014-07-07_172548 | 2014-07-07 10:26 | 2014-07-07 10:26 | PDT | 2014-07-07 17:26 | 615 | 59.983 | 59.9534 | 59.9193 | -0.029596 | -0.063699 | -2077.9528 | -965.4709 | No | No | 59.5 | 0.4193 | 2014
WI_2014-07-15_181909 | 2014-07-15 11:19 | 2014-07-15 11:19 | PDT | 2014-07-15 18:19 | 659 | 59.9801 | 59.9354 | 59.9028 | -0.044733 | -0.077298 | -1473.1847 | -852.5429 | No | No | 59.5 | 0.4028 | 2014
WI_2014-07-23_190118 | 2014-07-23 12:01 | 2014-07-23 12:01 | PDT | 2014-07-23 19:01 | 1159 | 60.0194 | 59.9412 | 59.9249 | -0.07822 | -0.094493 | -1481.7095 | -1226.5439 | No | No | 59.5 | 0.4249 | 2014
WI_2014-08-09_235857 | 2014-08-09 16:59 | 2014-08-09 16:59 | PDT | 2014-08-09 23:59 | 626 | 60.0313 | 59.9792 | 59.9574 | -0.052097 | -0.073892 | -1201.6068 | -847.1783 | No | No | 59.5 | 0.4574 | 2014
WI_2014-08-12_012945 | 2014-08-11 18:30 | 2014-08-11 18:30 | PDT | 2014-08-12 01:30 | 652 | 60.0188 | 59.9783 | 59.9509 | -0.040467 | -0.067905 | -1611.1942 | -960.1623 | No | No | 59.5 | 0.4509 | 2014
WI_2014-08-14_073242 | 2014-08-14 00:33 | 2014-08-14 00:33 | PDT | 2014-08-14 07:33 | 520 | 60.0403 | 59.9589 | 59.966 | -0.081317 | -0.074263 | -639.4714 | -700.2154 | No | No | 59.5 | 0.466 | 2014
WI_2014-08-23_064736 | 2014-08-22 23:48 | 2014-08-22 23:48 | PDT | 2014-08-23 06:48 | 733 | 60.0286 | 59.9478 | 59.9332 | -0.080861 | -0.095412 | -906.4924 | -768.2509 | No | No | 59.5 | 0.4332 | 2014
WI_2014-08-23_064932 | 2014-08-22 23:50 | 2014-08-22 23:50 | PDT | 2014-08-23 06:50 | 800 | 59.9749 | 59.9452 | 59.9047 | -0.029678 | -0.070168 | -2695.578 | -1140.1244 | No | No | 59.5 | 0.4047 | 2014
WI_2014-08-29_014551 | 2014-08-28 18:46 | 2014-08-28 18:46 | PDT | 2014-08-29 01:46 | 690 | 60.035 | 59.9715 | 59.9466 | -0.063516 | -0.088442 | -1086.3356 | -780.1694 | No | No | 59.5 | 0.4466 | 2014
WI_2014-09-03_214413 | 2014-09-03 14:44 | 2014-09-03 14:44 | PDT | 2014-09-03 21:44 | 565 | 59.9776 | 59.9489 | 59.9142 | -0.028691 | -0.063406 | -1969.2595 | -891.0763 | No | No | 59.5 | 0.4142 | 2014
WI_2014-09-07_154508 | 2014-09-07 08:45 | 2014-09-07 08:45 | PDT | 2014-09-07 15:45 | 400 | 59.958 | 59.918 | 59.9325 | -0.03992 | -0.025451 | -1002.0073 | -1571.6362 | No | No | 59.5 | 0.4325 | 2014
WI_2014-09-20_044508 | 2014-09-19 21:45 | 2014-09-19 21:45 | PDT | 2014-09-20 04:45 | 875 | 59.9976 | 59.9474 | 59.9204 | -0.050194 | -0.077214 | -1743.2394 | -1133.2211 | Yes | Yes | 59.5 | 0.4204 | 2014
WI_2014-09-24_091924 | 2014-09-24 02:19 | 2014-09-24 02:19 | PDT | 2014-09-24 09:19 | 740 | 60.0124 | 59.9306 | 59.9195 | -0.081772 | -0.092852 | -904.9601 | -796.9703 | Yes | Yes | 59.5 | 0.4195 | 2014
WI_2014-10-02_195947 | 2014-10-02 13:00 | 2014-10-02 13:00 | PDT | 2014-10-02 20:00 |  | 60.0148 | 59.9555 | 59.9395 | -0.059242 | -0.075276 |  |  | No | No | 59.5 | 0.4395 | 2014
WI_2014-10-07_214007 | 2014-10-07 14:40 | 2014-10-07 14:40 | PDT | 2014-10-07 21:40 | 1130 | 60.0119 | 59.9316 | 59.8942 | -0.080232 | -0.11766 | -1408.4145 | -960.3687 | Yes | Yes | 59.5 | 0.3942 | 2014
WI_2014-10-10_175631 | 2014-10-10 10:57 | 2014-10-10 10:57 | PDT | 2014-10-10 17:57 | 655 | 59.9975 | 59.9539 | 59.913 | -0.043609 | -0.084495 | -1501.9943 | -775.191 | No | No | 59.5 | 0.413 | 2014
WI_2014-10-18_100334 | 2014-10-18 03:04 | 2014-10-18 03:04 | PDT | 2014-10-18 10:04 | 863 | 60.0093 | 59.9318 | 59.9188 | -0.077414 | -0.090462 | -1114.7891 | -953.9895 | Yes | Yes | 59.5 | 0.4188 | 2014
WI_2014-10-18_102400 | 2014-10-18 03:24 | 2014-10-18 03:24 | PDT | 2014-10-18 10:24 | 729 | 60.0198 | 59.9285 | 59.9088 | -0.091315 | -0.11098 | -798.3363 | -656.8566 | No | No | 59.5 | 0.4088 | 2014
WI_2014-10-27_044128 | 2014-10-26 21:41 | 2014-10-26 21:41 | PDT | 2014-10-27 04:41 |  | 60.0274 | 59.9769 | 59.9464 | -0.050564 | -0.081032 |  |  | No | No | 59.5 | 0.4464 | 2014
WI_2014-10-28_195717 | 2014-10-28 12:57 | 2014-10-28 12:57 | PDT | 2014-10-28 19:57 | 516 | 60.0079 | 59.9476 | 59.9362 | -0.060306 | -0.071688 | -855.6355 | -719.7816 | No | No | 59.5 | 0.4362 | 2014
WI_2014-11-04_163314 | 2014-11-04 08:33 | 2014-11-04 08:33 | PST | 2014-11-04 16:33 | 951 | 60.0093 | 59.9146 | 59.8903 | -0.094671 | -0.11896 | -1004.5281 | -799.4162 | Yes | Yes | 59.5 | 0.3903 | 2014
WI_2014-11-23_171255 | 2014-11-23 09:13 | 2014-11-23 09:13 | PST | 2014-11-23 17:13 | 1022 | 60.009 | 59.9454 | 59.9154 | -0.063588 | -0.093617 | -1607.233 | -1091.6853 | Yes | Yes | 59.5 | 0.4154 | 2014
WI_2014-12-11_003016 | 2014-12-10 16:30 | 2014-12-10 16:30 | PST | 2014-12-11 00:30 | 700 | 59.9759 | 59.9367 | 59.8919 | -0.039298 | -0.08405 | -1781.2769 | -832.8358 | Yes | Yes | 59.5 | 0.3919 | 2015
WI_2014-12-28_131231 | 2014-12-28 05:13 | 2014-12-28 05:13 | PST | 2014-12-28 13:13 | 753 | 60.0045 | 59.946 | 59.9131 | -0.058439 | -0.091374 | -1288.5339 | -824.0885 | Yes | Yes | 59.5 | 0.4131 | 2015
WI_2014-12-29_220358 | 2014-12-29 14:04 | 2014-12-29 14:04 | PST | 2014-12-29 22:04 | 1170 | 60.0087 | 59.9174 | 59.8999 | -0.091306 | -0.10883 | -1281.4014 | -1075.1139 | Yes | Yes | 59.5 | 0.3999 | 2015
WI_2015-01-21_105153 | 2015-01-21 02:52 | 2015-01-21 02:52 | PST | 2015-01-21 10:52 | 860 | 60.0112 | 59.9259 | 59.9078 | -0.085349 | -0.10343 | -1007.6232 | -831.4608 | Yes | Yes | 59.5 | 0.4078 | 2015
WI_2015-01-21_112323 | 2015-01-21 03:23 | 2015-01-21 03:23 | PST | 2015-01-21 11:23 | 703 | 59.9912 | 59.9283 | 59.9054 | -0.062939 | -0.085807 | -1116.9482 | -819.2819 | Yes | Yes | 59.5 | 0.4054 | 2015
WI_2015-01-25_224735 | 2015-01-25 14:48 | 2015-01-25 14:48 | PST | 2015-01-25 22:48 | 764 | 59.9461 | 59.9267 | 59.937 | -0.019388 | -0.009094 | -3940.5311 | -8401.1437 | No | No | 59.5 | 0.437 | 2015
WI_2015-01-27_182332 | 2015-01-27 10:24 | 2015-01-27 10:24 | PST | 2015-01-27 18:24 | 800 | 59.9789 | 59.9431 | 59.9121 | -0.035791 | -0.066786 | -2235.2096 | -1197.8549 | No | No | 59.5 | 0.4121 | 2015
WI_2015-02-10_082952 | 2015-02-10 00:30 | 2015-02-10 00:30 | PST | 2015-02-10 08:30 | 428 | 60.0185 | 59.9685 | 59.9416 | -0.049949 | -0.076887 | -856.8819 | -556.6619 | No | No | 59.5 | 0.4416 | 2015
WI_2015-02-17_171400 | 2015-02-17 09:14 | 2015-02-17 09:14 | PST | 2015-02-17 17:14 | 728 | 60.0012 | 59.955 | 59.9223 | -0.046195 | -0.078939 | -1575.9244 | -922.2288 | Yes | Yes | 59.5 | 0.4223 | 2015
WI_2015-02-22_164350 | 2015-02-22 08:44 | 2015-02-22 08:44 | PST | 2015-02-22 16:44 | 660 | 59.9846 | 59.9563 | 59.9016 | -0.02832 | -0.082987 | -2330.5452 | -795.3092 | No | No | 59.5 | 0.4016 | 2015
WI_2015-02-25_010117 | 2015-02-24 17:01 | 2015-02-24 17:01 | PST | 2015-02-25 01:01 | 525 | 60.0129 | 59.9683 | 59.9446 | -0.044673 | -0.068332 | -1175.2044 | -768.3108 | No | No | 59.5 | 0.4446 | 2015
WI_2015-03-03_222452 | 2015-03-03 14:25 | 2015-03-03 14:25 | PST | 2015-03-03 22:25 | 700 | 59.976 | 59.9256 | 59.8919 | -0.050445 | -0.0841 | -1387.6491 | -832.3377 | Yes | Yes | 59.5 | 0.3919 | 2015
WI_2015-03-22_005349 | 2015-03-21 17:54 | 2015-03-21 17:54 | PDT | 2015-03-22 00:54 | 522 | 59.9847 | 59.9602 | 59.911 | -0.024489 | -0.073663 | -2131.5279 | -708.6303 | No | No | 59.5 | 0.411 | 2015
WI_2015-03-28_211525 | 2015-03-28 14:15 | 2015-03-28 14:15 | PDT | 2015-03-28 21:15 | 739 | 60.0014 | 59.9366 | 59.8988 | -0.064782 | -0.10259 | -1140.7577 | -720.3593 | Yes | Yes | 59.5 | 0.3988 | 2015
WI_2015-03-29_204844 | 2015-03-29 13:49 | 2015-03-29 13:49 | PDT | 2015-03-29 20:49 | 731 | 60.0104 | 59.9485 | 59.9046 | -0.061936 | -0.10579 | -1180.2549 | -690.9969 | Yes | Yes | 59.5 | 0.4046 | 2015
WI_2015-04-05_195754 | 2015-04-05 12:58 | 2015-04-05 12:58 | PDT | 2015-04-05 19:58 | 573 | 60.0048 | 59.9459 | 59.9141 | -0.058924 | -0.090693 | -972.4414 | -631.8002 | No | No | 59.5 | 0.4141 | 2015
WI_2015-04-07_131723 | 2015-04-07 06:17 | 2015-04-07 06:17 | PDT | 2015-04-07 13:17 | 465 | 59.9989 | 59.9701 | 59.9301 | -0.028816 | -0.068832 | -1613.695 | -675.561 | No | No | 59.5 | 0.4301 | 2015
WI_2015-04-16_090700 | 2015-04-16 02:07 | 2015-04-16 02:07 | PDT | 2015-04-16 09:07 |  | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.5 | -59.5 | 2015
WI_2015-04-17_161300 | 2015-04-17 09:13 | 2015-04-17 09:13 | PDT | 2015-04-17 16:13 |  | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.5 | -59.5 | 2015
WI_2015-04-23_072700 | 2015-04-23 00:27 | 2015-04-23 00:27 | PDT | 2015-04-23 07:27 |  | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.5 | -59.5 | 2015
WI_2015-04-26_175323 | 2015-04-26 10:53 | 2015-04-26 10:53 | PDT | 2015-04-26 17:53 | 504 | 59.9847 | 59.9405 | 59.9108 | -0.044201 | -0.073936 | -1140.2424 | -681.6664 | No | No | 59.5 | 0.4108 | 2015
WI_2015-04-28_130646 | 2015-04-28 06:07 | 2015-04-28 06:07 | PDT | 2015-04-28 13:07 | 1486 | 60.0233 | 59.8663 | 59.7999 | -0.15702 | -0.22343 | -946.3652 | -665.0834 | No | No | 59.5 | 0.2999 | 2015
WI_2015-04-28_130945 | 2015-04-28 06:10 | 2015-04-28 06:10 | PDT | 2015-04-28 13:10 | 300 | 59.865 | 59.8475 | 59.8343 | -0.017554 | -0.030704 | -1709.0381 | -977.0555 | No | No | 59.5 | 0.3343 | 2015
WI_2015-04-28_192623 | 2015-04-28 12:26 | 2015-04-28 12:26 | PDT | 2015-04-28 19:26 | 350 | 60.0228 | 59.9781 | 59.9508 | -0.04474 | -0.072004 | -782.3062 | -486.0836 | No | No | 59.5 | 0.4508 | 2015
WI_2015-04-28_203551 | 2015-04-28 13:36 | 2015-04-28 13:36 | PDT | 2015-04-28 20:36 | 350 | 60.0106 | 59.9683 | 59.9381 | -0.04233 | -0.072494 | -826.8444 | -482.7968 | No | No | 59.5 | 0.4381 | 2015
WI_2015-05-03_113947 | 2015-05-03 04:40 | 2015-05-03 04:40 | PDT | 2015-05-03 11:40 | 645 | 60.0017 | 59.951 | 59.9161 | -0.050736 | -0.085588 | -1271.296 | -753.6126 | No | Yes | 59.5 | 0.4161 | 2015
WI_2015-05-06_020026 | 2015-05-05 19:00 | 2015-05-05 19:00 | PDT | 2015-05-06 02:00 | 715 | 60.0155 | 59.9711 | 59.9234 | -0.044395 | -0.092067 | -1610.53 | -776.6043 | No | No | 59.5 | 0.4234 | 2015
WI_2015-05-12_170341 | 2015-05-12 10:04 | 2015-05-12 10:04 | PDT | 2015-05-12 17:04 | 418 | 60.0125 | 59.9789 | 59.9485 | -0.033607 | -0.064048 | -1243.7891 | -652.6399 | No | No | 59.5 | 0.4485 | 2015
WI_2015-05-12_174110 | 2015-05-12 10:41 | 2015-05-12 10:41 | PDT | 2015-05-12 17:41 | 671 | 59.9912 | 59.9552 | 59.9133 | -0.036055 | -0.077919 | -1861.069 | -861.1532 | No | No | 59.5 | 0.4133 | 2015
WI_2015-05-28_213706 | 2015-05-28 14:37 | 2015-05-28 14:37 | PDT | 2015-05-28 21:37 | 782 | 60.0003 | 59.9631 | 59.927 | -0.037259 | -0.073352 | -2098.8197 | -1066.0978 | Yes | Yes | 59.5 | 0.427 | 2015
WI_2015-05-30_211702 | 2015-05-30 14:17 | 2015-05-30 14:17 | PDT | 2015-05-30 21:17 | -510.2 | 60.0014 | 60.041 | 60.067 | 0.039641 | 0.065646 | -1287.0432 | -777.2025 | No | No | 59.5 | 0.567 | 2015
WI_2015-06-10_130119 | 2015-06-10 06:01 | 2015-06-10 06:01 | PDT | 2015-06-10 13:01 | 425 | 60.0357 | 59.9939 | 59.9769 | -0.041795 | -0.058827 | -1016.874 | -722.4612 | No | No | 59.5 | 0.4769 | 2015
WI_2015-06-22_221203 | 2015-06-22 15:12 | 2015-06-22 15:12 | PDT | 2015-06-22 22:12 | 750 | 59.9864 | 59.9396 | 59.9127 | -0.0468 | -0.073718 | -1602.5584 | -1017.3962 | Yes | Yes | 59.5 | 0.4127 | 2015
WI_2015-06-30_212756 | 2015-06-30 14:28 | 2015-06-30 14:28 | PDT | 2015-06-30 21:28 |  | 60.0164 | 59.9704 | 59.9461 | -0.045965 | -0.070302 |  |  | No | No | 59.5 | 0.4461 | 2015
WI_2015-07-01_141441 | 2015-07-01 07:15 | 2015-07-01 07:15 | PDT | 2015-07-01 14:15 | 812 | 60.0092 | 59.9491 | 59.9232 | -0.0601 | -0.085995 | -1351.0871 | -944.2414 | Yes | Yes | 59.5 | 0.4232 | 2015
WI_2015-07-10_100329 | 2015-07-10 03:03 | 2015-07-10 03:03 | PDT | 2015-07-10 10:03 | 699 | 59.9944 | 59.9365 | 59.9193 | -0.057851 | -0.075087 | -1208.2839 | -930.9222 | No | Yes | 59.5 | 0.4193 | 2015
WI_2015-07-10_235810 | 2015-07-10 16:58 | 2015-07-10 16:58 | PDT | 2015-07-10 23:58 | 1288 | 59.9996 | 59.9171 | 59.8753 | -0.082534 | -0.12431 | -1560.573 | -1036.1133 | Yes | Yes | 59.5 | 0.3753 | 2015
WI_2015-07-15_111948 | 2015-07-15 04:20 | 2015-07-15 04:20 | PDT | 2015-07-15 11:20 | 740 | 59.9866 | 59.9385 | 59.9141 | -0.048082 | -0.072518 | -1539.035 | -1020.4381 | No | No | 59.5 | 0.4141 | 2015
WI_2015-07-26_172525 | 2015-07-26 10:25 | 2015-07-26 10:25 | PDT | 2015-07-26 17:25 | 742 | 59.996 | 59.9305 | 59.9082 | -0.065528 | -0.087825 | -1132.3396 | -844.8591 | Yes | Yes | 59.5 | 0.4082 | 2015
WI_2015-07-30_001100 | 2015-07-29 17:11 | 2015-07-29 17:11 | PDT | 2015-07-30 00:11 | 778 | 60.0214 | 59.9635 | 59.933 | -0.057956 | -0.088446 | -1342.3883 | -879.6361 | No | No | 59.5 | 0.433 | 2015
WI_2015-08-05_020719 | 2015-08-04 19:07 | 2015-08-04 19:07 | PDT | 2015-08-05 02:07 | 1047 | 60.009 | 59.9438 | 59.9048 | -0.065158 | -0.10419 | -1606.8678 | -1004.9191 | Yes | Yes | 59.5 | 0.4048 | 2015
WI_2015-09-01_173013 | 2015-09-01 10:30 | 2015-09-01 10:30 | PDT | 2015-09-01 17:30 | 753 | 59.9879 | 59.9242 | 59.8981 | -0.06365 | -0.089761 | -1183.0283 | -838.8987 | Yes | Yes | 59.5 | 0.3981 | 2015
WI_2015-09-03_144820 | 2015-09-03 07:48 | 2015-09-03 07:48 | PDT | 2015-09-03 14:48 | 750 | 59.9806 | 59.9251 | 59.8983 | -0.055532 | -0.082313 | -1350.5832 | -911.1582 | Yes | Yes | 59.5 | 0.3983 | 2015
WI_2015-09-05_142512 | 2015-09-05 07:25 | 2015-09-05 07:25 | PDT | 2015-09-05 14:25 | 1465 | 59.9974 | 59.8887 | 59.8448 | -0.10864 | -0.15256 | -1348.5151 | -960.2584 | Yes | Yes | 59.5 | 0.3448 | 2015
WI_2015-09-15_155002 | 2015-09-15 08:50 | 2015-09-15 08:50 | PDT | 2015-09-15 15:50 | 750 | 60.0128 | 59.945 | 59.9271 | -0.067837 | -0.08573 | -1105.5883 | -874.8364 | No | No | 59.5 | 0.4271 | 2015
WI_2015-09-22_151031 | 2015-09-22 08:11 | 2015-09-22 08:11 | PDT | 2015-09-22 15:11 | 783 | 60.0116 | 59.9642 | 59.918 | -0.047411 | -0.09357 | -1651.5036 | -836.8089 | No | No | 59.5 | 0.418 | 2015
WI_2015-09-24_063150 | 2015-09-23 23:32 | 2015-09-23 23:32 | PDT | 2015-09-24 06:32 | 334 | 60.0269 | 59.9656 | 59.9625 | -0.061248 | -0.064386 | -545.3239 | -518.7491 | No | No | 59.5 | 0.4625 | 2015
WI_2015-10-01_052317 | 2015-09-30 22:23 | 2015-09-30 22:23 | PDT | 2015-10-01 05:23 | 750 | 60.0138 | 59.9631 | 59.9209 | -0.050729 | -0.092946 | -1478.4472 | -806.9238 | No | No | 59.5 | 0.4209 | 2015
WI_2015-10-06_211708 | 2015-10-06 14:17 | 2015-10-06 14:17 | PDT | 2015-10-06 21:17 |  | 60.0138 | 59.9619 | 59.9401 | -0.051861 | -0.073705 |  |  | No | No | 59.5 | 0.4401 | 2015
WI_2015-10-09_190832 | 2015-10-09 12:09 | 2015-10-09 12:09 | PDT | 2015-10-09 19:09 | 755 | 60.0089 | 59.9442 | 59.9135 | -0.064687 | -0.095355 | -1167.1621 | -791.7818 | Yes | Yes | 59.5 | 0.4135 | 2015
WI_2015-10-10_065924 | 2015-10-09 23:59 | 2015-10-09 23:59 | PDT | 2015-10-10 06:59 |  | 60.0113 | 59.9501 | 59.9402 | -0.061203 | -0.071112 |  |  | No | No | 59.5 | 0.4402 | 2015
WI_2015-10-30_153513 | 2015-10-30 08:35 | 2015-10-30 08:35 | PDT | 2015-10-30 15:35 | 801 | 60.0061 | 59.949 | 59.912 | -0.05703 | -0.094077 | -1404.5176 | -851.4335 | Yes | Yes | 59.5 | 0.412 | 2015
WI_2015-11-05_071818 | 2015-11-04 23:18 | 2015-11-04 23:18 | PST | 2015-11-05 07:18 | 670 | 60.0389 | 59.9812 | 59.971 | -0.057657 | -0.067899 | -1162.0401 | -986.7599 | No | No | 59.5 | 0.471 | 2015
WI_2015-11-08_211447 | 2015-11-08 13:15 | 2015-11-08 13:15 | PST | 2015-11-08 21:15 | 740 | 59.9997 | 59.9264 | 59.8994 | -0.07335 | -0.10033 | -1008.865 | -737.5477 | Yes | Yes | 59.5 | 0.3994 | 2015
WI_2015-11-13_153425 | 2015-11-13 07:34 | 2015-11-13 07:34 | PST | 2015-11-13 15:34 | 840 | 60.0143 | 59.9576 | 59.919 | -0.056648 | -0.095295 | -1482.8346 | -881.4716 | No | No | 59.5 | 0.419 | 2015
WI_2015-11-30_153016 | 2015-11-30 07:30 | 2015-11-30 07:30 | PST | 2015-11-30 15:30 | 816 | 60.0189 | 59.9498 | 59.9237 | -0.069125 | -0.095221 | -1180.4656 | -856.9556 | No | No | 59.5 | 0.4237 | 2015
WI_2015-12-10_160006 | 2015-12-10 08:00 | 2015-12-10 08:00 | PST | 2015-12-10 16:00 | -358 | 59.9903 | 60.034 | 60.0559 | 0.043774 | 0.06565 | -817.8352 | -545.3122 | No | No | 59.5 | 0.5559 | 2016
WI_2015-12-20_220439 | 2015-12-20 14:05 | 2015-12-20 14:05 | PST | 2015-12-20 22:05 | 510 | 60.034 | 60.0075 | 59.9723 | -0.026488 | -0.061693 | -1925.3807 | -826.6746 | No | No | 59.5 | 0.4723 | 2016
WI_2015-12-27_010857 | 2015-12-26 17:09 | 2015-12-26 17:09 | PST | 2015-12-27 01:09 | 380 | 60.0012 | 59.9604 | 59.9349 | -0.040827 | -0.066283 | -930.7609 | -573.3015 | No | No | 59.5 | 0.4349 | 2016
WI_2015-12-29_155446 | 2015-12-29 07:55 | 2015-12-29 07:55 | PST | 2015-12-29 15:55 | 532 | 60.0106 | 59.9672 | 59.9462 | -0.043378 | -0.06441 | -1226.4167 | -825.953 | No | No | 59.5 | 0.4462 | 2016
WI_2016-01-21_090853 | 2016-01-21 01:09 | 2016-01-21 01:09 | PST | 2016-01-21 09:09 | 1471 | 59.97 | 59.887 | 59.831 | -0.083 | -0.139 | -1772.2892 | -1058.2734 | Yes | Yes | 59.5 | 0.331 | 2016
WI_2016-01-23_204722 | 2016-01-23 12:47 | 2016-01-23 12:47 | PST | 2016-01-23 20:47 | 715 | 60.012 | 59.973 | 59.94 | -0.039 | -0.072 | -1833.3333 | -993.0556 | Yes | No | 59.5 | 0.44 | 2016
WI_2016-01-25_051837 | 2016-01-24 21:19 | 2016-01-24 21:19 | PST | 2016-01-25 05:19 | 733 | 60.0273 | 59.9905 | 59.939 | -0.036809 | -0.088282 | -1991.3727 | -830.2928 | No | No | 59.5 | 0.439 | 2016
WI_2016-01-27_001928 | 2016-01-26 16:19 | 2016-01-26 16:19 | PST | 2016-01-27 00:19 | 746 | 59.989 | 59.942 | 59.902 | -0.047 | -0.087 | -1587.234 | -857.4713 | Yes | Yes | 59.5 | 0.402 | 2016
WI_2016-02-28_174752 | 2016-02-28 09:48 | 2016-02-28 09:48 | PST | 2016-02-28 17:48 | 454 | 60.019 | 59.977 | 59.946 | -0.042 | -0.073 | -1080.9524 | -621.9178 | Yes | No | 59.5 | 0.446 | 2016
WI_2016-02-29_162422 | 2016-02-29 08:24 | 2016-02-29 08:24 | PST | 2016-02-29 16:24 | 757 | 60.015 | 59.969 | 59.924 | -0.046 | -0.091 | -1645.6522 | -831.8681 | Yes | No | 59.5 | 0.424 | 2016
WI_2016-03-03_230447 | 2016-03-03 15:05 | 2016-03-03 15:05 | PST | 2016-03-03 23:05 | 1030 | 59.9829 | 59.8348 | 59.8162 | -0.14808 | -0.16667 | -695.55 | -617.9926 | No | No | 59.5 | 0.3162 | 2016
WI_2016-03-07_222634 | 2016-03-07 14:27 | 2016-03-07 14:27 | PST | 2016-03-07 22:27 |  | 60.0258 | 59.9988 | 59.9502 | -0.027005 | -0.075645 |  |  | No | No | 59.5 | 0.4502 | 2016
WI_2016-03-08_223622 | 2016-03-08 14:36 | 2016-03-08 14:36 | PST | 2016-03-08 22:36 | 758 | 60.01 | 59.963 | 59.919 | -0.047 | -0.091 | -1612.766 | -832.967 | Yes | Yes | 59.5 | 0.419 | 2016
WI_2016-03-09_004415 | 2016-03-08 16:44 | 2016-03-08 16:44 | PST | 2016-03-09 00:44 | 830 | 59.985 | 59.968 | 59.923 | -0.017 | -0.062 | -4882.3529 | -1338.7097 | Yes | Yes | 59.5 | 0.423 | 2016
WI_2016-03-14_131024 | 2016-03-14 06:10 | 2016-03-14 06:10 | PDT | 2016-03-14 13:10 | 1550 | 59.9055 | 59.8729 | 59.8735 | -0.032544 | -0.031974 | -4762.7374 | -4847.7132 | No | No | 59.5 | 0.3735 | 2016
WI_2016-03-28_202141 | 2016-03-28 13:22 | 2016-03-28 13:22 | PDT | 2016-03-28 20:22 | 1151 | 59.98 | 59.902 | 59.88 | -0.078 | -0.1 | -1475.641 | -1151 | Yes | Yes | 59.5 | 0.38 | 2016
WI_2016-03-29_104630 | 2016-03-29 03:47 | 2016-03-29 03:47 | PDT | 2016-03-29 10:46 | 756 | 59.968 | 59.947 | 59.913 | -0.021 | -0.055 | -3600 | -1374.5455 | Yes | Yes | 59.5 | 0.413 | 2016
WI_2016-04-05_094923 | 2016-04-05 02:49 | 2016-04-05 02:49 | PDT | 2016-04-05 09:49 | 500 | 60.034 | 59.987 | 59.954 | -0.047 | -0.08 | -1063.8298 | -625 | Yes | No | 59.5 | 0.454 | 2016
WI_2016-04-10_095735 | 2016-04-10 02:58 | 2016-04-10 02:58 | PDT | 2016-04-10 09:58 | 497 | 59.998 | 59.959 | 59.918 | -0.039 | -0.08 | -1274.359 | -621.25 | Yes | Yes | 59.5 | 0.418 | 2016
WI_2016-04-10_153143 | 2016-04-10 08:32 | 2016-04-10 08:32 | PDT | 2016-04-10 15:32 | 0 | 59.965 | 60.016 | 59.956 | 0.051 | -0.009 |  |  | No | No | -0.015 | 59.971 | 2016
WI_2016-04-26_091503 | 2016-04-26 02:15 | 2016-04-26 02:15 | PDT | 2016-04-26 09:15 | 508 | 60.037 | 59.979 | 59.935 | -0.058 | -0.102 | -875.8621 | -498.0392 | Yes | No | 59.5 | 0.435 | 2016
WI_2016-04-27_161724 | 2016-04-27 09:17 | 2016-04-27 09:17 | PDT | 2016-04-27 16:17 |  | 60.027 | 60.008 | 59.9541 | -0.01899 | -0.072867 |  |  | No | No | 59.5 | 0.4541 | 2016
WI_2016-05-04_092039 | 2016-05-04 02:21 | 2016-05-04 02:21 | PDT | 2016-05-04 09:21 | 666 | 60.005 | 59.955 | 59.913 | -0.05 | -0.092 | -1332 | -723.913 | Yes | Yes | 59.5 | 0.413 | 2016
WI_2016-05-05_162800 | 2016-05-05 09:28 | 2016-05-05 09:28 | PDT | 2016-05-05 16:28 | 500 | 60.011 | 59.968 | 59.924 | -0.043 | -0.087 | -1162.7907 | -574.7126 | Yes | No | 59.5 | 0.424 | 2016
WI_2016-05-07_062001 | 2016-05-06 23:20 | 2016-05-06 23:20 | PDT | 2016-05-07 06:20 | 615 | 60.023 | 60.001 | 59.941 | -0.022 | -0.082 | -2795.4545 | -750 | Yes | No | 59.5 | 0.441 | 2016
WI_2016-05-18_112814 | 2016-05-18 04:28 | 2016-05-18 04:28 | PDT | 2016-05-18 11:28 | 753 | 60.005 | 59.94 | 59.892 | -0.065 | -0.113 | -1158.4615 | -666.3717 | Yes | Yes | 59.5 | 0.392 | 2016
WI_2016-05-22_124544 | 2016-05-22 05:46 | 2016-05-22 05:46 | PDT | 2016-05-22 12:46 | 752 | 60.01 | 59.939 | 59.887 | -0.071 | -0.123 | -1059.1549 | -611.3821 | Yes | Yes | 59.5 | 0.387 | 2016
WI_2016-05-29_073000 | 2016-05-29 00:30 | 2016-05-29 00:30 | PDT | 2016-05-29 07:30 | 401 | 60.012 | 59.974 | 59.94 | -0.038 | -0.072 | -1055.2632 | -556.9444 | Yes | No | 59.5 | 0.44 | 2016
WI_2016-05-30_135835 | 2016-05-30 06:59 | 2016-05-30 06:59 | PDT | 2016-05-30 13:59 | 624 | 60.011 | 59.972 | 59.935 | -0.039 | -0.076 | -1600 | -821.0526 | Yes | No | 59.5 | 0.435 | 2016
WI_2016-06-01_012933 | 2016-05-31 18:30 | 2016-05-31 18:30 | PDT | 2016-06-01 01:30 | 514 | 59.993 | 59.952 | 59.926 | -0.041 | -0.067 | -1253.6585 | -767.1642 | No | No | 59.5 | 0.426 | 2016
WI_2016-06-02_154954 | 2016-06-02 08:50 | 2016-06-02 08:50 | PDT | 2016-06-02 15:50 | 733 | 59.996 | 59.944 | 59.911 | -0.052 | -0.085 | -1409.6154 | -862.3529 | Yes | Yes | 59.5 | 0.411 | 2016
WI_2016-06-04_074910 | 2016-06-04 00:49 | 2016-06-04 00:49 | PDT | 2016-06-04 07:49 | 651 | 60.033 | 59.977 | 59.95 | -0.056 | -0.083 | -1162.5 | -784.3373 | Yes | No | 59.5 | 0.45 | 2016
WI_2016-06-06_115826 | 2016-06-06 04:58 | 2016-06-06 04:58 | PDT | 2016-06-06 11:58 | 594 | 60.01 | 59.962 | 59.934 | -0.048 | -0.076 | -1237.5 | -781.5789 | Yes | No | 59.5 | 0.434 | 2016
WI_2016-06-20_053448 | 2016-06-19 22:35 | 2016-06-19 22:35 | PDT | 2016-06-20 05:35 | 770 | 60.046 | 59.985 | 59.95 | -0.061 | -0.096 | -1262.2951 | -802.0833 | Yes | No | 59.5 | 0.45 | 2016
WI_2016-06-29_082215 | 2016-06-29 01:22 | 2016-06-29 01:22 | PDT | 2016-06-29 08:22 | 670 | 59.977 | 59.944 | 59.913 | -0.033 | -0.064 | -2030.303 | -1046.875 | Yes | No | 59.5 | 0.413 | 2016
WI_2016-07-14_000516 | 2016-07-13 17:05 | 2016-07-13 17:05 | PDT | 2016-07-14 00:05 | 0 | 60.027 | 59.988 | 59.975 | -0.039 | -0.052 |  |  | No | No | 59.5 | 0.475 | 2016
WI_2016-07-15_030648 | 2016-07-14 20:07 | 2016-07-14 20:07 | PDT | 2016-07-15 03:07 | 431 | 60.03 | 60.004 | 59.979 | -0.026 | -0.051 | -1657.6923 | -845.098 | No | No | 59.5 | 0.479 | 2016
WI_2016-07-21_155103 | 2016-07-21 08:51 | 2016-07-21 08:51 | PDT | 2016-07-21 15:51 | 703 | 59.991 | 59.95 | 59.922 | -0.041 | -0.069 | -1714.6341 | -1018.8406 | Yes | Yes | 59.5 | 0.422 | 2016
WI_2016-07-21_155500 | 2016-07-21 08:55 | 2016-07-21 08:55 | PDT | 2016-07-21 15:55 | 736 | 59.958 | 59.944 | 59.926 | -0.014 | -0.032 | -5257.1429 | -2300 | No | No | 59.5 | 0.426 | 2016
WI_2016-07-22_095109 | 2016-07-22 02:51 | 2016-07-22 02:51 | PDT | 2016-07-22 09:51 | 595 | 59.981 | 59.947 | 59.923 | -0.034 | -0.058 | -1750 | -1025.8621 | Yes | No | 59.5 | 0.423 | 2016
WI_2016-07-23_015732 | 2016-07-22 18:58 | 2016-07-22 18:58 | PDT | 2016-07-23 01:58 | 576 | 60.013 | 59.966 | 59.939 | -0.047 | -0.074 | -1225.5319 | -778.3784 | Yes | No | 59.5 | 0.439 | 2016
WI_2016-07-27_192201 | 2016-07-27 12:22 | 2016-07-27 12:22 | PDT | 2016-07-27 19:22 | 578 | 60.013 | 59.977 | 59.95 | -0.036 | -0.063 | -1605.5556 | -917.4603 | Yes | No | 59.5 | 0.45 | 2016
WI_2016-08-10_180820 | 2016-08-10 11:08 | 2016-08-10 11:08 | PDT | 2016-08-10 18:08 | 684 | 60.02 | 59.961 | 59.933 | -0.059 | -0.087 | -1159.322 | -786.2069 | Yes | No | 59.5 | 0.433 | 2016
WI_2016-08-13_020028 | 2016-08-12 19:00 | 2016-08-12 19:00 | PDT | 2016-08-13 02:00 | 941 | 60.021 | 59.941 | 59.996 | -0.08 | -0.025 | -1176.25 | -3764 | No | No | 59.5 | 0.496 | 2016
WI_2016-08-15_011923 | 2016-08-14 18:19 | 2016-08-14 18:19 | PDT | 2016-08-15 01:19 | 705 | 60.036 | 59.963 | 59.934 | -0.073 | -0.102 | -965.7534 | -691.1765 | Yes | No | 59.5 | 0.434 | 2016
WI_2016-08-16_184506 | 2016-08-16 11:45 | 2016-08-16 11:45 | PDT | 2016-08-16 18:45 | 1182 | 59.979 | 59.92 | 59.867 | -0.059 | -0.112 | -2003.3898 | -1055.3571 | Yes | Yes | 59.5 | 0.367 | 2016
WI_2016-08-24_025115 | 2016-08-23 19:51 | 2016-08-23 19:51 | PDT | 2016-08-24 02:51 | 570 | 60.027 | 59.975 | 59.957 | -0.052 | -0.07 | -1096.1538 | -814.2857 | Yes | No | 59.5 | 0.457 | 2016
WI_2016-09-06_201752 | 2016-09-06 13:18 | 2016-09-06 13:18 | PDT | 2016-09-06 20:18 | 754 | 59.983 | 59.939 | 59.901 | -0.044 | -0.082 | -1713.6364 | -919.5122 | Yes | Yes | 59.5 | 0.401 | 2016
WI_2016-09-08_043158 | 2016-09-07 21:32 | 2016-09-07 21:32 | PDT | 2016-09-08 04:32 | 1312 | 60.011 | 59.93 | 59.871 | -0.081 | -0.14 | -1619.7531 | -937.1429 | Yes | Yes | 59.5 | 0.371 | 2016
WI_2016-09-17_051916 | 2016-09-16 22:19 | 2016-09-16 22:19 | PDT | 2016-09-17 05:19 | 770 | 60.01 | 59.946 | 59.903 | -0.064 | -0.107 | -1203.125 | -719.6262 | Yes | Yes | 59.5 | 0.403 | 2016
WI_2016-09-19_213431 | 2016-09-19 14:35 | 2016-09-19 14:35 | PDT | 2016-09-19 21:35 | 1315 | 60.011 | 59.901 | 59.853 | -0.11 | -0.158 | -1195.4545 | -832.2785 | Yes | Yes | 59.5 | 0.353 | 2016
WI_2016-09-21_202635 | 2016-09-21 13:27 | 2016-09-21 13:27 | PDT | 2016-09-21 20:27 | 1423 | 59.985 | 59.89 | 59.819 | -0.095 | -0.166 | -1497.8947 | -857.2289 | Yes | Yes | 59.5 | 0.319 | 2016
WI_2016-10-01_062043 | 2016-09-30 23:21 | 2016-09-30 23:21 | PDT | 2016-10-01 06:21 | 435 | 60.034 | 59.99 | 59.964 | -0.044 | -0.07 | -988.6364 | -621.4286 | Yes | No | 59.5 | 0.464 | 2016
WI_2016-10-03_161047 | 2016-10-03 09:11 | 2016-10-03 09:11 | PDT | 2016-10-03 16:11 |  | 60.027 | 59.981 | 59.966 | -0.046 | -0.061 |  |  | No | No | 59.5 | 0.466 | 2016
WI_2016-10-06_064010 | 2016-10-05 23:40 | 2016-10-05 23:40 | PDT | 2016-10-06 06:40 | 730 | 60.021 | 59.948 | 59.922 | -0.073 | -0.099 | -1000 | -737.3737 | Yes | No | 59.5 | 0.422 | 2016
WI_2016-10-06_193018 | 2016-10-06 12:30 | 2016-10-06 12:30 | PDT | 2016-10-06 19:30 | -306 | 59.988 | 60.025 | 59.985 | 0.037 | -0.003 | -827.027 | 10200 | No | No | 59.5 | 0.485 | 2016
WI_2016-10-15_180023 | 2016-10-15 11:00 | 2016-10-15 11:00 | PDT | 2016-10-15 18:00 | -311 | 59.999 | 60.044 | 59.992 | 0.045 | -0.007 | -691.1111 | 4442.8571 | No | No | 59.5 | 0.492 | 2016
WI_2016-10-19_223017 | 2016-10-19 15:30 | 2016-10-19 15:30 | PDT | 2016-10-19 22:30 | -308 | 59.964 | 60.021 | 59.959 | 0.057 | -0.005 | -540.3509 | 6160 | No | No | 59.5 | 0.459 | 2016
WI_2016-10-25_083857 | 2016-10-25 01:39 | 2016-10-25 01:39 | PDT | 2016-10-25 08:39 | 716 | 59.998 | 59.954 | 59.916 | -0.044 | -0.082 | -1627.2727 | -873.1707 | Yes | Yes | 59.5 | 0.416 | 2016
WI_2016-10-26_233006 | 2016-10-26 16:30 | 1900-02-27 23:12 | PDT | 2016-10-26 23:30 | 507 | 59.991 | 59.967 | 59.922 | -0.024 | -0.069 | -2112.5 | -734.7826 | Yes | No | 59.5 | 0.422 | 2016
WI_2016-10-28_113126 | 2016-10-28 04:31 | 2016-10-28 04:31 | PDT | 2016-10-28 11:31 | 770 | 59.983 | 59.928 | 59.897 | -0.055 | -0.086 | -1400 | -895.3488 | Yes | Yes | 59.5 | 0.397 | 2016
WI_2016-11-16_195444 | 2016-11-16 11:55 | 2016-11-16 11:55 | PST | 2016-11-16 19:55 | 588 | 60.034 | 59.985 | 59.956 | -0.049 | -0.078 | -1200 | -753.8462 | Yes | No | 59.5 | 0.456 | 2016
WI_2016-11-16_220017 | 2016-11-16 14:00 | 2016-11-16 14:00 | PST | 2016-11-16 22:00 | -297 | 59.974 | 60.019 | 59.968 | 0.045 | -0.006 | -660 | 4950 | No | No | 59.5 | 0.468 | 2016
WI_2016-11-18_001220 | 2016-11-17 16:12 | 2016-11-17 16:12 | PST | 2016-11-18 00:12 | 588 | 59.99 | 59.952 | 59.927 | -0.038 | -0.063 | -1547.3684 | -933.3333 | No | No | 59.5 | 0.427 | 2016
WI_2016-11-21_185757 | 2016-11-21 10:58 | 2016-11-21 10:58 | PST | 2016-11-21 18:58 | 498 | 60.025 | 59.997 | 59.955 | -0.028 | -0.07 | -1778.5714 | -711.4286 | Yes | No | 59.5 | 0.455 | 2016
WI_2016-11-21_204230 | 2016-11-21 12:42 | 2016-11-21 12:42 | PST | 2016-11-21 20:42 | 822 | 60.018 | 59.96 | 59.915 | -0.058 | -0.103 | -1417.2414 | -798.0583 | Yes | No | 59.5 | 0.415 | 2016
WI_2016-11-21_211642 | 2016-11-21 13:17 | 2016-11-21 13:17 | PST | 2016-11-21 21:17 | 673 | 60.028 | 59.96 | 59.924 | -0.068 | -0.104 | -989.7059 | -647.1154 | Yes | No | 59.5 | 0.424 | 2016
WI_2016-11-22_022553 | 2016-11-21 18:26 | 2016-11-21 18:26 | PST | 2016-11-22 02:26 | 480 | 60.024 | 60.017 | 59.961 | -0.007 | -0.063 | -6857.1429 | -761.9048 | No | No | 59.5 | 0.461 | 2016
WI_2016-11-24_192440 | 2016-11-24 11:25 | 2016-11-24 11:25 | PST | 2016-11-24 19:25 | 709 | 60.02 | 59.973 | 59.935 | -0.047 | -0.085 | -1508.5106 | -834.1176 | Yes | No | 59.5 | 0.435 | 2016
WI_2016-12-12_010920 | 2016-12-11 17:09 | 2016-12-11 17:09 | PST | 2016-12-12 01:09 | 353 | 60.021 | 60.001 | 59.97 | -0.02 | -0.051 | -1765 | -692.1569 | No | No | 59.5 | 0.47 | 2017
WI_2016-12-12_162753 | 2016-12-12 08:28 | 2016-12-12 08:28 | PST | 2016-12-12 16:28 | 777 | 60.009 | 59.979 | 59.9479 | -0.03 | -0.0611 | -2590 | -1271.6858 | No | No | 59.5 | 0.4479 | 2017
WI_2016-12-18_192447 | 2016-12-18 11:25 | 2016-12-18 11:25 | PST | 2016-12-18 19:25 | 1152 | 60.024 | 59.946 | 59.9106 | -0.078 | -0.1134 | -1476.9231 | -1015.873 | No | No | 59.5 | 0.4106 | 2017
WI_2017-01-03_043926 | 2017-01-02 20:39 | 2017-01-02 20:39 | PST | 2017-01-03 04:39 | 463 | 60.021 | 59.988 | 59.9594 | -0.033 | -0.0616 | -1403.0303 | -751.6234 | No | No | 59.5 | 0.4594 | 2017
WI_2017-01-08_021206 | 2017-01-07 18:12 | 2017-01-07 18:12 | PST | 2017-01-08 02:12 | 523 | 60.038 | 59.984 | 59.9972 | -0.054 | -0.0408 | -968.5185 | -1281.8627 | No | No | 59.5 | 0.4972 | 2017
WI_2017-01-14_070616 | 2017-01-13 23:06 | 2017-01-13 23:06 | PST | 2017-01-14 07:06 | 585 | 60.024 | 59.971 | 59.9395 | -0.053 | -0.0845 | -1103.7736 | -692.3077 | No | No | 59.5 | 0.4395 | 2017
WI_2017-01-14_133516 | 2017-01-14 05:35 | 2017-01-14 05:35 | PST | 2017-01-14 13:35 | 291 | 59.996 | 59.962 | 59.9425 | -0.034 | -0.0535 | -855.8824 | -543.9252 | No | No | 59.5 | 0.4425 | 2017
WI_2017-01-19_042222 | 2017-01-18 20:22 | 2017-01-18 20:22 | PST | 2017-01-19 04:22 | 2054 | 60.02 | 59.939 | 59.89 | -0.081 | -0.13 | -2535.8025 | -1580 | Yes | Yes | 59.5 | 0.39 | 2017
WI_2017-01-19_051007 | 2017-01-18 21:10 | 2017-01-18 21:10 | PST | 2017-01-19 05:10 | 400 | 60.015 | 59.974 | 59.9532 | -0.041 | -0.0618 | -975.6098 | -647.2492 | No | No | 59.5 | 0.4532 | 2017
WI_2017-01-19_153917 | 2017-01-19 07:39 | 2017-01-19 07:39 | PST | 2017-01-19 15:39 | 600 | 60.021 | 59.967 | 59.946 | -0.054 | -0.075 | -1111.1111 | -800 | Yes | No | 59.5 | 0.446 | 2017
WI_2017-01-20_080105 | 2017-01-20 00:01 | 2017-01-20 00:01 | PST | 2017-01-20 08:01 | 1967 | 59.997 | 59.89 | 59.858 | -0.107 | -0.139 | -1838.3178 | -1415.1079 | Yes | Yes | 59.5 | 0.358 | 2017
WI_2017-01-20_112733 | 2017-01-20 03:28 | 2017-01-20 03:28 | PST | 2017-01-20 11:28 | 440 | 59.996 | 59.962 | 59.9359 | -0.034 | -0.0601 | -1294.1176 | -732.1131 | No | No | 59.5 | 0.4359 | 2017
WI_2017-01-20_133829 | 2017-01-20 05:38 | 2017-01-20 05:38 | PST | 2017-01-20 13:38 | 402 | 59.975 | 59.959 | 59.9299 | -0.016 | -0.0451 | -2512.5 | -891.3525 | No | No | 59.5 | 0.4299 | 2017
WI_2017-01-24_012703 | 2017-01-23 17:27 | 2017-01-23 17:27 | PST | 2017-01-24 01:27 | 883 | 59.955 | 59.922 | 59.876 | -0.033 | -0.079 | -2675.7576 | -1117.7215 | Yes | Yes | 59.5 | 0.376 | 2017
WI_2017-01-26_204154 | 2017-01-26 12:42 | 2017-01-26 12:42 | PST | 2017-01-26 20:42 | 485 | 59.997 | 59.976 | 59.951 | -0.021 | -0.046 | -2309.5238 | -1054.3478 | No | No | 59.5 | 0.451 | 2017
WI_2017-01-28_152544 | 2017-01-28 07:26 | 2017-01-28 07:26 | PST | 2017-01-28 15:26 | 474 | 60.03 | 59.988 | 59.9637 | -0.042 | -0.0663 | -1128.5714 | -714.9321 | No | No | 59.5 | 0.4637 | 2017
WI_2017-02-06_201338 | 2017-02-06 12:14 | 2017-02-06 12:14 | PST | 2017-02-06 20:14 | 658 | 59.994 | 59.952 | 59.911 | -0.042 | -0.083 | -1566.6667 | -792.7711 | Yes | Yes | 59.5 | 0.411 | 2017
WI_2017-02-06_210323 | 2017-02-06 13:03 | 2017-02-06 13:03 | PST | 2017-02-06 21:03 | 705 | 60.001 | 59.95 | 59.925 | -0.051 | -0.076 | -1382.3529 | -927.6316 | Yes | Yes | 59.5 | 0.425 | 2017
WI_2017-02-07_023502 | 2017-02-06 18:35 | 2017-02-06 18:35 | PST | 2017-02-07 02:35 | 436 | 60.006 | 59.984 | 59.9447 | -0.022 | -0.0613 | -1981.8182 | -711.2561 | No | No | 59.5 | 0.4447 | 2017
WI_2017-02-10_084638 | 2017-02-10 00:47 | 2017-02-10 00:47 | PST | 2017-02-10 08:47 | 597 | 60.008 | 59.967 | 59.9425 | -0.041 | -0.0655 | -1456.0976 | -911.4504 | No | No | 59.5 | 0.4425 | 2017
WI_2017-02-21_020957 | 2017-02-20 18:10 | 2017-02-20 18:10 | PST | 2017-02-21 02:10 | 509 | 60.015 | 59.969 | 59.944 | -0.046 | -0.071 | -1106.5217 | -716.9014 | Yes | No | 59.5 | 0.444 | 2017
WI_2017-02-24_121524 | 2017-02-24 04:15 | 2017-02-24 04:15 | PST | 2017-02-24 12:15 | -317 | 59.98 | 60.011 | 59.9742 | 0.031 | -0.0058 | -1022.5806 | 5465.5172 | No | No | 59.5 | 0.4742 | 2017
WI_2017-02-24_164727 | 2017-02-24 08:47 | 2017-02-24 08:47 | PST | 2017-02-24 16:47 | 473 | 60.031 | 60.002 | 59.9587 | -0.029 | -0.0723 | -1631.0345 | -654.2185 | No | No | 59.5 | 0.4587 | 2017
WI_2017-02-25_234512 | 2017-02-25 15:45 | 2017-02-25 15:45 | PST | 2017-02-25 23:45 | -332 | 59.963 | 60.002 | 59.96 | 0.039 | -0.003 | -851.2821 | 11066.6667 | No | No | 59.5 | 0.46 | 2017
WI_2017-02-28_000648 | 2017-02-27 16:07 | 2017-02-27 16:07 | PST | 2017-02-28 00:07 | 670 | 60.027 | 60.002 | 59.945 | -0.025 | -0.082 | -2680 | -817.0732 | Yes | No | 59.5 | 0.445 | 2017
WI_2017-03-04_040630 | 2017-03-03 20:06 | 2017-03-03 20:06 | PST | 2017-03-04 04:06 | 755 | 59.981 | 59.955 | 59.902 | -0.026 | -0.079 | -2903.8462 | -955.6962 | Yes | Yes | 59.5 | 0.402 | 2017
WI_2017-03-07_200048 | 2017-03-07 12:01 | 2017-03-07 12:01 | PST | 2017-03-07 20:01 | 744 | 60.013 | 59.957 | 59.943 | -0.056 | -0.07 | -1328.5714 | -1062.8571 | No | No | 59.5 | 0.443 | 2017
WI_2017-03-08_032311 | 2017-03-07 19:23 | 2017-03-07 19:23 | PST | 2017-03-08 03:23 | 1412 | 59.99 | 59.908 | 59.851 | -0.082 | -0.139 | -1721.9512 | -1015.8273 | Yes | Yes | 59.5 | 0.351 | 2017
WI_2017-03-09_030706 | 2017-03-08 19:07 | 2017-03-08 19:07 | PST | 2017-03-09 03:07 | 1744 | 59.997 | 59.871 | 59.786 | -0.126 | -0.211 | -1384.127 | -826.5403 | Yes | Yes | 59.5 | 0.286 | 2017
WI_2017-03-11_235815 | 2017-03-11 15:58 | 2017-03-11 15:58 | PST | 2017-03-11 23:58 | -612 | 59.958 | 59.999 | 59.964 | 0.041 | 0.006 | -1492.6829 | -10200 | No | No | 59.5 | 0.464 | 2017
WI_2017-03-14_233350 | 2017-03-14 16:34 | 2017-03-14 16:34 | PDT | 2017-03-14 23:34 | 400 | 59.984 | 59.983 | 59.934 | -0.001 | -0.05 | -40000 | -800 | No | No | 59.5 | 0.434 | 2017
WI_2017-03-16_113020 | 2017-03-16 04:30 | 2017-03-16 04:30 | PDT | 2017-03-16 11:30 | -315 | 59.992 | 60.022 | 59.977 | 0.03 | -0.015 | -1050 | 2100 | No | No | 59.5 | 0.477 | 2017
WI_2017-03-17_200936 | 2017-03-17 13:10 | 2017-03-17 13:10 | PDT | 2017-03-17 20:10 | 964 | 59.981 | 59.924 | 59.89 | -0.057 | -0.091 | -1691.2281 | -1059.3407 | Yes | Yes | 59.5 | 0.39 | 2017
WI_2017-03-18_160845 | 2017-03-18 09:09 | 2017-03-18 09:09 | PDT | 2017-03-18 16:09 | 290 | 60.024 | 59.974 | 59.945 | -0.05 | -0.079 | -580 | -367.0886 | No | No | 59.5 | 0.445 | 2017
WI_2017-03-18_190016 | 2017-03-18 12:00 | 2017-03-18 12:00 | PDT | 2017-03-18 19:00 | -327 | 60 | 60.025 | 60.004 | 0.025 | 0.004 | -1308 | -8175 | No | No | 59.5 | 0.504 | 2017
WI_2017-03-19_234515 | 2017-03-19 16:45 | 2017-03-19 16:45 | PDT | 2017-03-19 23:45 | 305 | 59.963 | 60 | 59.965 | 0.037 | 0.002 | 824.3243 | 15250 | No | No | 59.5 | 0.465 | 2017
WI_2017-03-24_082500 | 2017-03-24 01:25 | 2017-03-24 01:25 | PDT | 2017-03-24 08:25 | 380 | 60.017 | 60 | 59.95 | -0.017 | -0.067 | -2235.2941 | -567.1642 | No | No | 59.5 | 0.45 | 2017
WI_2017-03-24_214104 | 2017-03-24 14:41 | 2017-03-24 14:41 | PDT | 2017-03-24 21:41 | -301 | 59.955 | 60.003 | 59.96 | 0.048 | 0.005 | -627.0833 | -6020 | No | No | 59.5 | 0.46 | 2017
WI_2017-03-25_114526 | 2017-03-25 04:45 | 2017-03-25 04:45 | PDT | 2017-03-25 11:45 | -304 | 59.971 | 60.012 | 59.971 | 0.041 | 0 | -741.4634 | #DIV/0! | No | No | 59.5 | 0.471 | 2017
WI_2017-03-26_004522 | 2017-03-25 17:45 | 2017-03-25 17:45 | PDT | 2017-03-26 00:45 | -301 | 59.972 | 59.999 | 59.978 | 0.027 | 0.006 | -1114.8148 | -5016.6667 | No | No | 59.5 | 0.478 | 2017
WI_2017-03-26_101515 | 2017-03-26 03:15 | 2017-03-26 03:15 | PDT | 2017-03-26 10:15 | -298 | 59.961 | 59.991 | 60.041 | 0.03 | 0.08 | -993.3333 | -372.5 | Yes | No | 59.5 | NaN | 2017
WI_2017-03-26_123016 | 2017-03-26 05:30 | 2017-03-26 05:30 | PDT | 2017-03-26 12:30 | -303 | 59.96 | 59.983 | 60.032 | 0.023 | 0.072 | -1317.3913 | -420.8333 | Yes | No | 59.5 | NaN | 2017
WI_2017-03-28_085552 | 2017-03-28 01:56 | 2017-03-28 01:56 | PDT | 2017-03-28 08:56 | 363 | 60.024 | 59.979 | 59.955 | -0.045 | -0.069 | -806.6667 | -526.087 | No | No | 59.5 | 0.455 | 2017
WI_2017-03-28_091526 | 2017-03-28 02:15 | 2017-03-28 02:15 | PDT | 2017-03-28 09:15 | -300 | 59.988 | 60.022 | 59.985 | 0.034 | -0.003 | -882.3529 | 10000 | No | No | 59.5 | 0.485 | 2017
WI_2017-03-28_103047 | 2017-03-28 03:31 | 2017-03-28 03:31 | PDT | 2017-03-28 10:31 | 486 | 59.985 | 59.955 | 59.921 | -0.03 | -0.064 | -1620 | -759.375 | No | No | 59.5 | 0.421 | 2017
WI_2017-03-28_210632 | 2017-03-28 14:07 | 2017-03-28 14:07 | PDT | 2017-03-28 21:07 | 525 | 59.994 | 59.965 | 59.928 | -0.029 | -0.066 | -1810.3448 | -795.4545 | No | No | 59.5 | 0.428 | 2017
WI_2017-03-30_231536 | 2017-03-30 16:16 | 2017-03-30 16:16 | PDT | 2017-03-30 23:16 | -314 | 59.982 | 60.02 | 59.984 | 0.038 | 0.002 | -826.3158 | -15700 | No | No | 59.5 | 0.484 | 2017
WI_2017-03-31_140258 | 2017-03-31 07:03 | 2017-03-31 07:03 | PDT | 2017-03-31 14:03 | 471 | 59.987 | 59.945 | 59.922 | -0.042 | -0.065 | -1121.4286 | -724.6154 | No | No | 59.5 | 0.422 | 2017
WI_2017-04-02_000018 | 2017-04-01 17:00 | 2017-04-01 17:00 | PDT | 2017-04-02 | -304 | 59.987 | 60.017 | 59.988 | 0.03 | 0.001 | -1013.3333 | -30400 | No | No | 59.5 | 0.488 | 2017
WI_2017-04-03_001517 | 2017-04-02 17:15 | 2017-04-02 17:15 | PDT | 2017-04-03 00:15 | -298 | 59.964 | 59.983 | 59.962 | 0.019 | -0.002 | -1568.4211 | 14900 | No | No | 59.5 | 0.462 | 2017
WI_2017-04-03_113028 | 2017-04-03 04:30 | 2017-04-03 04:30 | PDT | 2017-04-03 11:30 | -306 | 59.977 | 60.01 | 59.974 | 0.033 | -0.003 | -927.2727 | 10200 | No | No | 59.5 | 0.474 | 2017
WI_2017-04-07_060000 | 2017-04-06 23:00 | 2017-04-06 23:00 | PDT | 2017-04-07 06:00 | 2776 | 60.019 | 59.856 | 59.71 | -0.163 | -0.309 | -1703.0675 | -898.3819 | Yes | Yes | 59.5 | 0.21 | 2017
WI_2017-04-08_205458 | 2017-04-08 13:55 | 2017-04-08 13:55 | PDT | 2017-04-08 20:55 | 571 | 60.02 | 59.981 | 59.936 | -0.039 | -0.084 | -1464.1026 | -679.7619 | Yes | No | 59.5 | 0.436 | 2017
WI_2017-04-09_231517 | 2017-04-09 16:15 | 2017-04-09 16:15 | PDT | 2017-04-09 23:15 | -308 | 59.965 | 59.978 | 59.96 | 0.013 | -0.005 | -2369.2308 | 6160 | No | No | 59.5 | 0.46 | 2017
WI_2017-04-11_231518 | 2017-04-11 16:15 | 2017-04-11 16:15 | PDT | 2017-04-11 23:15 | -309 | 59.98 | 60.029 | 59.984 | 0.049 | 0.004 | -630.6122 | -7725 | No | No | 59.5 | 0.484 | 2017
WI_2017-04-14_163416 | 2017-04-14 09:34 | 2017-04-14 09:34 | PDT | 2017-04-14 16:34 | 1300 | 60 | 59.896 | 59.828 | -0.104 | -0.172 | -1250 | -755.814 | Yes | Yes | 59.5 | 0.328 | 2017
WI_2017-04-15_010018 | 2017-04-14 18:00 | 2017-04-14 18:00 | PDT | 2017-04-15 01:00 | -321 | 60.013 | 60.039 | 60.007 | 0.026 | -0.006 | -1234.6154 | 5350 | No | No | 59.5 | 0.507 | 2017
WI_2017-04-17_113017 | 2017-04-17 04:30 | 2017-04-17 04:30 | PDT | 2017-04-17 11:30 | -306 | 59.975 | 60.005 | 59.98 | 0.03 | 0.005 | -1020 | -6120 | No | No | 59.5 | 0.48 | 2017
WI_2017-04-21_000449 | 2017-04-20 17:05 | 2017-04-20 17:05 | PDT | 2017-04-21 00:05 | -311 | 59.98 | 60.013 | 59.977 | 0.033 | -0.003 | -942.4242 | 10366.6667 | No | No | 59.5 | 0.477 | 2017
WI_2017-04-22_035912 | 2017-04-21 20:59 | 2017-04-21 20:59 | PDT | 2017-04-22 03:59 | 383 | 60.022 | 59.978 | 59.95 | -0.044 | -0.072 | -870.4545 | -531.9444 | Yes | No | 59.5 | 0.45 | 2017
WI_2017-04-22_090401 | 2017-04-22 02:04 | 2017-04-22 02:04 | PDT | 2017-04-22 09:04 | 419 | 60.015 | 59.975 | 59.936 | -0.04 | -0.079 | -1047.5 | -530.3797 | Yes | No | 59.5 | 0.436 | 2017
WI_2017-04-23_000017 | 2017-04-22 17:00 | 2017-04-22 17:00 | PDT | 2017-04-23 | -310 | 59.965 | 60.003 | 59.969 | 0.038 | 0.004 | -815.7895 | -7750 | No | No | 59.5 | 0.469 | 2017
WI_2017-04-23_090007 | 2017-04-23 02:00 | 2017-04-23 02:00 | PDT | 2017-04-23 09:00 | -313 | 59.986 | 60.018 | 59.981 | 0.032 | -0.005 | -978.125 | 6260 | No | No | 59.5 | 0.481 | 2017
WI_2017-04-24_004510 | 2017-04-23 17:45 | 2017-04-23 17:45 | PDT | 2017-04-24 00:45 | -308 | 59.977 | 60.003 | 59.979 | 0.026 | 0.002 | -1184.6154 | -15400 | No | No | 59.5 | 0.479 | 2017
WI_2017-04-25_171211 | 2017-04-25 10:12 | 2017-04-25 10:12 | PDT | 2017-04-25 17:12 | 474 | 60.01 | 59.977 | 59.943 | -0.033 | -0.067 | -1436.3636 | -707.4627 | No | No | 59.5 | 0.443 | 2017
WI_2017-04-25_233020 | 2017-04-25 16:30 | 2017-04-25 16:30 | PDT | 2017-04-25 23:30 | -295 | 59.965 | 60.012 | 59.969 | 0.047 | 0.004 | -627.6596 | -7375 | No | No | 59.5 | 0.469 | 2017
WI_2017-04-29_223010 | 2017-04-29 15:30 | 2017-04-29 15:30 | PDT | 2017-04-29 22:30 | -314 | 59.97 | 59.995 | 59.972 | 0.025 | 0.002 | -1256 | -15700 | No | No | 59.5 | 0.472 | 2017
WI_2017-04-30_213026 | 2017-04-30 14:30 | 2017-04-30 14:30 | PDT | 2017-04-30 21:30 | -312 | 59.978 | 59.998 | 59.98 | 0.02 | 0.002 | -1560 | -15600 | No | No | 59.5 | 0.48 | 2017
WI_2017-05-03_124756 | 2017-05-03 05:48 | 2017-05-03 05:48 | PDT | 2017-05-03 12:48 | 500 | 60.014 | 59.963 | 59.931 | -0.051 | -0.083 | -980.3922 | -602.4096 | Yes | No | 59.5 | 0.431 | 2017
WI_2017-05-07_203916 | 2017-05-07 13:39 | 2017-05-07 13:39 | PDT | 2017-05-07 20:39 | -309 | 59.955 | 59.985 | 59.957 | 0.03 | 0.002 | -1030 | -15450 | No | No | 59.5 | 0.457 | 2017
WI_2017-05-07_233016 | 2017-05-07 16:30 | 2017-05-07 16:30 | PDT | 2017-05-07 23:30 | -322 | 60.003 | 60.045 | 60.001 | 0.042 | -0.002 | -766.6667 | 16100 | No | No | 59.5 | 0.501 | 2017
WI_2017-05-10_171330 | 2017-05-10 10:14 | 2017-05-10 10:14 | PDT | 2017-05-10 17:13 | 765 | 60.009 | 59.96 | 59.89 | -0.049 | -0.119 | -1561.2245 | -642.8571 | No | No | 59.5 | 0.39 | 2017
WI_2017-05-12_230039 | 2017-05-12 16:01 | 2017-05-12 16:01 | PDT | 2017-05-12 23:01 | -316 | 59.978 | 60.018 | 59.975 | 0.04 | -0.003 | -790 | 10533.3333 | No | No | 59.5 | 0.475 | 2017
WI_2017-05-13_070954 | 2017-05-13 00:10 | 2017-05-13 00:10 | PDT | 2017-05-13 07:10 | 481 | 59.983 | 59.952 | 59.924 | -0.031 | -0.059 | -1551.6129 | -815.2542 | No | No | 59.5 | 0.424 | 2017
WI_2017-05-15_000017 | 2017-05-14 17:00 | 2017-05-14 17:00 | PDT | 2017-05-15 | -314 | 59.987 | 60.035 | 59.987 | 0.048 | 0 | -654.1667 | #DIV/0! | No | No | 59.5 | 0.487 | 2017
WI_2017-05-15_011517 | 2017-05-14 18:15 | 2017-05-14 18:15 | PDT | 2017-05-15 01:15 | -318 | 59.986 | 60.007 | 59.982 | 0.021 | -0.004 | -1514.2857 | 7950 | No | No | 59.5 | 0.482 | 2017
WI_2017-05-17_062846 | 2017-05-16 23:29 | 2017-05-16 23:29 | PDT | 2017-05-17 06:29 | 491 | 60.014 | 59.981 | 59.936 | -0.033 | -0.078 | -1487.8788 | -629.4872 | Yes | No | 59.5 | 0.436 | 2017
WI_2017-05-17_114524 | 2017-05-17 04:45 | 2017-05-17 04:45 | PDT | 2017-05-17 11:45 | -317 | 59.989 | 60.035 | 59.99 | 0.046 | 0.001 | -689.1304 | -31700 | No | No | 59.5 | 0.49 | 2017
WI_2017-05-18_223050 | 2017-05-18 15:31 | 2017-05-18 15:31 | PDT | 2017-05-18 22:31 | -311 | 59.997 | 60.034 | 59.998 | 0.037 | 0.001 | -840.5405 | -31100 | No | No | 59.5 | 0.498 | 2017
WI_2017-05-20_213033 | 2017-05-20 14:31 | 2017-05-20 14:31 | PDT | 2017-05-20 21:31 | -311 | 59.965 | 59.992 | 59.97 | 0.027 | 0.005 | -1151.8519 | -6220 | No | No | 59.5 | 0.47 | 2017
WI_2017-05-21_094308 | 2017-05-21 02:43 | 2017-05-21 02:43 | PDT | 2017-05-21 09:43 | 500 | 60.022 | 59.999 | 59.954 | -0.023 | -0.068 | -2173.913 | -735.2941 | No | No | 59.5 | 0.454 | 2017
WI_2017-05-23_110042 | 2017-05-23 04:01 | 2017-05-23 04:01 | PDT | 2017-05-23 11:01 | -314 | 59.966 | 59.998 | 59.965 | 0.032 | -0.001 | -981.25 | 31400 | No | No | 59.5 | 0.465 | 2017
WI_2017-05-27_124655 | 2017-05-27 05:47 | 2017-05-27 05:47 | PDT | 2017-05-27 12:47 | 578 | 60.009 | 59.966 | 59.926 | -0.043 | -0.083 | -1344.186 | -696.3855 | Yes | No | 59.5 | 0.426 | 2017
WI_2017-05-31_043333 | 2017-05-30 21:34 | 2017-05-30 21:34 | PDT | 2017-05-31 04:34 | 632 | 59.986 | 59.949 | 59.919 | -0.037 | -0.067 | -1708.1081 | -943.2836 | No | No | 59.5 | 0.419 | 2017
WI_2017-06-02_114532 | 2017-06-02 04:46 | 2017-06-02 04:46 | PDT | 2017-06-02 11:46 | -308 | 59.969 | 59.992 | 60.036 | 0.023 | 0.067 | -1339.1304 | -459.7015 | No | No | 59.5 | 0.536 | 2017
WI_2017-06-04_131653 | 2017-06-04 06:17 | 2017-06-04 06:17 | PDT | 2017-06-04 13:17 | 312 | 60.02 | 59.996 | 59.961 | -0.024 | -0.059 | -1300 | -528.8136 | No | No | 59.5 | 0.461 | 2017
WI_2017-06-07_111523 | 2017-06-07 04:15 | 2017-06-07 04:15 | PDT | 2017-06-07 11:15 | -308 | 59.98 | 60.007 | 60.038 | 0.027 | 0.058 | -1140.7407 | -531.0345 | No | No | 59.5 | 0.538 | 2017
WI_2017-06-07_224114 | 2017-06-07 15:41 | 2017-06-07 15:41 | PDT | 2017-06-07 22:41 | 491 | 60.002 | 59.966 | 59.935 | -0.036 | -0.067 | -1363.8889 | -732.8358 | No | No | 59.5 | 0.435 | 2017
WI_2017-06-08_144717 | 2017-06-08 07:47 | 2017-06-08 07:47 | PDT | 2017-06-08 14:47 | 766 | 59.974 | 59.949 | 59.893 | -0.025 | -0.081 | -3064 | -945.679 | Yes | Yes | 59.5 | 0.393 | 2017
WI_2017-06-08_213000 | 2017-06-08 14:30 | 2017-06-08 14:30 | PDT | 2017-06-08 21:30 | 537 | 60.012 | 60.019 | 60.004 | 0.007 | -0.008 | 7671.4286 | -6712.5 | No | No | 59.5 | 0.504 | 2017
WI_2017-06-15_200018 | 2017-06-15 13:00 | 2017-06-15 13:00 | PDT | 2017-06-15 20:00 | 875 | 60.013 | 59.941 | 59.902 | -0.072 | -0.111 | -1215.2778 | -788.2883 | Yes | Yes | 59.5 | 0.402 | 2017
WI_2017-06-15_203017 | 2017-06-15 13:30 | 2017-06-15 13:30 | PDT | 2017-06-15 20:30 | -316 | 59.973 | 60.015 | 60.036 | 0.042 | 0.063 | -752.381 | -501.5873 | No | No | 59.5 | 0.536 | 2017
WI_2017-06-16_121400 | 2017-06-16 05:14 | 2017-06-16 05:14 | PDT | 2017-06-16 12:14 | 2685 | 59.974 | 59.85 | 59.697 | -0.124 | -0.277 | -2165.3226 | -969.3141 | Yes | Yes | 59.5 | 0.197 | 2017
WI_2017-06-19_214320 | 2017-06-19 14:43 | 2017-06-19 14:43 | PDT | 2017-06-19 21:43 | 1313 | 59.991 | 59.915 | 59.855 | -0.076 | -0.136 | -1727.6316 | -965.4412 | Yes | Yes | 59.5 | 0.355 | 2017
WI_2017-06-23_174501 | 2017-06-23 10:45 | 2017-06-23 10:45 | PDT | 2017-06-23 17:45 | 2619 | 59.98 | 59.862 | 59.764 | -0.118 | -0.216 | -2219.4915 | -1212.5 | Yes | Yes | 59.5 | 0.264 | 2017
WI_2017-06-29_124516 | 2017-06-29 05:45 | 2017-06-29 05:45 | PDT | 2017-06-29 12:45 | -314 | 59.97 | 59.999 | 60.026 | 0.029 | 0.056 | -1082.7586 | -560.7143 | No | No | 59.5 | 0.526 | 2017
WI_2017-07-04_182353 | 2017-07-04 11:24 | 2017-07-04 11:24 | PDT | 2017-07-04 18:24 | 706 | 60.002 | 59.95 | 59.924 | -0.052 | -0.078 | -1357.6923 | -905.1282 | Yes | Yes | 59.5 | 0.424 | 2017
WI_2017-07-05_075543 | 2017-07-05 00:56 | 2017-07-05 00:56 | PDT | 2017-07-05 07:56 | 633 | 60.032 | 59.985 | 59.947 | -0.047 | -0.085 | -1346.8085 | -744.7059 | Yes | No | 59.5 | 0.447 | 2017
WI_2017-07-10_202538 | 2017-07-10 13:26 | 2017-07-10 13:26 | PDT | 2017-07-10 20:26 | 375 | 60.02 | 60.012 | 59.954 | -0.008 | -0.066 | -4687.5 | -568.1818 | No | No | 59.5 | 0.454 | 2017
WI_2017-07-13_125653 | 2017-07-13 05:57 | 2017-07-13 05:57 | PDT | 2017-07-13 12:57 | 606 | 60.029 | 59.993 | 59.962 | -0.036 | -0.067 | -1683.3333 | -904.4776 | No | No | 59.5 | 0.462 | 2017
WI_2017-07-15_183907 | 2017-07-15 11:39 | 2017-07-15 11:39 | PDT | 2017-07-15 18:39 | 708 | 60.008 | 59.962 | 59.935 | -0.046 | -0.073 | -1539.1304 | -969.863 | Yes | Yes | 59.5 | 0.435 | 2017
WI_2017-07-29_164834 | 2017-07-29 09:49 | 2017-07-29 09:49 | PDT | 2017-07-29 16:49 | 928 | 59.991 | 59.948 | 59.907 | -0.043 | -0.084 | -2158.1395 | -1104.7619 | Yes | Yes | 59.5 | 0.407 | 2017
WI_2017-07-29_170649 | 2017-07-29 10:07 | 2017-07-29 10:07 | PDT | 2017-07-29 17:07 | 561 | 59.978 | 59.948 | 59.895 | -0.03 | -0.083 | -1870 | -675.9036 | No | No | 59.5 | 0.395 | 2017
WI_2017-07-30_185540 | 2017-07-30 11:56 | 2017-07-30 11:56 | PDT | 2017-07-30 18:56 | 1494 | 59.989 | 59.909 | 59.862 | -0.08 | -0.127 | -1867.5 | -1176.378 | Yes | Yes | 59.5 | 0.362 | 2017
WI_2017-08-02_013242 | 2017-08-01 18:33 | 2017-08-01 18:33 | PDT | 2017-08-02 01:33 | 525 | 60.018 | 60.013 | 59.957 | -0.005 | -0.061 | -10500 | -860.6557 | No | No | 59.5 | 0.457 | 2017
WI_2017-08-02_062937 | 2017-08-01 23:30 | 2017-08-01 23:30 | PDT | 2017-08-02 06:30 | 500 | 60.001 | 59.97 | 59.942 | -0.031 | -0.059 | -1612.9032 | -847.4576 | No | No | 59.5 | 0.442 | 2017
WI_2017-08-02_070333 | 2017-08-02 00:04 | 2017-08-02 00:04 | PDT | 2017-08-02 07:04 | 500 | 60.018 | 59.991 | 59.956 | -0.027 | -0.062 | -1851.8519 | -806.4516 | No | No | 59.5 | 0.456 | 2017
WI_2017-08-02_183045 | 2017-08-02 11:31 | 2017-08-02 11:31 | PDT | 2017-08-02 18:31 | -400 | 59.966 | 60.002 | 60.03 | 0.036 | 0.064 | -1111.1111 | -625 | No | No | 59.5 | 0.53 | 2017
WI_2017-08-03_200623 | 2017-08-03 13:06 | 2017-08-03 13:06 | PDT | 2017-08-03 20:06 | 761 | 60.053 | 60 | 59.986 | -0.053 | -0.067 | -1435.8491 | -1135.8209 | No | No | 59.5 | 0.486 | 2017
WI_2017-08-04_120211 | 2017-08-04 05:02 | 2017-08-04 05:02 | PDT | 2017-08-04 12:02 | -309 | 59.961 | 60.015 | 60.012 | 0.054 | 0.051 | -572.2222 | -605.8824 | No | No | 59.5 | 0.512 | 2017
WI_2017-08-04_122341 | 2017-08-04 05:24 | 2017-08-04 05:24 | PDT | 2017-08-04 12:24 | -311 | 59.997 | 60 | 59.994 | 0.003 | -0.003 | -10366.6667 | 10366.6667 | No | No | 59.5 | 0.494 | 2017
WI_2017-08-08_100816 | 2017-08-08 03:08 | 2017-08-08 03:08 | PDT | 2017-08-08 10:08 | 1634 | 60.005 | 59.898 | 59.827 | -0.107 | -0.178 | -1527.1028 | -917.9775 | Yes | Yes | 59.5 | 0.327 | 2017
WI_2017-08-10_235052 | 2017-08-10 16:51 | 2017-08-10 16:51 | PDT | 2017-08-10 23:51 | 547 | 60.001 | 59.959 | 59.93 | -0.042 | -0.071 | -1302.381 | -770.4225 | Yes | No | 59.5 | 0.43 | 2017
WI_2017-08-12_100139 | 2017-08-12 03:02 | 2017-08-12 03:02 | PDT | 2017-08-12 10:02 | 360 | 60.021 | 59.977 | 59.958 | -0.044 | -0.063 | -818.1818 | -571.4286 | No | No | 59.5 | 0.458 | 2017
WI_2017-08-13_135536 | 2017-08-13 06:56 | 2017-08-13 06:56 | PDT | 2017-08-13 13:56 | 391 | 60.02 | 59.995 | 59.956 | -0.025 | -0.064 | -1564 | -610.9375 | No | No | 59.5 | 0.456 | 2017
WI_2017-08-20_230542 | 2017-08-20 16:06 | 2017-08-20 16:06 | PDT | 2017-08-20 23:06 | 833 | 60.025 | 59.961 | 59.931 | -0.064 | -0.094 | -1301.5625 | -886.1702 | Yes | No | 59.5 | 0.431 | 2017
WI_2017-08-25_185000 | 2017-08-25 11:50 | 2017-08-25 11:50 | PDT | 2017-08-25 18:50 | 508 | 59.978 | 59.963 | 59.94 | -0.015 | -0.038 | -3386.6667 | -1336.8421 | No | No | 59.5 | 0.44 | 2017
WI_2017-09-10_034555 | 2017-09-09 20:46 | 2017-09-09 20:46 | PDT | 2017-09-10 03:46 | 1370 | 59.993 | 59.93 | 59.878 | -0.063 | -0.115 | -2174.6032 | -1191.3043 | Yes | Yes | 59.5 | 0.378 | 2017
WI_2017-09-12_002352 | 2017-09-11 17:24 | 2017-09-11 17:24 | PDT | 2017-09-12 00:24 | 779 | 59.978 | 59.953 | 59.914 | -0.025 | -0.064 | -3116 | -1217.1875 | Yes | No | 59.5 | 0.414 | 2017
WI_2017-09-14_215509 | 2017-09-14 14:55 | 2017-09-14 14:55 | PDT | 2017-09-14 21:55 | 458 | 60.03 | 59.992 | 59.964 | -0.038 | -0.066 | -1205.2632 | -693.9394 | No | No | 59.5 | 0.464 | 2017
WI_2017-09-15_040444 | 2017-09-14 21:05 | 2017-09-14 21:05 | PDT | 2017-09-15 04:05 | 1623 | 59.979 | 59.908 | 59.817 | -0.071 | -0.162 | -2285.9155 | -1001.8519 | Yes | Yes | 59.5 | 0.317 | 2017
WI_2017-09-20_151429 | 2017-09-20 08:14 | 2017-09-20 08:14 | PDT | 2017-09-20 15:14 | 731 | 59.976 | 59.965 | 59.901 | -0.011 | -0.075 | -6645.4545 | -974.6667 | Yes | Yes | 59.5 | 0.401 | 2017
WI_2017-09-23_030244 | 2017-09-22 20:03 | 2017-09-22 20:03 | PDT | 2017-09-23 03:03 | 406 | 59.999 | 59.971 | 59.945 | -0.028 | -0.054 | -1450 | -751.8519 | No | No | 59.5 | 0.445 | 2017
WI_2017-09-24_051747 | 2017-09-23 22:18 | 2017-09-23 22:18 | PDT | 2017-09-24 05:18 | 396 | 59.992 | 59.978 | 59.941 | -0.014 | -0.051 | -2828.5714 | -776.4706 | No | No | 59.5 | 0.441 | 2017
WI_2017-09-25_031947 | 2017-09-24 20:20 | 2017-09-24 20:20 | PDT | 2017-09-25 03:20 | 392 | 60.01 | 59.983 | 59.953 | -0.027 | -0.057 | -1451.8519 | -687.7193 | No | No | 59.5 | 0.453 | 2017
WI_2017-09-30_103937 | 2017-09-30 03:40 | 2017-09-30 03:40 | PDT | 2017-09-30 10:40 | 310 | 59.997 | 59.967 | 59.948 | -0.03 | -0.049 | -1033.3333 | -632.6531 | No | No | 59.5 | 0.448 | 2017
WI_2017-10-03_182237 | 2017-10-03 11:23 | 2017-10-03 11:23 | PDT | 2017-10-03 18:23 | 295 | 59.997 | 59.972 | 59.95 | -0.025 | -0.047 | -1180 | -627.6596 | No | No | 59.5 | 0.45 | 2017
WI_2017-10-05_001720 | 2017-10-04 17:17 | 2017-10-04 17:17 | PDT | 2017-10-05 00:17 | 245 | 59.999 | 59.968 | 59.948 | -0.031 | -0.051 | -790.3226 | -480.3922 | No | No | 59.5 | 0.448 | 2017
WI_2017-10-06_083718 | 2017-10-06 01:37 | 2017-10-06 01:37 | PDT | 2017-10-06 08:37 | 363 | 60.021 | 59.997 | 59.948 | -0.024 | -0.073 | -1512.5 | -497.2603 | Yes | No | 59.5 | 0.448 | 2017
WI_2017-10-09_191428 | 2017-10-09 12:14 | 2017-10-09 12:14 | PDT | 2017-10-09 19:14 | 973 | 60.002 | 59.948 | 59.878 | -0.054 | -0.124 | -1801.8519 | -784.6774 | No | No | 59.5 | 0.378 | 2017
WI_2017-10-16_224521 | 2017-10-16 15:45 | 2017-10-16 15:45 | PDT | 2017-10-16 22:45 | 1447 | 60.007 | 59.904 | 59.847 | -0.103 | -0.16 | -1404.8544 | -904.375 | No | No | 59.5 | 0.347 | 2017
WI_2017-10-18_000022 | 2017-10-17 17:00 | 2017-10-17 17:00 | PDT | 2017-10-18 | 523 | 60.012 | 59.986 | 59.974 | -0.026 | -0.038 | -2011.5385 | -1376.3158 | No | No | 59.5 | 0.474 | 2017
WI_2017-10-20_224437 | 2017-10-20 15:45 | 2017-10-20 15:45 | PDT | 2017-10-20 22:45 | -700 | 60.007 | 60.029 | 60.087 | 0.022 | 0.08 | -3181.8182 | -875 | No | No | 59.5 | 0.587 | 2017
WI_2017-10-25_234240 | 2017-10-25 16:43 | 2017-10-25 16:43 | PDT | 2017-10-25 23:43 | 220 | 59.974 | 59.953 | 59.942 | -0.021 | -0.032 | -1047.619 | -687.5 | No | No | 59.5 | 0.442 | 2017
WI_2017-10-26_151736 | 2017-10-26 08:18 | 2017-10-26 08:18 | PDT | 2017-10-26 15:18 | 886 | 60.002 | 59.939 | 59.902 | -0.063 | -0.1 | -1406.3492 | -886 | No | No | 59.5 | 0.402 | 2017
WI_2017-10-27_060346 | 2017-10-26 23:04 | 2017-10-26 23:04 | PDT | 2017-10-27 06:04 | 574 | 59.966 | 59.943 | 59.914 | -0.023 | -0.052 | -2495.6522 | -1103.8462 | No | No | 59.5 | 0.414 | 2017
WI_2017-11-04_164041 | 2017-11-04 09:41 | 2017-11-04 09:41 | PDT | 2017-11-04 16:41 | 320 | 60.021 | 59.981 | 59.961 | -0.04 | -0.06 | -800 | -533.3333 | No | No | 59.5 | 0.461 | 2017
WI_2017-11-08_161858 | 2017-11-08 08:19 | 2017-11-08 08:19 | PST | 2017-11-08 16:19 | 420 | 60.012 | 59.972 | 59.951 | -0.04 | -0.061 | -1050 | -688.5246 | No | No | 59.5 | 0.451 | 2017
WI_2017-11-14_193841 | 2017-11-14 11:39 | 2017-11-14 11:39 | PST | 2017-11-14 19:39 | 460 | 60.008 | 59.973 | 59.942 | -0.035 | -0.066 | -1314.2857 | -696.9697 | No | No | 59.5 | 0.442 | 2017
WI_2017-11-16_212006 | 2017-11-16 13:20 | 2017-11-16 13:20 | PST | 2017-11-16 21:20 | 561 | 59.996 | 59.962 | 59.93 | -0.034 | -0.066 | -1650 | -850 | No | No | 59.5 | 0.43 | 2017
WI_2017-11-24_151731 | 2017-11-24 07:18 | 2017-11-24 07:18 | PST | 2017-11-24 15:18 | -547 | 60.014 | 60.046 | 60.086 | 0.032 | 0.072 | -1709.375 | -759.7222 | Yes | Yes | 59.5 | 0.586 | 2017
WI_2017-11-30_143543 | 2017-11-30 06:36 | 2017-11-30 06:36 | PST | 2017-11-30 14:36 | 742 | 60 | 59.985 | 59.941 | -0.015 | -0.059 | -4946.6667 | -1257.6271 | No | No | 59.5 | 0.441 | 2017
WI_2017-12-02_195659 | 2017-12-02 11:57 | 2017-12-02 11:57 | PST | 2017-12-02 19:57 | 731 | 60.015 | 59.975 | 59.914 | -0.04 | -0.101 | -1827.5 | -723.7624 | Yes | No | 59.5 | 0.414 | 2018
WI_2017-12-02_233452 | 2017-12-02 15:35 | 2017-12-02 15:35 | PST | 2017-12-02 23:35 | -311 | 59.973 | 59.982 | 60.032 | 0.009 | 0.059 | -3455.5556 | -527.1186 | No | No | 59.5 | 0.532 | 2018
WI_2017-12-08_114531 | 2017-12-08 03:46 | 2017-12-08 03:46 | PST | 2017-12-08 11:46 | -291 | 59.962 | 60 | 60.023 | 0.038 | 0.061 | -765.7895 | -477.0492 | No | No | 59.5 | 0.523 | 2018
WI_2017-12-11_221518 | 2017-12-11 14:15 | 2017-12-11 14:15 | PST | 2017-12-11 22:15 | -292 | 59.967 | 60.012 | 60.032 | 0.045 | 0.065 | -648.8889 | -449.2308 | No | No | 59.5 | 0.532 | 2018
WI_2017-12-21_222200 | 2017-12-21 14:22 | 2017-12-21 14:22 | PST | 2017-12-21 22:22 | 1050 | 59.99 | 59.932 | 59.947 | -0.058 | -0.043 | -1810.3448 | -2441.8605 | No | No | 59.5 | 0.447 | 2018
WI_2017-12-28_045209 | 2017-12-27 20:52 | 2017-12-27 20:52 | PST | 2017-12-28 04:52 | 755 | 60.008 | 59.96 | 59.924 | -0.048 | -0.084 | -1572.9167 | -898.8095 | Yes | Yes | 59.5 | 0.424 | 2018
WI_2017-12-28_100542 | 2017-12-28 02:06 | 2017-12-28 02:06 | PST | 2017-12-28 10:06 | 628 | 60.004 | 59.961 | 59.929 | -0.043 | -0.075 | -1460.4651 | -837.3333 | Yes | Yes | 59.5 | 0.429 | 2018
WI_2018-01-25_224518 | 2018-01-25 14:45 | 2018-01-25 14:45 | PST | 2018-01-25 22:45 | -306 | 59.968 | 60.013 | 60.028 | 0.045 | 0.06 | -680 | -510 | No | No | 59.5 | 0.528 | 2018
WI_2018-02-16_045335 | 2018-02-15 20:54 | 2018-02-15 20:54 | PST | 2018-02-16 04:54 | 1336 | 60.011 | 59.941 | 59.876 | -0.07 | -0.135 | -1908.5714 | -989.6296 | Yes | Yes | 59.5 | 0.376 | 2018
WI_2018-02-18_013547 | 2018-02-17 17:36 | 2018-02-17 17:36 | PST | 2018-02-18 01:36 | 1059 | 59.993 | 59.942 | 59.868 | -0.051 | -0.125 | -2076.4706 | -847.2 | Yes | Yes | 59.5 | 0.368 | 2018
WI_2018-02-22_123137 | 2018-02-22 04:32 | 2018-02-22 04:32 | PST | 2018-02-22 12:32 | 567 | 60.008 | 59.96 | 59.934 | -0.048 | -0.074 | -1181.25 | -766.2162 | Yes | Yes | 59.5 | 0.434 | 2018
WI_2018-02-23_144538 | 2018-02-23 06:46 | 2018-02-23 06:46 | PST | 2018-02-23 14:46 | 750 | 59.987 | 59.939 | 59.908 | -0.048 | -0.079 | -1562.5 | -949.3671 | Yes | No | 59.5 | 0.408 | 2018
WI_2018-03-04_174357 | 2018-03-04 09:44 | 2018-03-04 09:44 | PST | 2018-03-04 17:44 | 542 | 60.011 | 59.972 | 59.932 | -0.039 | -0.079 | -1389.7436 | -686.0759 | Yes | No | 59.5 | 0.432 | 2018
WI_2018-03-07_003211 | 2018-03-06 16:32 | 2018-03-06 16:32 | PST | 2018-03-07 00:32 | 752 | 59.96 | 59.934 | 59.888 | -0.026 | -0.072 | -2892.3077 | -1044.4444 | Yes | Yes | 59.5 | 0.388 | 2018
WI_2018-03-12_221515 | 2018-03-12 15:15 | 2018-03-12 15:15 | PDT | 2018-03-12 22:15 | -320 | 59.969 | 60 | 60.036 | 0.031 | 0.067 | -1032.2581 | -477.6119 | No | No | 59.5 | 0.536 | 2018
WI_2018-03-13_113015 | 2018-03-13 04:30 | 2018-03-13 04:30 | PDT | 2018-03-13 11:30 | -320 | 59.972 | 60.003 | 60.045 | 0.031 | 0.073 | -1032.2581 | -438.3562 | Yes | No | 59.5 | 0.545 | 2018
WI_2018-03-14_162442 | 2018-03-14 09:25 | 2018-03-14 09:25 | PDT | 2018-03-14 16:25 | 1575 | 60.036 | 59.945 | 59.864 | -0.091 | -0.172 | -1730.7692 | -915.6977 | Yes | No | 59.5 | 0.364 | 2018
WI_2018-03-15_115420 | 2018-03-15 04:54 | 2018-03-15 04:54 | PDT | 2018-03-15 11:54 | 968 | 59.989 | 59.945 | 59.894 | -0.044 | -0.095 | -2200 | -1018.9474 | Yes | Yes | 59.5 | 0.394 | 2018
WI_2018-03-16_070544 | 2018-03-16 00:06 | 2018-03-16 00:06 | PDT | 2018-03-16 07:06 | 881 | 60.016 | 59.964 | 59.898 | -0.052 | -0.118 | -1694.2308 | -746.6102 | No | Yes | 59.5 | 0.398 | 2018
WI_2018-03-16_104109 | 2018-03-16 03:41 | 2018-03-16 03:41 | PDT | 2018-03-16 10:41 | 596 | 59.986 | 59.949 | 59.897 | -0.037 | -0.089 | -1610.8108 | -669.6629 | Yes | Yes | 59.5 | 0.397 | 2018
WI_2018-03-17_230021 | 2018-03-17 16:00 | 2018-03-17 16:00 | PDT | 2018-03-17 23:00 | -313 | 59.982 | 60.01 | 60.048 | 0.028 | 0.066 | -1117.8571 | -474.2424 | No | No | 59.5 | 0.548 | 2018
WI_2018-03-18_230034 | 2018-03-18 16:01 | 2018-03-18 16:01 | PDT | 2018-03-18 23:01 | -306 | 59.984 | 60.027 | 60.049 | 0.043 | 0.065 | -711.6279 | -470.7692 | No | No | 59.5 | 0.549 | 2018
WI_2018-03-25_223326 | 2018-03-25 15:33 | 2018-03-25 15:33 | PDT | 2018-03-25 22:33 | 277 | 60.006 | 59.972 | 59.998 | -0.034 | -0.008 | -814.7059 | -3462.5 | No | No | 59.5 | 0.498 | 2018
WI_2018-03-26_203152 | 2018-03-26 13:32 | 2018-03-26 13:32 | PDT | 2018-03-26 20:32 | 707 | 60.004 | 59.971 | 59.921 | -0.033 | -0.083 | -2142.4242 | -851.8072 | Yes | No | 59.5 | 0.421 | 2018
WI_2018-04-03_221515 | 2018-04-03 15:15 | 2018-04-03 15:15 | PDT | 2018-04-03 22:15 | -320 | 59.979 | 59.993 | 60.047 | 0.014 | 0.068 | -2285.7143 | -470.5882 | No | No | 59.5 | 0.547 | 2018
WI_2018-04-09_181631 | 2018-04-09 11:17 | 2018-04-09 11:17 | PDT | 2018-04-09 18:17 | -857 | 60 | 60.04 | 60.07 | 0.04 | 0.07 | -2142.5 | -1224.2857 | No | No | 59.5 | 0.57 | 2018
WI_2018-04-11_043831 | 2018-04-10 21:39 | 2018-04-10 21:39 | PDT | 2018-04-11 04:39 | 479 | 60.017 | 59.984 | 59.952 | -0.033 | -0.065 | -1451.5152 | -736.9231 | No | No | 59.5 | 0.452 | 2018
WI_2018-04-12_113033 | 2018-04-12 04:31 | 2018-04-12 04:31 | PDT | 2018-04-12 11:31 | -319 | 59.968 | 59.987 | 60.036 | 0.019 | 0.068 | -1678.9474 | -469.1176 | No | No | 59.5 | 0.536 | 2018
WI_2018-04-21_001103 | 2018-04-20 17:11 | 2018-04-20 17:11 | PDT | 2018-04-21 00:11 | 1060 | 60.015 | 59.945 | 59.855 | -0.07 | -0.16 | -1514.2857 | -662.5 | No | No | 59.5 | 0.355 | 2018
WI_2018-04-30_124522 | 2018-04-30 05:45 | 2018-04-30 05:45 | PDT | 2018-04-30 12:45 | -321 | 59.967 | 60.004 | 60.036 | 0.037 | 0.069 | -867.5676 | -465.2174 | No | No | 59.5 | 0.536 | 2018
WI_2018-04-30_160100 | 2018-04-30 09:01 | 2018-04-30 09:01 | PDT | 2018-04-30 16:01 | 497 | 60.01 | 59.983 | 59.928 | -0.027 | -0.082 | -1840.7407 | -606.0976 | Yes | No | 59.5 | 0.428 | 2018
WI_2018-05-01_015514 | 2018-04-30 18:55 | 2018-04-30 18:55 | PDT | 2018-05-01 01:55 | 482 | 60.015 | 59.974 | 59.933 | -0.041 | -0.082 | -1175.6098 | -587.8049 | Yes | No | 59.5 | 0.433 | 2018
WI_2018-05-02_200532 | 2018-05-02 13:06 | 2018-05-02 13:06 | PDT | 2018-05-02 20:06 | 693 | 59.983 | 59.941 | 59.902 | -0.042 | -0.081 | -1650 | -855.5556 | Yes | Yes | 59.5 | 0.402 | 2018
WI_2018-05-03_193852 | 2018-05-03 12:39 | 2018-05-03 12:39 | PDT | 2018-05-03 19:39 | -292 | 59.974 | 60.007 | 60.036 | 0.033 | 0.062 | -884.8485 | -470.9677 | No | No | 59.5 | 0.536 | 2018
WI_2018-05-05_021054 | 2018-05-04 19:11 | 2018-05-04 19:11 | PDT | 2018-05-05 02:11 | 1126 | 60.013 | 59.971 | 59.898 | -0.042 | -0.115 | -2680.9524 | -979.1304 | Yes | No | 59.5 | 0.398 | 2018
WI_2018-05-10_020048 | 2018-05-09 19:01 | 2018-05-09 19:01 | PDT | 2018-05-10 02:01 | 642 | 60.008 | 59.972 | 59.915 | -0.036 | -0.093 | -1783.3333 | -690.3226 | Yes | No | 59.5 | 0.415 | 2018
WI_2018-05-10_165903 | 2018-05-10 09:59 | 2018-05-10 09:59 | PDT | 2018-05-10 16:59 | 745 | 60.011 | 59.95 | 59.906 | -0.061 | -0.105 | -1221.3115 | -709.5238 | Yes | Yes | 59.5 | 0.406 | 2018
WI_2018-05-11_222011 | 2018-05-11 15:20 | 2018-05-11 15:20 | PDT | 2018-05-11 22:20 | 700 | 59.988 | 59.952 | 59.878 | -0.036 | -0.11 | -1944.4444 | -636.3636 | No | No | 59.5 | 0.378 | 2018
WI_2018-05-12_230222 | 2018-05-12 16:02 | 2018-05-12 16:02 | PDT | 2018-05-12 23:02 | 602 | 60.009 | 59.967 | 59.93 | -0.042 | -0.079 | -1433.3333 | -762.0253 | Yes | No | 59.5 | 0.43 | 2018
WI_2018-05-16_072257 | 2018-05-16 00:23 | 2018-05-16 00:23 | PDT | 2018-05-16 07:23 | 406 | 60.01 | 59.987 | 59.945 | -0.023 | -0.065 | -1765.2174 | -624.6154 | No | No | 59.5 | 0.445 | 2018
WI_2018-05-17_000028 | 2018-05-16 17:00 | 2018-05-16 17:00 | PDT | 2018-05-17 | -310 | 59.983 | 60.014 | 60.048 | 0.031 | 0.065 | -1000 | -476.9231 | No | No | 59.5 | 0.548 | 2018
WI_2018-05-17_111515 | 2018-05-17 04:15 | 2018-05-17 04:15 | PDT | 2018-05-17 11:15 | -310 | 59.983 | 60.017 | 60.057 | 0.034 | 0.074 | -911.7647 | -418.9189 | Yes | No | 59.5 | 0.557 | 2018
WI_2018-05-18_135111 | 2018-05-18 06:51 | 2018-05-18 06:51 | PDT | 2018-05-18 13:51 | 1156 | 60.013 | 59.939 | 59.858 | -0.074 | -0.155 | -1562.1622 | -745.8065 | Yes | Yes | 59.5 | 0.358 | 2018
WI_2018-05-19_214515 | 2018-05-19 14:45 | 2018-05-19 14:45 | PDT | 2018-05-19 21:45 | -314 | 59.977 | 60.002 | 60.044 | 0.025 | 0.067 | -1256 | -468.6567 | No | No | 59.5 | 0.544 | 2018
WI_2018-05-22_045301 | 2018-05-21 21:53 | 2018-05-21 21:53 | PDT | 2018-05-22 04:53 | 580 | 60.018 | 59.992 | 59.943 | -0.026 | -0.075 | -2230.7692 | -773.3333 | Yes | No | 59.5 | 0.443 | 2018
WI_2018-05-23_182812 | 2018-05-23 11:28 | 2018-05-23 11:28 | PDT | 2018-05-23 18:28 | 1334 | 59.981 | 59.895 | 59.84 | -0.086 | -0.141 | -1551.1628 | -946.0993 | No | No | 59.5 | 0.34 | 2018
WI_2018-05-29_123017 | 2018-05-29 05:30 | 2018-05-29 05:30 | PDT | 2018-05-29 12:30 | -306 | 59.975 | 59.997 | 60.038 | 0.022 | 0.063 | -1390.9091 | -485.7143 | No | No | 59.5 | 0.538 | 2018
WI_2018-05-29_124517 | 2018-05-29 05:45 | 2018-05-29 05:45 | PDT | 2018-05-29 12:45 | -318 | 59.991 | 60.022 | 60.059 | 0.031 | 0.068 | -1025.8065 | -467.6471 | No | No | 59.5 | 0.559 | 2018
WI_2018-06-01_194037 | 2018-06-01 12:41 | 2018-06-01 12:41 | PDT | 2018-06-01 19:41 | 405 | 60.022 | 59.987 | 59.956 | -0.035 | -0.066 | -1157.1429 | -613.6364 | No | No | 59.5 | 0.456 | 2018
WI_2018-06-06_202351 | 2018-06-06 13:24 | 2018-06-06 13:24 | PDT | 2018-06-06 20:24 | 716 | 59.991 | 59.963 | 59.912 | -0.028 | -0.079 | -2557.1429 | -906.3291 | Yes | Yes | 59.5 | 0.412 | 2018
WI_2018-06-11_130959 | 2018-06-11 06:10 | 2018-06-11 06:10 | PDT | 2018-06-11 13:10 | 534 | 60.026 | 59.966 | 59.934 | -0.06 | -0.092 | -890 | -580.4348 | Yes | No | 59.5 | 0.434 | 2018
WI_2018-06-21_023655 | 2018-06-20 19:37 | 2018-06-20 19:37 | PDT | 2018-06-21 02:37 | 0 | 60.023 | 60.01 | 59.954 | -0.013 | -0.069 |  |  | No | No | 59.5 | 0.454 | 2018
WI_2018-06-21_032028 | 2018-06-20 20:20 | 2018-06-20 20:20 | PDT | 2018-06-21 03:20 | 1236 | 60.011 | 59.943 | 59.893 | -0.068 | -0.118 | -1817.6471 | -1047.4576 | Yes | Yes | 59.5 | 0.393 | 2018
WI_2018-06-22_001620 | 2018-06-21 17:16 | 2018-06-21 17:16 | PDT | 2018-06-22 00:16 | 778 | 59.988 | 59.957 | 59.922 | -0.031 | -0.066 | -2509.6774 | -1178.7879 | Yes | No | 59.5 | 0.422 | 2018
WI_2018-06-22_213834 | 2018-06-22 14:39 | 2018-06-22 14:39 | PDT | 2018-06-22 21:39 | -1 | 60.008 | 60.038 | 60.084 | 0.03 | 0.076 | -3.3333 | -1.3158 | No | No | 59.5 | 0.584 | 2018
WI_2018-06-27_224744 | 2018-06-27 15:48 | 2018-06-27 15:48 | PDT | 2018-06-27 22:48 | 721 | 60.007 | 59.963 | 59.916 | -0.044 | -0.091 | -1638.6364 | -792.3077 | Yes | Yes | 59.5 | 0.416 | 2018
WI_2018-06-28_061217 | 2018-06-27 23:12 | 2018-06-27 23:12 | PDT | 2018-06-28 06:12 | 881 | 59.973 | 59.935 | 59.885 | -0.038 | -0.088 | -2318.4211 | -1001.1364 | Yes | No | 59.5 | 0.385 | 2018
WI_2018-07-04_122735 | 2018-07-04 05:28 | 2018-07-04 05:28 | PDT | 2018-07-04 12:28 | 461 | 60.004 | 59.972 | 59.938 | -0.032 | -0.066 | -1440.625 | -698.4848 | No | No | 59.5 | 0.438 | 2018
WI_2018-07-16_195057 | 2018-07-16 12:51 | 2018-07-16 12:51 | PDT | 2018-07-16 19:51 | 657 | 59.979 | 59.944 | 59.915 | -0.035 | -0.064 | -1877.1429 | -1026.5625 | No | No | 59.5 | 0.415 | 2018
WI_2018-07-18_230927 | 2018-07-18 16:09 | 2018-07-18 16:09 | PDT | 2018-07-18 23:09 | 1007 | 59.976 | 59.93 | 59.887 | -0.046 | -0.089 | -2189.1304 | -1131.4607 | Yes | Yes | 59.5 | 0.387 | 2018
WI_2018-07-19_003022 | 2018-07-18 17:30 | 2018-07-18 17:30 | PDT | 2018-07-19 00:30 | 2741 | 59.985 | 59.863 | 59.746 | -0.122 | -0.239 | -2246.7213 | -1146.8619 | Yes | Yes | 59.5 | 0.246 | 2018
WI_2018-08-03_083647 | 2018-08-03 01:37 | 2018-08-03 01:37 | PDT | 2018-08-03 08:37 | 411 | 60.007 | 59.968 | 59.943 | -0.039 | -0.064 | -1053.8462 | -642.1875 | No | No | 59.5 | 0.443 | 2018
WI_2018-08-04_185025 | 2018-08-04 11:50 | 2018-08-04 11:50 | PDT | 2018-08-04 18:50 | 650 | 60.006 | 59.945 | 59.962 | -0.061 | -0.044 | -1065.5738 | -1477.2727 | No | No | 59.5 | 0.462 | 2018
WI_2018-08-04_193015 | 2018-08-04 12:30 | 2018-08-04 12:30 | PDT | 2018-08-04 19:30 | -315 | 59.968 | 59.998 | 60.034 | 0.03 | 0.066 | -1050 | -477.2727 | No | No | 59.5 | 0.534 | 2018
WI_2018-08-05_053528 | 2018-08-04 22:35 | 2018-08-04 22:35 | PDT | 2018-08-05 05:35 | 651 | 60.002 | 59.976 | 59.95 | -0.026 | -0.052 | -2503.8462 | -1251.9231 | No | No | 59.5 | 0.45 | 2018
WI_2018-08-12_101109 | 2018-08-12 03:11 | 2018-08-12 03:11 | PDT | 2018-08-12 10:11 | 850 | 59.994 | 59.947 | 59.898 | -0.047 | -0.096 | -1808.5106 | -885.4167 | Yes | Yes | 59.5 | 0.398 | 2018
WI_2018-08-17_124509 | 2018-08-17 05:45 | 2018-08-17 05:45 | PDT | 2018-08-17 12:45 | -315 | 59.98 | 60.007 | 60.045 | 0.027 | 0.065 | -1166.6667 | -484.6154 | No | No | 59.5 | 0.545 | 2018
WI_2018-09-02_115548 | 2018-09-02 04:56 | 2018-09-02 04:56 | PDT | 2018-09-02 11:56 | 710 | 59.991 | 59.942 | 59.906 | -0.049 | -0.085 | -1448.9796 | -835.2941 | Yes | Yes | 59.5 | 0.406 | 2018
WI_2018-09-07_143008 | 2018-09-07 07:30 | 2018-09-07 07:30 | PDT | 2018-09-07 14:30 | 450 | 60.022 | 59.983 | 59.947 | -0.039 | -0.075 | -1153.8462 | -600 | Yes | No | 59.5 | 0.447 | 2018
WI_2018-09-19_111514 | 2018-09-19 04:15 | 2018-09-19 04:15 | PDT | 2018-09-19 11:15 | -314 | 59.982 | 60.025 | 60.046 | 0.043 | 0.064 | -730.2326 | -490.625 | No | No | 59.5 | 0.546 | 2018
WI_2018-09-22_174655 | 2018-09-22 10:47 | 2018-09-22 10:47 | PDT | 2018-09-22 17:47 | 593 | 59.998 | 59.954 | 59.928 | -0.044 | -0.07 | -1347.7273 | -847.1429 | Yes | Yes | 59.5 | 0.428 | 2018
WI_2018-09-24_140618 | 2018-09-24 07:06 | 2018-09-24 07:06 | PDT | 2018-09-24 14:06 | 653 | 59.993 | 59.966 | 59.924 | -0.027 | -0.069 | -2418.5185 | -946.3768 | No | No | 59.5 | 0.424 | 2018
WI_2018-10-12_143748 | 2018-10-12 07:38 | 2018-10-12 07:38 | PDT | 2018-10-12 14:38 | 743 | 59.983 | 59.956 | 59.916 | -0.027 | -0.067 | -2751.8519 | -1108.9552 | Yes | No | 59.5 | 0.416 | 2018
WI_2018-10-15_180728 | 2018-10-15 11:07 | 2018-10-15 11:07 | PDT | 2018-10-15 18:07 | 611 | 59.998 | 59.966 | 59.933 | -0.032 | -0.065 | -1909.375 | -940 | No | No | 59.5 | 0.433 | 2018
WI_2018-10-22_120016 | 2018-10-22 05:00 | 2018-10-22 05:00 | PDT | 2018-10-22 12:00 | -309 | 59.986 | 60.031 | 60.05 | 0.045 | 0.064 | -686.6667 | -482.8125 | No | No | 59.5 | 0.55 | 2018
WI_2018-10-29_165404 | 2018-10-29 09:54 | 2018-10-29 09:54 | PDT | 2018-10-29 16:54 | 765 | 60.009 | 59.966 | 59.924 | -0.043 | -0.085 | -1779.0698 | -900 | Yes | Yes | 59.5 | 0.424 | 2018
WI_2018-10-30_015611 | 2018-10-29 18:56 | 2018-10-29 18:56 | PDT | 2018-10-30 01:56 | 660 | 60.005 | 59.969 | 59.922 | -0.036 | -0.083 | -1833.3333 | -795.1807 | Yes | No | 59.5 | 0.422 | 2018
WI_2018-10-30_050119 | 2018-10-29 22:01 | 2018-10-29 22:01 | PDT | 2018-10-30 05:01 | 734 | 59.997 | 59.945 | 59.906 | -0.052 | -0.091 | -1411.5385 | -806.5934 | Yes | Yes | 59.5 | 0.406 | 2018
WI_2018-11-03_081514 | 2018-11-03 01:15 | 2018-11-03 01:15 | PDT | 2018-11-03 08:15 | -317 | 59.973 | 60.022 | 60.044 | 0.049 | 0.071 | -646.9388 | -446.4789 | Yes | No | 59.5 | 0.544 | 2018
WI_2018-11-08_061750 | 2018-11-07 22:18 | 2018-11-07 22:18 | PST | 2018-11-08 06:18 | 477 | 59.989 | 59.966 | 59.927 | -0.023 | -0.062 | -2073.913 | -769.3548 | No | No | 59.5 | 0.427 | 2018
WI_2018-11-09_111653 | 2018-11-09 03:17 | 2018-11-09 03:17 | PST | 2018-11-09 11:17 | 658 | 60.021 | 59.963 | 59.955 | -0.058 | -0.066 | -1134.4828 | -996.9697 | No | No | 59.5 | 0.455 | 2018
WI_2018-11-09_152815 | 2018-11-09 07:28 | 2018-11-09 07:28 | PST | 2018-11-09 15:28 | 784 | 60.029 | 59.982 | 59.931 | -0.047 | -0.098 | -1668.0851 | -800 | Yes | No | 59.5 | 0.431 | 2018
WI_2018-11-18_173617 | 2018-11-18 09:36 | 2018-11-18 09:36 | PST | 2018-11-18 17:36 | 386 | 60.025 | 59.993 | 59.959 | -0.032 | -0.066 | -1206.25 | -584.8485 | No | No | 59.5 | 0.459 | 2018
WI_2018-11-19_224529 | 2018-11-19 14:45 | 2018-11-19 14:45 | PST | 2018-11-19 22:45 | 672 | 59.98 | 59.953 | 59.913 | -0.027 | -0.067 | -2488.8889 | -1002.9851 | No | No | 59.5 | 0.413 | 2018
WI_2018-11-20_143939 | 2018-11-20 06:40 | 2018-11-20 06:40 | PST | 2018-11-20 14:40 | 757 | 59.978 | 59.95 | 59.908 | -0.028 | -0.07 | -2703.5714 | -1081.4286 | Yes | Yes | 59.5 | 0.408 | 2018
WI_2018-11-29_144451 | 2018-11-29 06:45 | 2018-11-29 06:45 | PST | 2018-11-29 14:45 | 1208 | 59.991 | 59.923 | 59.86 | -0.068 | -0.131 | -1776.4706 | -922.1374 | Yes | Yes | 59.5 | 0.36 | 2018
WI_2018-12-01_180644 | 2018-12-01 10:07 | 2018-12-01 10:07 | PST | 2018-12-01 18:07 | 1114 | 60.018 | 59.944 | 59.888 | -0.074 | -0.13 | -1505.4054 | -856.9231 | Yes | Yes | 59.5 | 0.388 | 2019
WI_2018-12-10_234349 | 2018-12-10 15:44 | 2018-12-10 15:44 | PST | 2018-12-10 23:44 | 695 | 59.965 | 59.94 | 59.896 | -0.025 | -0.069 | -2780 | -1007.2464 | No | No | 59.5 | 0.396 | 2019
WI_2018-12-19_033647 | 2018-12-18 19:37 | 2018-12-18 19:37 | PST | 2018-12-19 03:37 | 726 | 60.004 | 59.956 | 59.909 | -0.048 | -0.095 | -1512.5 | -764.2105 | Yes | Yes | 59.5 | 0.409 | 2019
WI_2018-12-23_181844 | 2018-12-23 10:19 | 2018-12-23 10:19 | PST | 2018-12-23 18:19 | 507 | 60.009 | 59.981 | 59.94 | -0.028 | -0.069 | -1810.7143 | -734.7826 | No | No | 59.5 | 0.44 | 2019
WI_2019-01-02_045209 | 2019-01-01 20:52 | 2019-01-01 20:52 | PST | 2019-01-02 04:52 | 495 | 60.022 | 60.014 | 59.968 | -0.008 | -0.054 | -6187.5 | -916.6667 | No | No | 59.5 | 0.468 | 2019
WI_2019-01-02_082143 | 2019-01-02 00:22 | 2019-01-02 00:22 | PST | 2019-01-02 08:22 | 807 | 59.977 | 59.94 | 59.891 | -0.037 | -0.086 | -2181.0811 | -938.3721 | Yes | Yes | 59.5 | 0.391 | 2019
WI_2019-01-06_020750 | 2019-01-05 18:08 | 2019-01-05 18:08 | PST | 2019-01-06 02:08 | 743 | 60.015 | 59.975 | 59.937 | -0.04 | -0.078 | -1857.5 | -952.5641 | Yes | Yes | 59.5 | 0.437 | 2019
WI_2019-01-06_130623 | 2019-01-06 05:06 | 2019-01-06 05:06 | PST | 2019-01-06 13:06 | 440 | 60.024 | 59.98 | 59.956 | -0.044 | -0.068 | -1000 | -647.0588 | No | No | 59.5 | 0.456 | 2019
WI_2019-01-07_073123 | 2019-01-06 23:31 | 2019-01-06 23:31 | PST | 2019-01-07 07:31 | 675 | 60.011 | 59.956 | 59.923 | -0.055 | -0.088 | -1227.2727 | -767.0455 | Yes | Yes | 59.5 | 0.423 | 2019
WI_2019-01-12_230015 | 2019-01-12 15:00 | 2019-01-12 15:00 | PST | 2019-01-12 23:00 | -310 | 59.971 | 60 | 60.033 | 0.029 | 0.062 | -1068.9655 | -500 | No | No | 59.5 | 0.533 | 2019
WI_2019-01-16_031539 | 2019-01-15 19:16 | 2019-01-15 19:16 | PST | 2019-01-16 03:16 | 1122 | 59.986 | 59.934 | 59.882 | -0.052 | -0.104 | -2157.6923 | -1078.8462 | Yes | Yes | 59.5 | 0.382 | 2019
WI_2019-01-19_011911 | 2019-01-18 17:19 | 2019-01-18 17:19 | PST | 2019-01-19 01:19 | 650 | 59.977 | 59.971 | 59.926 | -0.006 | -0.051 | -10833.3333 | -1274.5098 | No | No | 59.5 | 0.426 | 2019
WI_2019-01-25_134515 | 2019-01-25 05:45 | 2019-01-25 05:45 | PST | 2019-01-25 13:45 | -311 | 59.95 | 59.996 | 60.01 | 0.046 | 0.06 | -676.087 | -518.3333 | No | No | 59.5 | 0.51 | 2019
WI_2019-01-27_231519 | 2019-01-27 15:15 | 2019-01-27 15:15 | PST | 2019-01-27 23:15 | -311 | 59.956 | 60.009 | 60.022 | 0.053 | 0.066 | -586.7925 | -471.2121 | No | No | 59.5 | 0.522 | 2019
WI_2019-01-29_120017 | 2019-01-29 04:00 | 2019-01-29 04:00 | PST | 2019-01-29 12:00 | -289 | 59.962 | 60.001 | 60.031 | 0.039 | 0.069 | -741.0256 | -418.8406 | No | No | 59.5 | 0.531 | 2019
WI_2019-02-28_150348 | 2019-02-28 07:04 | 2019-02-28 07:04 | PST | 2019-02-28 15:04 | 512 | 60.018 | 59.979 | 59.946 | -0.039 | -0.072 | -1312.8205 | -711.1111 | Yes | No | 59.5 | 0.446 | 2019
WI_2019-02-28_231930 | 2019-02-28 15:20 | 2019-02-28 15:20 | PST | 2019-02-28 23:20 | 421 | 59.983 | 59.959 | 59.928 | -0.024 | -0.055 | -1754.1667 | -765.4545 | No | No | 59.5 | 0.428 | 2019
WI_2019-03-03_000021 | 2019-03-02 16:00 | 2019-03-02 16:00 | PST | 2019-03-03 | -327 | 59.978 | 60.018 | 60.042 | 0.04 | 0.064 | -817.5 | -510.9375 | No | No | 59.5 | 0.542 | 2019
WI_2019-03-11_020655 | 2019-03-10 19:07 | 2019-03-10 19:07 | PDT | 2019-03-11 02:07 | 698 | 59.972 | 59.941 | 59.892 | -0.031 | -0.08 | -2251.6129 | -872.5 | Yes | Yes | 59.5 | 0.392 | 2019
WI_2019-03-11_204811 | 2019-03-11 13:48 | 2019-03-11 13:48 | PDT | 2019-03-11 20:48 | 541 | 60.004 | 59.987 | 59.934 | -0.017 | -0.07 | -3182.3529 | -772.8571 | Yes | No | 59.5 | 0.434 | 2019
WI_2019-03-12_205453 | 2019-03-12 13:55 | 2019-03-12 13:55 | PDT | 2019-03-12 20:55 | 380 | 60.013 | 59.999 | 59.943 | -0.014 | -0.07 | -2714.2857 | -542.8571 | Yes | No | 59.5 | 0.443 | 2019
WI_2019-03-13_184756 | 2019-03-13 11:48 | 2019-03-13 11:48 | PDT | 2019-03-13 18:48 | 290 | 60.032 | 60.019 | 59.961 | -0.013 | -0.071 | -2230.7692 | -408.4507 | Yes | No | 59.5 | 0.461 | 2019
WI_2019-03-18_192945 | 2019-03-18 12:30 | 2019-03-18 12:30 | PDT | 2019-03-18 19:30 | 558 | 60.005 | 59.965 | 59.93 | -0.04 | -0.075 | -1395 | -744 | Yes | Yes | 59.5 | 0.43 | 2019
WI_2019-03-25_011045 | 2019-03-24 18:11 | 2019-03-24 18:11 | PDT | 2019-03-25 01:11 | 1533 | 59.991 | 59.927 | 59.875 | -0.064 | -0.116 | -2395.3125 | -1321.5517 | Yes | Yes | 59.5 | 0.375 | 2019
WI_2019-04-05_210021 | 2019-04-05 14:00 | 2019-04-05 14:00 | PDT | 2019-04-05 21:00 | -306 | 59.958 | 59.973 | 60.029 | 0.015 | 0.071 | -2040 | -430.9859 | No | No | 59.5 | 0.529 | 2019
WI_2019-04-09_101641 | 2019-04-09 03:17 | 2019-04-09 03:17 | PDT | 2019-04-09 10:17 | 638 | 59.98 | 59.961 | 59.91 | -0.019 | -0.07 | -3357.8947 | -911.4286 | No | No | 59.5 | 0.41 | 2019
WI_2019-04-10_202256 | 2019-04-10 13:23 | 2019-04-10 13:23 | PDT | 2019-04-10 20:23 | -314 | 59.965 | 59.994 | 60.017 | 0.029 | 0.052 | -1082.7586 | -603.8462 | No | No | 59.5 | 0.517 | 2019
WI_2019-04-27_220015 | 2019-04-27 15:00 | 2019-04-27 15:00 | PDT | 2019-04-27 22:00 | -301 | 59.985 | 59.992 | 60.056 | 0.007 | 0.071 | -4300 | -423.9437 | No | No | 59.5 | 0.556 | 2019
WI_2019-04-28_213009 | 2019-04-28 14:30 | 2019-04-28 14:30 | PDT | 2019-04-28 21:30 | -1 | 59.987 | 60.013 | 60.047 | 0.026 | 0.06 | -3.8462 | -1.6667 | No | No | 59.5 | 0.547 | 2019
WI_2019-04-29_111456 | 2019-04-29 04:15 | 2019-04-29 04:15 | PDT | 2019-04-29 11:15 | 438 | 60.01 | 59.962 | 59.936 | -0.048 | -0.074 | -912.5 | -591.8919 | Yes | Yes | 59.5 | 0.436 | 2019
WI_2019-05-07_230011 | 2019-05-07 16:00 | 2019-05-07 16:00 | PDT | 2019-05-07 23:00 | -296 | 59.973 | 60.002 | 60.042 | 0.029 | 0.069 | -1020.6897 | -428.9855 | No | No | 59.5 | 0.542 | 2019
WI_2019-05-09_152644 | 2019-05-09 08:27 | 2019-05-09 08:27 | PDT | 2019-05-09 15:27 | 340 | 60.034 | 60.012 | 59.967 | -0.022 | -0.067 | -1545.4545 | -507.4627 | No | No | 59.5 | 0.467 | 2019
WI_2019-05-10_035828 | 2019-05-09 20:58 | 2019-05-09 20:58 | PDT | 2019-05-10 03:58 | 396 | 60.025 | 59.994 | 59.951 | -0.031 | -0.074 | -1277.4194 | -535.1351 | Yes | No | 59.5 | 0.451 | 2019
WI_2019-05-14_110013 | 2019-05-14 04:00 | 2019-05-14 04:00 | PDT | 2019-05-14 11:00 | -300 | 59.964 | 60.008 | 60.037 | 0.044 | 0.073 | -681.8182 | -410.9589 | No | No | 59.5 | 0.537 | 2019
WI_2019-05-21_010019 | 2019-05-20 18:00 | 2019-05-20 18:00 | PDT | 2019-05-21 01:00 | -289 | 59.958 | 59.981 | 60.028 | 0.023 | 0.07 | -1256.5217 | -412.8571 | Yes | No | 59.5 | 0.528 | 2019
WI_2019-05-21_210007 | 2019-05-21 14:00 | 2019-05-21 14:00 | PDT | 2019-05-21 21:00 | -261 | 59.976 | 59.993 | 60.037 | 0.017 | 0.061 | -1535.2941 | -427.8689 | No | No | 59.5 | 0.537 | 2019
WI_2019-05-26_003007 | 2019-05-25 17:30 | 2019-05-25 17:30 | PDT | 2019-05-26 00:30 | -432 | 59.962 | 59.99 | 60.031 | 0.028 | 0.069 | -1542.8571 | -626.087 | No | No | 59.5 | 0.531 | 2019
WI_2019-05-26_173013 | 2019-05-26 10:30 | 2019-05-26 10:30 | PDT | 2019-05-26 17:30 | -236 | 59.987 | 60.016 | 60.058 | 0.029 | 0.071 | -813.7931 | -332.3944 | No | No | 59.5 | 0.558 | 2019
WI_2019-05-31_202145 | 2019-05-31 13:22 | 2019-05-31 13:22 | PDT | 2019-05-31 20:22 | 496 | 60.016 | 59.967 | 59.935 | -0.049 | -0.081 | -1012.2449 | -612.3457 | Yes | No | 59.5 | 0.435 | 2019
WI_2019-06-02_190537 | 2019-06-02 12:06 | 2019-06-02 12:06 | PDT | 2019-06-02 19:06 | 573 | 60.027 | 59.982 | 59.931 | -0.045 | -0.096 | -1273.3333 | -596.875 | Yes | No | 59.5 | 0.431 | 2019
WI_2019-06-19_151126 | 2019-06-19 08:11 | 2019-06-19 08:11 | PDT | 2019-06-19 15:11 | 486 | 60 | 59.968 | 59.934 | -0.032 | -0.066 | -1518.75 | -736.3636 | No | No | 59.5 | 0.434 | 2019
WI_2019-06-28_043132 | 2019-06-27 21:32 | 2019-06-27 21:32 | PDT | 2019-06-28 04:32 | 418 | 60.026 | 59.99 | 59.966 | -0.036 | -0.06 | -1161.1111 | -696.6667 | No | No | 59.5 | 0.466 | 2019
WI_2019-07-24_072645 | 2019-07-24 00:27 | 2019-07-24 00:27 | PDT | 2019-07-24 07:27 | 550 | 60.031 | 59.979 | 59.955 | -0.052 | -0.076 | -1057.6923 | -723.6842 | Yes | No | 59.5 | 0.455 | 2019
WI_2019-07-26_071213 | 2019-07-26 00:12 | 2019-07-26 00:12 | PDT | 2019-07-26 07:12 | 738 | 59.999 | 59.955 | 59.906 | -0.044 | -0.093 | -1677.2727 | -793.5484 | Yes | Yes | 59.5 | 0.406 | 2019
WI_2019-07-28_181517 | 2019-07-28 11:15 | 2019-07-28 11:15 | PDT | 2019-07-28 18:15 | -301 | 59.97 | 59.997 | 60.031 | 0.027 | 0.061 | -1114.8148 | -493.4426 | Yes | No | 59.5 | 0.531 | 2019
WI_2019-08-01_195136 | 2019-08-01 12:52 | 2019-08-01 12:52 | PDT | 2019-08-01 19:52 | 750 | 59.976 | 59.949 | 59.907 | -0.027 | -0.069 | -2777.7778 | -1086.9565 | Yes | No | 59.5 | 0.407 | 2019
WI_2019-08-02_223351 | 2019-08-02 15:34 | 2019-08-02 15:34 | PDT | 2019-08-02 22:34 | -888 | 60.008 | 60.052 | 60.081 | 0.044 | 0.073 | -2018.1818 | -1216.4384 | Yes | Yes | 59.5 | 0.581 | 2019
WI_2019-08-03_204104 | 2019-08-03 13:41 | 2019-08-03 13:41 | PDT | 2019-08-03 20:41 | 757 | 59.981 | 59.945 | 59.906 | -0.036 | -0.075 | -2102.7778 | -1009.3333 | Yes | Yes | 59.5 | 0.406 | 2019
WI_2019-08-06_002322 | 2019-08-05 17:23 | 2019-08-05 17:23 | PDT | 2019-08-06 00:23 | 712 | 59.987 | 59.963 | 59.946 | -0.024 | -0.041 | -2966.6667 | -1736.5854 | Yes | No | 59.5 | 0.446 | 2019
WI_2019-08-16_152106 | 2019-08-16 08:21 | 2019-08-16 08:21 | PDT | 2019-08-16 15:21 | 1311 | 60.009 | 59.938 | 59.887 | -0.071 | -0.122 | -1846.4789 | -1074.5902 | Yes | Yes | 59.5 | 0.387 | 2019
WI_2019-08-23_174301 | 2019-08-23 10:43 | 2019-08-23 10:43 | PDT | 2019-08-23 17:43 | 1442 | 59.989 | 59.926 | 59.857 | -0.063 | -0.132 | -2288.8889 | -1092.4242 | Yes | Yes | 59.5 | 0.357 | 2019
WI_2019-08-25_150818 | 2019-08-25 08:08 | 2019-08-25 08:08 | PDT | 2019-08-25 15:08 | 749 | 60.022 | 59.967 | 59.932 | -0.055 | -0.09 | -1361.8182 | -832.2222 | Yes | No | 59.5 | 0.432 | 2019
WI_2019-08-31_144432 | 2019-08-31 07:45 | 2019-08-31 07:45 | PDT | 2019-08-31 14:45 | 702 | 59.962 | 59.945 | 59.901 | -0.017 | -0.061 | -4129.4118 | -1150.8197 | Yes | No | 59.5 | 0.401 | 2019
WI_2019-09-02_092929 | 2019-09-02 02:29 | 2019-09-02 02:29 | PDT | 2019-09-02 09:29 | 765 | 60.026 | 59.967 | 59.923 | -0.059 | -0.103 | -1296.6102 | -742.7184 | No | No | 59.5 | 0.423 | 2019
WI_2019-09-03_191505 | 2019-09-03 12:15 | 2019-09-03 12:15 | PDT | 2019-09-03 19:15 | 744 | 59.977 | 59.952 | 59.905 | -0.025 | -0.072 | -2976 | -1033.3333 | Yes | Yes | 59.5 | 0.405 | 2019
WI_2019-09-11_042240 | 2019-09-10 21:23 | 2019-09-10 21:23 | PDT | 2019-09-11 04:23 | 855 | 59.981 | 59.936 | 59.9 | -0.045 | -0.081 | -1900 | -1055.5556 | Yes | Yes | 59.5 | 0.4 | 2019
WI_2019-09-12_035206 | 2019-09-11 20:52 | 2019-09-11 20:52 | PDT | 2019-09-12 03:52 | 1678 | 60.029 | 59.949 | 59.888 | -0.08 | -0.141 | -2097.5 | -1190.0709 | No | No | 59.5 | 0.388 | 2019
WI_2019-09-19_090113 | 2019-09-19 02:01 | 2019-09-19 02:01 | PDT | 2019-09-19 09:01 | 757 | 59.968 | 59.941 | 59.906 | -0.027 | -0.062 | -2803.7037 | -1220.9677 | No | No | 59.5 | 0.406 | 2019
WI_2019-10-04_011938 | 2019-10-03 18:20 | 2019-10-03 18:20 | PDT | 2019-10-04 01:20 | 450 | 60.015 | 59.984 | 59.939 | -0.031 | -0.076 | -1451.6129 | -592.1053 | Yes | No | 59.5 | 0.439 | 2019
WI_2019-10-13_211522 | 2019-10-13 14:15 | 2019-10-13 14:15 | PDT | 2019-10-13 21:15 | -313 | 59.969 | 60.013 | 60.043 | 0.044 | 0.074 | -711.3636 | -422.973 | No | No | 59.5 | 0.543 | 2019
WI_2019-11-04_123205 | 2019-11-04 04:32 | 2019-11-04 04:32 | PST | 2019-11-04 12:32 | 611 | 59.968 | 59.938 | 59.892 | -0.03 | -0.076 | -2036.6667 | -803.9474 | Yes | Yes | 59.5 | 0.392 | 2019
WI_2019-11-10_195121 | 2019-11-10 11:51 | 2019-11-10 11:51 | PST | 2019-11-10 19:51 | 715 | 59.992 | 59.952 | 59.914 | -0.04 | -0.078 | -1787.5 | -916.6667 | Yes | Yes | 59.5 | 0.414 | 2019
WI_2019-11-14_075200 | 2019-11-13 23:52 | 2019-11-13 23:52 | PST | 2019-11-14 07:52 | 500 | 60.016 | 59.961 | 59.936 | -0.055 | -0.08 | -909.0909 | -625 | Yes | No | 59.5 | 0.436 | 2019
WI_2019-11-20_100946 | 2019-11-20 02:10 | 2019-11-20 02:10 | PST | 2019-11-20 10:10 | 449 | 59.992 | 59.962 | 59.935 | -0.03 | -0.057 | -1496.6667 | -787.7193 | No | No | 59.5 | 0.435 | 2019
WI_2019-11-28_164436 | 2019-11-28 08:45 | 2019-11-28 08:45 | PST | 2019-11-28 16:45 | 769 | 59.988 | 59.955 | 59.918 | -0.033 | -0.07 | -2330.303 | -1098.5714 | Yes | Yes | 59.5 | 0.418 | 2019
WI_2019-11-29_171839 | 2019-11-29 09:19 | 2019-11-29 09:19 | PST | 2019-11-29 17:19 | 650 | 60.015 | 59.977 | 59.938 | -0.038 | -0.077 | -1710.5263 | -844.1558 | Yes | No | 59.5 | 0.438 | 2019
WI_2019-12-17_184837 | 2019-12-17 10:49 | 2019-12-17 10:49 | PST | 2019-12-17 18:49 | 743.9 | 60.013 | 59.963 | 59.941 | -0.05 | -0.072 | -1487.8 | -1033.1944 | Yes | Yes | 59.5 | 0.441 | 2020
WI_2019-12-21_050545 | 2019-12-20 21:06 | 2019-12-20 21:06 | PST | 2019-12-21 05:06 | 750 | 60.008 | 59.975 | 59.94 | -0.033 | -0.068 | -2272.7273 | -1102.9412 | Yes | No | 59.5 | 0.44 | 2020
WI_2019-12-23_045723 | 2019-12-22 20:57 | 2019-12-22 20:57 | PST | 2019-12-23 04:57 | 775 | 60.005 | 59.954 | 59.916 | -0.051 | -0.089 | -1519.6078 | -870.7865 | Yes | Yes | 59.5 | 0.416 | 2020
WI_2019-12-26_093026 | 2019-12-26 01:30 | 2019-12-26 01:30 | PST | 2019-12-26 09:30 | 771 | 60.001 | 59.961 | 59.922 | -0.04 | -0.079 | -1927.5 | -975.9494 | Yes | Yes | 59.5 | 0.422 | 2020
WI_2020-01-01_120656 | 2020-01-01 04:07 | 2020-01-01 04:07 | PST | 2020-01-01 12:07 | 1035 | 60.033 | 59.961 | 59.907 | -0.072 | -0.126 | -1437.5 | -821.4286 | Yes | No | 59.5 | 0.407 | 2020
WI_2020-01-16_071824 | 2020-01-15 23:18 | 2020-01-15 23:18 | PST | 2020-01-16 07:18 | 450 | 60.024 | 59.981 | 59.958 | -0.043 | -0.066 | -1046.5116 | -681.8182 | No | No | 59.5 | 0.458 | 2020
WI_2020-01-20_135854 | 2020-01-20 05:59 | 2020-01-20 05:59 | PST | 2020-01-20 13:59 | 1167 | 60.014 | 59.957 | 59.888 | -0.057 | -0.126 | -2047.3684 | -926.1905 | Yes | Yes | 59.5 | 0.388 | 2020
WI_2020-02-11_200628 | 2020-02-11 12:06 | 2020-02-11 12:06 | PST | 2020-02-11 20:06 | 404 | 60.031 | 59.992 | 59.961 | -0.039 | -0.07 | -1035.8974 | -577.1429 | Yes | No | 59.5 | 0.461 | 2020
WI_2020-02-17_160251 | 2020-02-17 08:03 | 2020-02-17 08:03 | PST | 2020-02-17 16:03 | 334 | 60 | 60.001 | 59.961 | 0.001 | -0.039 | 33400 | -856.4103 | No | No | 59.5 | 0.461 | 2020
WI_2020-02-21_173018 | 2020-02-21 09:30 | 2020-02-21 09:30 | PST | 2020-02-21 17:30 | 432 | 59.994 | 59.976 | 59.948 | -0.018 | -0.046 | -2400 | -939.1304 | No | No | 59.5 | 0.448 | 2020
WI_2020-02-25_100924 | 2020-02-25 02:09 | 2020-02-25 02:09 | PST | 2020-02-25 10:09 | 300 | 59.977 | 59.962 | 59.939 | -0.015 | -0.038 | -2000 | -789.4737 | No | No | 59.5 | 0.439 | 2020
WI_2020-03-03_072530 | 2020-03-02 23:25 | 2020-03-02 23:25 | PST | 2020-03-03 07:25 | 567 | 60.015 | 59.971 | 59.939 | -0.044 | -0.076 | -1288.6364 | -746.0526 | Yes | Yes | 59.5 | 0.439 | 2020
WI_2020-03-04_034941 | 2020-03-03 19:50 | 2020-03-03 19:50 | PST | 2020-03-04 03:50 | 967 | 59.959 | 59.946 | 59.875 | -0.013 | -0.084 | -7438.4615 | -1151.1905 | Yes | Yes | 59.5 | 0.375 | 2020
WI_2020-03-19_120700 | 2020-03-19 05:07 | 2020-03-19 05:07 | PDT | 2020-03-19 12:07 | 573 | 59.99 | 59.975 | 59.922 | -0.015 | -0.068 | -3820 | -842.6471 | No | No | 59.5 | 0.422 | 2020
WI_2020-04-11_182424 | 2020-04-11 11:24 | 2020-04-11 11:24 | PDT | 2020-04-11 18:24 | 504 | 59.993 | 59.956 | 59.927 | -0.037 | -0.066 | -1362.1622 | -763.6364 | No | No | 59.5 | 0.427 | 2020
WI_2020-04-20_211500 | 2020-04-20 14:15 | 2020-04-20 14:15 | PDT | 2020-04-20 21:15 | 650 | 59.98 | 59.961 | 59.913 | -0.019 | -0.067 | -3421.0526 | -970.1493 | No | No | 59.5 | 0.413 | 2020
WI_2020-05-05_235235 | 2020-05-05 16:53 | 2020-05-05 16:53 | PDT | 2020-05-05 23:53 | 593 | 60.003 | 59.977 | 59.928 | -0.026 | -0.075 | -2280.7692 | -790.6667 | Yes | Yes | 59.5 | 0.428 | 2020
WI_2020-05-08_131100 | 2020-05-08 06:11 | 2020-05-08 06:11 | PDT | 2020-05-08 13:11 | 750 | 60.009 | 59.971 | 59.916 | -0.038 | -0.093 | -1973.6842 | -806.4516 | Yes | Yes | 59.5 | 0.416 | 2020
WI_2020-05-19_212652 | 2020-05-19 14:27 | 2020-05-19 14:27 | PDT | 2020-05-19 21:27 | 560 | 60.035 | 60.003 | 59.953 | -0.032 | -0.082 | -1750 | -682.9268 | Yes | No | 59.5 | 0.453 | 2020
WI_2020-06-07_233346 | 2020-06-07 16:34 | 2020-06-07 16:34 | PDT | 2020-06-07 23:34 | 668 | 60 | 59.968 | 59.926 | -0.032 | -0.074 | -2087.5 | -902.7027 | Yes | Yes | 59.5 | 0.426 | 2020
WI_2020-06-08_195833 | 2020-06-08 12:59 | 2020-06-08 12:59 | PDT | 2020-06-08 19:59 | 600 | 60.015 | 59.99 | 59.942 | -0.025 | -0.073 | -2400 | -821.9178 | Yes | No | 59.5 | 0.442 | 2020
WI_2020-06-09_061119 | 2020-06-08 23:11 | 2020-06-08 23:11 | PDT | 2020-06-09 06:11 | 650 | 60.001 | 59.969 | 59.926 | -0.032 | -0.075 | -2031.25 | -866.6667 | Yes | Yes | 59.5 | 0.426 | 2020
WI_2020-06-13_191336 | 2020-06-13 12:14 | 2020-06-13 12:14 | PDT | 2020-06-13 19:14 | 530 | 60.021 | 59.982 | 59.949 | -0.039 | -0.072 | -1358.9744 | -736.1111 | Yes | No | 59.5 | 0.449 | 2020
WI_2020-06-18_222059 | 2020-06-18 15:21 | 2020-06-18 15:21 | PDT | 2020-06-18 22:21 | 800 | 59.981 | 59.962 | 59.914 | -0.019 | -0.067 | -4210.5263 | -1194.0299 | Yes | No | 59.5 | 0.414 | 2020
WI_2020-07-17_204615 | 2020-07-17 13:46 | 2020-07-17 13:46 | PDT | 2020-07-17 20:46 | 1113 | 59.996 | 59.957 | 59.888 | -0.039 | -0.108 | -2853.8462 | -1030.5556 | Yes | Yes | 59.5 | 0.388 | 2020
WI_2020-07-25_072904 | 2020-07-25 00:29 | 2020-07-25 00:29 | PDT | 2020-07-25 07:29 | 747 | 60.014 | 59.978 | 59.919 | -0.036 | -0.095 | -2075 | -786.3158 | Yes | No | 59.5 | 0.419 | 2020
WI_2020-07-26_182706 | 2020-07-26 11:27 | 2020-07-26 11:27 | PDT | 2020-07-26 18:27 | 747 | 59.972 | 59.954 | 59.913 | -0.018 | -0.059 | -4150 | -1266.1017 | Yes | No | 59.5 | 0.413 | 2020
WI_2020-07-28_162626 | 2020-07-28 09:26 | 2020-07-28 09:26 | PDT | 2020-07-28 16:26 | 750 | 59.986 | 59.947 | 59.91 | -0.039 | -0.076 | -1923.0769 | -986.8421 | Yes | Yes | 59.5 | 0.41 | 2020
WI_2020-07-31_004732 | 2020-07-30 17:48 | 2020-07-30 17:48 | PDT | 2020-07-31 00:48 | 1384 | 59.973 | 59.936 | 59.913 | -0.037 | -0.06 | -3740.5405 | -2306.6667 | No | No | 59.5 | 0.413 | 2020
WI_2020-08-03_210810 | 2020-08-03 14:08 | 2020-08-03 14:08 | PDT | 2020-08-03 21:08 | 810 | 59.978 | 59.969 | 59.914 | -0.009 | -0.064 | -9000 | -1265.625 | No | No | 59.5 | 0.414 | 2020
WI_2020-08-06_140633 | 2020-08-06 07:07 | 2020-08-06 07:07 | PDT | 2020-08-06 14:07 | 304 | 60.015 | 59.989 | 59.974 | -0.026 | -0.041 | -1169.2308 | -741.4634 | No | No | 59.5 | 0.474 | 2020
WI_2020-08-10_041042 | 2020-08-09 21:11 | 2020-08-09 21:11 | PDT | 2020-08-10 04:11 | 297 | 59.991 | 59.965 | 59.913 | -0.026 | -0.078 | -1142.3077 | -380.7692 | Yes | No | 59.5 | 0.413 | 2020
WI_2020-08-21_225436 | 2020-08-21 15:55 | 2020-08-21 15:55 | PDT | 2020-08-21 22:55 | 979 | 60.006 | 59.978 | 59.926 | -0.028 | -0.08 | -3496.4286 | -1223.75 | Yes | No | 59.5 | 0.426 | 2020
WI_2020-08-28_232715 | 2020-08-28 16:27 | 2020-08-28 16:27 | PDT | 2020-08-28 23:27 | 1966 | 59.969 | 59.896 | 59.81 | -0.073 | -0.159 | -2693.1507 | -1236.478 | Yes | Yes | 59.5 | 0.31 | 2020
WI_2020-09-04_031633 | 2020-09-03 20:17 | 2020-09-03 20:17 | PDT | 2020-09-04 03:17 | 1390 | 60.002 | 59.944 | 59.873 | -0.058 | -0.129 | -2396.5517 | -1077.5194 | Yes | Yes | 59.5 | 0.373 | 2020
WI_2020-09-05_220211 | 2020-09-05 15:02 | 2020-09-05 15:02 | PDT | 2020-09-05 22:02 | 754 | 60.009 | 59.964 | 59.877 | -0.045 | -0.132 | -1675.5556 | -571.2121 | Yes | Yes | 59.5 | 0.377 | 2020
WI_2020-09-06_022256 | 2020-09-05 19:23 | 2020-09-05 19:23 | PDT | 2020-09-06 02:23 | 984 | 60.034 | 59.982 | 59.942 | -0.052 | -0.092 | -1892.3077 | -1069.5652 | Yes | No | 59.5 | 0.442 | 2020
WI_2020-09-07_005003 | 2020-09-06 17:50 | 2020-09-06 17:50 | PDT | 2020-09-07 00:50 | 2507 | 59.896 | 59.853 | 59.744 | -0.043 | -0.152 | -5830.2326 | -1649.3421 | Yes | Yes | 59.5 | 0.244 | 2020
WI_2020-09-07_222901 | 2020-09-07 15:29 | 2020-09-07 15:29 | PDT | 2020-09-07 22:29 | 928 | 59.985 | 59.943 | 59.9 | -0.042 | -0.085 | -2209.5238 | -1091.7647 | Yes | Yes | 59.5 | 0.4 | 2020
WI_2020-09-08_085218 | 2020-09-08 01:52 | 2020-09-08 01:52 | PDT | 2020-09-08 08:52 | 1450 | 59.999 | 59.926 | 59.867 | -0.073 | -0.132 | -1986.3014 | -1098.4848 | Yes | Yes | 59.5 | 0.367 | 2020
WI_2020-10-09_164401 | 2020-10-09 09:44 | 2020-10-09 09:44 | PDT | 2020-10-09 16:44 | 814 | 59.983 | 59.948 | 59.9 | -0.035 | -0.083 | -2325.7143 | -980.7229 | Yes | Yes | 59.5 | 0.4 | 2020
WI_2020-11-08_004034 | 2020-11-07 16:41 | 2020-11-07 16:41 | PST | 2020-11-08 00:41 | 934 | 59.963 | 59.923 | 59.878 | -0.04 | -0.085 | -2335 | -1098.8235 | Yes | Yes | 59.5 | 0.378 | 2020
WI_2020-12-06_034044 | 2020-12-05 19:41 | 2020-12-05 19:41 | PST | 2020-12-06 03:41 | 540 | 60.012 | 59.986 | 59.932 | -0.026 | -0.08 | -2076.9231 | -675 | Yes | Yes | 59.5 | 0.432 | 2021
WI_2021-01-13_212841 | 2021-01-13 13:29 | 2021-01-13 13:29 | PST | 2021-01-13 21:29 | 347 | 60.011 | 59.973 | 59.942 | -0.038 | -0.069 | -913.1579 | -502.8986 | No | No | 59.5 | 0.442 | 2021
WI_2021-01-27_072559 | 2021-01-26 23:26 | 2021-01-26 23:26 | PST | 2021-01-27 07:26 | 575 | 60.022 | 59.989 | 59.946 | -0.033 | -0.076 | -1742.4242 | -756.5789 | Yes | No | 59.5 | 0.446 | 2021
WI_2021-02-06_121245 | 2021-02-06 04:13 | 2021-02-06 04:13 | PST | 2021-02-06 12:13 | 1810 | 60.023 | 59.905 | 59.82 | -0.118 | -0.203 | -1533.8983 | -891.6256 | Yes | Yes | 59.5 | 0.32 | 2021
WI_2021-02-11_144823 | 2021-02-11 06:48 | 2021-02-11 06:48 | PST | 2021-02-11 14:48 | 785 | 59.993 | 59.965 | 59.919 | -0.028 | -0.074 | -2803.5714 | -1060.8108 | Yes | Yes | 59.5 | 0.419 | 2021
WI_2021-02-26_173308 | 2021-02-26 09:33 | 2021-02-26 09:33 | PST | 2021-02-26 17:33 | 1341 | 60.022 | 59.944 | 59.874 | -0.078 | -0.148 | -1719.2308 | -906.0811 | Yes | Yes | 59.5 | 0.374 | 2021
Note on A565: Brad Gordon: Check event ID due to start time.

## TI
Initial Start Time
(From Fnet)
UTC Initial t0
Event ID (From UTC Initial t0) | Local Date / Time (MM/DD/YY HH:MM:SS) | Day | Time Zone | Date / Time (MM/DD/YY HH:MM:SS) | NERC Confirmed MW Loss | A Value Hz | B Value Hz | Point C Hz | B-A Delta Hz | C-A Delta Hz | A to B IFRM | A to C IFRM | FWG Sel. M-4 | FWG Sel. BAL-003 | 1st Step UFLS Hz | C - UFLS Margin Hz | Oper Year (Local)
TI_2011-12-08_023144 | 2011-12-07 20:32 | 2011-12-07 20:32 | CST | 2011-12-08 02:32 | 475.12 | 60.0153 | 59.9153 | 59.903 | -0.099956 | -0.11225 | -475.3268 | -423.2665 | Yes | Yes | 59.3 | 0.603 | 2012
TI_2011-12-14_165542 | 2011-12-14 10:56 | 2011-12-14 10:56 | CST | 2011-12-14 16:56 | 392 | 60.0326 | 59.8968 | 59.894 | -0.1358 | -0.13862 | -288.6561 | -282.7799 | No | Yes | 59.3 | 0.594 | 2012
TI_2011-12-14_184604 | 2011-12-14 12:46 | 2011-12-14 12:46 | CST | 2011-12-14 18:46 | 560 | 59.9797 | 59.8565 | 59.8172 | -0.12317 | -0.16248 | -454.6636 | -344.6575 | Yes | Yes | 59.3 | 0.5172 | 2012
TI_2011-12-14_204626 | 2011-12-14 14:46 | 2011-12-14 14:46 | CST | 2011-12-14 20:46 | 483.4 | 59.9619 | 59.8628 | 59.8268 | -0.099052 | -0.13507 | -488.0267 | -357.883 | Yes | Yes | 59.3 | 0.5268 | 2012
TI_2011-12-15_191628 | 2011-12-15 13:16 | 2011-12-15 13:16 | CST | 2011-12-15 19:16 | 606.2 | 60.0042 | 59.8442 | 59.7898 | -0.15999 | -0.21441 | -378.9086 | -282.7231 | Yes | Yes | 59.3 | 0.4898 | 2012
TI_2011-12-18_141504 | 2011-12-18 08:15 | 2011-12-18 08:15 | CST | 2011-12-18 14:15 | 778.7 | 59.9845 | 59.8435 | 59.763 | -0.14097 | -0.2215 | -552.384 | -351.5577 | Yes | Yes | 59.3 | 0.463 | 2012
TI_2011-12-22_111525 | 2011-12-22 05:15 | 2011-12-22 05:15 | CST | 2011-12-22 11:15 | 593.8 | 59.9786 | 59.8597 | 59.8006 | -0.11893 | -0.17802 | -499.2787 | -333.5557 | Yes | Yes | 59.3 | 0.5006 | 2012
TI_2011-12-26_094608 | 2011-12-26 03:46 | 2011-12-26 03:46 | CST | 2011-12-26 09:46 | 546 | 60.0021 | 59.8838 | 59.8347 | -0.11825 | -0.1674 | -461.7277 | -326.1676 | Yes | Yes | 59.3 | 0.5347 | 2012
TI_2011-12-28_154908 | 2011-12-28 09:49 | 2011-12-28 09:49 | CST | 2011-12-28 15:49 | 718.4 | 59.9881 | 59.8654 | 59.7963 | -0.12272 | -0.19178 | -585.4024 | -374.5942 | Yes | Yes | 59.3 | 0.4963 | 2012
TI_2011-12-30_215707 | 2011-12-30 15:57 | 2011-12-30 15:57 | CST | 2011-12-30 21:57 | 629 | 59.9781 | 59.8611 | 59.7915 | -0.11708 | -0.18664 | -537.2562 | -337.0126 | Yes | Yes | 59.3 | 0.4915 | 2012
TI_2012-01-01_073746 | 2012-01-01 01:38 | 2012-01-01 01:38 | CST | 2012-01-01 07:38 |  | 60.0001 | 60.0028 | 59.9016 | 0.0026663 | -0.098525 |  |  | No | No | 59.3 | 0.6016 | 2012
TI_2012-01-15_200435 | 2012-01-15 14:05 | 2012-01-15 14:05 | CST | 2012-01-15 20:05 | 485.1 | 59.9646 | 59.8836 | 59.8501 | -0.081076 | -0.11453 | -598.3242 | -423.5595 | Yes | Yes | 59.3 | 0.5501 | 2012
TI_2012-01-21_193355 | 2012-01-21 13:34 | 2012-01-21 13:34 | CST | 2012-01-21 19:34 | 583.8 | 59.9627 | 59.8147 | 59.7519 | -0.14805 | -0.21082 | -394.3379 | -276.9203 | Yes | Yes | 59.3 | 0.4519 | 2012
TI_2012-01-24_054900 | 2012-01-23 23:49 | 2012-01-23 23:49 | CST | 2012-01-24 05:49 | 503.9 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.3 | -59.3 | 2012
TI_2012-02-15_100304 | 2012-02-15 04:03 | 2012-02-15 04:03 | CST | 2012-02-15 10:03 | 439 | 60.0077 | 59.8983 | 59.9847 | -0.10943 | -0.023 | -401.1804 | -1908.6559 | No | Yes | 59.3 | 0.6847 | 2012
TI_2012-02-19_010037 | 2012-02-18 19:01 | 2012-02-18 19:01 | CST | 2012-02-19 01:01 |  | 59.969 | 59.924 | 59.8781 | -0.044932 | -0.090867 |  |  | No | No | 59.3 | 0.5781 | 2012
TI_2012-02-19_031658 | 2012-02-18 21:17 | 2012-02-18 21:17 | CST | 2012-02-19 03:17 | 725.4 | 59.9692 | 59.8171 | 59.7289 | -0.15211 | -0.24027 | -476.8785 | -301.9054 | Yes | Yes | 59.3 | 0.4289 | 2012
TI_2012-02-23_190837 | 2012-02-23 13:09 | 2012-02-23 13:09 | CST | 2012-02-23 19:09 |  | 59.9002 | 60.0055 | 60.0069 | 0.10531 | 0.10667 |  |  | No | No | 59.3 | 0.7069 | 2012
TI_2012-03-06_071057 | 2012-03-06 01:11 | 2012-03-06 01:11 | CST | 2012-03-06 07:11 | 878.5 | 59.9914 | 59.8927 | 59.8064 | -0.098685 | -0.18501 | -890.2058 | -474.8332 | Yes | Yes | 59.3 | 0.5064 | 2012
TI_2012-03-09_225210 | 2012-03-09 16:52 | 2012-03-09 16:52 | CST | 2012-03-09 22:52 | 824.9 | 60.0195 | 59.8376 | 59.7534 | -0.18191 | -0.26611 | -453.4677 | -309.9872 | Yes | Yes | 59.3 | 0.4534 | 2012
TI_2012-03-15_025249 | 2012-03-14 21:53 | 2012-03-14 21:53 | CDT | 2012-03-15 02:53 | 477 | 60.0157 | 59.9113 | 59.8509 | -0.10443 | -0.16481 | -456.7729 | -289.4172 | Yes | Yes | 59.3 | 0.5509 | 2012
TI_2012-03-19_215758 | 2012-03-19 16:58 | 2012-03-19 16:58 | CDT | 2012-03-19 21:58 | 422 | 60.0182 | 59.9101 | 59.9062 | -0.1081 | -0.11202 | -390.3682 | -376.7256 | No | No | 59.3 | 0.6062 | 2012
TI_2012-03-19_221505 | 2012-03-19 17:15 | 2012-03-19 17:15 | CDT | 2012-03-19 22:15 | 275 | 60.0109 | 59.9349 | 60.0036 | -0.075976 | -0.0072992 | -361.9559 | -3767.544 | No | No | 59.3 | 0.7036 | 2012
TI_2012-03-19_223155 | 2012-03-19 17:32 | 2012-03-19 17:32 | CDT | 2012-03-19 22:32 | 548 | 60.0291 | 59.898 | 59.87 | -0.13116 | -0.15914 | -417.7959 | -344.3408 | Yes | Yes | 59.3 | 0.57 | 2012
TI_2012-03-22_083638 | 2012-03-22 03:37 | 2012-03-22 03:37 | CDT | 2012-03-22 08:37 | 834.2 | 59.9977 | 59.8859 | 59.8139 | -0.11187 | -0.18383 | -745.6795 | -453.7852 | Yes | Yes | 59.3 | 0.5139 | 2012
TI_2012-03-30_195606 | 2012-03-30 14:56 | 2012-03-30 14:56 | CDT | 2012-03-30 19:56 | 855.3 | 60.0125 | 59.8694 | 59.846 | -0.14313 | -0.16649 | -597.5686 | -513.7155 | Yes | Yes | 59.3 | 0.546 | 2012
TI_2012-04-02_225433 | 2012-04-02 17:55 | 2012-04-02 17:55 | CDT | 2012-04-02 22:55 | 855.3 | 60.0067 | 59.8616 | 59.8421 | -0.14506 | -0.16458 | -589.605 | -519.6952 | Yes | Yes | 59.3 | 0.5421 | 2012
TI_2012-04-03_070747 | 2012-04-03 02:08 | 2012-04-03 02:08 | CDT | 2012-04-03 07:08 | 734.5 | 60.0146 | 59.898 | 59.874 | -0.11661 | -0.14064 | -629.8768 | -522.2668 | Yes | Yes | 59.3 | 0.574 | 2012
TI_2012-04-04_101620 | 2012-04-04 05:16 | 2012-04-04 05:16 | CDT | 2012-04-04 10:16 |  | 60.0304 | 59.955 | 59.9467 | -0.075387 | -0.083686 |  |  | No | No | 59.3 | 0.6467 | 2012
TI_2012-04-04_121727 | 2012-04-04 07:17 | 2012-04-04 07:17 | CDT | 2012-04-04 12:17 | 598 | 59.99 | 59.8504 | 59.8327 | -0.13968 | -0.15734 | -428.1202 | -380.0714 | Yes | Yes | 59.3 | 0.5327 | 2012
TI_2012-04-07_160238 | 2012-04-07 11:03 | 2012-04-07 11:03 | CDT | 2012-04-07 16:03 |  | 60.0146 | 59.9363 | 59.9265 | -0.078253 | -0.088058 |  |  | No | No | 59.3 | 0.6265 | 2012
TI_2012-04-18_131608 | 2012-04-18 08:16 | 2012-04-18 08:16 | CDT | 2012-04-18 13:16 |  | 59.997 | 59.9348 | 59.8897 | -0.06219 | -0.10725 |  |  | No | No | 59.3 | 0.5897 | 2012
TI_2012-04-19_210831 | 2012-04-19 16:09 | 2012-04-19 16:09 | CDT | 2012-04-19 21:09 |  | 59.9822 | 59.9145 | 59.8905 | -0.067749 | -0.091732 |  |  | No | No | 59.3 | 0.5905 | 2012
TI_2012-04-20_034114 | 2012-04-19 22:41 | 2012-04-19 22:41 | CDT | 2012-04-20 03:41 |  | 60.0215 | 59.9464 | 59.9296 | -0.075042 | -0.091888 |  |  | No | No | 59.3 | 0.6296 | 2012
TI_2012-04-23_011701 | 2012-04-22 20:17 | 2012-04-22 20:17 | CDT | 2012-04-23 01:17 |  | 60.0224 | 59.9456 | 59.9231 | -0.07679 | -0.099288 |  |  | No | No | 59.3 | 0.6231 | 2012
TI_2012-04-29_005635 | 2012-04-28 19:57 | 2012-04-28 19:57 | CDT | 2012-04-29 00:57 |  | 60.0017 | 59.9209 | 59.9065 | -0.080804 | -0.095229 |  |  | No | No | 59.3 | 0.6065 | 2012
TI_2012-05-07_224943 | 2012-05-07 17:50 | 2012-05-07 17:50 | CDT | 2012-05-07 22:50 | 515.7 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.3 | -59.3 | 2012
TI_2012-05-09_150715 | 2012-05-09 10:07 | 2012-05-09 10:07 | CDT | 2012-05-09 15:07 | 748 | 59.9797 | 59.8765 | 59.9879 | -0.10316 | 0.0082312 | -725.1111 | 9087.4157 | No | Yes | 59.3 | 0.6879 | 2012
TI_2012-05-23_104631 | 2012-05-23 05:47 | 2012-05-23 05:47 | CDT | 2012-05-23 10:47 |  | 60.0062 | 59.9364 | 59.9046 | -0.069776 | -0.1016 |  |  | No | No | 59.3 | 0.6046 | 2012
TI_2012-05-27_073230 | 2012-05-27 02:32 | 2012-05-27 02:32 | CDT | 2012-05-27 07:32 | 510 | 60.0215 | 59.9155 | 59.8748 | -0.10601 | -0.14672 | -481.0742 | -347.6072 | Yes | Yes | 59.3 | 0.5748 | 2012
TI_2012-06-01_185745 | 2012-06-01 13:58 | 2012-06-01 13:58 | CDT | 2012-06-01 18:58 |  | 60.0151 | 59.9212 | 59.9055 | -0.093888 | -0.10962 |  |  | No | No | 59.3 | 0.6055 | 2012
TI_2012-06-02_050900 | 2012-06-02 00:09 | 2012-06-02 00:09 | CDT | 2012-06-02 05:09 | 824 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.3 | -59.3 | 2012
TI_2012-06-02_182315 | 2012-06-02 13:23 | 2012-06-02 13:23 | CDT | 2012-06-02 18:23 | 688.5 | 59.9616 | 59.8337 | 59.7873 | -0.12796 | -0.17431 | -538.0651 | -394.979 | Yes | Yes | 59.3 | 0.4873 | 2012
TI_2012-06-08_164634 | 2012-06-08 11:47 | 2012-06-08 11:47 | CDT | 2012-06-08 16:47 | 565 | 60.0016 | 59.9055 | 59.8849 | -0.09614 | -0.11671 | -587.6854 | -484.116 | Yes | Yes | 59.3 | 0.5849 | 2012
TI_2012-06-09_062147 | 2012-06-09 01:22 | 2012-06-09 01:22 | CDT | 2012-06-09 06:22 | 450 | 60.0074 | 59.917 | 59.8922 | -0.09045 | -0.11524 | -497.5112 | -390.477 | Yes | Yes | 59.3 | 0.5922 | 2012
TI_2012-06-11_185722 | 2012-06-11 13:57 | 2012-06-11 13:57 | CDT | 2012-06-11 18:57 | 706.6 | 60.0001 | 59.8988 | 59.8815 | -0.10124 | -0.11856 | -697.9593 | -596.0051 | Yes | Yes | 59.3 | 0.5815 | 2012
TI_2012-06-12_080903 | 2012-06-12 03:09 | 2012-06-12 03:09 | CDT | 2012-06-12 08:09 |  | 59.9999 | 59.9241 | 59.9046 | -0.075757 | -0.095289 |  |  | No | No | 59.3 | 0.6046 | 2012
TI_2012-06-16_062113 | 2012-06-16 01:21 | 2012-06-16 01:21 | CDT | 2012-06-16 06:21 |  | 59.9886 | 60.0173 | 59.889 | 0.028687 | -0.099637 |  |  | No | No | 59.3 | 0.589 | 2012
TI_2012-06-20_050916 | 2012-06-20 00:09 | 2012-06-20 00:09 | CDT | 2012-06-20 05:09 | 837.3 | 59.9852 | 59.8769 | 59.8008 | -0.10825 | -0.1844 | -773.4788 | -454.0682 | Yes | Yes | 59.3 | 0.5008 | 2012
TI_2012-06-27_075732 | 2012-06-27 02:58 | 2012-06-27 02:58 | CDT | 2012-06-27 07:58 | 560.6 | 60.012 | 59.9263 | 59.8994 | -0.085693 | -0.11255 | -654.1969 | -498.0833 | Yes | Yes | 59.3 | 0.5994 | 2012
TI_2012-07-07_124751 | 2012-07-07 07:48 | 2012-07-07 07:48 | CDT | 2012-07-07 12:48 | 673.3 | 59.9501 | 59.8791 | 59.8291 | -0.070981 | -0.12096 | -948.5633 | -556.6237 | Yes | Yes | 59.3 | 0.5291 | 2012
TI_2012-07-09_015715 | 2012-07-08 20:57 | 2012-07-08 20:57 | CDT | 2012-07-09 01:57 | 750.2 | 59.9731 | 59.8496 | 59.7971 | -0.12355 | -0.17601 | -607.1947 | -426.2353 | Yes | Yes | 59.3 | 0.4971 | 2012
TI_2012-07-11_014612 | 2012-07-10 20:46 | 2012-07-10 20:46 | CDT | 2012-07-11 01:46 | 1122 | 60.0085 | 59.7891 | 59.7383 | -0.21938 | -0.27022 | -511.4498 | -415.2106 | No | No | 59.3 | 0.4383 | 2012
TI_2012-07-11_134545 | 2012-07-11 08:46 | 2012-07-11 08:46 | CDT | 2012-07-11 13:46 |  | 59.987 | 59.9295 | 59.9009 | -0.057549 | -0.086123 |  |  | No | No | 59.3 | 0.6009 | 2012
TI_2012-07-13_212743 | 2012-07-13 16:28 | 2012-07-13 16:28 | CDT | 2012-07-13 21:28 |  | 59.9908 | 59.9305 | 59.8991 | -0.060258 | -0.091686 |  |  | No | No | 59.3 | 0.5991 | 2012
TI_2012-07-17_000312 | 2012-07-16 19:03 | 2012-07-16 19:03 | CDT | 2012-07-17 00:03 | 599 | 60.0149 | 59.8807 | 59.8787 | -0.13418 | -0.13622 | -446.4269 | -439.7138 | Yes | Yes | 59.3 | 0.5787 | 2012
TI_2012-07-22_212714 | 2012-07-22 16:27 | 2012-07-22 16:27 | CDT | 2012-07-22 21:27 |  | 60.0013 | 59.9211 | 59.9125 | -0.08017 | -0.08882 |  |  | No | No | 59.3 | 0.6125 | 2012
TI_2012-07-23_194118 | 2012-07-23 14:41 | 2012-07-23 14:41 | CDT | 2012-07-23 19:41 | 520.6 | 60.0117 | 59.8937 | 59.889 | -0.11799 | -0.12271 | -441.2082 | -424.2433 | Yes | Yes | 59.3 | 0.589 | 2012
TI_2012-07-30_065227 | 2012-07-30 01:52 | 2012-07-30 01:52 | CDT | 2012-07-30 06:52 |  | 60.0009 | 60.0234 | 59.9876 | 0.022476 | -0.013283 |  |  | No | No | 59.3 | 0.6876 | 2012
TI_2012-07-30_205044 | 2012-07-30 15:51 | 2012-07-30 15:51 | CDT | 2012-07-30 20:51 | 553.3 | 59.9897 | 59.8253 | 59.8207 | -0.16435 | -0.16899 | -336.6519 | -327.4239 | Yes | Yes | 59.3 | 0.5207 | 2012
TI_2012-07-30_210324 | 2012-07-30 16:03 | 2012-07-30 16:03 | CDT | 2012-07-30 21:03 | 1306.6 | 59.994 | 59.7534 | 59.7571 | -0.24059 | -0.23688 | -543.0802 | -551.596 | Yes | Yes | 59.3 | 0.4571 | 2012
TI_2012-08-01_162428 | 2012-08-01 11:24 | 2012-08-01 11:24 | CDT | 2012-08-01 16:24 | 773.9 | 59.9945 | 59.8605 | 59.8315 | -0.13392 | -0.16296 | -577.8813 | -474.9156 | Yes | Yes | 59.3 | 0.5315 | 2012
TI_2012-08-08_012955 | 2012-08-07 20:30 | 2012-08-07 20:30 | CDT | 2012-08-08 01:30 | 733.6 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.3 | -59.3 | 2012
TI_2012-08-18_033100 | 2012-08-17 22:31 | 2012-08-17 22:31 | CDT | 2012-08-18 03:31 | 542 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.3 | -59.3 | 2012
TI_2012-08-19_013000 | 2012-08-18 20:30 | 2012-08-18 20:30 | CDT | 2012-08-19 01:30 | 480 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.3 | -59.3 | 2012
TI_2012-08-19_035400 | 2012-08-18 22:54 | 2012-08-18 22:54 | CDT | 2012-08-19 03:54 | 545 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.3 | -59.3 | 2012
TI_2012-08-24_203023 | 2012-08-24 15:30 | 2012-08-24 15:30 | CDT | 2012-08-24 20:30 | 805.3 | 60.0216 | 59.8292 | 59.8095 | -0.19248 | -0.21214 | -418.3746 | -379.6038 | Yes | Yes | 59.3 | 0.5095 | 2012
TI_2012-08-24_210200 | 2012-08-24 16:02 | 2012-08-24 16:02 | CDT | 2012-08-24 21:02 | 507 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.3 | -59.3 | 2012
TI_2012-09-04_162755 | 2012-09-04 11:28 | 2012-09-04 11:28 | CDT | 2012-09-04 16:28 | 672.8 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.3 | -59.3 | 2012
TI_2012-09-14_063123 | 2012-09-14 01:31 | 2012-09-14 01:31 | CDT | 2012-09-14 06:31 | 782 | 60.0259 | 59.873 | 59.8303 | -0.15288 | -0.19558 | -511.5182 | -399.8325 | Yes | Yes | 59.3 | 0.5303 | 2012
TI_2012-09-17_152908 | 2012-09-17 10:29 | 2012-09-17 10:29 | CDT | 2012-09-17 15:29 | 786.7 | 59.973 | 59.8859 | 59.8117 | -0.087024 | -0.16127 | -904.0083 | -487.815 | Yes | Yes | 59.3 | 0.5117 | 2012
TI_2012-09-21_232100 | 2012-09-21 18:21 | 2012-09-21 18:21 | CDT | 2012-09-21 23:21 | 514.2 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.3 | -59.3 | 2012
TI_2012-09-24_002554 | 2012-09-23 19:26 | 2012-09-23 19:26 | CDT | 2012-09-24 00:26 | 523.5 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.3 | -59.3 | 2012
TI_2012-09-27_164333 | 2012-09-27 11:44 | 2012-09-27 11:44 | CDT | 2012-09-27 16:44 | 475.9 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.3 | -59.3 | 2012
TI_2012-10-03_202925 | 2012-10-03 15:29 | 2012-10-03 15:29 | CDT | 2012-10-03 20:29 | 464 | 59.9867 | 59.917 | 59.8836 | -0.069648 | -0.10307 | -666.2108 | -450.1773 | No | No | 59.3 | 0.5836 | 2012
TI_2012-10-05_214135 | 2012-10-05 16:42 | 2012-10-05 16:42 | CDT | 2012-10-05 21:42 | 577.5 | 60.0157 | 59.8898 | 59.8667 | -0.1259 | -0.149 | -458.6843 | -387.5804 | Yes | Yes | 59.3 | 0.5667 | 2012
TI_2012-10-13_002202 | 2012-10-12 19:22 | 2012-10-12 19:22 | CDT | 2012-10-13 00:22 | 842.6 | 59.986 | 59.8295 | 59.7336 | -0.15649 | -0.25236 | -538.4285 | -333.894 | Yes | Yes | 59.3 | 0.4336 | 2012
TI_2012-10-13_072804 | 2012-10-13 02:28 | 2012-10-13 02:28 | CDT | 2012-10-13 07:28 | 588.3 | 59.9966 | 59.9086 | 59.8413 | -0.08799 | -0.15527 | -668.6019 | -378.8794 | Yes | Yes | 59.3 | 0.5413 | 2012
TI_2012-10-14_085630 | 2012-10-14 03:56 | 2012-10-14 03:56 | CDT | 2012-10-14 08:56 | 460 | 59.9942 | 59.913 | 59.8724 | -0.081189 | -0.12184 | -566.5813 | -377.548 | Yes | Yes | 59.3 | 0.5724 | 2012
TI_2012-10-19_175458 | 2012-10-19 12:55 | 2012-10-19 12:55 | CDT | 2012-10-19 17:55 | 680 | 59.9454 | 59.9331 | 59.8838 | -0.012327 | -0.061581 | -5516.3854 | -1104.2386 | No | No | 59.3 | 0.5838 | 2012
TI_2012-10-25_201624 | 2012-10-25 15:16 | 2012-10-25 15:16 | CDT | 2012-10-25 20:16 | 859 | 59.9722 | 59.9387 | 59.8982 | -0.033535 | -0.074043 | -2561.5032 | -1160.1361 | No | No | 59.3 | 0.5982 | 2012
TI_2012-11-02_064129 | 2012-11-02 01:41 | 2012-11-02 01:41 | CDT | 2012-11-02 06:41 | 1178 | 60.0057 | 59.9675 | 59.7027 | -0.038214 | -0.30297 | -3082.6378 | -388.8208 | No | No | 59.3 | 0.4027 | 2012
TI_2012-11-09_110948 | 2012-11-09 05:10 | 2012-11-09 05:10 | CST | 2012-11-09 11:10 |  | 59.8889 | 59.893 | 59.8779 | 0.0041581 | -0.010957 |  |  | No | No | 59.3 | 0.5779 | 2012
TI_2012-11-11_164936 | 2012-11-11 10:50 | 2012-11-11 10:50 | CST | 2012-11-11 16:50 | 412 | 59.9863 | 59.9118 | 59.8575 | -0.074555 | -0.12881 | -552.6135 | -319.8553 | No | No | 59.3 | 0.5575 | 2012
TI_2012-11-17_162307 | 2012-11-17 10:23 | 2012-11-17 10:23 | CST | 2012-11-17 16:23 | 1231 | 59.923 | 59.8318 | 59.7211 | -0.091123 | -0.20186 | -1350.9178 | -609.8388 | No | No | 59.3 | 0.4211 | 2012
TI_2012-11-17_183341 | 2012-11-17 12:34 | 2012-11-17 12:34 | CST | 2012-11-17 18:34 | 582 | 59.9759 | 59.8689 | 59.8881 | -0.10697 | -0.0878 | -544.0806 | -662.8718 | No | No | 59.3 | 0.5881 | 2012
TI_2012-11-22_175337 | 2012-11-22 11:54 | 2012-11-22 11:54 | CST | 2012-11-22 17:54 | 822 | 60.0048 | 59.875 | 59.7682 | -0.12978 | -0.23658 | -633.3882 | -347.4492 | Yes | Yes | 59.3 | 0.4682 | 2012
TI_2012-11-24_110103 | 2012-11-24 05:01 | 2012-11-24 05:01 | CST | 2012-11-24 11:01 | 462 | 59.9705 | 59.8876 | 59.8325 | -0.082867 | -0.13798 | -557.5222 | -334.8283 | Yes | Yes | 59.3 | 0.5325 | 2012
TI_2012-11-26_220505 | 2012-11-26 16:05 | 2012-11-26 16:05 | CST | 2012-11-26 22:05 | 693 | 60.004 | 59.8938 | 59.8203 | -0.11018 | -0.18367 | -628.9658 | -377.3119 | Yes | Yes | 59.3 | 0.5203 | 2012
TI_2012-11-28_182918 | 2012-11-28 12:29 | 2012-11-28 12:29 | CST | 2012-11-28 18:29 | 814 | 59.9999 | 59.8845 | 59.7928 | -0.11539 | -0.20712 | -705.4051 | -393.0122 | Yes | Yes | 59.3 | 0.4928 | 2012
TI_2012-12-10_183240 | 2012-12-10 12:33 | 2012-12-10 12:33 | CST | 2012-12-10 18:33 | 790.9 | 59.9762 | 59.9017 | 59.8239 | -0.074509 | -0.1523 | -1061.4885 | -519.3207 | Yes | Yes | 59.3 | 0.5239 | 2013
TI_2012-12-12_133056 | 2012-12-12 07:31 | 2012-12-12 07:31 | CST | 2012-12-12 13:31 | 641.6 | 59.9907 | 59.8988 | 59.8552 | -0.091928 | -0.13552 | -697.9342 | -473.444 | Yes | Yes | 59.3 | 0.5552 | 2013
TI_2012-12-13_191701 | 2012-12-13 13:17 | 2012-12-13 13:17 | CST | 2012-12-13 19:17 |  | 59.9646 | 59.9116 | 59.8608 | -0.052992 | -0.10382 |  |  | No | No | 59.3 | 0.5608 | 2013
TI_2012-12-14_121243 | 2012-12-14 06:13 | 2012-12-14 06:13 | CST | 2012-12-14 12:13 |  | 60.0247 | 59.9505 | 59.925 | -0.07412 | -0.099663 |  |  | No | No | 59.3 | 0.625 | 2013
TI_2012-12-14_221255 | 2012-12-14 16:13 | 2012-12-14 16:13 | CST | 2012-12-14 22:13 | 463 | 59.9632 | 59.9061 | 59.8404 | -0.057083 | -0.12275 | -811.0961 | -377.1915 | No | No | 59.3 | 0.5404 | 2013
TI_2012-12-25_103006 | 2012-12-25 04:30 | 2012-12-25 04:30 | CST | 2012-12-25 10:30 | 912.6 | 60.0122 | 59.8825 | 59.7656 | -0.1297 | -0.24664 | -703.6328 | -370.0137 | Yes | Yes | 59.3 | 0.4656 | 2013
TI_2012-12-29_001212 | 2012-12-28 18:12 | 2012-12-28 18:12 | CST | 2012-12-29 00:12 |  | 59.9987 | 59.9263 | 59.8967 | -0.072407 | -0.10205 |  |  | No | No | 59.3 | 0.5967 | 2013
TI_2012-12-29_222200 | 2012-12-29 16:22 | 2012-12-29 16:22 | CST | 2012-12-29 22:22 | 630 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.3 | -59.3 | 2013
TI_2013-01-02_204113 | 2013-01-02 14:41 | 2013-01-02 14:41 | CST | 2013-01-02 20:41 | 827.4 | 60.0083 | 59.8774 | 59.7916 | -0.13083 | -0.21668 | -632.4141 | -381.8613 | Yes | Yes | 59.3 | 0.4916 | 2013
TI_2013-01-04_154130 | 2013-01-04 09:42 | 2013-01-04 09:42 | CST | 2013-01-04 15:42 | 1370 | 59.9778 | 59.9242 | 59.7031 | -0.053668 | -0.27472 | -2552.755 | -498.6888 | No | No | 59.3 | 0.4031 | 2013
TI_2013-01-07_034855 | 2013-01-06 21:49 | 2013-01-06 21:49 | CST | 2013-01-07 03:49 | 527 | 59.9854 | 59.9247 | 59.8629 | -0.060648 | -0.12247 | -868.9492 | -430.3132 | No | No | 59.3 | 0.5629 | 2013
TI_2013-01-08_224013 | 2013-01-08 16:40 | 2013-01-08 16:40 | CST | 2013-01-08 22:40 | 1368 | 59.9702 | 59.9454 | 59.7016 | -0.024736 | -0.26858 | -5530.4996 | -509.3415 | No | No | 59.3 | 0.4016 | 2013
TI_2013-01-12_043654 | 2013-01-11 22:37 | 2013-01-11 22:37 | CST | 2013-01-12 04:37 | 460 | 59.9974 | 59.9071 | 59.8527 | -0.090327 | -0.14471 | -509.2585 | -317.8843 | No | No | 59.3 | 0.5527 | 2013
TI_2013-01-14_023452 | 2013-01-13 20:35 | 2013-01-13 20:35 | CST | 2013-01-14 02:35 | 810.1 | 59.9999 | 59.8912 | 59.8185 | -0.10866 | -0.18136 | -745.563 | -446.6912 | Yes | Yes | 59.3 | 0.5185 | 2013
TI_2013-01-15_160358 | 2013-01-15 10:04 | 2013-01-15 10:04 | CST | 2013-01-15 16:04 | 740 | 60.02 | 59.8623 | 59.8358 | -0.15769 | -0.18423 | -469.2607 | -401.6695 | Yes | Yes | 59.3 | 0.5358 | 2013
TI_2013-01-20_051003 | 2013-01-19 23:10 | 2013-01-19 23:10 | CST | 2013-01-20 05:10 | 714.6 | 59.9886 | 59.9049 | 59.8137 | -0.083666 | -0.17489 | -854.1111 | -408.6096 | Yes | Yes | 59.3 | 0.5137 | 2013
TI_2013-01-22_220610 | 2013-01-22 16:06 | 2013-01-22 16:06 | CST | 2013-01-22 22:06 | 857 | 59.9691 | 59.8967 | 59.7647 | -0.072425 | -0.20444 | -1183.2877 | -419.2029 | Yes | Yes | 59.3 | 0.4647 | 2013
TI_2013-01-25_032425 | 2013-01-24 21:24 | 2013-01-24 21:24 | CST | 2013-01-25 03:24 | 449 | 59.9572 | 59.9247 | 59.8781 | -0.032499 | -0.079049 | -1381.579 | -568.003 | No | No | 59.3 | 0.5781 | 2013
TI_2013-02-04_165141 | 2013-02-04 10:52 | 2013-02-04 10:52 | CST | 2013-02-04 16:52 |  | 59.9876 | 59.9434 | 59.9234 | -0.044168 | -0.064155 |  |  | No | No | 59.3 | 0.6234 | 2013
TI_2013-02-08_130859 | 2013-02-08 07:09 | 2013-02-08 07:09 | CST | 2013-02-08 13:09 |  | 60.0202 | 59.9473 | 59.9205 | -0.072935 | -0.099748 |  |  | No | No | 59.3 | 0.6205 | 2013
TI_2013-02-10_040139 | 2013-02-09 22:02 | 2013-02-09 22:02 | CST | 2013-02-10 04:02 |  | 60.0348 | 59.952 | 59.9373 | -0.082794 | -0.097517 |  |  | No | No | 59.3 | 0.6373 | 2013
TI_2013-02-11_194041 | 2013-02-11 13:41 | 2013-02-11 13:41 | CST | 2013-02-11 19:41 |  | 60.0253 | 59.9461 | 59.9239 | -0.079136 | -0.10137 |  |  | No | No | 59.3 | 0.6239 | 2013
TI_2013-02-16_235556 | 2013-02-16 17:56 | 2013-02-16 17:56 | CST | 2013-02-16 23:56 | 1202 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.3 | -59.3 | 2013
TI_2013-02-17_020325 | 2013-02-16 20:03 | 2013-02-16 20:03 | CST | 2013-02-17 02:03 |  | 59.9133 | 59.9148 | 59.896 | 0.0015108 | -0.017262 |  |  | No | No | 59.3 | 0.596 | 2013
TI_2013-02-24_122827 | 2013-02-24 06:28 | 2013-02-24 06:28 | CST | 2013-02-24 12:28 |  | 60.0231 | 59.9539 | 59.9351 | -0.069123 | -0.08795 |  |  | No | No | 59.3 | 0.6351 | 2013
TI_2013-03-05_034734 | 2013-03-04 21:48 | 2013-03-04 21:48 | CST | 2013-03-05 03:48 | 595 | 60.0222 | 59.8759 | 59.8213 | -0.14633 | -0.20094 | -406.6025 | -296.1035 | Yes | Yes | 59.3 | 0.5213 | 2013
TI_2013-03-06_060509 | 2013-03-06 00:05 | 2013-03-06 00:05 | CST | 2013-03-06 06:05 |  | 59.9225 | 59.8979 | 59.8878 | -0.024519 | -0.034664 |  |  | No | No | 59.3 | 0.5878 | 2013
TI_2013-03-07_230541 | 2013-03-07 17:06 | 2013-03-07 17:06 | CST | 2013-03-07 23:06 | 781.1 | 60.0024 | 59.9191 | 59.7829 | -0.08325 | -0.21946 | -938.2527 | -355.9175 | Yes | Yes | 59.3 | 0.4829 | 2013
TI_2013-03-10_050955 | 2013-03-09 23:10 | 2013-03-09 23:10 | CST | 2013-03-10 05:10 |  | 60.035 | 60.0176 | 59.9635 | -0.017459 | -0.071549 |  |  | No | No | 59.3 | 0.6635 | 2013
TI_2013-03-13_001921 | 2013-03-12 19:19 | 2013-03-12 19:19 | CDT | 2013-03-13 00:19 |  | 59.9983 | 59.9324 | 59.9004 | -0.065903 | -0.097883 |  |  | No | No | 59.3 | 0.6004 | 2013
TI_2013-03-15_233936 | 2013-03-15 18:40 | 2013-03-15 18:40 | CDT | 2013-03-15 23:40 | 528.9 | 59.9992 | 59.9149 | 59.8617 | -0.084318 | -0.13751 | -627.2675 | -384.6324 | Yes | Yes | 59.3 | 0.5617 | 2013
TI_2013-03-17_020241 | 2013-03-16 21:03 | 2013-03-16 21:03 | CDT | 2013-03-17 02:03 |  | 59.914 | 59.8884 | 59.9085 | -0.02564 | -0.005549 |  |  | No | No | 59.3 | 0.6085 | 2013
TI_2013-03-18_030403 | 2013-03-17 22:04 | 2013-03-17 22:04 | CDT | 2013-03-18 03:04 |  | 59.908 | 59.9091 | 59.8997 | 0.0011193 | -0.0082746 |  |  | No | No | 59.3 | 0.5997 | 2013
TI_2013-03-18_222108 | 2013-03-18 17:21 | 2013-03-18 17:21 | CDT | 2013-03-18 22:21 | 494.6 | 59.9791 | 59.8982 | 59.8576 | -0.080881 | -0.12149 | -611.5128 | -407.1253 | Yes | Yes | 59.3 | 0.5576 | 2013
TI_2013-04-03_022519 | 2013-04-02 21:25 | 2013-04-02 21:25 | CDT | 2013-04-03 02:25 | 758.2 | 60.012 | 59.9152 | 59.8353 | -0.096867 | -0.17672 | -782.7238 | -429.0301 | Yes | Yes | 59.3 | 0.5353 | 2013
TI_2013-04-09_105845 | 2013-04-09 05:59 | 2013-04-09 05:59 | CDT | 2013-04-09 10:59 |  | 60.0857 | 60.0842 | 60.1003 | -0.0014458 | 0.014606 |  |  | No | No | 59.3 | 0.8003 | 2013
TI_2013-04-09_232125 | 2013-04-09 18:21 | 2013-04-09 18:21 | CDT | 2013-04-09 23:21 | 758.5 | 59.978 | 59.9049 | 59.7826 | -0.073101 | -0.19542 | -1037.6068 | -388.1412 | Yes | Yes | 59.3 | 0.4826 | 2013
TI_2013-04-15_041955 | 2013-04-14 23:20 | 2013-04-14 23:20 | CDT | 2013-04-15 04:20 |  | 60.0185 | 59.9422 | 59.9305 | -0.076321 | -0.088012 |  |  | No | No | 59.3 | 0.6305 | 2013
TI_2013-04-23_161914 | 2013-04-23 11:19 | 2013-04-23 11:19 | CDT | 2013-04-23 16:19 | 469.1 | 59.9721 | 59.9079 | 59.8659 | -0.064154 | -0.10618 | -731.2075 | -441.8091 | Yes | Yes | 59.3 | 0.5659 | 2013
TI_2013-04-24_135919 | 2013-04-24 08:59 | 2013-04-24 08:59 | CDT | 2013-04-24 13:59 |  | 59.9575 | 59.897 | 59.8396 | -0.060481 | -0.11788 |  |  | No | No | 59.3 | 0.5396 | 2013
TI_2013-04-25_163727 | 2013-04-25 11:37 | 2013-04-25 11:37 | CDT | 2013-04-25 16:37 |  | 59.938 | 59.8685 | 59.8862 | -0.069476 | -0.051812 |  |  | No | No | 59.3 | 0.5862 | 2013
TI_2013-04-26_184404 | 2013-04-26 13:44 | 2013-04-26 13:44 | CDT | 2013-04-26 18:44 |  | 60.0144 | 59.9377 | 59.9211 | -0.076663 | -0.093299 |  |  | No | No | 59.3 | 0.6211 | 2013
TI_2013-04-27_043437 | 2013-04-26 23:35 | 2013-04-26 23:35 | CDT | 2013-04-27 04:35 |  | 59.9074 | 59.8908 | 59.8959 | -0.01653 | -0.011474 |  |  | No | No | 59.3 | 0.5959 | 2013
TI_2013-04-27_075942 | 2013-04-27 03:00 | 2013-04-27 03:00 | CDT | 2013-04-27 08:00 |  | 60.0117 | 59.9468 | 59.9225 | -0.064904 | -0.089237 |  |  | No | No | 59.3 | 0.6225 | 2013
TI_2013-04-29_053416 | 2013-04-29 00:34 | 2013-04-29 00:34 | CDT | 2013-04-29 05:34 |  | 59.9816 | 59.9006 | 59.8834 | -0.081021 | -0.0982 |  |  | No | No | 59.3 | 0.5834 | 2013
TI_2013-04-29_185859 | 2013-04-29 13:59 | 2013-04-29 13:59 | CDT | 2013-04-29 18:59 | 522.1 | 59.9895 | 59.8643 | 59.8423 | -0.12522 | -0.14719 | -416.9543 | -354.7194 | Yes | Yes | 59.3 | 0.5423 | 2013
TI_2013-05-03_095755 | 2013-05-03 04:58 | 2013-05-03 04:58 | CDT | 2013-05-03 09:58 |  | 60.0881 | 60.1051 | 60.1052 | 0.016993 | 0.017071 |  |  | No | No | 59.3 | 0.8052 | 2013
TI_2013-05-03_100126 | 2013-05-03 05:01 | 2013-05-03 05:01 | CDT | 2013-05-03 10:01 |  | 60.0872 | 60.0911 | 60.1076 | 0.0039365 | 0.020407 |  |  | No | No | 59.3 | 0.8076 | 2013
TI_2013-05-07_080712 | 2013-05-07 03:07 | 2013-05-07 03:07 | CDT | 2013-05-07 08:07 | 504.8 | 60.0174 | 59.8997 | 59.8505 | -0.11771 | -0.16691 | -428.8531 | -302.442 | Yes | Yes | 59.3 | 0.5505 | 2013
TI_2013-05-12_011336 | 2013-05-11 20:14 | 2013-05-11 20:14 | CDT | 2013-05-12 01:14 | 392 | 59.9938 | 59.9071 | 59.8623 | -0.08674 | -0.13151 | -451.9279 | -298.0729 | No | Yes | 59.3 | 0.5623 | 2013
TI_2013-05-17_183807 | 2013-05-17 13:38 | 2013-05-17 13:38 | CDT | 2013-05-17 18:38 | 473.1 | 59.9773 | 59.9251 | 59.8748 | -0.052186 | -0.10253 | -906.5621 | -461.427 | Yes | Yes | 59.3 | 0.5748 | 2013
TI_2013-05-22_211116 | 2013-05-22 16:11 | 2013-05-22 16:11 | CDT | 2013-05-22 21:11 | 846 | 59.9525 | 59.8016 | 59.7385 | -0.15091 | -0.21403 | -560.6002 | -395.2672 | Yes | Yes | 59.3 | 0.4385 | 2013
TI_2013-05-30_044719 | 2013-05-29 23:47 | 2013-05-29 23:47 | CDT | 2013-05-30 04:47 | 716.3 | 59.9922 | 59.8841 | 59.8246 | -0.10811 | -0.16759 | -662.5743 | -427.4197 | Yes | Yes | 59.3 | 0.5246 | 2013
TI_2013-05-30_194605 | 2013-05-30 14:46 | 2013-05-30 14:46 | CDT | 2013-05-30 19:46 | 784.2 | 60.0058 | 59.8816 | 59.8536 | -0.12423 | -0.15219 | -631.2313 | -515.2827 | Yes | Yes | 59.3 | 0.5536 | 2013
TI_2013-06-04_230400 | 2013-06-04 18:04 | 2013-06-04 18:04 | CDT | 2013-06-04 23:04 | 606.4 | 60.035 | 59.9427 | 59.9149 | -0.09229 | -0.12006 | -657.0599 | -505.0779 | Yes | Yes | 59.3 | 0.6149 | 2013
TI_2013-06-06_101256 | 2013-06-06 05:13 | 2013-06-06 05:13 | CDT | 2013-06-06 10:13 |  | 59.9722 | 59.9372 | 59.8941 | -0.034972 | -0.078068 |  |  | No | No | 59.3 | 0.5941 | 2013
TI_2013-06-07_165250 | 2013-06-07 11:53 | 2013-06-07 11:53 | CDT | 2013-06-07 16:53 |  | 59.9072 | 59.903 | 59.8946 | -0.0041656 | -0.012557 |  |  | No | No | 59.3 | 0.5946 | 2013
TI_2013-06-11_155623 | 2013-06-11 10:56 | 2013-06-11 10:56 | CDT | 2013-06-11 15:56 | 910 | 60.0166 | 59.8746 | 59.823 | -0.14203 | -0.1936 | -640.7101 | -470.0467 | Yes | Yes | 59.3 | 0.523 | 2013
TI_2013-06-13_004508 | 2013-06-12 19:45 | 2013-06-12 19:45 | CDT | 2013-06-13 00:45 | 825.4 | 60.0047 | 59.877 | 59.8292 | -0.12778 | -0.17553 | -645.955 | -470.2312 | Yes | Yes | 59.3 | 0.5292 | 2013
TI_2013-06-27_040943 | 2013-06-26 23:10 | 2013-06-26 23:10 | CDT | 2013-06-27 04:10 | 804.4 | 60.0262 | 59.9094 | 59.8632 | -0.11679 | -0.16302 | -688.7305 | -493.4439 | Yes | Yes | 59.3 | 0.5632 | 2013
TI_2013-07-08_195009 | 2013-07-08 14:50 | 2013-07-08 14:50 | CDT | 2013-07-08 19:50 |  | 59.9378 | 59.9029 | 59.8813 | -0.034928 | -0.05651 |  |  | No | No | 59.3 | 0.5813 | 2013
TI_2013-07-14_050425 | 2013-07-14 00:04 | 2013-07-14 00:04 | CDT | 2013-07-14 05:04 |  | 59.9135 | 59.8934 | 59.8983 | -0.020102 | -0.015175 |  |  | No | No | 59.3 | 0.5983 | 2013
TI_2013-07-18_085452 | 2013-07-18 03:55 | 2013-07-18 03:55 | CDT | 2013-07-18 08:55 |  | 59.9685 | 59.9372 | 59.8961 | -0.031292 | -0.072351 |  |  | No | No | 59.3 | 0.5961 | 2013
TI_2013-07-21_230023 | 2013-07-21 18:00 | 2013-07-21 18:00 | CDT | 2013-07-21 23:00 | 599.2 | 60.022 | 59.9046 | 59.8809 | -0.11741 | -0.14114 | -510.3349 | -424.5373 | Yes | Yes | 59.3 | 0.5809 | 2013
TI_2013-07-25_061525 | 2013-07-25 01:15 | 2013-07-25 01:15 | CDT | 2013-07-25 06:15 | 827.3 | 59.9781 | 59.8944 | 59.8354 | -0.083696 | -0.14273 | -988.4624 | -579.6181 | Yes | Yes | 59.3 | 0.5354 | 2013
TI_2013-08-02_203441 | 2013-08-02 15:35 | 2013-08-02 15:35 | CDT | 2013-08-02 20:35 | 916.6 | 59.9815 | 59.8596 | 59.8319 | -0.12185 | -0.14956 | -752.2332 | -612.8606 | Yes | Yes | 59.3 | 0.5319 | 2013
TI_2013-08-11_104312 | 2013-08-11 05:43 | 2013-08-11 05:43 | CDT | 2013-08-11 10:43 | 827.5 | 60.0078 | 59.9065 | 59.8557 | -0.10128 | -0.15212 | -817.0245 | -543.9866 | Yes | Yes | 59.3 | 0.5557 | 2013
TI_2013-08-12_075740 | 2013-08-12 02:58 | 2013-08-12 02:58 | CDT | 2013-08-12 07:58 | 783.3 | 59.9722 | 59.8981 | 59.826 | -0.074096 | -0.14618 | -1057.1399 | -535.843 | Yes | Yes | 59.3 | 0.526 | 2013
TI_2013-08-16_210233 | 2013-08-16 16:03 | 2013-08-16 16:03 | CDT | 2013-08-16 21:03 |  | 60.0022 | 59.9275 | 59.9103 | -0.074708 | -0.091874 |  |  | No | No | 59.3 | 0.6103 | 2013
TI_2013-08-16_213350 | 2013-08-16 16:34 | 2013-08-16 16:34 | CDT | 2013-08-16 21:34 |  | 59.9621 | 59.9182 | 59.8991 | -0.043928 | -0.063048 |  |  | No | No | 59.3 | 0.5991 | 2013
TI_2013-08-18_214510 | 2013-08-18 16:45 | 2013-08-18 16:45 | CDT | 2013-08-18 21:45 | 605.8 | 60.002 | 59.8951 | 59.8667 | -0.10688 | -0.13528 | -566.7837 | -447.806 | Yes | Yes | 59.3 | 0.5667 | 2013
TI_2013-08-20_191845 | 2013-08-20 14:19 | 2013-08-20 14:19 | CDT | 2013-08-20 19:19 | 601.4 | 60.0065 | 59.9233 | 59.8941 | -0.083152 | -0.11239 | -723.2578 | -535.0838 | Yes | Yes | 59.3 | 0.5941 | 2013
TI_2013-08-24_064708 | 2013-08-24 01:47 | 2013-08-24 01:47 | CDT | 2013-08-24 06:47 |  | 60.0101 | 59.9527 | 59.9219 | -0.057354 | -0.088186 |  |  | No | No | 59.3 | 0.6219 | 2013
TI_2013-08-24_234544 | 2013-08-24 18:46 | 2013-08-24 18:46 | CDT | 2013-08-24 23:46 | 563.1 | 59.9688 | 59.8871 | 59.8486 | -0.081664 | -0.12018 | -689.5365 | -468.5364 | Yes | Yes | 59.3 | 0.5486 | 2013
TI_2013-08-25_115656 | 2013-08-25 06:57 | 2013-08-25 06:57 | CDT | 2013-08-25 11:57 |  | 60.0194 | 59.9541 | 59.9267 | -0.065229 | -0.092668 |  |  | No | No | 59.3 | 0.6267 | 2013
TI_2013-08-29_235458 | 2013-08-29 18:55 | 2013-08-29 18:55 | CDT | 2013-08-29 23:55 | 804.4 | 59.9713 | 59.9119 | 59.8801 | -0.059413 | -0.091249 | -1353.9062 | -881.5394 | Yes | Yes | 59.3 | 0.5801 | 2013
TI_2013-09-03_202441 | 2013-09-03 15:25 | 2013-09-03 15:25 | CDT | 2013-09-03 20:25 |  | 59.9818 | 59.8885 | 59.8827 | -0.093294 | -0.099092 |  |  | No | No | 59.3 | 0.5827 | 2013
TI_2013-09-20_192923 | 2013-09-20 14:29 | 2013-09-20 14:29 | CDT | 2013-09-20 19:29 | 780 | 59.9734 | 59.892 | 59.8487 | -0.081471 | -0.12474 | -957.394 | -625.3203 | No | No | 59.3 | 0.5487 | 2013
TI_2013-09-25_141702 | 2013-09-25 09:17 | 2013-09-25 09:17 | CDT | 2013-09-25 14:17 | 717.8 | 60.0168 | 59.9152 | 59.8665 | -0.10164 | -0.15032 | -706.2172 | -477.5023 | Yes | Yes | 59.3 | 0.5665 | 2013
TI_2013-10-08_165540 | 2013-10-08 11:56 | 2013-10-08 11:56 | CDT | 2013-10-08 16:56 | 460.8 | 60.0165 | 59.9463 | 59.9144 | -0.070182 | -0.10208 | -656.5769 | -451.3944 | Yes | Yes | 59.3 | 0.6144 | 2013
TI_2013-10-13_015357 | 2013-10-12 20:54 | 2013-10-12 20:54 | CDT | 2013-10-13 01:54 | 547.9 | 59.9529 | 59.8883 | 59.8377 | -0.064613 | -0.11522 | -847.9701 | -475.5268 | Yes | Yes | 59.3 | 0.5377 | 2013
TI_2013-10-18_051053 | 2013-10-18 00:11 | 2013-10-18 00:11 | CDT | 2013-10-18 05:11 |  | 59.9688 | 59.9282 | 59.8683 | -0.040605 | -0.10048 |  |  | No | No | 59.3 | 0.5683 | 2013
TI_2013-10-30_125905 | 2013-10-30 07:59 | 2013-10-30 07:59 | CDT | 2013-10-30 12:59 |  | 60.0194 | 59.9344 | 59.906 | -0.085046 | -0.11342 |  |  | No | No | 59.3 | 0.606 | 2013
TI_2013-10-31_120903 | 2013-10-31 07:09 | 2013-10-31 07:09 | CDT | 2013-10-31 12:09 | 440 | 59.991 | 59.8749 | 59.8627 | -0.11618 | -0.12833 | -378.7156 | -342.8527 | No | No | 59.3 | 0.5627 | 2013
TI_2013-11-02_024704 | 2013-11-01 21:47 | 2013-11-01 21:47 | CDT | 2013-11-02 02:47 | 1286.6 | 60.0181 | 59.913 | 59.7322 | -0.10514 | -0.28591 | -1223.6708 | -449.9989 | Yes | Yes | 59.3 | 0.4322 | 2013
TI_2013-11-09_180137 | 2013-11-09 12:02 | 2013-11-09 12:02 | CST | 2013-11-09 18:02 |  | 60.0006 | 59.9376 | 59.9077 | -0.063059 | -0.092944 |  |  | No | No | 59.3 | 0.6077 | 2013
TI_2013-11-10_180133 | 2013-11-10 12:02 | 2013-11-10 12:02 | CST | 2013-11-10 18:02 |  | 59.9984 | 59.9397 | 59.9068 | -0.058705 | -0.091557 |  |  | No | No | 59.3 | 0.6068 | 2013
TI_2013-11-12_223338 | 2013-11-12 16:34 | 2013-11-12 16:34 | CST | 2013-11-12 22:34 | 449.9 | 60.0068 | 59.9265 | 59.9042 | -0.080214 | -0.10255 | -560.8754 | -438.7188 | No | Yes | 59.3 | 0.6042 | 2013
TI_2013-11-14_083835 | 2013-11-14 02:39 | 2013-11-14 02:39 | CST | 2013-11-14 08:39 | 779 | 60.0019 | 59.8974 | 59.8048 | -0.1045 | -0.19715 | -745.4636 | -395.1392 | Yes | Yes | 59.3 | 0.5048 | 2013
TI_2013-11-14_170129 | 2013-11-14 11:01 | 2013-11-14 11:01 | CST | 2013-11-14 17:01 | 496 | 59.9664 | 59.9083 | 59.8633 | -0.058113 | -0.1031 | -853.5129 | -481.0838 | No | No | 59.3 | 0.5633 | 2013
TI_2013-11-20_172516 | 2013-11-20 11:25 | 2013-11-20 11:25 | CST | 2013-11-20 17:25 |  | 60.0247 | 59.9416 | 59.9271 | -0.083171 | -0.097624 |  |  | No | No | 59.3 | 0.6271 | 2013
TI_2013-11-22_222318 | 2013-11-22 16:23 | 2013-11-22 16:23 | CST | 2013-11-22 22:23 | 447 | 59.9905 | 59.9015 | 59.8804 | -0.088997 | -0.11009 | -502.2651 | -406.0454 | No | Yes | 59.3 | 0.5804 | 2013
TI_2013-11-23_215819 | 2013-11-23 15:58 | 2013-11-23 15:58 | CST | 2013-11-23 21:58 | 282 | 59.9624 | 59.9333 | 59.8981 | -0.029164 | -0.064323 | -966.9363 | -438.4111 | No | No | 59.3 | 0.5981 | 2013
TI_2013-11-26_200646 | 2013-11-26 14:07 | 2013-11-26 14:07 | CST | 2013-11-26 20:07 | 386 | 59.9998 | 59.9473 | 59.9078 | -0.052476 | -0.09202 | -735.5701 | -419.4739 | No | Yes | 59.3 | 0.6078 | 2013
TI_2013-11-27_121552 | 2013-11-27 06:16 | 2013-11-27 06:16 | CST | 2013-11-27 12:16 | 853.6 | 60.0134 | 59.8958 | 59.8588 | -0.1176 | -0.15459 | -725.8371 | -552.1553 | Yes | Yes | 59.3 | 0.5588 | 2013
TI_2013-11-29_172139 | 2013-11-29 11:22 | 2013-11-29 11:22 | CST | 2013-11-29 17:22 |  | 59.9998 | 59.936 | 59.9105 | -0.063826 | -0.089332 |  |  | No | No | 59.3 | 0.6105 | 2013
TI_2013-12-02_220328 | 2013-12-02 16:03 | 2013-12-02 16:03 | CST | 2013-12-02 22:03 | 842.2 | 59.9785 | 59.8666 | 59.7442 | -0.11186 | -0.23429 | -752.92 | -359.4652 | Yes | Yes | 59.3 | 0.4442 | 2014
TI_2013-12-04_135931 | 2013-12-04 08:00 | 2013-12-04 08:00 | CST | 2013-12-04 14:00 |  | 59.9789 | 60.0713 | 60.0985 | 0.092393 | 0.11957 |  |  | No | No | 59.3 | 0.7985 | 2014
TI_2013-12-08_190703 | 2013-12-08 13:07 | 2013-12-08 13:07 | CST | 2013-12-08 19:07 | 576.7 | 59.9959 | 59.9287 | 59.895 | -0.067241 | -0.10093 | -857.6639 | -571.3808 | Yes | Yes | 59.3 | 0.595 | 2014
TI_2013-12-09_144305 | 2013-12-09 08:43 | 2013-12-09 08:43 | CST | 2013-12-09 14:43 | 905.2 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.3 | -59.3 | 2014
TI_2013-12-14_013727 | 2013-12-13 19:37 | 2013-12-13 19:37 | CST | 2013-12-14 01:37 | 816 | 60.0188 | 59.8334 | 59.8297 | -0.1854 | -0.18908 | -440.129 | -431.5737 | No | No | 59.3 | 0.5297 | 2014
TI_2013-12-14_013803 | 2013-12-13 19:38 | 2013-12-13 19:38 | CST | 2013-12-14 01:38 | 549 | 59.8849 | 59.8582 | 59.7417 | -0.026752 | -0.14323 | -2052.1579 | -383.3112 | No | No | 59.3 | 0.4417 | 2014
TI_2013-12-17_174516 | 2013-12-17 11:45 | 2013-12-17 11:45 | CST | 2013-12-17 17:45 | 785.6 | 59.9805 | 59.8932 | 59.8254 | -0.087261 | -0.15509 | -900.2927 | -506.556 | Yes | Yes | 59.3 | 0.5254 | 2014
TI_2013-12-20_230911 | 2013-12-20 17:09 | 2013-12-20 17:09 | CST | 2013-12-20 23:09 |  | 60.0196 | 59.9458 | 59.9304 | -0.073834 | -0.089224 |  |  | No | No | 59.3 | 0.6304 | 2014
TI_2013-12-30_154356 | 2013-12-30 09:44 | 2013-12-30 09:44 | CST | 2013-12-30 15:44 | 784.5 | 59.9973 | 59.8884 | 59.832 | -0.10893 | -0.16532 | -720.1626 | -474.5228 | Yes | Yes | 59.3 | 0.532 | 2014
TI_2014-01-06_063004 | 2014-01-06 00:30 | 2014-01-06 00:30 | CST | 2014-01-06 06:30 | 468 | 59.98 | 59.9232 | 59.8999 | -0.056778 | -0.080128 | -824.2686 | -584.0676 | No | No | 59.3 | 0.5999 | 2014
TI_2014-01-06_124915 | 2014-01-06 06:49 | 2014-01-06 06:49 | CST | 2014-01-06 12:49 |  | 59.8422 | 59.8407 | 59.831 | -0.0015285 | -0.011237 |  |  | No | No | 59.3 | 0.531 | 2014
TI_2014-01-06_141020 | 2014-01-06 08:10 | 2014-01-06 08:10 | CST | 2014-01-06 14:10 | 880.8 | 60.0135 | 59.8806 | 59.8535 | -0.13296 | -0.16004 | -662.4322 | -550.3504 | Yes | Yes | 59.3 | 0.5535 | 2014
TI_2014-01-13_101900 | 2014-01-13 04:19 | 2014-01-13 04:19 | CST | 2014-01-13 10:19 | 834.6 | 0 | 0 | 0 | 0 | 0 |  |  | No | No | 59.3 | -59.3 | 2014
TI_2014-01-18_144032 | 2014-01-18 08:41 | 2014-01-18 08:41 | CST | 2014-01-18 14:41 | 1231 | 60.0063 | 59.981 | 59.7659 | -0.025227 | -0.24037 | -4879.7166 | -512.1281 | No | No | 59.3 | 0.4659 | 2014
TI_2014-01-25_180636 | 2014-01-25 12:07 | 2014-01-25 12:07 | CST | 2014-01-25 18:07 | 656.9 | 59.9742 | 59.8877 | 59.8189 | -0.086433 | -0.15527 | -760.0098 | -423.0575 | Yes | Yes | 59.3 | 0.5189 | 2014
TI_2014-01-26_021957 | 2014-01-25 20:20 | 2014-01-25 20:20 | CST | 2014-01-26 02:20 |  | 60.0179 | 59.9408 | 59.9162 | -0.077103 | -0.10173 |  |  | No | No | 59.3 | 0.6162 | 2014
TI_2014-01-30_232751 | 2014-01-30 17:28 | 2014-01-30 17:28 | CST | 2014-01-30 23:28 |  | 59.9656 | 59.9303 | 59.8928 | -0.035271 | -0.072769 |  |  | No | No | 59.3 | 0.5928 | 2014
TI_2014-02-18_133058 | 2014-02-18 07:31 | 2014-02-18 07:31 | CST | 2014-02-18 13:31 |  | 60.0026 | 59.9331 | 59.911 | -0.069442 | -0.091588 |  |  | No | No | 59.3 | 0.611 | 2014
TI_2014-02-21_030627 | 2014-02-20 21:06 | 2014-02-20 21:06 | CST | 2014-02-21 03:06 | 454.2 | 60.0049 | 59.8982 | 59.8671 | -0.1067 | -0.13783 | -425.6624 | -329.546 | Yes | Yes | 59.3 | 0.5671 | 2014
TI_2014-02-26_120226 | 2014-02-26 06:02 | 2014-02-26 06:02 | CST | 2014-02-26 12:02 |  | 60.0904 | 60.0923 | 60.1042 | 0.001882 | 0.013811 |  |  | No | No | 59.3 | 0.8042 | 2014
TI_2014-02-28_192531 | 2014-02-28 13:26 | 2014-02-28 13:26 | CST | 2014-02-28 19:26 | 515.5 | 60.0142 | 59.9147 | 59.8827 | -0.099471 | -0.13145 | -518.2398 | -392.1531 | Yes | Yes | 59.3 | 0.5827 | 2014
TI_2014-03-02_133714 | 2014-03-02 07:37 | 2014-03-02 07:37 | CST | 2014-03-02 13:37 | 542.2 | 60.0086 | 59.9046 | 59.8642 | -0.10397 | -0.14435 | -521.4742 | -375.6159 | Yes | Yes | 59.3 | 0.5642 | 2014
TI_2014-03-03_133123 | 2014-03-03 07:31 | 2014-03-03 07:31 | CST | 2014-03-03 13:31 | 540.9 | 59.9901 | 59.913 | 59.8966 | -0.077156 | -0.093526 | -701.0515 | -578.3396 | Yes | Yes | 59.3 | 0.5966 | 2014
TI_2014-03-10_135704 | 2014-03-10 08:57 | 2014-03-10 08:57 | CDT | 2014-03-10 13:57 | 958 | 59.9816 | 59.9047 | 59.8937 | -0.076918 | -0.087913 | -1245.4797 | -1089.7132 | No | No | 59.3 | 0.5937 | 2014
TI_2014-03-10_232900 | 2014-03-10 18:29 | 2014-03-10 18:29 | CDT | 2014-03-10 23:29 | 798.2 | 59.9815 | 59.8821 | 59.7799 | -0.099423 | -0.20164 | -802.8313 | -395.8453 | Yes | Yes | 59.3 | 0.4799 | 2014
TI_2014-03-19_134040 | 2014-03-19 08:41 | 2014-03-19 08:41 | CDT | 2014-03-19 13:41 | 770.2 | 59.979 | 59.8804 | 59.8028 | -0.098588 | -0.1762 | -781.2304 | -437.1148 | Yes | Yes | 59.3 | 0.5028 | 2014
TI_2014-03-21_105652 | 2014-03-21 05:57 | 2014-03-21 05:57 | CDT | 2014-03-21 10:57 |  | 60.0781 | 60.1031 | 60.1028 | 0.024972 | 0.024692 |  |  | No | No | 59.3 | 0.8028 | 2014
TI_2014-03-22_054606 | 2014-03-22 00:46 | 2014-03-22 00:46 | CDT | 2014-03-22 05:46 |  | 59.9737 | 60.0002 | 60.04 | 0.026524 | 0.066295 |  |  | No | No | 59.3 | 0.74 | 2014
TI_2014-04-02_053259 | 2014-04-02 00:33 | 2014-04-02 00:33 | CDT | 2014-04-02 05:33 | 470.7 | 60.0235 | 59.9176 | 59.8755 | -0.10594 | -0.14802 | -444.3184 | -317.9985 | Yes | Yes | 59.3 | 0.5755 | 2014
TI_2014-04-06_123445 | 2014-04-06 07:35 | 2014-04-06 07:35 | CDT | 2014-04-06 12:35 |  | 59.9925 | 59.8295 | 59.8574 | -0.16302 | -0.13513 |  |  | No | No | 59.3 | 0.5574 | 2014
TI_2014-04-14_082341 | 2014-04-14 03:24 | 2014-04-14 03:24 | CDT | 2014-04-14 08:24 |  | 60.0178 | 59.9423 | 59.9205 | -0.075486 | -0.097249 |  |  | No | No | 59.3 | 0.6205 | 2014
TI_2014-04-23_144629 | 2014-04-23 09:46 | 2014-04-23 09:46 | CDT | 2014-04-23 14:46 |  | 59.9236 | 60.0021 | 60.0142 | 0.078438 | 0.090574 |  |  | No | No | 59.3 | 0.7142 | 2014
TI_2014-04-29_135731 | 2014-04-29 08:58 | 2014-04-29 08:58 | CDT | 2014-04-29 13:58 | 464 | 59.9643 | 59.9072 | 59.8625 | -0.057066 | -0.10176 | -813.0999 | -455.9881 | Yes | Yes | 59.3 | 0.5625 | 2014
TI_2014-05-01_201323 | 2014-05-01 15:13 | 2014-05-01 15:13 | CDT | 2014-05-01 20:13 | 559.1 | 60.0146 | 59.917 | 59.8537 | -0.097623 | -0.16094 | -572.7128 | -347.3982 | Yes | Yes | 59.3 | 0.5537 | 2014
TI_2014-05-06_125322 | 2014-05-06 07:53 | 2014-05-06 07:53 | CDT | 2014-05-06 12:53 |  | 59.9716 | 60.0268 | 60.0237 | 0.055185 | 0.052088 |  |  | No | No | 59.3 | 0.7237 | 2014
TI_2014-05-12_050433 | 2014-05-12 00:05 | 2014-05-12 00:05 | CDT | 2014-05-12 05:05 |  | 59.8952 | 59.9054 | 59.8836 | 0.010205 | -0.011563 |  |  | No | No | 59.3 | 0.5836 | 2014
TI_2014-05-13_173033 | 2014-05-13 12:31 | 2014-05-13 12:31 | CDT | 2014-05-13 17:31 | -420.1 | 59.9736 | 60.0421 | 60.0616 | 0.06853 | 0.088006 | -613.0118 | -477.3537 | No | Yes | 59.3 | 0.7616 | 2014
TI_2014-05-14_022335 | 2014-05-13 21:24 | 2014-05-13 21:24 | CDT | 2014-05-14 02:24 |  | 60.0269 | 59.95 | 59.9221 | -0.076863 | -0.10478 |  |  | No | No | 59.3 | 0.6221 | 2014
TI_2014-05-15_091958 | 2014-05-15 04:20 | 2014-05-15 04:20 | CDT | 2014-05-15 09:20 | 447.1 | 59.9749 | 59.9086 | 59.8596 | -0.066294 | -0.11531 | -674.4219 | -387.7303 | No | Yes | 59.3 | 0.5596 | 2014
TI_2014-05-17_054658 | 2014-05-17 00:47 | 2014-05-17 00:47 | CDT | 2014-05-17 05:47 | 573.6 | 59.9665 | 59.9059 | 59.8195 | -0.060616 | -0.14704 | -946.2837 | -390.0881 | Yes | Yes | 59.3 | 0.5195 | 2014
TI_2014-06-07_153119 | 2014-06-07 10:31 | 2014-06-07 10:31 | CDT | 2014-06-07 15:31 | 523 | 60.0026 | 59.9388 | 59.9151 | -0.063792 | -0.087538 | -819.8509 | -597.4564 | Yes | Yes | 59.3 | 0.6151 | 2014
TI_2014-06-11_071052 | 2014-06-11 02:11 | 2014-06-11 02:11 | CDT | 2014-06-11 07:11 |  | 60.0238 | 59.9443 | 59.9265 | -0.079454 | -0.097265 |  |  | No | No | 59.3 | 0.6265 | 2014
TI_2014-06-21_055804 | 2014-06-21 00:58 | 2014-06-21 00:58 | CDT | 2014-06-21 05:58 | 625.9 | 59.9943 | 59.909 | 59.8548 | -0.08527 | -0.1395 | -734.0231 | -448.6772 | Yes | Yes | 59.3 | 0.5548 | 2014
TI_2014-06-21_103521 | 2014-06-21 05:35 | 2014-06-21 05:35 | CDT | 2014-06-21 10:35 |  | 59.959 | 59.9306 | 59.8963 | -0.028396 | -0.06268 |  |  | No | No | 59.3 | 0.5963 | 2014
TI_2014-06-23_180138 | 2014-06-23 13:02 | 2014-06-23 13:02 | CDT | 2014-06-23 18:02 | 861.1 | 59.9628 | 59.8933 | 59.7821 | -0.069521 | -0.18069 | -1238.6171 | -476.5538 | Yes | Yes | 59.3 | 0.4821 | 2014
TI_2014-06-27_141233 | 2014-06-27 09:13 | 2014-06-27 09:13 | CDT | 2014-06-27 14:13 |  | 59.9197 | 60.0008 | 60.018 | 0.081065 | 0.098252 |  |  | No | No | 59.3 | 0.718 | 2014
TI_2014-06-27_141704 | 2014-06-27 09:17 | 2014-06-27 09:17 | CDT | 2014-06-27 14:17 |  | 59.9623 | 59.9339 | 59.8966 | -0.028332 | -0.065663 |  |  | No | No | 59.3 | 0.5966 | 2014
TI_2014-07-01_151149 | 2014-07-01 10:12 | 2014-07-01 10:12 | CDT | 2014-07-01 15:12 | 472.4 | 59.9821 | 59.9295 | 59.8903 | -0.052582 | -0.091763 | -898.4119 | -514.807 | Yes | Yes | 59.3 | 0.5903 | 2014
TI_2014-07-17_225505 | 2014-07-17 17:55 | 2014-07-17 17:55 | CDT | 2014-07-17 22:55 | 739.1 | 60.0013 | 59.8902 | 59.8444 | -0.11113 | -0.15693 | -665.0881 | -470.9665 | Yes | Yes | 59.3 | 0.5444 | 2014
TI_2014-07-21_215312 | 2014-07-21 16:53 | 2014-07-21 16:53 | CDT | 2014-07-21 21:53 |  | 59.9531 | 59.9087 | 59.8996 | -0.044439 | -0.053505 |  |  | No | No | 59.3 | 0.5996 | 2014
TI_2014-07-24_010850 | 2014-07-23 20:09 | 2014-07-23 20:09 | CDT | 2014-07-24 01:09 | 781 | 60.019 | 59.9 | 59.8234 | -0.11898 | -0.19559 | -656.4259 | -399.2954 | No | No | 59.3 | 0.5234 | 2014
TI_2014-07-24_011009 | 2014-07-23 20:10 | 2014-07-23 20:10 | CDT | 2014-07-24 01:10 | 554 | 59.881 | 59.8285 | 59.776 | -0.052499 | -0.10498 | -1055.2558 | -527.7196 | No | No | 59.3 | 0.476 | 2014
TI_2014-07-24_152425 | 2014-07-24 10:24 | 2014-07-24 10:24 | CDT | 2014-07-24 15:24 | 590.6 | 59.9716 | 59.9146 | 59.8829 | -0.056978 | -0.088705 | -1036.532 | -665.8001 | Yes | Yes | 59.3 | 0.5829 | 2014
TI_2014-08-04_192456 | 2014-08-04 14:25 | 2014-08-04 14:25 | CDT | 2014-08-04 19:25 | 839 | 59.9023 | 59.8705 | 59.8004 | -0.031763 | -0.10188 | -2641.4564 | -823.5577 | No | No | 59.3 | 0.5004 | 2014
TI_2014-08-04_192728 | 2014-08-04 14:27 | 2014-08-04 14:27 | CDT | 2014-08-04 19:27 | 781 | 59.9359 | 59.8282 | 59.8292 | -0.10769 | -0.10666 | -725.2558 | -732.2651 | No | No | 59.3 | 0.5292 | 2014
TI_2014-08-13_154554 | 2014-08-13 10:46 | 2014-08-13 10:46 | CDT | 2014-08-13 15:46 |  | 60.0071 | 59.9281 | 59.9083 | -0.078929 | -0.098776 |  |  | No | No | 59.3 | 0.6083 | 2014
TI_2014-08-20_144638 | 2014-08-20 09:47 | 2014-08-20 09:47 | CDT | 2014-08-20 14:47 |  | 59.9108 | 60.013 | 60.0096 | 0.10216 | 0.098801 |  |  | No | No | 59.3 | 0.7096 | 2014
TI_2014-08-31_031728 | 2014-08-30 22:17 | 2014-08-30 22:17 | CDT | 2014-08-31 03:17 | 577.2 | 60.0167 | 59.9124 | 59.8719 | -0.10429 | -0.14476 | -553.4742 | -398.7351 | Yes | Yes | 59.3 | 0.5719 | 2014
TI_2014-09-03_153727 | 2014-09-03 10:37 | 2014-09-03 10:37 | CDT | 2014-09-03 15:37 | 446 | 60.0108 | 59.9255 | 59.9165 | -0.085305 | -0.094281 | -522.8286 | -473.0554 | No | No | 59.3 | 0.6165 | 2014
TI_2014-09-03_193755 | 2014-09-03 14:38 | 2014-09-03 14:38 | CDT | 2014-09-03 19:38 | 892 | 60.0234 | 59.8743 | 59.838 | -0.14915 | -0.1854 | -598.0638 | -481.1256 | Yes | Yes | 59.3 | 0.538 | 2014
TI_2014-09-09_135732 | 2014-09-09 08:58 | 2014-09-09 08:58 | CDT | 2014-09-09 13:58 |  | 59.9999 | 59.9378 | 59.9098 | -0.062103 | -0.090117 |  |  | No | No | 59.3 | 0.6098 | 2014
TI_2014-09-11_114114 | 2014-09-11 06:41 | 2014-09-11 06:41 | CDT | 2014-09-11 11:41 | 603.8 | 60.0147 | 59.8772 | 59.8947 | -0.13746 | -0.12 | -439.2524 | -503.1621 | Yes | Yes | 59.3 | 0.5947 | 2014
TI_2014-09-11_123241 | 2014-09-11 07:33 | 2014-09-11 07:33 | CDT | 2014-09-11 12:33 | 572.3 | 60.0236 | 59.9124 | 59.8869 | -0.11113 | -0.13667 | -515.0016 | -418.7558 | Yes | Yes | 59.3 | 0.5869 | 2014
TI_2014-09-29_204117 | 2014-09-29 15:41 | 2014-09-29 15:41 | CDT | 2014-09-29 20:41 | 644.6 | 59.9707 | 59.883 | 59.8391 | -0.087642 | -0.13158 | -735.4901 | -489.8863 | Yes | Yes | 59.3 | 0.5391 | 2014
TI_2014-10-08_205025 | 2014-10-08 15:50 | 2014-10-08 15:50 | CDT | 2014-10-08 20:50 | 244 | 60.0133 | 59.9533 | 59.9522 | -0.059987 | -0.061092 | -406.7523 | -399.3998 | No | No | 59.3 | 0.6522 | 2014
TI_2014-10-08_205128 | 2014-10-08 15:51 | 2014-10-08 15:51 | CDT | 2014-10-08 20:51 | 408 | 59.9543 | 59.8943 | 59.8631 | -0.059992 | -0.091233 | -680.0902 | -447.2042 | No | No | 59.3 | 0.5631 | 2014
TI_2014-10-08_215347 | 2014-10-08 16:54 | 2014-10-08 16:54 | CDT | 2014-10-08 21:54 | -807 | 60.0258 | 60.0754 | 60.1232 | 0.04957 | 0.097387 | -1628.0097 | -828.6521 | Yes | Yes | 59.3 | 0.8232 | 2014
TI_2014-10-09_182914 | 2014-10-09 13:29 | 2014-10-09 13:29 | CDT | 2014-10-09 18:29 | 738.5 | 59.9946 | 59.8962 | 59.8271 | -0.098357 | -0.16749 | -750.8388 | -440.9262 | Yes | Yes | 59.3 | 0.5271 | 2014
TI_2014-10-10_211609 | 2014-10-10 16:16 | 2014-10-10 16:16 | CDT | 2014-10-10 21:16 |  | 60.0263 | 59.9395 | 59.9314 | -0.086781 | -0.09485 |  |  | No | No | 59.3 | 0.6314 | 2014
TI_2014-10-13_132722 | 2014-10-13 08:27 | 2014-10-13 08:27 | CDT | 2014-10-13 13:27 | 563.4 | 60.0184 | 59.9315 | 59.8819 | -0.086918 | -0.13647 | -648.2007 | -412.8248 | Yes | Yes | 59.3 | 0.5819 | 2014
TI_2014-10-21_212622 | 2014-10-21 16:26 | 2014-10-21 16:26 | CDT | 2014-10-21 21:26 |  | 60.0185 | 59.939 | 59.924 | -0.079514 | -0.094494 |  |  | No | No | 59.3 | 0.624 | 2014
TI_2014-10-25_025543 | 2014-10-24 21:56 | 2014-10-24 21:56 | CDT | 2014-10-25 02:56 |  | 59.9391 | 59.9215 | 59.8807 | -0.017588 | -0.058376 |  |  | No | No | 59.3 | 0.5807 | 2014
TI_2014-10-26_071251 | 2014-10-26 02:13 | 2014-10-26 02:13 | CDT | 2014-10-26 07:13 |  | 60.0119 | 59.9392 | 59.9214 | -0.072683 | -0.090527 |  |  | No | No | 59.3 | 0.6214 | 2014
TI_2014-10-29_170617 | 2014-10-29 12:06 | 2014-10-29 12:06 | CDT | 2014-10-29 17:06 | 567.5 | 60.005 | 59.8981 | 59.8676 | -0.10693 | -0.13739 | -530.733 | -413.0444 | Yes | Yes | 59.3 | 0.5676 | 2014
TI_2014-11-12_140609 | 2014-11-12 08:06 | 2014-11-12 08:06 | CST | 2014-11-12 14:06 |  | 60.1228 | 60.1156 | 60.0233 | -0.0072252 | -0.099519 |  |  | No | No | 59.3 | 0.7233 | 2014
TI_2014-11-20_050858 | 2014-11-19 23:09 | 2014-11-19 23:09 | CST | 2014-11-20 05:09 |  | 60.022 | 59.9306 | 59.9018 | -0.091335 | -0.12018 |  |  | No | No | 59.3 | 0.6018 | 2014
TI_2014-11-21_111325 | 2014-11-21 05:13 | 2014-11-21 05:13 | CST | 2014-11-21 11:13 | 787 | 59.9797 | 59.8469 | 59.7629 | -0.13278 | -0.21677 | -592.6931 | -363.0625 | Yes | Yes | 59.3 | 0.4629 | 2014
TI_2014-11-21_223855 | 2014-11-21 16:39 | 2014-11-21 16:39 | CST | 2014-11-21 22:39 |  | 59.9527 | 59.9176 | 59.8727 | -0.035084 | -0.079988 |  |  | No | No | 59.3 | 0.5727 | 2014
TI_2014-11-29_021134 | 2014-11-28 20:12 | 2014-11-28 20:12 | CST | 2014-11-29 02:12 | 479 | 60.0186 | 59.9078 | 59.8759 | -0.1108 | -0.14271 | -432.3198 | -335.6548 | Yes | Yes | 59.3 | 0.5759 | 2014
TI_2014-12-23_105148 | 2014-12-23 04:52 | 2014-12-23 04:52 | CST | 2014-12-23 10:52 | 771.85 | 59.9777 | 59.9145 | 59.7835 | -0.063126 | -0.19416 | -1222.7102 | -397.5418 | Yes | Yes | 59.3 | 0.4835 | 2015
TI_2014-12-31_111127 | 2014-12-31 05:11 | 2014-12-31 05:11 | CST | 2014-12-31 11:11 | 580.86 | 60.0038 | 59.9148 | 59.8798 | -0.089033 | -0.12401 | -652.4073 | -468.3848 | Yes | Yes | 59.3 | 0.5798 | 2015
TI_2015-01-09_043832 | 2015-01-08 22:39 | 2015-01-08 22:39 | CST | 2015-01-09 04:39 |  | 60.0147 | 59.9598 | 59.945 | -0.054933 | -0.069713 |  |  | No | No | 59.3 | 0.645 | 2015
TI_2015-01-15_193930 | 2015-01-15 13:40 | 2015-01-15 13:40 | CST | 2015-01-15 19:40 |  | 60.004 | 59.9457 | 59.9226 | -0.05838 | -0.081438 |  |  | No | No | 59.3 | 0.6226 | 2015
TI_2015-01-21_141729 | 2015-01-21 08:17 | 2015-01-21 08:17 | CST | 2015-01-21 14:17 |  | 60.0303 | 59.99 | 59.9673 | -0.040235 | -0.062968 |  |  | No | No | 59.3 | 0.6673 | 2015
TI_2015-01-28_185726 | 2015-01-28 12:57 | 2015-01-28 12:57 | CST | 2015-01-28 18:57 |  | 60.0222 | 59.9469 | 59.9467 | -0.075266 | -0.075493 |  |  | No | No | 59.3 | 0.6467 | 2015
TI_2015-02-02_004308 | 2015-02-01 18:43 | 2015-02-01 18:43 | CST | 2015-02-02 00:43 | 570.31 | 59.9807 | 59.912 | 59.8706 | -0.068717 | -0.11007 | -829.937 | -518.1194 | Yes | Yes | 59.3 | 0.5706 | 2015
TI_2015-02-12_225319 | 2015-02-12 16:53 | 2015-02-12 16:53 | CST | 2015-02-12 22:53 | 525.01 | 60.0245 | 59.922 | 59.8928 | -0.10248 | -0.13169 | -512.3187 | -398.679 | Yes | Yes | 59.3 | 0.5928 | 2015
TI_2015-02-17_073920 | 2015-02-17 01:39 | 2015-02-17 01:39 | CST | 2015-02-17 07:39 | 450 | 60.0137 | 59.9289 | 59.9124 | -0.084804 | -0.10133 | -530.6352 | -444.084 | Yes | Yes | 59.3 | 0.6124 | 2015
TI_2015-02-28_123535 | 2015-02-28 06:36 | 2015-02-28 06:36 | CST | 2015-02-28 12:36 |  | 59.9954 | 59.9094 | 59.8951 | -0.085929 | -0.10028 |  |  | No | No | 59.3 | 0.5951 | 2015
TI_2015-03-01_023201 | 2015-02-28 20:32 | 2015-02-28 20:32 | CST | 2015-03-01 02:32 |  | 60.0291 | 59.946 | 59.9288 | -0.083047 | -0.10025 |  |  | No | No | 59.3 | 0.6288 | 2015
TI_2015-03-02_033708 | 2015-03-01 21:37 | 2015-03-01 21:37 | CST | 2015-03-02 03:37 | 599.8 | 60.0103 | 59.9167 | 59.8873 | -0.093634 | -0.12302 | -640.5781 | -487.5623 | Yes | Yes | 59.3 | 0.5873 | 2015
TI_2015-03-12_213949 | 2015-03-12 16:40 | 2015-03-12 16:40 | CDT | 2015-03-12 21:40 | 400 | 59.9982 | 59.924 | 59.8875 | -0.074194 | -0.11069 | -539.128 | -361.3793 | No | No | 59.3 | 0.5875 | 2015
TI_2015-03-28_160105 | 2015-03-28 11:01 | 2015-03-28 11:01 | CDT | 2015-03-28 16:01 | 698.9 | 60.018 | 59.8919 | 59.9648 | -0.12603 | -0.053154 | -554.5562 | -1314.8471 | No | No | 59.3 | 0.6648 | 2015
TI_2015-04-10_022325 | 2015-04-09 21:23 | 2015-04-09 21:23 | CDT | 2015-04-10 02:23 | 582.7 | 59.9921 | 59.9136 | 59.8671 | -0.078574 | -0.12504 | -741.5932 | -466.0196 | Yes | Yes | 59.3 | 0.5671 | 2015
TI_2015-04-13_214324 | 2015-04-13 16:43 | 2015-04-13 16:43 | CDT | 2015-04-13 21:43 | 487 | 60.0005 | 59.9144 | 59.8734 | -0.086066 | -0.1271 | -565.8423 | -383.1694 | Yes | Yes | 59.3 | 0.5734 | 2015
TI_2015-04-14_115848 | 2015-04-14 06:59 | 2015-04-14 06:59 | CDT | 2015-04-14 11:59 |  | 59.9835 | 60.0921 | 60.1004 | 0.1086 | 0.11692 |  |  | No | No | 59.3 | 0.8004 | 2015
TI_2015-04-15_023944 | 2015-04-14 21:40 | 2015-04-14 21:40 | CDT | 2015-04-15 02:40 |  | 59.9546 | 59.9321 | 59.8964 | -0.022464 | -0.058194 |  |  | No | No | 59.3 | 0.5964 | 2015
TI_2015-04-24_095647 | 2015-04-24 04:57 | 2015-04-24 04:57 | CDT | 2015-04-24 09:57 |  | 59.9922 | 60.0797 | 60.1015 | 0.087543 | 0.10935 |  |  | No | No | 59.3 | 0.8015 | 2015
TI_2015-04-27_091510 | 2015-04-27 04:15 | 2015-04-27 04:15 | CDT | 2015-04-27 09:15 | 539.8 | 60.0127 | 59.9163 | 59.8913 | -0.096378 | -0.12139 | -560.0845 | -444.6925 | Yes | Yes | 59.3 | 0.5913 | 2015
TI_2015-05-03_122455 | 2015-05-03 07:25 | 2015-05-03 07:25 | CDT | 2015-05-03 12:25 |  | 60.0115 | 59.9413 | 59.9211 | -0.070178 | -0.09038 |  |  | No | No | 59.3 | 0.6211 | 2015
TI_2015-05-06_182816 | 2015-05-06 13:28 | 2015-05-06 13:28 | CDT | 2015-05-06 18:28 | 464 | 59.9717 | 59.9176 | 59.8767 | -0.054048 | -0.094992 | -858.4949 | -488.4638 | No | No | 59.3 | 0.5767 | 2015
TI_2015-05-07_173710 | 2015-05-07 12:37 | 2015-05-07 12:37 | CDT | 2015-05-07 17:37 | 555 | 59.9517 | 59.9191 | 59.8885 | -0.032627 | -0.063193 | -1701.0656 | -878.2607 | No | No | 59.3 | 0.5885 | 2015
TI_2015-05-08_023401 | 2015-05-07 21:34 | 2015-05-07 21:34 | CDT | 2015-05-08 02:34 | 429.6 | 60.0126 | 59.9151 | 59.8926 | -0.097494 | -0.12001 | -440.6419 | -357.9847 | No | No | 59.3 | 0.5926 | 2015
TI_2015-05-08_214819 | 2015-05-08 16:48 | 2015-05-08 16:48 | CDT | 2015-05-08 21:48 | 624.3 | 60.0029 | 59.9215 | 59.8848 | -0.081465 | -0.11814 | -766.3402 | -528.4249 | Yes | Yes | 59.3 | 0.5848 | 2015
TI_2015-05-09_020413 | 2015-05-08 21:04 | 2015-05-08 21:04 | CDT | 2015-05-09 02:04 | 606.7 | 60.0116 | 59.8821 | 59.8587 | -0.12947 | -0.15285 | -468.596 | -396.9228 | Yes | Yes | 59.3 | 0.5587 | 2015
TI_2015-05-09_045341 | 2015-05-08 23:54 | 2015-05-08 23:54 | CDT | 2015-05-09 04:54 | 511.3 | 60.0097 | 59.9152 | 59.8716 | -0.094522 | -0.13812 | -540.9315 | -370.1734 | Yes | Yes | 59.3 | 0.5716 | 2015
TI_2015-05-09_125131 | 2015-05-09 07:52 | 2015-05-09 07:52 | CDT | 2015-05-09 12:52 | 771.3 | 59.9946 | 59.8984 | 59.8309 | -0.096139 | -0.16368 | -802.2775 | -471.233 | Yes | Yes | 59.3 | 0.5309 | 2015
TI_2015-05-12_083536 | 2015-05-12 03:36 | 2015-05-12 03:36 | CDT | 2015-05-12 08:36 |  | 59.9869 | 60.1097 | 60.1098 | 0.12277 | 0.12288 |  |  | No | No | 59.3 | 0.8098 | 2015
TI_2015-05-14_172918 | 2015-05-14 12:29 | 2015-05-14 12:29 | CDT | 2015-05-14 17:29 | 446 | 59.9689 | 59.9139 | 59.873 | -0.054973 | -0.095905 | -811.3122 | -465.0432 | No | No | 59.3 | 0.573 | 2015
TI_2015-05-19_051959 | 2015-05-19 00:20 | 2015-05-19 00:20 | CDT | 2015-05-19 05:20 | 394 | 60.0202 | 59.9432 | 59.926 | -0.077017 | -0.09417 | -511.5721 | -418.3908 | No | No | 59.3 | 0.626 | 2015
TI_2015-05-25_184705 | 2015-05-25 13:47 | 2015-05-25 13:47 | CDT | 2015-05-25 18:47 | 493 | 59.9746 | 59.8966 | 59.8675 | -0.078013 | -0.10714 | -631.9449 | -460.1597 | Yes | Yes | 59.3 | 0.5675 | 2015
TI_2015-05-27_120303 | 2015-05-27 07:03 | 2015-05-27 07:03 | CDT | 2015-05-27 12:03 |  | 59.9695 | 59.9346 | 59.8983 | -0.03491 | -0.071225 |  |  | No | No | 59.3 | 0.5983 | 2015
TI_2015-05-27_143710 | 2015-05-27 09:37 | 2015-05-27 09:37 | CDT | 2015-05-27 14:37 |  | 59.9137 | 59.9102 | 59.8677 | -0.0034968 | -0.046001 |  |  | No | No | 59.3 | 0.5677 | 2015
TI_2015-05-28_013212 | 2015-05-27 20:32 | 2015-05-27 20:32 | CDT | 2015-05-28 01:32 | 764.2 | 60.0086 | 59.8998 | 59.8613 | -0.1088 | -0.14732 | -702.382 | -518.7195 | Yes | Yes | 59.3 | 0.5613 | 2015
TI_2015-05-29_131443 | 2015-05-29 08:15 | 2015-05-29 08:15 | CDT | 2015-05-29 13:15 | 491 | 59.9607 | 59.9328 | 59.8971 | -0.027898 | -0.063639 | -1759.9764 | -771.5404 | No | No | 59.3 | 0.5971 | 2015
TI_2015-05-30_092033 | 2015-05-30 04:21 | 2015-05-30 04:21 | CDT | 2015-05-30 09:21 | 449 | 60.0038 | 59.9311 | 59.9101 | -0.072669 | -0.093682 | -617.8703 | -479.2795 | No | No | 59.3 | 0.6101 | 2015
TI_2015-05-31_230608 | 2015-05-31 18:06 | 2015-05-31 18:06 | CDT | 2015-05-31 23:06 | 512 | 59.9864 | 59.9425 | 59.9102 | -0.043986 | -0.076252 | -1164.0101 | -671.4621 | No | No | 59.3 | 0.6102 | 2015
TI_2015-06-02_204627 | 2015-06-02 15:46 | 2015-06-02 15:46 | CDT | 2015-06-02 20:46 | 556 | 60.0037 | 59.9539 | 59.9631 | -0.049837 | -0.040606 | -1115.6419 | -1369.255 | No | No | 59.3 | 0.6631 | 2015
TI_2015-06-03_143043 | 2015-06-03 09:31 | 2015-06-03 09:31 | CDT | 2015-06-03 14:31 |  | 59.9321 | 59.8968 | 59.8948 | -0.035325 | -0.037326 |  |  | No | No | 59.3 | 0.5948 | 2015
TI_2015-06-04_204436 | 2015-06-04 15:45 | 2015-06-04 15:45 | CDT | 2015-06-04 20:45 | 488 | 60.0141 | 59.9438 | 59.9184 | -0.070325 | -0.095725 | -693.9228 | -509.7959 | Yes | Yes | 59.3 | 0.6184 | 2015
TI_2015-06-06_210153 | 2015-06-06 16:02 | 2015-06-06 16:02 | CDT | 2015-06-06 21:02 | 697 | 60.02 | 59.9437 | 59.9313 | -0.076269 | -0.088649 | -913.8739 | -786.2445 | No | No | 59.3 | 0.6313 | 2015
TI_2015-06-09_190642 | 2015-06-09 14:07 | 2015-06-09 14:07 | CDT | 2015-06-09 19:07 | 690 | 60.0041 | 59.9426 | 59.9589 | -0.061429 | -0.045162 | -1123.2482 | -1527.8344 | No | No | 59.3 | 0.6589 | 2015
TI_2015-06-10_140228 | 2015-06-10 09:02 | 2015-06-10 09:02 | CDT | 2015-06-10 14:02 |  | 60.0697 | 60.0358 | 59.9299 | -0.033901 | -0.13982 |  |  | No | No | 59.3 | 0.6299 | 2015
TI_2015-06-10_143547 | 2015-06-10 09:36 | 2015-06-10 09:36 | CDT | 2015-06-10 14:36 |  | 59.9066 | 59.9069 | 59.8814 | 0.00028052 | -0.025224 |  |  | No | No | 59.3 | 0.5814 | 2015
TI_2015-06-17_144340 | 2015-06-17 09:44 | 2015-06-17 09:44 | CDT | 2015-06-17 14:44 |  | 59.9227 | 59.9206 | 59.8595 | -0.0021519 | -0.063205 |  |  | No | No | 59.3 | 0.5595 | 2015
TI_2015-06-17_181437 | 2015-06-17 13:15 | 2015-06-17 13:15 | CDT | 2015-06-17 18:15 | 537 | 60.0099 | 59.9311 | 59.8967 | -0.078838 | -0.11324 | -681.1405 | -474.231 | Yes | Yes | 59.3 | 0.5967 | 2015
TI_2015-06-22_071004 | 2015-06-22 02:10 | 2015-06-22 02:10 | CDT | 2015-06-22 07:10 |  | 59.9764 | 59.9265 | 59.8893 | -0.049906 | -0.087111 |  |  | No | No | 59.3 | 0.5893 | 2015
TI_2015-06-26_040916 | 2015-06-25 23:09 | 2015-06-25 23:09 | CDT | 2015-06-26 04:09 |  | 59.9578 | 59.9171 | 59.8824 | -0.040699 | -0.075387 |  |  | No | No | 59.3 | 0.5824 | 2015
TI_2015-06-26_154303 | 2015-06-26 10:43 | 2015-06-26 10:43 | CDT | 2015-06-26 15:43 | 634 | 60.0101 | 59.928 | 59.8976 | -0.082143 | -0.11255 | -771.8205 | -563.2991 | Yes | Yes | 59.3 | 0.5976 | 2015
TI_2015-06-30_193610 | 2015-06-30 14:36 | 2015-06-30 14:36 | CDT | 2015-06-30 19:36 | 501 | 60.0214 | 59.9439 | 59.923 | -0.077493 | -0.098387 | -646.5072 | -509.2124 | Yes | Yes | 59.3 | 0.623 | 2015
TI_2015-07-01_061503 | 2015-07-01 01:15 | 2015-07-01 01:15 | CDT | 2015-07-01 06:15 | 750 | 59.9764 | 59.9179 | 59.8501 | -0.058559 | -0.12633 | -1280.7692 | -593.6848 | No | No | 59.3 | 0.5501 | 2015
TI_2015-07-05_153027 | 2015-07-05 10:30 | 2015-07-05 10:30 | CDT | 2015-07-05 15:30 | 847 | 60.0045 | 59.9073 | 59.8647 | -0.097163 | -0.13979 | -871.727 | -605.8962 | Yes | Yes | 59.3 | 0.5647 | 2015
TI_2015-07-19_183345 | 2015-07-19 13:34 | 2015-07-19 13:34 | CDT | 2015-07-19 18:34 | 642 | 59.966 | 59.892 | 59.846 | -0.074 | -0.12 | -867.5676 | -535 | Yes | Yes | 59.3 | 0.546 | 2015
TI_2015-07-22_020617 | 2015-07-21 21:06 | 2015-07-21 21:06 | CDT | 2015-07-22 02:06 |  | 59.9618 | 59.9306 | 59.8966 | -0.03128 | -0.065239 |  |  | No | No | 59.3 | 0.5966 | 2015
TI_2015-07-29_231642 | 2015-07-29 18:17 | 2015-07-29 18:17 | CDT | 2015-07-29 23:17 | 1507 | 60.0125 | 59.8094 | 59.7278 | -0.20307 | -0.2847 | -742.1213 | -529.3381 | Yes | Yes | 59.3 | 0.4278 | 2015
TI_2015-08-19_233717 | 2015-08-19 18:37 | 2015-08-19 18:37 | CDT | 2015-08-19 23:37 | 450 | 60.007 | 59.948 | 59.9305 | -0.059015 | -0.076476 | -762.5232 | -588.4228 | No | Yes | 59.3 | 0.6305 | 2015
TI_2015-08-25_211854 | 2015-08-25 16:19 | 2015-08-25 16:19 | CDT | 2015-08-25 21:19 | -503.25 | 60.002 | 60.039 | 60.062 | 0.037 | 0.06 | -1360.1351 | -838.75 | No | Yes | 59.3 | 0.762 | 2015
TI_2015-08-26_034127 | 2015-08-25 22:41 | 2015-08-25 22:41 | CDT | 2015-08-26 03:41 | 481 | 59.9749 | 59.9568 | 59.9091 | -0.018168 | -0.065832 | -2647.5193 | -730.6488 | No | No | 59.3 | 0.6091 | 2015
TI_2015-08-26_193704 | 2015-08-26 14:37 | 2015-08-26 14:37 | CDT | 2015-08-26 19:37 | 472 | 59.9987 | 59.9391 | 59.9108 | -0.059601 | -0.08793 | -791.9347 | -536.7894 | Yes | Yes | 59.3 | 0.6108 | 2015
TI_2015-08-28_021144 | 2015-08-27 21:12 | 2015-08-27 21:12 | CDT | 2015-08-28 02:12 | 634 | 59.9966 | 59.9298 | 59.8911 | -0.066859 | -0.10552 | -948.2707 | -600.8502 | Yes | Yes | 59.3 | 0.5911 | 2015
TI_2015-09-06_202220 | 2015-09-06 15:22 | 2015-09-06 15:22 | CDT | 2015-09-06 20:22 | 418 | 59.9886 | 59.933 | 59.9078 | -0.055576 | -0.080801 | -752.1196 | -517.3203 | No | No | 59.3 | 0.6078 | 2015
TI_2015-09-10_181058 | 2015-09-10 13:11 | 2015-09-10 13:11 | CDT | 2015-09-10 18:11 | 513 | 59.9666 | 59.9011 | 59.852 | -0.065482 | -0.11459 | -783.4183 | -447.6721 | Yes | Yes | 59.3 | 0.552 | 2015
TI_2015-09-12_183646 | 2015-09-12 13:37 | 2015-09-12 13:37 | CDT | 2015-09-12 18:37 | 464 | 60.0097 | 59.9415 | 59.9024 | -0.068227 | -0.10728 | -680.085 | -432.513 | Yes | Yes | 59.3 | 0.6024 | 2015
TI_2015-09-17_124502 | 2015-09-17 07:45 | 2015-09-17 07:45 | CDT | 2015-09-17 12:45 | 813 | 59.9766 | 59.9043 | 59.8409 | -0.072361 | -0.13572 | -1123.5358 | -599.0347 | Yes | Yes | 59.3 | 0.5409 | 2015
TI_2015-09-18_022221 | 2015-09-17 21:22 | 2015-09-17 21:22 | CDT | 2015-09-18 02:22 | 350 | 60.0045 | 59.9596 | 59.9356 | -0.044884 | -0.068893 | -779.7826 | -508.031 | No | No | 59.3 | 0.6356 | 2015
TI_2015-09-18_032014 | 2015-09-17 22:20 | 2015-09-17 22:20 | CDT | 2015-09-18 03:20 | 638 | 59.9791 | 59.921 | 59.8691 | -0.058132 | -0.11003 | -1097.5113 | -579.8284 | Yes | Yes | 59.3 | 0.5691 | 2015
TI_2015-10-03_150032 | 2015-10-03 10:01 | 2015-10-03 10:01 | CDT | 2015-10-03 15:01 | 491 | 60.0242 | 59.949 | 59.9108 | -0.075161 | -0.11338 | -653.2685 | -433.0553 | No | No | 59.3 | 0.6108 | 2015
TI_2015-10-23_103137 | 2015-10-23 05:32 | 2015-10-23 05:32 | CDT | 2015-10-23 10:32 | 825 | 60.0043 | 59.8984 | 59.8267 | -0.10596 | -0.17763 | -778.5602 | -464.4406 | Yes | Yes | 59.3 | 0.5267 | 2015
TI_2015-10-23_110523 | 2015-10-23 06:05 | 2015-10-23 06:05 | CDT | 2015-10-23 11:05 | 857 | 59.9705 | 59.9054 | 59.7977 | -0.065131 | -0.17283 | -1315.8053 | -495.8558 | Yes | Yes | 59.3 | 0.4977 | 2015
TI_2015-10-27_204722 | 2015-10-27 15:47 | 2015-10-27 15:47 | CDT | 2015-10-27 20:47 | 679 | 60.0124 | 59.8956 | 59.8494 | -0.11676 | -0.16296 | -581.5512 | -416.6738 | Yes | Yes | 59.3 | 0.5494 | 2015
TI_2015-11-07_093946 | 2015-11-07 03:40 | 2015-11-07 03:40 | CST | 2015-11-07 09:40 | 755 | 60.0017 | 59.9018 | 59.828 | -0.0999 | -0.17371 | -755.7543 | -434.625 | Yes | Yes | 59.3 | 0.528 | 2015
TI_2015-11-30_164536 | 2015-11-30 10:46 | 2015-11-30 10:46 | CST | 2015-11-30 16:46 | 574 | 60.0023 | 59.9197 | 59.8852 | -0.082632 | -0.11715 | -694.6501 | -489.9748 | Yes | Yes | 59.3 | 0.5852 | 2015
TI_2015-12-01_014242 | 2015-11-30 19:43 | 2015-11-30 19:43 | CST | 2015-12-01 01:43 | 575 | 60.005 | 59.922 | 59.87 | -0.083 | -0.135 | -692.7711 | -425.9259 | Yes | Yes | 59.3 | 0.57 | 2015
TI_2015-12-03_052545 | 2015-12-02 23:26 | 2015-12-02 23:26 | CST | 2015-12-03 05:26 | 477 | 60.004 | 59.936 | 59.894 | -0.068 | -0.11 | -701.4706 | -433.6364 | Yes | No | 59.3 | 0.594 | 2016
TI_2015-12-07_174740 | 2015-12-07 11:48 | 2015-12-07 11:48 | CST | 2015-12-07 17:48 | 281 | 60.01 | 59.942 | 59.92 | -0.068 | -0.09 | -413.2353 | -312.2222 | Yes | No | 59.3 | 0.62 | 2016
TI_2015-12-11_141700 | 2015-12-11 08:17 | 2015-12-11 08:17 | CST | 2015-12-11 14:17 | 450 | 59.9726 | 59.9359 | 59.9211 | -0.036761 | -0.051518 | -1224.1277 | -873.4777 | No | No | 59.3 | 0.6211 | 2016
TI_2015-12-21_211955 | 2015-12-21 15:20 | 2015-12-21 15:20 | CST | 2015-12-21 21:20 | 380 | 60.008 | 59.947 | 59.912 | -0.061 | -0.096 | -622.9508 | -395.8333 | Yes | No | 59.3 | 0.612 | 2016
TI_2015-12-30_171720 | 2015-12-30 11:17 | 2015-12-30 11:17 | CST | 2015-12-30 17:17 | 690 | 60.014 | 59.908 | 59.868 | -0.106 | -0.146 | -650.9434 | -472.6027 | Yes | Yes | 59.3 | 0.568 | 2016
TI_2016-01-08_163022 | 2016-01-08 10:30 | 2016-01-08 10:30 | CST | 2016-01-08 16:30 | 392 | 60.0159 | 59.9316 | 59.904 | -0.0843 | -0.1119 | -465.0059 | -350.3128 | No | No | 59.3 | 0.604 | 2016
TI_2016-01-13_202231 | 2016-01-13 14:23 | 2016-01-13 14:23 | CST | 2016-01-13 20:23 | 408 | 60.0039 | 59.9411 | 59.916 | -0.0628 | -0.0879 | -649.6815 | -464.1638 | No | No | 59.3 | 0.616 | 2016
TI_2016-01-22_051443 | 2016-01-21 23:15 | 2016-01-21 23:15 | CST | 2016-01-22 05:15 | 823 | 60.019 | 59.887 | 59.835 | -0.132 | -0.184 | -623.4848 | -447.2826 | Yes | Yes | 59.3 | 0.535 | 2016
TI_2016-01-27_052506 | 2016-01-26 23:25 | 2016-01-26 23:25 | CST | 2016-01-27 05:25 | 1346 | 60.015 | 59.873 | 59.727 | -0.142 | -0.288 | -947.8873 | -467.3611 | Yes | Yes | 59.3 | 0.427 | 2016
TI_2016-02-02_181727 | 2016-02-02 12:17 | 2016-02-02 12:17 | CST | 2016-02-02 18:17 | 375 | 60.0116 | 59.9437 | 59.917 | -0.0679 | -0.0946 | -552.2828 | -396.4059 | No | No | 59.3 | 0.617 | 2016
TI_2016-02-08_163108 | 2016-02-08 10:31 | 2016-02-08 10:31 | CST | 2016-02-08 16:31 | 331 | 60.0142 | 59.9523 | 59.933 | -0.0619 | -0.0812 | -534.7334 | -407.6355 | No | No | 59.3 | 0.633 | 2016
TI_2016-02-11_024514 | 2016-02-10 20:45 | 2016-02-10 20:45 | CST | 2016-02-11 02:45 | 312 | 60.0174 | 59.9527 | 59.931 | -0.0647 | -0.0864 | -482.2257 | -361.1111 | No | No | 59.3 | 0.631 | 2016
TI_2016-02-12_030919 | 2016-02-11 21:09 | 2016-02-11 21:09 | CST | 2016-02-12 03:09 | 385 | 59.9809 | 59.9299 | 59.898 | -0.051 | -0.0829 | -754.902 | -464.415 | No | No | 59.3 | 0.598 | 2016
TI_2016-02-19_030742 | 2016-02-18 21:08 | 2016-02-18 21:08 | CST | 2016-02-19 03:08 | 468 | 59.97 | 59.908 | 59.845 | -0.062 | -0.125 | -754.8387 | -374.4 | Yes | Yes | 59.3 | 0.545 | 2016
TI_2016-02-20_040131 | 2016-02-19 22:02 | 2016-02-19 22:02 | CST | 2016-02-20 04:02 |  |  |  |  | 0 | 0 |  |  | No | No | 59.3 | -59.3 | 2016
TI_2016-02-22_025439 | 2016-02-21 20:55 | 2016-02-21 20:55 | CST | 2016-02-22 02:55 | 343 | 59.96 | 59.9186 | 59.871 | -0.0414 | -0.089 | -828.5024 | -385.3933 | No | No | 59.3 | 0.571 | 2016
TI_2016-02-23_222213 | 2016-02-23 16:22 | 2016-02-23 16:22 | CST | 2016-02-23 22:22 | 239 | 59.9786 | 59.9596 | 59.935 | -0.019 | -0.0436 | -1257.8947 | -548.1651 | No | No | 59.3 | 0.635 | 2016
TI_2016-03-08_110311 | 2016-03-08 05:03 | 2016-03-08 05:03 | CST | 2016-03-08 11:03 | 266 | 60.0145 | 59.9453 | 59.924 | -0.0692 | -0.0905 | -384.3931 | -293.9227 | No | No | 59.3 | 0.624 | 2016
TI_2016-03-08_161826 | 2016-03-08 10:18 | 2016-03-08 10:18 | CST | 2016-03-08 16:18 | 468 | 59.981 | 59.902 | 59.869 | -0.079 | -0.112 | -592.4051 | -417.8571 | Yes | Yes | 59.3 | 0.569 | 2016
TI_2016-03-10_012523 | 2016-03-09 19:25 | 2016-03-09 19:25 | CST | 2016-03-10 01:25 | 155 | 60.0124 | 59.9513 | 59.922 | -0.0611 | -0.0904 | -253.6825 | -171.4602 | No | No | 59.3 | 0.622 | 2016
TI_2016-03-16_010042 | 2016-03-15 20:01 | 2016-03-15 20:01 | CDT | 2016-03-16 01:01 | 425 | 59.975 | 59.9316 | 59.897 | -0.0434 | -0.078 | -979.2627 | -544.8718 | No | No | 59.3 | 0.597 | 2016
TI_2016-03-21_121348 | 2016-03-21 07:14 | 2016-03-21 07:14 | CDT | 2016-03-21 12:14 | 416 | 60.029 | 59.966 | 59.932 | -0.063 | -0.097 | -660.3175 | -428.866 | Yes | No | 59.3 | 0.632 | 2016
TI_2016-03-23_022934 | 2016-03-22 21:30 | 2016-03-22 21:30 | CDT | 2016-03-23 02:30 | 342 | 60.014 | 59.949 | 59.906 | -0.065 | -0.108 | -526.1538 | -316.6667 | No | No | 59.3 | 0.606 | 2016
TI_2016-04-09_100004 | 2016-04-09 05:00 | 2016-04-09 05:00 | CDT | 2016-04-09 10:00 | 343 | 59.968 | 59.919 | 59.862 | -0.049 | -0.106 | -700 | -323.5849 | Yes | Yes | 59.3 | 0.562 | 2016
TI_2016-04-18_042605 | 2016-04-17 23:26 | 2016-04-17 23:26 | CDT | 2016-04-18 04:26 | 296 | 60.016 | 59.942 | 59.901 | -0.074 | -0.115 | -400 | -257.3913 | Yes | Yes | 59.3 | 0.601 | 2016
TI_2016-04-18_043044 | 2016-04-17 23:31 | 2016-04-17 23:31 | CDT | 2016-04-18 04:31 | 663 | 60.01 | 59.924 | 59.807 | -0.086 | -0.203 | -770.9302 | -326.601 | Yes | Yes | 59.3 | 0.507 | 2016
TI_2016-04-20_180453 | 2016-04-20 13:05 | 2016-04-20 13:05 | CDT | 2016-04-20 18:05 | 282.5222 | 59.9781 | 59.9459 | 59.91 | -0.032134 | -0.068072 | -879.1958 | -415.0332 | No | No | 59.3 | 0.61 | 2016
TI_2016-04-23_065422 | 2016-04-23 01:54 | 2016-04-23 01:54 | CDT | 2016-04-23 06:54 | 402 | 60.017 | 59.941 | 59.905 | -0.076 | -0.112 | -528.9474 | -358.9286 | Yes | No | 59.3 | 0.605 | 2016
TI_2016-04-23_190241 | 2016-04-23 14:03 | 2016-04-23 14:03 | CDT | 2016-04-23 19:03 | 382 | 59.977 | 59.923 | 59.867 | -0.054 | -0.11 | -707.4074 | -347.2727 | Yes | Yes | 59.3 | 0.567 | 2016
TI_2016-04-30_023746 | 2016-04-29 21:38 | 2016-04-29 21:38 | CDT | 2016-04-30 02:38 | 347.8742 | 60.0111 | 59.9507 | 59.916 | -0.060393 | -0.095142 | -576.0198 | -365.6354 | No | No | 59.3 | 0.616 | 2016
TI_2016-04-30_061620 | 2016-04-30 01:16 | 2016-04-30 01:16 | CDT | 2016-04-30 06:16 | 432 | 60.003 | 59.926 | 59.883 | -0.077 | -0.12 | -561.039 | -360 | Yes | Yes | 59.3 | 0.583 | 2016
TI_2016-04-30_085810 | 2016-04-30 03:58 | 2016-04-30 03:58 | CDT | 2016-04-30 08:58 | 411 | 59.988 | 59.935 | 59.884 | -0.053 | -0.104 | -775.4717 | -395.1923 | Yes | Yes | 59.3 | 0.584 | 2016
TI_2016-05-01_173230 | 2016-05-01 12:32 | 2016-05-01 12:32 | CDT | 2016-05-01 17:33 | 562 | 60.016 | 59.937 | 59.882 | -0.079 | -0.134 | -711.3924 | -419.403 | Yes | Yes | 59.3 | 0.582 | 2016
TI_2016-05-02_012000 | 2016-05-01 20:20 | 2016-05-01 20:20 | CDT | 2016-05-02 01:20 | 1311 | 60.013 | 59.957 | 59.704 | -0.056 | -0.309 | -2341.0714 | -424.2718 | Yes | Yes | 59.3 | 0.404 | 2016
TI_2016-05-05_173101 | 2016-05-05 12:31 | 2016-05-05 12:31 | CDT | 2016-05-05 17:31 | 627 | 60.013 | 59.907 | 59.867 | -0.106 | -0.146 | -591.5094 | -429.4521 | Yes | Yes | 59.3 | 0.567 | 2016
TI_2016-05-07_230030 | 2016-05-07 18:00 | 2016-05-07 18:00 | CDT | 2016-05-07 23:01 | 306.6249 | 59.9757 | 59.9353 | 59.909 | -0.040434 | -0.066714 | -758.3408 | -459.6082 | No | No | 59.3 | 0.609 | 2016
TI_2016-05-12_193129 | 2016-05-12 14:31 | 2016-05-12 14:31 | CDT | 2016-05-12 19:31 | 588 | 60.019 | 59.923 | 59.895 | -0.096 | -0.124 | -612.5 | -474.1935 | Yes | Yes | 59.3 | 0.595 | 2016
TI_2016-05-21_131849 | 2016-05-21 08:19 | 2016-05-21 08:19 | CDT | 2016-05-21 13:19 | 559 | 59.99 | 59.933 | 59.877 | -0.057 | -0.113 | -980.7018 | -494.6903 | Yes | Yes | 59.3 | 0.577 | 2016
TI_2016-05-26_073912 | 2016-05-26 02:39 | 2016-05-26 02:39 | CDT | 2016-05-26 07:39 | 454 | 59.969 | 59.928 | 59.87 | -0.041 | -0.099 | -1107.3171 | -458.5859 | Yes | Yes | 59.3 | 0.57 | 2016
TI_2016-06-06_212142 | 2016-06-06 16:22 | 2016-06-06 16:22 | CDT | 2016-06-06 21:22 | 517 | 60.001 | 59.937 | 59.894 | -0.064 | -0.107 | -807.8125 | -483.1776 | Yes | Yes | 59.3 | 0.594 | 2016
TI_2016-06-19_231433 | 2016-06-19 18:15 | 2016-06-19 18:15 | CDT | 2016-06-19 23:15 | 669 | 60.003 | 59.922 | 59.881 | -0.081 | -0.122 | -825.9259 | -548.3607 | Yes | Yes | 59.3 | 0.581 | 2016
TI_2016-06-24_194440 | 2016-06-24 14:45 | 2016-06-24 14:45 | CDT | 2016-06-24 19:45 | 484 | 59.958 | 59.911 | 59.879 | -0.047 | -0.079 | -1029.7872 | -612.6582 | Yes | Yes | 59.3 | 0.579 | 2016
TI_2016-07-07_180100 | 2016-07-07 13:01 | 2016-07-07 13:01 | CDT | 2016-07-07 18:01 | 634 | 59.949 | 59.902 | 59.848 | -0.047 | -0.101 | -1348.9362 | -627.7228 | Yes | Yes | 59.3 | 0.548 | 2016
TI_2016-07-10_061400 | 2016-07-10 01:14 | 2016-07-10 01:14 | CDT | 2016-07-10 06:14 | 541 | 59.954 | 59.905 | 59.858 | -0.049 | -0.096 | -1104.0816 | -563.5417 | Yes | Yes | 59.3 | 0.558 | 2016
TI_2016-07-10_235424 | 2016-07-10 18:54 | 2016-07-10 18:54 | CDT | 2016-07-10 23:54 | 1376 | 59.978 | 59.895 | 59.789 | -0.083 | -0.189 | -1657.8313 | -728.0423 | Yes | Yes | 59.3 | 0.489 | 2016
TI_2016-07-13_182959 | 2016-07-13 13:30 | 2016-07-13 13:30 | CDT | 2016-07-13 18:30 | 722.4432 | 59.988 | 59.913 | 59.857 | -0.075 | -0.131 | -963.2576 | -551.4834 | Yes | Yes | 59.3 | 0.557 | 2016
TI_2016-07-14_205050 | 2016-07-14 15:51 | 2016-07-14 15:51 | CDT | 2016-07-14 20:51 | 580.6546 | 59.987 | 59.912 | 59.887 | -0.075 | -0.1 | -774.2061 | -580.6546 | Yes | Yes | 59.3 | 0.587 | 2016
TI_2016-07-18_230318 | 2016-07-18 18:03 | 2016-07-18 18:03 | CDT | 2016-07-18 23:03 | 532.7941 | 59.96 | 59.902 | 59.857 | -0.058 | -0.103 | -918.6105 | -517.2758 | Yes | Yes | 59.3 | 0.557 | 2016
TI_2016-07-21_195322 | 2016-07-21 14:53 | 2016-07-21 14:53 | CDT | 2016-07-21 19:53 | 703.0527 | 60.009 | 59.892 | 59.878 | -0.117 | -0.131 | -600.8997 | -536.6815 | Yes | Yes | 59.3 | 0.578 | 2016
TI_2016-07-24_212252 | 2016-07-24 16:23 | 2016-07-24 16:23 | CDT | 2016-07-24 21:23 | 546.5757 | 60.01 | 59.903 | 59.891 | -0.107 | -0.119 | -510.8184 | -459.3073 | Yes | Yes | 59.3 | 0.591 | 2016
TI_2016-07-25_214551 | 2016-07-25 16:46 | 2016-07-25 16:46 | CDT | 2016-07-25 21:46 | 733.2143 | 59.991 | 59.906 | 59.875 | -0.085 | -0.116 | -862.6051 | -632.0813 | Yes | Yes | 59.3 | 0.575 | 2016
TI_2016-07-30_213909 | 2016-07-30 16:39 | 2016-07-30 16:39 | CDT | 2016-07-30 21:39 | 392.7446 | 60.011 | 59.944 | 59.926 | -0.067 | -0.085 | -586.186 | -462.0525 | No | No | 59.3 | 0.626 | 2016
TI_2016-08-02_233736 | 2016-08-02 18:38 | 2016-08-02 18:38 | CDT | 2016-08-02 23:38 | 526.3385 | 60.008 | 59.936 | 59.912 | -0.072 | -0.096 | -731.0257 | -548.2693 | Yes | Yes | 59.3 | 0.612 | 2016
TI_2016-08-16_003938 | 2016-08-15 19:40 | 2016-08-15 19:40 | CDT | 2016-08-16 00:40 | 855.8 | 59.998 | 59.906 | 59.83 | -0.092 | -0.168 | -930.2174 | -509.4048 | Yes | Yes | 59.3 | 0.53 | 2016
TI_2016-08-23_230520 | 2016-08-23 18:05 | 2016-08-23 18:05 | CDT | 2016-08-23 23:05 | -495 | 60.022 | 60.03 | 60.027 | 0.008 | 0.005 | -6187.5 | -9900 | No | No | 59.3 | 0.727 | 2016
TI_2016-08-27_194333 | 2016-08-27 14:44 | 2016-08-27 14:44 | CDT | 2016-08-27 19:44 | 484.0009 | 60.019 | 59.95 | 59.918 | -0.069 | -0.101 | -701.4506 | -479.2088 | Yes | Yes | 59.3 | 0.618 | 2016
TI_2016-08-28_191331 | 2016-08-28 14:14 | 2016-08-28 14:14 | CDT | 2016-08-28 19:14 | 533.7219 | 60.011 | 59.915 | 59.885 | -0.096 | -0.126 | -555.9603 | -423.5888 | Yes | Yes | 59.3 | 0.585 | 2016
TI_2016-08-31_075313 | 2016-08-31 02:53 | 2016-08-31 02:53 | CDT | 2016-08-31 07:53 | 596.3795 | 60.006 | 59.931 | 59.886 | -0.075 | -0.12 | -795.1727 | -496.9829 | Yes | Yes | 59.3 | 0.586 | 2016
TI_2016-08-31_181829 | 2016-08-31 13:18 | 2016-08-31 13:18 | CDT | 2016-08-31 18:18 | 453.4957 | 59.996 | 59.94 | 59.911 | -0.056 | -0.085 | -809.8137 | -533.5244 | Yes | Yes | 59.3 | 0.611 | 2016
TI_2016-09-08_182253 | 2016-09-08 13:23 | 2016-09-08 13:23 | CDT | 2016-09-08 18:23 | 581.5468 | 60.018 | 59.922 | 59.895 | -0.096 | -0.123 | -605.7779 | -472.8023 | Yes | Yes | 59.3 | 0.595 | 2016
TI_2016-09-18_141611 | 2016-09-18 09:16 | 2016-09-18 09:16 | CDT | 2016-09-18 14:16 | 452.8914 | 60.007 | 59.954 | 59.934 | -0.053 | -0.073 | -854.5121 | -620.3992 | Yes | Yes | 59.3 | 0.634 | 2016
TI_2016-09-18_170033 | 2016-09-18 12:01 | 2016-09-18 12:01 | CDT | 2016-09-18 17:01 | 436.7385 | 60.018 | 59.946 | 59.923 | -0.072 | -0.095 | -606.5812 | -459.7247 | Yes | Yes | 59.3 | 0.623 | 2016
TI_2016-09-19_212352 | 2016-09-19 16:24 | 2016-09-19 16:24 | CDT | 2016-09-19 21:24 | 418.9979 | 59.993 | 59.979 | 59.986 | -0.014 | -0.007 | -2992.8421 | -5985.6843 | No | No | 59.3 | 0.686 | 2016
TI_2016-10-06_202757 | 2016-10-06 15:28 | 2016-10-06 15:28 | CDT | 2016-10-06 20:28 | 573 | 59.996 | 59.917 | 59.853 | -0.079 | -0.143 | -725.3165 | -400.6993 | Yes | Yes | 59.3 | 0.553 | 2016
TI_2016-10-13_164610 | 2016-10-13 11:46 | 2016-10-13 11:46 | CDT | 2016-10-13 16:46 | 809 | 59.975 | 59.905 | 59.81 | -0.07 | -0.165 | -1155.7143 | -490.303 | Yes | Yes | 59.3 | 0.51 | 2016
TI_2016-10-23_193435 | 2016-10-23 14:35 | 2016-10-23 14:35 | CDT | 2016-10-23 19:35 | 621 | 59.968 | 59.905 | 59.835 | -0.063 | -0.133 | -985.7143 | -466.9173 | Yes | Yes | 59.3 | 0.535 | 2016
TI_2016-10-28_171433 | 2016-10-28 12:15 | 2016-10-28 12:15 | CDT | 2016-10-28 17:15 | 599 | 59.988 | 59.922 | 59.87 | -0.066 | -0.118 | -907.5758 | -507.6271 | Yes | Yes | 59.3 | 0.57 | 2016
TI_2016-11-03_193109 | 2016-11-03 14:31 | 2016-11-03 14:31 | CDT | 2016-11-03 19:31 | 816 | 60.012 | 59.872 | 59.801 | -0.14 | -0.211 | -582.8571 | -386.7299 | Yes | Yes | 59.3 | 0.501 | 2016
TI_2016-11-05_225621 | 2016-11-05 17:56 | 2016-11-05 17:56 | CDT | 2016-11-05 22:56 | 830 | 60.005 | 59.895 | 59.815 | -0.11 | -0.19 | -754.5455 | -436.8421 | Yes | Yes | 59.3 | 0.515 | 2016
TI_2016-11-19_183011 | 2016-11-19 12:30 | 2016-11-19 12:30 | CST | 2016-11-19 18:30 | 467 | 60.021 | 59.941 | 59.907 | -0.08 | -0.114 | -583.75 | -409.6491 | Yes | No | 59.3 | 0.607 | 2016
TI_2016-11-20_055430 | 2016-11-19 23:54 | 2016-11-19 23:54 | CST | 2016-11-20 05:54 | 372 | 60.024 | 60.017 | 60.018 | -0.007 | -0.006 | -5314.2857 | -6200 | No | No | 59.3 | 0.718 | 2016
TI_2016-11-29_144541 | 2016-11-29 08:46 | 2016-11-29 08:46 | CST | 2016-11-29 14:46 | 317 | 60.017 | 60.013 | 60.01 | -0.004 | -0.007 | -7925 | -4528.5714 | No | No | 59.3 | 0.71 | 2016
TI_2016-12-23_225410 | 2016-12-23 16:54 | 2016-12-23 16:54 | CST | 2016-12-23 22:54 | 570.159 | 60.009 | 59.909 | 59.867 | -0.1 | -0.142 | -570.159 | -401.5204 | Yes | Yes | 59.3 | 0.567 | 2017
TI_2017-01-07_055849 | 2017-01-06 23:59 | 2017-01-06 23:59 | CST | 2017-01-07 05:59 | 731 | 60.022 | 59.935 | 59.89 | -0.087 | -0.132 | -840.2299 | -553.7879 | Yes | Yes | 59.3 | 0.59 | 2017
TI_2017-01-24_035018 | 2017-01-23 21:50 | 2017-01-23 21:50 | CST | 2017-01-24 03:50 | 795.95 | 59.979 | 59.94 | 59.808 | -0.039 | -0.171 | -2040.8974 | -465.4678 | Yes | Yes | 59.3 | 0.508 | 2017
TI_2017-02-14_055237 | 2017-02-13 23:53 | 2017-02-13 23:53 | CST | 2017-02-14 05:53 | 447 | 60.028 | 59.942 | 59.909 | -0.086 | -0.119 | -519.7674 | -375.6303 | Yes | Yes | 59.3 | 0.609 | 2017
TI_2017-02-20_044905 | 2017-02-19 22:49 | 2017-02-19 22:49 | CST | 2017-02-20 04:49 | 429 | 59.941 | 59.886 | 59.842 | -0.055 | -0.099 | -780 | -433.3333 | Yes | Yes | 59.3 | 0.542 | 2017
TI_2017-03-10_003646 | 2017-03-09 18:37 | 2017-03-09 18:37 | CST | 2017-03-10 00:37 | 823 | 60.023 | 59.923 | 59.796 | -0.1 | -0.227 | -823 | -362.5551 | Yes | Yes | 59.3 | 0.496 | 2017
TI_2017-03-15_032054 | 2017-03-14 22:21 | 2017-03-14 22:21 | CDT | 2017-03-15 03:21 | 375 | 59.977 | 59.921 | 59.879 | -0.056 | -0.098 | -669.6429 | -382.6531 | Yes | Yes | 59.3 | 0.579 | 2017
TI_2017-03-15_063619 | 2017-03-15 01:36 | 2017-03-15 01:36 | CDT | 2017-03-15 06:36 | 811 | 60.011 | 59.886 | 59.778 | -0.125 | -0.233 | -648.8 | -348.0687 | No | No | 59.3 | 0.478 | 2017
TI_2017-03-30_005425 | 2017-03-29 19:54 | 2017-03-29 19:54 | CDT | 2017-03-30 00:54 | 727 | 59.965 | 59.885 | 59.801 | -0.08 | -0.164 | -908.75 | -443.2927 | Yes | Yes | 59.3 | 0.501 | 2017
TI_2017-04-07_013200 | 2017-04-06 20:32 | 2017-04-06 20:32 | CDT | 2017-04-07 01:32 | 297.52 | 60.012 | 59.958 | 59.926 | -0.054 | -0.086 | -550.963 | -345.9535 | Yes | No | 59.3 | 0.626 | 2017
TI_2017-04-10_220259 | 2017-04-10 17:03 | 2017-04-10 17:03 | CDT | 2017-04-10 22:03 | 343.7 | 59.996 | 59.949 | 59.909 | -0.047 | -0.087 | -731.2766 | -395.0575 | Yes | Yes | 59.3 | 0.609 | 2017
TI_2017-04-13_141433 | 2017-04-13 09:15 | 2017-04-13 09:15 | CDT | 2017-04-13 14:15 | 559.75 | 60.009 | 59.9 | 59.856 | -0.109 | -0.153 | -513.5321 | -365.8497 | Yes | Yes | 59.3 | 0.556 | 2017
TI_2017-04-16_134750 | 2017-04-16 08:48 | 2017-04-16 08:48 | CDT | 2017-04-16 13:48 | 368.55 | 60.011 | 59.936 | 59.903 | -0.075 | -0.108 | -491.4 | -341.25 | Yes | Yes | 59.3 | 0.603 | 2017
TI_2017-04-26_232926 | 2017-04-26 18:29 | 2017-04-26 18:29 | CDT | 2017-04-26 23:29 | 438 | 59.975 | 59.936 | 59.892 | -0.039 | -0.083 | -1123.0769 | -527.7108 | Yes | Yes | 59.3 | 0.592 | 2017
TI_2017-04-30_103148 | 2017-04-30 05:32 | 2017-04-30 05:32 | CDT | 2017-04-30 10:32 | 299.21 | 60.016 | 59.984 | 59.906 | -0.032 | -0.11 | -935.0313 | -272.0091 | Yes | No | 59.3 | 0.606 | 2017
TI_2017-05-11_013847 | 2017-05-10 20:39 | 2017-05-10 20:39 | CDT | 2017-05-11 01:39 | 380.79 | 59.992 | 59.94 | 59.908 | -0.052 | -0.084 | -732.2885 | -453.3214 | Yes | Yes | 59.3 | 0.608 | 2017
TI_2017-05-11_195357 | 2017-05-11 14:54 | 2017-05-11 14:54 | CDT | 2017-05-11 19:54 | 487 | 60.013 | 59.956 | 59.913 | -0.057 | -0.1 | -854.386 | -487 | Yes | No | 59.3 | 0.613 | 2017
TI_2017-05-17_032529 | 2017-05-16 22:25 | 2017-05-16 22:25 | CDT | 2017-05-17 03:25 | 189.79 | 59.938 | 59.926 | 59.9 | -0.012 | -0.038 | -1581.5833 | -499.4474 | No | No | 59.3 | 0.6 | 2017
TI_2017-05-19_220004 | 2017-05-19 17:00 | 2017-05-19 17:00 | CDT | 2017-05-19 22:00 | 339.88 | 59.981 | 59.944 | 59.896 | -0.037 | -0.085 | -918.5946 | -399.8588 | Yes | Yes | 59.3 | 0.596 | 2017
TI_2017-05-20_002534 | 2017-05-19 19:26 | 2017-05-19 19:26 | CDT | 2017-05-20 00:26 | 416.16 | 60.014 | 59.948 | 59.914 | -0.066 | -0.1 | -630.5455 | -416.16 | Yes | No | 59.3 | 0.614 | 2017
TI_2017-05-21_232501 | 2017-05-21 18:25 | 2017-05-21 18:25 | CDT | 2017-05-21 23:25 | 447.93 | 60.01 | 59.946 | 59.895 | -0.064 | -0.115 | -699.8906 | -389.5043 | Yes | Yes | 59.3 | 0.595 | 2017
TI_2017-05-23_185928 | 2017-05-23 13:59 | 2017-05-23 13:59 | CDT | 2017-05-23 18:59 | 214.64 | 59.975 | 59.934 | 59.914 | -0.041 | -0.061 | -523.5122 | -351.8689 | No | No | 59.3 | 0.614 | 2017
TI_2017-05-30_203900 | 2017-05-30 15:39 | 2017-05-30 15:39 | CDT | 2017-05-30 20:39 | 638.3 | 59.987 | 59.956 | 59.935 | -0.031 | -0.052 | -2059.0323 | -1227.5 | No | No | 59.3 | 0.635 | 2017
TI_2017-06-02_150306 | 2017-06-02 10:03 | 2017-06-02 10:03 | CDT | 2017-06-02 15:03 | 589 | 60.017 | 59.936 | 59.899 | -0.081 | -0.118 | -727.1605 | -499.1525 | Yes | Yes | 59.3 | 0.599 | 2017
TI_2017-06-06_230758 | 2017-06-06 18:08 | 2017-06-06 18:08 | CDT | 2017-06-06 23:08 | 452 | 60.012 | 59.938 | 59.9 | -0.074 | -0.112 | -610.8108 | -403.5714 | Yes | Yes | 59.3 | 0.6 | 2017
TI_2017-06-07_222500 | 2017-06-07 17:25 | 2017-06-07 17:25 | CDT | 2017-06-07 22:25 | 472 | 59.961 | 59.919 | 59.88 | -0.042 | -0.081 | -1123.8095 | -582.716 | Yes | Yes | 59.3 | 0.58 | 2017
TI_2017-06-08_170314 | 2017-06-08 12:03 | 2017-06-08 12:03 | CDT | 2017-06-08 17:03 | 444 | 59.988 | 59.948 | 59.906 | -0.04 | -0.082 | -1110 | -541.4634 | No | No | 59.3 | 0.606 | 2017
TI_2017-06-11_085231 | 2017-06-11 03:53 | 2017-06-11 03:53 | CDT | 2017-06-11 08:53 | 443 | 60.01 | 59.944 | 59.904 | -0.066 | -0.106 | -671.2121 | -417.9245 | Yes | Yes | 59.3 | 0.604 | 2017
TI_2017-06-12_024213 | 2017-06-11 21:42 | 2017-06-11 21:42 | CDT | 2017-06-12 02:42 | 848 | 60.016 | 59.903 | 59.837 | -0.113 | -0.179 | -750.4425 | -473.743 | Yes | Yes | 59.3 | 0.537 | 2017
TI_2017-06-14_215531 | 2017-06-14 16:56 | 2017-06-14 16:56 | CDT | 2017-06-14 21:56 | 522 | 60.012 | 59.931 | 59.908 | -0.081 | -0.104 | -644.4444 | -501.9231 | Yes | No | 59.3 | 0.608 | 2017
TI_2017-06-16_124623 | 2017-06-16 07:46 | 2017-06-16 07:46 | CDT | 2017-06-16 12:46 | 550 | 59.979 | 59.941 | 59.885 | -0.038 | -0.094 | -1447.3684 | -585.1064 | Yes | Yes | 59.3 | 0.585 | 2017
TI_2017-06-16_211423 | 2017-06-16 16:14 | 2017-06-16 16:14 | CDT | 2017-06-16 21:14 | 508 | 60.005 | 59.939 | 59.909 | -0.066 | -0.096 | -769.697 | -529.1667 | Yes | No | 59.3 | 0.609 | 2017
TI_2017-06-19_141019 | 2017-06-19 09:10 | 2017-06-19 09:10 | CDT | 2017-06-19 14:10 | 449 | 60.013 | 59.952 | 59.926 | -0.061 | -0.087 | -736.0656 | -516.092 | Yes | No | 59.3 | 0.626 | 2017
TI_2017-06-27_205033 | 2017-06-27 15:51 | 2017-06-27 15:51 | CDT | 2017-06-27 20:51 | 594 | 60 | 59.925 | 59.871 | -0.075 | -0.129 | -792 | -460.4651 | Yes | Yes | 59.3 | 0.571 | 2017
TI_2017-07-02_051935 | 2017-07-02 00:20 | 2017-07-02 00:20 | CDT | 2017-07-02 05:20 | 595.5216 | 59.998 | 59.921 | 59.869 | -0.077 | -0.129 | -773.4047 | -461.6447 | Yes | Yes | 59.3 | 0.569 | 2017
TI_2017-07-07_052756 | 2017-07-07 00:28 | 2017-07-07 00:28 | CDT | 2017-07-07 05:28 | 424.592 | 60.022 | 59.967 | 59.931 | -0.055 | -0.091 | -771.9855 | -466.5846 | Yes | No | 59.3 | 0.631 | 2017
TI_2017-07-26_193039 | 2017-07-26 14:31 | 2017-07-26 14:31 | CDT | 2017-07-26 19:31 | 702.0165 | 59.994 | 59.894 | 59.852 | -0.1 | -0.142 | -702.0165 | -494.3778 | Yes | Yes | 59.3 | 0.552 | 2017
TI_2017-08-04_185054 | 2017-08-04 13:51 | 2017-08-04 13:51 | CDT | 2017-08-04 18:51 | 345.1563 | 59.97 | 59.936 | 59.908 | -0.034 | -0.062 | -1015.1655 | -556.7037 | No | No | 59.3 | 0.608 | 2017
TI_2017-08-05_233148 | 2017-08-05 18:32 | 2017-08-05 18:32 | CDT | 2017-08-05 23:32 | 434.0527 | 60.007 | 59.952 | 59.928 | -0.055 | -0.079 | -789.1868 | -549.4338 | No | No | 59.3 | 0.628 | 2017
TI_2017-08-09_233354 | 2017-08-09 18:34 | 2017-08-09 18:34 | CDT | 2017-08-09 23:34 | 700.4571 | 60.016 | 59.905 | 59.865 | -0.111 | -0.151 | -631.0425 | -463.8789 | Yes | Yes | 59.3 | 0.565 | 2017
TI_2017-08-23_175125 | 2017-08-23 12:51 | 2017-08-23 12:51 | CDT | 2017-08-23 17:51 | 797.1952 | 59.993 | 59.893 | 59.841 | -0.1 | -0.152 | -797.1952 | -524.4705 | Yes | Yes | 59.3 | 0.541 | 2017
TI_2017-08-28_204759 | 2017-08-28 15:48 | 2017-08-28 15:48 | CDT | 2017-08-28 20:48 | 439.6464 | 59.99 | 59.956 | 59.905 | -0.034 | -0.085 | -1293.0776 | -517.231 | Yes | No | 59.3 | 0.605 | 2017
TI_2017-09-01_215608 | 2017-09-01 16:56 | 2017-09-01 16:56 | CDT | 2017-09-01 21:56 | 456.46 | 59.985 | 59.941 | 59.891 | -0.044 | -0.094 | -1037.4091 | -485.5957 | Yes | Yes | 59.3 | 0.591 | 2017
TI_2017-09-02_024145 | 2017-09-01 21:42 | 2017-09-01 21:42 | CDT | 2017-09-02 02:42 | 1203.57 | 59.989 | 59.906 | 59.757 | -0.083 | -0.232 | -1450.0843 | -518.7802 | Yes | Yes | 59.3 | 0.457 | 2017
TI_2017-09-09_170940 | 2017-09-09 12:10 | 2017-09-09 12:10 | CDT | 2017-09-09 17:10 | 524.86 | 59.979 | 59.936 | 59.889 | -0.043 | -0.09 | -1220.6047 | -583.1778 | Yes | Yes | 59.3 | 0.589 | 2017
TI_2017-09-15_225045 | 2017-09-15 17:51 | 2017-09-15 17:51 | CDT | 2017-09-15 22:51 | 812.11 | 60.014 | 59.906 | 59.834 | -0.108 | -0.18 | -751.9537 | -451.1722 | Yes | Yes | 59.3 | 0.534 | 2017
TI_2017-09-17_211304 | 2017-09-17 16:13 | 2017-09-17 16:13 | CDT | 2017-09-17 21:13 | 175.12 | 60.014 | 59.973 | 59.943 | -0.041 | -0.071 | -427.122 | -246.6479 | No | No | 59.3 | 0.643 | 2017
TI_2017-09-17_224050 | 2017-09-17 17:41 | 2017-09-17 17:41 | CDT | 2017-09-17 22:41 | 387.93 | 60.016 | 59.969 | 59.928 | -0.047 | -0.088 | -825.383 | -440.8295 | Yes | No | 59.3 | 0.628 | 2017
TI_2017-09-20_044356 | 2017-09-19 23:44 | 2017-09-19 23:44 | CDT | 2017-09-20 04:44 | 447.83 | 59.964 | 59.919 | 59.885 | -0.045 | -0.079 | -995.1778 | -566.8734 | No | No | 59.3 | 0.585 | 2017
TI_2017-09-26_200504 | 2017-09-26 15:05 | 2017-09-26 15:05 | CDT | 2017-09-26 20:05 | 403 | 60.015 | 59.965 | 59.958 | -0.05 | -0.057 | -806 | -707.0175 | No | No | 59.3 | 0.658 | 2017
TI_2017-10-06_161637 | 2017-10-06 11:17 | 2017-10-06 11:17 | CDT | 2017-10-06 16:17 | 831 | 60.009 | 59.91 | 59.848 | -0.099 | -0.161 | -839.3939 | -516.1491 | Yes | Yes | 59.3 | 0.548 | 2017
TI_2017-10-08_100054 | 2017-10-08 05:01 | 2017-10-08 05:01 | CDT | 2017-10-08 10:01 | 692 | 59.987 | 59.925 | 59.854 | -0.062 | -0.133 | -1116.129 | -520.3008 | Yes | Yes | 59.3 | 0.554 | 2017
TI_2017-10-28_104109 | 2017-10-28 05:41 | 2017-10-28 05:41 | CDT | 2017-10-28 10:41 | 536 | 60.018 | 59.941 | 59.9 | -0.077 | -0.118 | -696.1039 | -454.2373 | Yes | No | 59.3 | 0.6 | 2017
TI_2017-10-30_002415 | 2017-10-29 19:24 | 2017-10-29 19:24 | CDT | 2017-10-30 00:24 | 561 | 60.007 | 59.925 | 59.873 | -0.082 | -0.134 | -684.1463 | -418.6567 | Yes | Yes | 59.3 | 0.573 | 2017
TI_2017-10-30_112843 | 2017-10-30 06:29 | 2017-10-30 06:29 | CDT | 2017-10-30 11:29 | 348 | 60.009 | 59.954 | 59.909 | -0.055 | -0.1 | -632.7273 | -348 | Yes | No | 59.3 | 0.609 | 2017
TI_2017-11-06_150819 | 2017-11-06 09:08 | 2017-11-06 09:08 | CST | 2017-11-06 15:08 | 550 | 60.019 | 59.947 | 59.898 | -0.072 | -0.121 | -763.8889 | -454.5455 | Yes | Yes | 59.3 | 0.598 | 2017
TI_2017-11-13_211610 | 2017-11-13 15:16 | 2017-11-13 15:16 | CST | 2017-11-13 21:16 | 660 | 60.006 | 59.91 | 59.862 | -0.096 | -0.144 | -687.5 | -458.3333 | Yes | Yes | 59.3 | 0.562 | 2017
TI_2017-11-18_083034 | 2017-11-18 02:31 | 2017-11-18 02:31 | CST | 2017-11-18 08:31 | 474 | 60.016 | 59.942 | 59.879 | -0.074 | -0.137 | -640.5405 | -345.9854 | Yes | Yes | 59.3 | 0.579 | 2017
TI_2017-11-26_022432 | 2017-11-25 20:25 | 2017-11-25 20:25 | CST | 2017-11-26 02:25 | 1219 | 60.005 | 59.882 | 59.733 | -0.123 | -0.272 | -991.0569 | -448.1618 | No | No | 59.3 | 0.433 | 2017
TI_2017-12-05_180510 | 2017-12-05 12:05 | 2017-12-05 12:05 | CST | 2017-12-05 18:05 | 293.6562 | 59.966 | 59.942 | 59.908 | -0.024 | -0.058 | -1223.5673 | -506.3037 | No | No | 59.3 | 0.608 | 2018
TI_2017-12-08_022411 | 2017-12-07 20:24 | 2017-12-07 20:24 | CST | 2017-12-08 02:24 | 707.4428 | 59.996 | 59.958 | 59.928 | -0.038 | -0.068 | -1861.6917 | -1040.3571 | Yes | No | 59.3 | 0.628 | 2018
TI_2017-12-17_175435 | 2017-12-17 11:55 | 2017-12-17 11:55 | CST | 2017-12-17 17:55 | 173.357 | 59.95 | 59.932 | 59.906 | -0.018 | -0.044 | -963.0946 | -393.9932 | No | No | 59.3 | 0.606 | 2018
TI_2017-12-26_042705 | 2017-12-25 22:27 | 2017-12-25 22:27 | CST | 2017-12-26 04:27 | 357.8714 | 60.009 | 59.952 | 59.912 | -0.057 | -0.097 | -627.8446 | -368.9396 | Yes | No | 59.3 | 0.612 | 2018
TI_2017-12-29_190718 | 2017-12-29 13:07 | 2017-12-29 13:07 | CST | 2017-12-29 19:07 | 427.7949 | 59.993 | 59.947 | 59.96 | -0.046 | -0.033 | -929.9888 | -1296.3481 | No | No | 59.3 | 0.66 | 2018
TI_2017-12-30_170529 | 2017-12-30 11:05 | 2017-12-30 11:05 | CST | 2017-12-30 17:05 | 266.0914 | 59.97 | 59.96 | 59.923 | -0.01 | -0.047 | -2660.9144 | -566.152 | No | No | 59.3 | 0.623 | 2018
TI_2018-01-01_094815 | 2018-01-01 03:48 | 2018-01-01 03:48 | CST | 2018-01-01 09:48 | 307 | 59.978 | 59.959 | 59.936 | -0.019 | -0.042 | -1615.7895 | -730.9524 | No | No | 59.3 | 0.636 | 2018
TI_2018-01-01_140551 | 2018-01-01 08:06 | 2018-01-01 08:06 | CST | 2018-01-01 14:06 | 487 | 60 | 59.945 | 59.988 | -0.055 | -0.012 | -885.4545 | -4058.3333 | No | No | 59.3 | 0.688 | 2018
TI_2018-01-05_151055 | 2018-01-05 09:11 | 2018-01-05 09:11 | CST | 2018-01-05 15:11 | 496 | 59.982 | 59.955 | 59.902 | -0.027 | -0.08 | -1837.037 | -620 | Yes | No | 59.3 | 0.602 | 2018
TI_2018-01-16_142421 | 2018-01-16 08:24 | 2018-01-16 08:24 | CST | 2018-01-16 14:24 | 354 | 59.99 | 59.959 | 59.945 | -0.031 | -0.045 | -1141.9355 | -786.6667 | No | No | 59.3 | 0.645 | 2018
TI_2018-01-17_124433 | 2018-01-17 06:45 | 2018-01-17 06:45 | CST | 2018-01-17 12:45 | 606 | 59.994 | 59.946 | 59.92 | -0.048 | -0.074 | -1262.5 | -818.9189 | Yes | No | 59.3 | 0.62 | 2018
TI_2018-02-03_054634 | 2018-02-02 23:47 | 2018-02-02 23:47 | CST | 2018-02-03 05:47 | 292.4171 | 59.949 | 59.91 | 59.878 | -0.039 | -0.071 | -749.7874 | -411.855 | No | No | 59.3 | 0.578 | 2018
TI_2018-02-05_200441 | 2018-02-05 14:05 | 2018-02-05 14:05 | CST | 2018-02-05 20:05 | 816.0282 | 59.996 | 59.899 | 59.822 | -0.097 | -0.174 | -841.2662 | -468.9817 | Yes | Yes | 59.3 | 0.522 | 2018
TI_2018-02-07_001940 | 2018-02-06 18:20 | 2018-02-06 18:20 | CST | 2018-02-07 00:20 | 362.6292 | 59.969 | 59.94 | 59.897 | -0.029 | -0.072 | -1250.4456 | -503.6517 | No | No | 59.3 | 0.597 | 2018
TI_2018-02-14_123017 | 2018-02-14 06:30 | 2018-02-14 06:30 | CST | 2018-02-14 12:30 | 784.1693 | 60.016 | 59.911 | 59.853 | -0.105 | -0.163 | -746.8279 | -481.0855 | Yes | Yes | 59.3 | 0.553 | 2018
TI_2018-02-22_123901 | 2018-02-22 06:39 | 2018-02-22 06:39 | CST | 2018-02-22 12:39 | 491.2309 | 60.012 | 59.961 | 59.923 | -0.051 | -0.089 | -963.1979 | -551.9448 | Yes | No | 59.3 | 0.623 | 2018
TI_2018-02-22_212456 | 2018-02-22 15:25 | 2018-02-22 15:25 | CST | 2018-02-22 21:25 | 328.057 | 59.981 | 59.962 | 59.918 | -0.019 | -0.063 | -1726.616 | -520.7255 | No | No | 59.3 | 0.618 | 2018
TI_2018-03-05_125119 | 2018-03-05 06:51 | 2018-03-05 06:51 | CST | 2018-03-05 12:51 | 513.4751 | 59.983 | 59.95 | 59.882 | -0.033 | -0.101 | -1555.985 | -508.3911 | Yes | Yes | 59.3 | 0.582 | 2018
TI_2018-03-25_014715 | 2018-03-24 20:47 | 2018-03-24 20:47 | CDT | 2018-03-25 01:47 | 797.2537 | 60.013 | 59.928 | 59.851 | -0.085 | -0.162 | -937.9456 | -492.1319 | Yes | Yes | 59.3 | 0.551 | 2018
TI_2018-03-29_013525 | 2018-03-28 20:35 | 2018-03-28 20:35 | CDT | 2018-03-29 01:35 | 354.1014 | 59.98 | 59.951 | 59.905 | -0.029 | -0.075 | -1221.0392 | -472.1352 | No | No | 59.3 | 0.605 | 2018
TI_2018-03-29_210939 | 2018-03-29 16:10 | 2018-03-29 16:10 | CDT | 2018-03-29 21:10 | 434.0501 | 59.975 | 59.934 | 59.889 | -0.041 | -0.086 | -1058.6588 | -504.7094 | Yes | Yes | 59.3 | 0.589 | 2018
TI_2018-04-14_070203 | 2018-04-14 02:02 | 2018-04-14 02:02 | CDT | 2018-04-14 07:02 | 438 | 60.019 | 59.944 | 59.894 | -0.075 | -0.125 | -584 | -350.4 | Yes | Yes | 59.3 | 0.594 | 2018
TI_2018-04-15_061100 | 2018-04-15 01:11 | 2018-04-15 01:11 | CDT | 2018-04-15 06:11 | 349 | 60.003 | 59.956 | 59.908 | -0.047 | -0.095 | -742.5532 | -367.3684 | Yes | No | 59.3 | 0.608 | 2018
TI_2018-04-18_152011 | 2018-04-18 10:20 | 2018-04-18 10:20 | CDT | 2018-04-18 15:20 | 460 | 60.012 | 59.954 | 59.912 | -0.058 | -0.1 | -793.1034 | -460 | Yes | No | 59.3 | 0.612 | 2018
TI_2018-04-21_221100 | 2018-04-21 17:11 | 2018-04-21 17:11 | CDT | 2018-04-21 22:11 | 1250 | 59.969 | 59.949 | 59.709 | -0.02 | -0.26 | -6250 | -480.7692 | No | No | 59.3 | 0.409 | 2018
TI_2018-04-28_231539 | 2018-04-28 18:16 | 2018-04-28 18:16 | CDT | 2018-04-28 23:16 | 408 | 60.013 | 59.964 | 59.909 | -0.049 | -0.104 | -832.6531 | -392.3077 | No | No | 59.3 | 0.609 | 2018
TI_2018-05-05_211859 | 2018-05-05 16:19 | 2018-05-05 16:19 | CDT | 2018-05-05 21:19 | 536.286 | 60.006 | 59.912 | 59.873 | -0.094 | -0.133 | -570.517 | -403.2226 | Yes | Yes | 59.3 | 0.573 | 2018
TI_2018-05-21_130619 | 2018-05-21 08:06 | 2018-05-21 08:06 | CDT | 2018-05-21 13:06 | 460.498 | 59.997 | 59.915 | 59.887 | -0.082 | -0.11 | -561.5829 | -418.6345 | Yes | Yes | 59.3 | 0.587 | 2018
TI_2018-05-23_234243 | 2018-05-23 18:43 | 2018-05-23 18:43 | CDT | 2018-05-23 23:43 | 393.207 | 60.004 | 59.97 | 59.931 | -0.034 | -0.073 | -1156.4913 | -538.6398 | No | No | 59.3 | 0.631 | 2018
TI_2018-06-08_132307 | 2018-06-08 08:23 | 2018-06-08 08:23 | CDT | 2018-06-08 13:23 | 423 | 60.008 | 59.948 | 59.922 | -0.06 | -0.086 | -705 | -491.8605 | Yes | No | 59.3 | 0.622 | 2018
TI_2018-07-02_083603 | 2018-07-02 03:36 | 2018-07-02 03:36 | CDT | 2018-07-02 08:36 | 414.2064 | 60.006 | 59.96 | 59.919 | -0.046 | -0.087 | -900.4486 | -476.0993 | Yes | No | 59.3 | 0.619 | 2018
TI_2018-07-06_181053 | 2018-07-06 13:11 | 2018-07-06 13:11 | CDT | 2018-07-06 18:11 | 812.6879 | 60.018 | 59.917 | 59.886 | -0.101 | -0.132 | -804.6415 | -615.6727 | Yes | Yes | 59.3 | 0.586 | 2018
TI_2018-07-18_224455 | 2018-07-18 17:45 | 2018-07-18 17:45 | CDT | 2018-07-18 22:45 | 494.3177 | 59.977 | 59.926 | 59.89 | -0.051 | -0.087 | -969.2505 | -568.1813 | Yes | Yes | 59.3 | 0.59 | 2018
TI_2018-07-30_190110 | 2018-07-30 14:01 | 2018-07-30 14:01 | CDT | 2018-07-30 19:01 | 827.4857 | 60.005 | 59.877 | 59.896 | -0.128 | -0.109 | -646.4732 | -759.1612 | No | No | 59.3 | 0.596 | 2018
TI_2018-08-04_132033 | 2018-08-04 08:21 | 2018-08-04 08:21 | CDT | 2018-08-04 13:21 | 366.21 | 59.956 | 59.935 | 59.895 | -0.021 | -0.061 | -1743.8571 | -600.3443 | No | No | 59.3 | 0.595 | 2018
TI_2018-08-11_192122 | 2018-08-11 14:21 | 2018-08-11 14:21 | CDT | 2018-08-11 19:21 | 437.92 | 60.025 | 59.977 | 59.928 | -0.048 | -0.097 | -912.3333 | -451.4639 | Yes | No | 59.3 | 0.628 | 2018
TI_2018-08-14_035953 | 2018-08-13 23:00 | 2018-08-13 23:00 | CDT | 2018-08-14 04:00 | 1197.88 | 59.996 | 59.912 | 59.798 | -0.084 | -0.198 | -1426.0476 | -604.9899 | Yes | Yes | 59.3 | 0.498 | 2018
TI_2018-08-15_231039 | 2018-08-15 18:11 | 2018-08-15 18:11 | CDT | 2018-08-15 23:11 | 486.54 | 59.949 | 59.894 | 59.859 | -0.055 | -0.09 | -884.6182 | -540.6 | No | No | 59.3 | 0.559 | 2018
TI_2018-08-18_211225 | 2018-08-18 16:12 | 2018-08-18 16:12 | CDT | 2018-08-18 21:12 | 717.8 | 59.979 | 59.901 | 59.852 | -0.078 | -0.127 | -920.2564 | -565.1969 | Yes | Yes | 59.3 | 0.552 | 2018
TI_2018-08-31_170354 | 2018-08-31 12:04 | 2018-08-31 12:04 | CDT | 2018-08-31 17:04 | 526.96 | 59.988 | 59.947 | 59.9 | -0.041 | -0.088 | -1285.2683 | -598.8182 | Yes | Yes | 59.3 | 0.6 | 2018
TI_2018-09-01_000000 | 2018-08-31 19:00 | 2018-08-31 19:00 | CDT | 2018-09-01 | 645.7793 | 60.014 | 59.943 | 59.908 | -0.071 | -0.106 | -909.5483 | -609.2258 | Yes | No | 59.3 | 0.608 | 2018
TI_2018-09-04_151215 | 2018-09-04 10:12 | 2018-09-04 10:12 | CDT | 2018-09-04 15:12 | 318.1953 | 60.011 | 59.964 | 59.934 | -0.047 | -0.077 | -677.0112 | -413.2406 | No | No | 59.3 | 0.634 | 2018
TI_2018-09-05_003017 | 2018-09-04 19:30 | 2018-09-04 19:30 | CDT | 2018-09-05 00:30 | 860.34 | 60.014 | 59.912 | 59.839 | -0.102 | -0.175 | -843.4706 | -491.6229 | Yes | Yes | 59.3 | 0.539 | 2018
TI_2018-09-12_222010 | 2018-09-12 17:20 | 2018-09-12 17:20 | CDT | 2018-09-12 22:20 | 366.8224 | 60 | 59.946 | 59.915 | -0.054 | -0.085 | -679.3008 | -431.5558 | Yes | No | 59.3 | 0.615 | 2018
TI_2018-09-13_112837 | 2018-09-13 06:29 | 2018-09-13 06:29 | CDT | 2018-09-13 11:29 | 387.3 | 60.01 | 59.961 | 59.927 | -0.049 | -0.083 | -790.4081 | -466.6265 | Yes | No | 59.3 | 0.627 | 2018
TI_2018-09-16_192853 | 2018-09-16 14:29 | 2018-09-16 14:29 | CDT | 2018-09-16 19:29 | 373.3264 | 59.991 | 59.962 | 59.909 | -0.029 | -0.082 | -1287.3324 | -455.2761 | Yes | No | 59.3 | 0.609 | 2018
TI_2018-09-18_205106 | 2018-09-18 15:51 | 2018-09-18 15:51 | CDT | 2018-09-18 20:51 | 426.0926 | 60.008 | 59.959 | 59.923 | -0.049 | -0.085 | -869.5767 | -501.2854 | Yes | No | 59.3 | 0.623 | 2018
TI_2018-09-20_014316 | 2018-09-19 20:43 | 2018-09-19 20:43 | CDT | 2018-09-20 01:43 | 769.15 | 59.974 | 59.899 | 59.825 | -0.075 | -0.149 | -1025.5334 | -516.2081 | Yes | Yes | 59.3 | 0.525 | 2018
TI_2018-09-24_063911 | 2018-09-24 01:39 | 2018-09-24 01:39 | CDT | 2018-09-24 06:39 | 653.2183 | 59.978 | 59.924 | 59.857 | -0.054 | -0.121 | -1209.6634 | -539.8498 | Yes | Yes | 59.3 | 0.557 | 2018
TI_2018-09-26_185400 | 2018-09-26 13:54 | 2018-09-26 13:54 | CDT | 2018-09-26 18:54 | 1017.9796 | 60.005 | 59.883 | 59.85 | -0.122 | -0.155 | -834.4095 | -656.761 | No | No | 59.3 | 0.55 | 2018
TI_2018-09-28_061153 | 2018-09-28 01:12 | 2018-09-28 01:12 | CDT | 2018-09-28 06:12 | 843.7714 | 60.009 | 59.908 | 59.906 | -0.101 | -0.103 | -835.4173 | -819.1956 | No | No | 59.3 | 0.606 | 2018
TI_2018-09-28_170008 | 2018-09-28 12:00 | 2018-09-28 12:00 | CDT | 2018-09-28 17:00 | 826.0893 | 59.98 | 59.892 | 59.887 | -0.088 | -0.093 | -938.7378 | -888.268 | No | No | 59.3 | 0.587 | 2018
TI_2018-10-13_082331 | 2018-10-13 03:24 | 2018-10-13 03:24 | CDT | 2018-10-13 08:24 | 368.7 | 60.011 | 59.955 | 59.907 | -0.056 | -0.104 | -658.3928 | -354.5192 | Yes | No | 59.3 | 0.607 | 2018
TI_2018-10-15_112934 | 2018-10-15 06:30 | 2018-10-15 06:30 | CDT | 2018-10-15 11:30 | 422 | 60.003 | 59.943 | 59.902 | -0.06 | -0.101 | -703.3333 | -417.8218 | Yes | No | 59.3 | 0.602 | 2018
TI_2018-10-17_011523 | 2018-10-16 20:15 | 2018-10-16 20:15 | CDT | 2018-10-17 01:15 | 475.1643 | 60.013 | 59.937 | 59.904 | -0.076 | -0.109 | -625.2162 | -435.9305 | Yes | No | 59.3 | 0.604 | 2018
TI_2018-10-19_202319 | 2018-10-19 15:23 | 2018-10-19 15:23 | CDT | 2018-10-19 20:23 | 630.4293 | 60.001 | 59.913 | 59.859 | -0.088 | -0.142 | -716.397 | -443.9643 | Yes | Yes | 59.3 | 0.559 | 2018
TI_2018-10-27_174356 | 2018-10-27 12:44 | 2018-10-27 12:44 | CDT | 2018-10-27 17:44 | 331.217 | 60.004 | 59.966 | 59.918 | -0.038 | -0.086 | -871.6237 | -385.1361 | Yes | No | 59.3 | 0.618 | 2018
TI_2018-11-06_135325 | 2018-11-06 07:53 | 2018-11-06 07:53 | CST | 2018-11-06 13:53 | 428.2471 | 59.998 | 59.943 | 59.953 | -0.055 | -0.045 | -778.631 | -951.6601 | No | No | 59.3 | 0.653 | 2018
TI_2018-11-10_152518 | 2018-11-10 09:25 | 2018-11-10 09:25 | CST | 2018-11-10 15:25 | 515.9929 | 60.015 | 59.961 | 59.904 | -0.054 | -0.111 | -955.5423 | -464.8584 | Yes | No | 59.3 | 0.604 | 2018
TI_2018-11-15_043020 | 2018-11-14 22:30 | 2018-11-14 22:30 | CST | 2018-11-15 04:30 | 454.3286 | 60.013 | 59.953 | 59.917 | -0.06 | -0.096 | -757.2143 | -473.2589 | Yes | No | 59.3 | 0.617 | 2018
TI_2018-11-20_052651 | 2018-11-19 23:27 | 2018-11-19 23:27 | CST | 2018-11-20 05:27 | 317.5774 | 59.981 | 59.956 | 59.92 | -0.025 | -0.061 | -1270.3097 | -520.6187 | No | No | 59.3 | 0.62 | 2018
TI_2018-11-30_215117 | 2018-11-30 15:51 | 2018-11-30 15:51 | CST | 2018-11-30 21:51 | 335.5697 | 60.005 | 59.951 | 59.927 | -0.054 | -0.078 | -621.4254 | -430.2176 | No | No | 59.3 | 0.627 | 2018
TI_2018-12-02_063432 | 2018-12-02 00:35 | 2018-12-02 00:35 | CST | 2018-12-02 06:35 | 483.25 | 59.98 | 59.929 | 59.911 | -0.051 | -0.069 | -947.5491 | -700.3624 | No | No | 59.3 | 0.611 | 2019
TI_2018-12-23_125311 | 2018-12-23 06:53 | 2018-12-23 06:53 | CST | 2018-12-23 12:53 | 854.3729 | 59.983 | 59.904 | 59.822 | -0.079 | -0.161 | -1081.4847 | -530.6664 | Yes | Yes | 59.3 | 0.522 | 2019
TI_2018-12-24_002806 | 2018-12-23 18:28 | 2018-12-23 18:28 | CST | 2018-12-24 00:28 | 393.5 | 60.002 | 59.943 | 59.91 | -0.059 | -0.092 | -666.9492 | -427.7174 | Yes | No | 59.3 | 0.61 | 2019
TI_2018-12-26_152411 | 2018-12-26 09:24 | 2018-12-26 09:24 | CST | 2018-12-26 15:24 | 491.333 | 59.982 | 59.94 | 59.886 | -0.042 | -0.096 | -1169.8405 | -511.8052 | Yes | No | 59.3 | 0.586 | 2019
TI_2019-01-02_172547 | 2019-01-02 11:26 | 2019-01-02 11:26 | CST | 2019-01-02 17:26 | 367.71 | 60.016 | 59.945 | 59.971 | -0.071 | -0.045 | -517.9014 | -817.1333 | No | No | 59.3 | 0.671 | 2019
TI_2019-01-02_235934 | 2019-01-02 18:00 | 2019-01-02 18:00 | CST | 2019-01-03 | 424.6634 | 60.03 | 59.976 | 59.951 | -0.054 | -0.079 | -786.4137 | -537.5486 | No | No | 59.3 | 0.651 | 2019
TI_2019-01-10_181402 | 2019-01-10 12:14 | 2019-01-10 12:14 | CST | 2019-01-10 18:14 | 382.8429 | 59.994 | 59.947 | 59.908 | -0.047 | -0.086 | -814.5593 | -445.1661 | Yes | No | 59.3 | 0.608 | 2019
TI_2019-01-22_130501 | 2019-01-22 07:05 | 2019-01-22 07:05 | CST | 2019-01-22 13:05 | 657.153 | 59.962 | 59.888 | 59.869 | -0.074 | -0.093 | -888.0446 | -706.6161 | Yes | No | 59.3 | 0.569 | 2019
TI_2019-01-22_194247 | 2019-01-22 13:43 | 2019-01-22 13:43 | CST | 2019-01-22 19:43 | 461.298 | 60.044 | 60.02 | 59.937 | -0.024 | -0.107 | -1922.075 | -431.1196 | No | No | 59.3 | 0.637 | 2019
TI_2019-01-27_120302 | 2019-01-27 06:03 | 2019-01-27 06:03 | CST | 2019-01-27 12:03 | 510.3357 | 60.015 | 59.953 | 59.909 | -0.062 | -0.106 | -823.1222 | -481.4488 | Yes | No | 59.3 | 0.609 | 2019
TI_2019-02-26_123030 | 2019-02-26 06:31 | 2019-02-26 06:31 | CST | 2019-02-26 12:31 | 413.7634 | 60.01 | 59.942 | 59.903 | -0.068 | -0.107 | -608.4756 | -386.6948 | Yes | No | 59.3 | 0.603 | 2019
TI_2019-02-27_012152 | 2019-02-26 19:22 | 2019-02-26 19:22 | CST | 2019-02-27 01:22 | 658.1993 | 60.024 | 59.937 | 59.876 | -0.087 | -0.148 | -756.5509 | -444.7292 | Yes | Yes | 59.3 | 0.576 | 2019
TI_2019-03-02_091850 | 2019-03-02 03:19 | 2019-03-02 03:19 | CST | 2019-03-02 09:19 | 650.1554 | 60.001 | 59.905 | 59.773 | -0.096 | -0.228 | -677.2452 | -285.1559 | Yes | Yes | 59.3 | 0.473 | 2019
TI_2019-03-12_022401 | 2019-03-11 21:24 | 2019-03-11 21:24 | CDT | 2019-03-12 02:24 | 610.6454 | 59.973 | 59.882 | 59.822 | -0.091 | -0.151 | -671.0389 | -404.4009 | Yes | Yes | 59.3 | 0.522 | 2019
TI_2019-03-21_183952 | 2019-03-21 13:40 | 2019-03-21 13:40 | CDT | 2019-03-21 18:40 | 1224.4 | 60.014 | 59.919 | 59.864 | -0.095 | -0.15 | -1288.8421 | -816.2667 | Yes | Yes | 59.3 | 0.564 | 2019
TI_2019-04-11_083752 | 2019-04-11 03:38 | 2019-04-11 03:38 | CDT | 2019-04-11 08:38 | 664.0374 | 59.983 | 59.902 | 59.812 | -0.081 | -0.171 | -819.7992 | -388.326 | Yes | Yes | 59.3 | 0.512 | 2019
TI_2019-04-17_130208 | 2019-04-17 08:02 | 2019-04-17 08:02 | CDT | 2019-04-17 13:02 | 340.77 | 60.013 | 59.955 | 59.915 | -0.058 | -0.098 | -587.5345 | -347.7245 | Yes | No | 59.3 | 0.615 | 2019
TI_2019-04-18_220448 | 2019-04-18 17:05 | 2019-04-18 17:05 | CDT | 2019-04-18 22:05 | 760 | 60 | 59.921 | 59.853 | -0.079 | -0.147 | -962.0253 | -517.0068 | Yes | No | 59.3 | 0.553 | 2019
TI_2019-04-21_203028 | 2019-04-21 15:30 | 2019-04-21 15:30 | CDT | 2019-04-21 20:30 | 423.2143 | 60.016 | 59.95 | 59.897 | -0.066 | -0.119 | -641.2337 | -355.6422 | Yes | No | 59.3 | 0.597 | 2019
TI_2019-04-25_162001 | 2019-04-25 11:20 | 2019-04-25 11:20 | CDT | 2019-04-25 16:20 | 554.64 | 59.96 | 59.899 | 59.854 | -0.061 | -0.106 | -909.2459 | -523.2453 | No | No | 59.3 | 0.554 | 2019
TI_2019-04-30_143711 | 2019-04-30 09:37 | 2019-04-30 09:37 | CDT | 2019-04-30 14:37 | 576.0244 | 59.987 | 59.917 | 59.865 | -0.07 | -0.122 | -822.892 | -472.1511 | Yes | No | 59.3 | 0.565 | 2019
TI_2019-05-01_021138 | 2019-04-30 21:12 | 2019-04-30 21:12 | CDT | 2019-05-01 02:12 | 595 | 59.986 | 59.93 | 59.869 | -0.056 | -0.117 | -1062.5 | -508.547 | Yes | No | 59.3 | 0.569 | 2019
TI_2019-05-01_151740 | 2019-05-01 10:18 | 2019-05-01 10:18 | CDT | 2019-05-01 15:18 | 396.93 | 60.004 | 59.947 | 59.904 | -0.057 | -0.1 | -696.3684 | -396.93 | Yes | No | 59.3 | 0.604 | 2019
TI_2019-05-01_185603 | 2019-05-01 13:56 | 2019-05-01 13:56 | CDT | 2019-05-01 18:56 | 422 | 60.029 | 59.989 | 59.946 | -0.04 | -0.083 | -1055 | -508.4337 | No | No | 59.3 | 0.646 | 2019
TI_2019-05-02_105346 | 2019-05-02 05:54 | 2019-05-02 05:54 | CDT | 2019-05-02 10:54 | 361 | 60.011 | 59.957 | 59.911 | -0.054 | -0.1 | -668.5185 | -361 | Yes | No | 59.3 | 0.611 | 2019
TI_2019-05-08_171514 | 2019-05-08 12:15 | 2019-05-08 12:15 | CDT | 2019-05-08 17:15 | 414.07 | 59.99 | 59.942 | 59.909 | -0.048 | -0.081 | -862.6458 | -511.1975 | Yes | No | 59.3 | 0.609 | 2019
TI_2019-05-12_135714 | 2019-05-12 08:57 | 2019-05-12 08:57 | CDT | 2019-05-12 13:57 | 374.76 | 60.008 | 59.948 | 59.902 | -0.06 | -0.106 | -624.6 | -353.5472 | Yes | No | 59.3 | 0.602 | 2019
TI_2019-05-17_024209 | 2019-05-16 21:42 | 2019-05-16 21:42 | CDT | 2019-05-17 02:42 | 729 | 60.02 | 59.942 | 59.909 | -0.078 | -0.111 | -934.6154 | -656.7568 | No | No | 59.3 | 0.609 | 2019
TI_2019-05-18_202452 | 2019-05-18 15:25 | 2019-05-18 15:25 | CDT | 2019-05-18 20:25 | 728.84 | 60.017 | 59.939 | 59.869 | -0.078 | -0.148 | -934.4103 | -492.4595 | Yes | No | 59.3 | 0.569 | 2019
TI_2019-05-20_185111 | 2019-05-20 13:51 | 2019-05-20 13:51 | CDT | 2019-05-20 18:51 | 450 | 60.017 | 59.975 | 59.929 | -0.042 | -0.088 | -1071.4286 | -511.3636 | Yes | No | 59.3 | 0.629 | 2019
TI_2019-05-23_214108 | 2019-05-23 16:41 | 2019-05-23 16:41 | CDT | 2019-05-23 21:41 | 568.98 | 59.978 | 59.915 | 59.868 | -0.063 | -0.11 | -903.1429 | -517.2545 | Yes | No | 59.3 | 0.568 | 2019
TI_2019-05-30_075620 | 2019-05-30 02:56 | 2019-05-30 02:56 | CDT | 2019-05-30 07:56 | 596.9 | 59.965 | 59.916 | 59.854 | -0.049 | -0.111 | -1218.1633 | -537.7477 | No | No | 59.3 | 0.554 | 2019
TI_2019-05-31_165644 | 2019-05-31 11:57 | 2019-05-31 11:57 | CDT | 2019-05-31 16:57 | 367.64 | 59.947 | 59.907 | 59.853 | -0.04 | -0.094 | -919.1 | -391.1064 | No | No | 59.3 | 0.553 | 2019
TI_2019-05-31_210629 | 2019-05-31 16:06 | 2019-05-31 16:06 | CDT | 2019-05-31 21:06 | 849 | 59.977 | 59.9 | 59.812 | -0.077 | -0.165 | -1102.5974 | -514.5455 | Yes | No | 59.3 | 0.512 | 2019
TI_2019-06-01_020629 | 2019-05-31 21:06 | 2019-05-31 21:06 | CDT | 2019-06-01 02:06 | 848.84 | 59.978 | 59.9 | 59.812 | -0.078 | -0.166 | -1088.2564 | -511.3494 | Yes | Yes | 59.3 | 0.512 | 2019
TI_2019-06-10_003516 | 2019-06-09 19:35 | 2019-06-09 19:35 | CDT | 2019-06-10 00:35 | 503.32 | 60.002 | 59.96 | 59.924 | -0.042 | -0.078 | -1198.381 | -645.2821 | Yes | No | 59.3 | 0.624 | 2019
TI_2019-06-18_090532 | 2019-06-18 04:06 | 2019-06-18 04:06 | CDT | 2019-06-18 09:06 | 415.96 | 60.018 | 59.983 | 59.924 | -0.035 | -0.094 | -1188.4571 | -442.5106 | Yes | No | 59.3 | 0.624 | 2019
TI_2019-07-15_193719 | 2019-07-15 14:37 | 2019-07-15 14:37 | CDT | 2019-07-15 19:37 | 586.8121 | 59.969 | 59.93 | 59.903 | -0.039 | -0.066 | -1504.6464 | -889.1092 | No | No | 59.3 | 0.603 | 2019
TI_2019-07-22_153436 | 2019-07-22 10:35 | 2019-07-22 10:35 | CDT | 2019-07-22 15:35 | 736.4599 | 60.011 | 59.915 | 59.876 | -0.096 | -0.135 | -767.1457 | -545.5259 | Yes | No | 59.3 | 0.576 | 2019
TI_2019-07-23_141050 | 2019-07-23 09:11 | 2019-07-23 09:11 | CDT | 2019-07-23 14:11 | 624.9 | 59.984 | 59.931 | 59.886 | -0.053 | -0.098 | -1179.0566 | -637.6531 | Yes | No | 59.3 | 0.586 | 2019
TI_2019-07-23_184755 | 2019-07-23 13:48 | 2019-07-23 13:48 | CDT | 2019-07-23 18:48 | 470.17 | 59.98 | 59.943 | 59.909 | -0.037 | -0.071 | -1270.7297 | -662.2113 | Yes | No | 59.3 | 0.609 | 2019
TI_2019-07-29_225909 | 2019-07-29 17:59 | 2019-07-29 17:59 | CDT | 2019-07-29 22:59 | 817.34 | 59.972 | 59.885 | 59.834 | -0.087 | -0.138 | -939.4713 | -592.2754 | Yes | No | 59.3 | 0.534 | 2019
TI_2019-08-10_114926 | 2019-08-10 06:49 | 2019-08-10 06:49 | CDT | 2019-08-10 11:49 | 1081.29 | 59.992 | 59.92 | 59.868 | -0.072 | -0.124 | -1501.7917 | -872.0081 | Yes | No | 59.3 | 0.568 | 2019
TI_2019-08-11_111839 | 2019-08-11 06:19 | 2019-08-11 06:19 | CDT | 2019-08-11 11:19 | 503.9024 | 60.02 | 59.972 | 59.932 | -0.048 | -0.088 | -1049.7966 | -572.6163 | Yes | No | 59.3 | 0.632 | 2019
TI_2019-08-15_012558 | 2019-08-14 20:26 | 2019-08-14 20:26 | CDT | 2019-08-15 01:26 | 400 | 59.988 | 59.965 | 59.936 | -0.023 | -0.052 | -1739.1304 | -769.2308 | No | No | 59.3 | 0.636 | 2019
TI_2019-08-15_013101 | 2019-08-14 20:31 | 2019-08-14 20:31 | CDT | 2019-08-15 01:31 | 432.7 | 59.966 | 59.934 | 59.899 | -0.032 | -0.067 | -1352.1875 | -645.8209 | No | No | 59.3 | 0.599 | 2019
TI_2019-09-21_080014 | 2019-09-21 03:00 | 2019-09-21 03:00 | CDT | 2019-09-21 08:00 | 461.8138 | 59.98 | 59.941 | 59.89 | -0.039 | -0.09 | -1184.138 | -513.1265 | Yes | No | 59.3 | 0.59 | 2019
TI_2019-09-22_194954 | 2019-09-22 14:50 | 2019-09-22 14:50 | CDT | 2019-09-22 19:50 | 696.8167 | 60.025 | 59.97 | 59.897 | -0.055 | -0.128 | -1266.9394 | -544.388 | Yes | No | 59.3 | 0.597 | 2019
TI_2019-09-22_202730 | 2019-09-22 15:27 | 2019-09-22 15:27 | CDT | 2019-09-22 20:28 | 418.4032 | 59.996 | 59.941 | 59.905 | -0.055 | -0.091 | -760.7331 | -459.7837 | Yes | No | 59.3 | 0.605 | 2019
TI_2019-10-14_203132 | 2019-10-14 15:32 | 2019-10-14 15:32 | CDT | 2019-10-14 20:32 | 575.77 | 60.016 | 59.931 | 59.895 | -0.085 | -0.121 | -677.3765 | -475.843 | Yes | No | 59.3 | 0.595 | 2019
TI_2019-10-25_053514 | 2019-10-25 00:35 | 2019-10-25 00:35 | CDT | 2019-10-25 05:35 | 460 | 60.011 | 59.949 | 59.915 | -0.062 | -0.096 | -741.9355 | -479.1667 | No | No | 59.3 | 0.615 | 2019
TI_2019-10-31_022935 | 2019-10-30 21:30 | 2019-10-30 21:30 | CDT | 2019-10-31 02:30 | 745.7 | 60.004 | 59.917 | 59.84 | -0.087 | -0.164 | -857.1264 | -454.6951 | Yes | Yes | 59.3 | 0.54 | 2019
TI_2019-11-18_133428 | 2019-11-18 07:34 | 2019-11-18 07:34 | CST | 2019-11-18 13:34 | 312.14 | 60.012 | 59.951 | 59.91 | -0.061 | -0.102 | -511.7049 | -306.0196 | Yes | No | 59.3 | 0.61 | 2019
TI_2019-11-18_222033 | 2019-11-18 16:21 | 2019-11-18 16:21 | CST | 2019-11-18 22:21 | 466.25 | 60.009 | 59.936 | 59.89 | -0.073 | -0.119 | -638.6986 | -391.8067 | Yes | No | 59.3 | 0.59 | 2019
TI_2019-12-30_042715 | 2019-12-29 22:27 | 2019-12-29 22:27 | CST | 2019-12-30 04:27 | 451 | 59.985 | 59.937 | 59.892 | -0.048 | -0.093 | -939.5833 | -484.9462 | Yes | No | 59.3 | 0.592 | 2020
TI_2020-01-01_185316 | 2020-01-01 12:53 | 2020-01-01 12:53 | CST | 2020-01-01 18:53 | 1209.6 | 60.001 | 59.897 | 59.743 | -0.104 | -0.258 | -1163.0769 | -468.8372 | Yes | Yes | 59.3 | 0.443 | 2020
TI_2020-01-11_025406 | 2020-01-10 20:54 | 2020-01-10 20:54 | CST | 2020-01-11 02:54 | 773 | 59.978 | 59.916 | 59.846 | -0.062 | -0.132 | -1246.7742 | -585.6061 | Yes | No | 59.3 | 0.546 | 2020
TI_2020-01-17_000424 | 2020-01-16 18:04 | 2020-01-16 18:04 | CST | 2020-01-17 00:04 | 543.05 | 60.003 | 59.901 | 59.864 | -0.102 | -0.139 | -532.402 | -390.6835 | Yes | No | 59.3 | 0.564 | 2020
TI_2020-01-17_160102 | 2020-01-17 10:01 | 2020-01-17 10:01 | CST | 2020-01-17 16:01 | 663.25 | 60.011 | 59.877 | 59.827 | -0.134 | -0.184 | -494.9627 | -360.462 | Yes | Yes | 59.3 | 0.527 | 2020
TI_2020-02-06_071613 | 2020-02-06 01:16 | 2020-02-06 01:16 | CST | 2020-02-06 07:16 | 596 | 60.01 | 59.943 | 59.904 | -0.067 | -0.106 | -889.5522 | -562.2642 | Yes | No | 59.3 | 0.604 | 2020
TI_2020-02-07_032249 | 2020-02-06 21:23 | 2020-02-06 21:23 | CST | 2020-02-07 03:23 | 623 | 60.015 | 59.908 | 59.862 | -0.107 | -0.153 | -582.243 | -407.1895 | Yes | Yes | 59.3 | 0.562 | 2020
TI_2020-02-07_225326 | 2020-02-07 16:53 | 2020-02-07 16:53 | CST | 2020-02-07 22:53 | 355.3 | 60.015 | 59.974 | 59.935 | -0.041 | -0.08 | -866.5854 | -444.125 | No | No | 59.3 | 0.635 | 2020
TI_2020-02-10_220659 | 2020-02-10 16:07 | 2020-02-10 16:07 | CST | 2020-02-10 22:07 | 510 | 60.004 | 59.897 | 59.86 | -0.107 | -0.144 | -476.6355 | -354.1667 | Yes | No | 59.3 | 0.56 | 2020
TI_2020-02-12_162800 | 2020-02-12 10:28 | 2020-02-12 10:28 | CST | 2020-02-12 16:28 | 339 | 59.993 | 59.952 | 59.915 | -0.041 | -0.078 | -826.8293 | -434.6154 | No | No | 59.3 | 0.615 | 2020
TI_2020-02-14_143226 | 2020-02-14 08:32 | 2020-02-14 08:32 | CST | 2020-02-14 14:32 | 370 | 60.015 | 59.971 | 59.932 | -0.044 | -0.083 | -840.9091 | -445.7831 | No | No | 59.3 | 0.632 | 2020
TI_2020-03-01_234311 | 2020-03-01 17:43 | 2020-03-01 17:43 | CST | 2020-03-01 23:43 | 442 | 59.997 | 59.931 | 59.892 | -0.066 | -0.105 | -669.697 | -420.9524 | Yes | No | 59.3 | 0.592 | 2020
TI_2020-03-02_191340 | 2020-03-02 13:14 | 2020-03-02 13:14 | CST | 2020-03-02 19:14 | 420 | 59.985 | 59.928 | 59.895 | -0.057 | -0.09 | -736.8421 | -466.6667 | No | No | 59.3 | 0.595 | 2020
TI_2020-03-16_110229 | 2020-03-16 06:02 | 2020-03-16 06:02 | CDT | 2020-03-16 11:02 | -543 | 59.974 | 60.059 | 60.108 | 0.085 | 0.134 | -638.8235 | -405.2239 | Yes | No | 59.3 | 0.808 | 2020
TI_2020-03-16_123940 | 2020-03-16 07:40 | 2020-03-16 07:40 | CDT | 2020-03-16 12:40 | 272 | 60.004 | 59.95 | 59.922 | -0.054 | -0.082 | -503.7037 | -331.7073 | Yes | No | 59.3 | 0.622 | 2020
TI_2020-03-19_001552 | 2020-03-18 19:16 | 2020-03-18 19:16 | CDT | 2020-03-19 00:16 | 691 | 59.968 | 59.894 | 59.852 | -0.074 | -0.116 | -933.7838 | -595.6897 | Yes | No | 59.3 | 0.552 | 2020
TI_2020-03-19_025643 | 2020-03-18 21:57 | 2020-03-18 21:57 | CDT | 2020-03-19 02:57 | 372 | 60.013 | 59.964 | 59.926 | -0.049 | -0.087 | -759.1837 | -427.5862 | Yes | No | 59.3 | 0.626 | 2020
TI_2020-03-20_161224 | 2020-03-20 11:12 | 2020-03-20 11:12 | CDT | 2020-03-20 16:12 | 280 | 60.017 | 59.96 | 59.931 | -0.057 | -0.086 | -491.2281 | -325.5814 | Yes | No | 59.3 | 0.631 | 2020
TI_2020-03-22_131029 | 2020-03-22 08:10 | 2020-03-22 08:10 | CDT | 2020-03-22 13:10 | 699 | 60.021 | 59.931 | 59.854 | -0.09 | -0.167 | -776.6667 | -418.5629 | Yes | No | 59.3 | 0.554 | 2020
TI_2020-04-02_191855 | 2020-04-02 14:19 | 2020-04-02 14:19 | CDT | 2020-04-02 19:19 | 309 | 60.004 | 59.957 | 59.923 | -0.047 | -0.081 | -657.4468 | -381.4815 | Yes | No | 59.3 | 0.623 | 2020
TI_2020-04-22_174424 | 2020-04-22 12:44 | 2020-04-22 12:44 | CDT | 2020-04-22 17:44 | 329 | 59.978 | 59.938 | 59.902 | -0.04 | -0.076 | -822.5 | -432.8947 | No | No | 59.3 | 0.602 | 2020
TI_2020-04-28_224810 | 2020-04-28 17:48 | 2020-04-28 17:48 | CDT | 2020-04-28 22:48 | 332 | 60.015 | 59.954 | 59.931 | -0.061 | -0.084 | -544.2623 | -395.2381 | Yes | No | 59.3 | 0.631 | 2020
TI_2020-05-03_194436 | 2020-05-03 14:45 | 2020-05-03 14:45 | CDT | 2020-05-03 19:45 | 346 | 60.006 | 59.958 | 59.924 | -0.048 | -0.082 | -720.8333 | -421.9512 | Yes | No | 59.3 | 0.624 | 2020
TI_2020-05-05_180533 | 2020-05-05 13:06 | 2020-05-05 13:06 | CDT | 2020-05-05 18:06 | 434 | 60.016 | 59.969 | 59.926 | -0.047 | -0.09 | -923.4043 | -482.2222 | Yes | No | 59.3 | 0.626 | 2020
TI_2020-05-06_105742 | 2020-05-06 05:58 | 2020-05-06 05:58 | CDT | 2020-05-06 10:58 | 384 | 59.971 | 59.941 | 59.89 | -0.03 | -0.081 | -1280 | -474.0741 | Yes | No | 59.3 | 0.59 | 2020
TI_2020-05-07_184812 | 2020-05-07 13:48 | 2020-05-07 13:48 | CDT | 2020-05-07 18:48 | 279 | 60.011 | 59.961 | 59.932 | -0.05 | -0.079 | -558 | -353.1646 | No | No | 59.3 | 0.632 | 2020
TI_2020-05-08_042924 | 2020-05-07 23:29 | 2020-05-07 23:29 | CDT | 2020-05-08 04:29 | 406 | 60.004 | 59.943 | 59.9 | -0.061 | -0.104 | -665.5738 | -390.3846 | Yes | No | 59.3 | 0.6 | 2020
TI_2020-05-10_081117 | 2020-05-10 03:11 | 2020-05-10 03:11 | CDT | 2020-05-10 08:11 | 252 | 60.009 | 59.957 | 59.931 | -0.052 | -0.078 | -484.6154 | -323.0769 | No | No | 59.3 | 0.631 | 2020
TI_2020-05-27_022337 | 2020-05-26 21:24 | 2020-05-26 21:24 | CDT | 2020-05-27 02:24 | 481 | 60.018 | 59.953 | 59.905 | -0.065 | -0.113 | -740 | -425.6637 | Yes | No | 59.3 | 0.605 | 2020
TI_2020-05-31_154522 | 2020-05-31 10:45 | 2020-05-31 10:45 | CDT | 2020-05-31 15:45 | 820 | 59.992 | 59.885 | 59.818 | -0.107 | -0.174 | -766.3551 | -471.2644 | Yes | Yes | 59.3 | 0.518 | 2020
TI_2020-06-13_170044 | 2020-06-13 12:01 | 2020-06-13 12:01 | CDT | 2020-06-13 17:01 | 679 | 60.009 | 59.948 | 59.891 | -0.061 | -0.118 | -1113.1148 | -575.4237 | Yes | No | 59.3 | 0.591 | 2020
TI_2020-06-15_222228 | 2020-06-15 17:22 | 2020-06-15 17:22 | CDT | 2020-06-15 22:22 | 511 | 60.013 | 59.953 | 59.905 | -0.06 | -0.108 | -851.6667 | -473.1481 | Yes | No | 59.3 | 0.605 | 2020
TI_2020-06-23_215356 | 2020-06-23 16:54 | 2020-06-23 16:54 | CDT | 2020-06-23 21:54 | 502 | 60.01 | 59.942 | 59.896 | -0.068 | -0.114 | -738.2353 | -440.3509 | Yes | No | 59.3 | 0.596 | 2020
TI_2020-07-01_232758 | 2020-07-01 18:28 | 2020-07-01 18:28 | CDT | 2020-07-01 23:28 | 801 | 59.97 | 59.91 | 59.846 | -0.06 | -0.124 | -1335 | -645.9677 | Yes | No | 59.3 | 0.546 | 2020
TI_2020-07-05_214420 | 2020-07-05 16:44 | 2020-07-05 16:44 | CDT | 2020-07-05 21:44 | 433 | 60.013 | 59.95 | 59.909 | -0.063 | -0.104 | -687.3016 | -416.3462 | Yes | No | 59.3 | 0.609 | 2020
TI_2020-07-06_200923 | 2020-07-06 15:09 | 2020-07-06 15:09 | CDT | 2020-07-06 20:09 | 762 | 59.981 | 59.885 | 59.806 | -0.096 | -0.175 | -793.75 | -435.4286 | Yes | Yes | 59.3 | 0.506 | 2020
TI_2020-07-10_011410 | 2020-07-09 20:14 | 2020-07-09 20:14 | CDT | 2020-07-10 01:14 | 843 | 59.978 | 59.909 | 59.838 | -0.069 | -0.14 | -1221.7391 | -602.1429 | Yes | No | 59.3 | 0.538 | 2020
TI_2020-07-16_201320 | 2020-07-16 15:13 | 2020-07-16 15:13 | CDT | 2020-07-16 20:13 | 511 | 59.971 | 59.914 | 59.881 | -0.057 | -0.09 | -896.4912 | -567.7778 | Yes | No | 59.3 | 0.581 | 2020
TI_2020-07-20_164740 | 2020-07-20 11:48 | 2020-07-20 11:48 | CDT | 2020-07-20 16:48 | 806 | 59.974 | 59.872 | 59.814 | -0.102 | -0.16 | -790.1961 | -503.75 | Yes | Yes | 59.3 | 0.514 | 2020
TI_2020-08-09_202302 | 2020-08-09 15:23 | 2020-08-09 15:23 | CDT | 2020-08-09 20:23 | 457 | 59.982 | 59.941 | 59.909 | -0.041 | -0.073 | -1114.6341 | -626.0274 | Yes | No | 59.3 | 0.609 | 2020
TI_2020-08-17_025311 | 2020-08-16 21:53 | 2020-08-16 21:53 | CDT | 2020-08-17 02:53 | 450 | 60.017 | 59.971 | 59.938 | -0.046 | -0.079 | -978.2609 | -569.6203 | Yes | No | 59.3 | 0.638 | 2020
TI_2020-08-23_044650 | 2020-08-22 23:47 | 2020-08-22 23:47 | CDT | 2020-08-23 04:47 | 664 | 59.998 | 59.949 | 59.883 | -0.049 | -0.115 | -1355.102 | -577.3913 | Yes | No | 59.3 | 0.583 | 2020
TI_2020-09-04_154455 | 2020-09-04 10:45 | 2020-09-04 10:45 | CDT | 2020-09-04 15:45 | 305.67 | 59.998 | 59.964 | 59.925 | -0.034 | -0.073 | -899.0294 | -418.726 | No | No | 59.3 | 0.625 | 2020
TI_2020-09-21_192049 | 2020-09-21 14:21 | 2020-09-21 14:21 | CDT | 2020-09-21 19:21 | -218 | 59.997 | 60.039 | 60.071 | 0.042 | 0.074 | -519.0476 | -294.5946 | No | No | 59.3 | 0.771 | 2020
TI_2020-09-25_143654 | 2020-09-25 09:37 | 2020-09-25 09:37 | CDT | 2020-09-25 14:37 | 416.5 | 59.985 | 59.96 | 59.913 | -0.025 | -0.072 | -1666 | -578.4722 | No | No | 59.3 | 0.613 | 2020
TI_2020-10-08_160909 | 2020-10-08 11:09 | 2020-10-08 11:09 | CDT | 2020-10-08 16:09 | 364.73 | 59.991 | 59.958 | 59.908 | -0.033 | -0.083 | -1105.2424 | -439.4337 | Yes | No | 59.3 | 0.608 | 2020
TI_2020-10-10_214423 | 2020-10-10 16:44 | 2020-10-10 16:44 | CDT | 2020-10-10 21:44 | 561.98 | 59.958 | 59.871 | 59.828 | -0.087 | -0.13 | -645.954 | -432.2923 | Yes | No | 59.3 | 0.528 | 2020
TI_2020-10-13_194612 | 2020-10-13 14:46 | 2020-10-13 14:46 | CDT | 2020-10-13 19:46 | 368 | 59.987 | 59.943 | 59.91 | -0.044 | -0.077 | -836.3636 | -477.9221 | No | No | 59.3 | 0.61 | 2020
TI_2020-10-13_221337 | 2020-10-13 17:14 | 2020-10-13 17:14 | CDT | 2020-10-13 22:14 | 473.35 | 59.981 | 59.936 | 59.898 | -0.045 | -0.083 | -1051.8889 | -570.3012 | Yes | No | 59.3 | 0.598 | 2020
TI_2020-10-16_095103 | 2020-10-16 04:51 | 2020-10-16 04:51 | CDT | 2020-10-16 09:51 | 141.25 | 59.974 | 59.962 | 59.93 | -0.012 | -0.044 | -1177.0833 | -321.0227 | No | No | 59.3 | 0.63 | 2020
TI_2020-10-19_195042 | 2020-10-19 14:51 | 2020-10-19 14:51 | CDT | 2020-10-19 19:51 | 296.6 | 59.988 | 59.953 | 59.93 | -0.035 | -0.058 | -847.4286 | -511.3793 | No | No | 59.3 | 0.63 | 2020
TI_2020-10-26_182314 | 2020-10-26 13:23 | 2020-10-26 13:23 | CDT | 2020-10-26 18:23 | 469 | 60.01 | 59.909 | 59.876 | -0.101 | -0.134 | -464.3564 | -350 | Yes | No | 59.3 | 0.576 | 2020
TI_2020-10-27_134131 | 2020-10-27 08:42 | 2020-10-27 08:42 | CDT | 2020-10-27 13:42 | 845 | 59.973 | 59.896 | 59.817 | -0.077 | -0.156 | -1097.4026 | -541.6667 | Yes | Yes | 59.3 | 0.517 | 2020
TI_2020-11-08_000510 | 2020-11-07 18:05 | 2020-11-07 18:05 | CST | 2020-11-08 00:05 | 474 | 59.99 | 59.924 | 59.888 | -0.066 | -0.102 | -718.1818 | -464.7059 | Yes | No | 59.3 | 0.588 | 2020
TI_2020-11-15_164732 | 2020-11-15 10:48 | 2020-11-15 10:48 | CST | 2020-11-15 16:48 | -579 | 60.016 | 60.055 | 60.113 | 0.039 | 0.097 | -1484.6154 | -596.9072 | Yes | No | 59.3 | 0.813 | 2020
TI_2020-11-16_155133 | 2020-11-16 09:52 | 2020-11-16 09:52 | CST | 2020-11-16 15:52 | 1020 | 60.005 | 59.937 | 59.795 | -0.068 | -0.21 | -1500 | -485.7143 | Yes | Yes | 59.3 | 0.495 | 2020
TI_2020-11-21_062003 | 2020-11-21 00:20 | 2020-11-21 00:20 | CST | 2020-11-21 06:20 | 740 | 59.993 | 59.902 | 59.828 | -0.091 | -0.165 | -813.1868 | -448.4848 | Yes | Yes | 59.3 | 0.528 | 2020
TI_2020-11-22_183507 | 2020-11-22 12:35 | 2020-11-22 12:35 | CST | 2020-11-22 18:35 | 734 | 59.976 | 59.95 | 59.902 | -0.026 | -0.074 | -2823.0769 | -991.8919 | Yes | No | 59.3 | 0.602 | 2020
TI_2020-11-27_151925 | 2020-11-27 09:19 | 2020-11-27 09:19 | CST | 2020-11-27 15:19 | 367 | 60 | 59.947 | 59.908 | -0.053 | -0.092 | -692.4528 | -398.913 | No | No | 59.3 | 0.608 | 2020
TI_2020-12-04_134441 | 2020-12-04 07:45 | 2020-12-04 07:45 | CST | 2020-12-04 13:45 | 595 | 59.979 | 59.941 | 59.868 | -0.038 | -0.111 | -1565.7895 | -536.036 | Yes | Yes | 59.3 | 0.568 | 2021
TI_2020-12-07_110931 | 2020-12-07 05:10 | 2020-12-07 05:10 | CST | 2020-12-07 11:10 | 422 | 60.021 | 59.971 | 59.959 | -0.05 | -0.062 | -844 | -680.6452 | No | No | 59.3 | 0.659 | 2021
TI_2020-12-10_203428 | 2020-12-10 14:34 | 2020-12-10 14:34 | CST | 2020-12-10 20:34 | 571 | 60.008 | 59.942 | 59.888 | -0.066 | -0.12 | -865.1515 | -475.8333 | Yes | No | 59.3 | 0.588 | 2021
TI_2020-12-26_085536 | 2020-12-26 02:56 | 2020-12-26 02:56 | CST | 2020-12-26 08:56 | 312 | 59.999 | 59.952 | 59.911 | -0.047 | -0.088 | -663.8298 | -354.5455 | Yes | No | 59.3 | 0.611 | 2021
TI_2020-12-26_142421 | 2020-12-26 08:24 | 2020-12-26 08:24 | CST | 2020-12-26 14:24 | 289 | 60.011 | 59.964 | 59.929 | -0.047 | -0.082 | -614.8936 | -352.439 | Yes | No | 59.3 | 0.629 | 2021
TI_2021-01-03_173411 | 2021-01-03 11:34 | 2021-01-03 11:34 | CST | 2021-01-03 17:34 | 768 | 59.977 | 59.906 | 59.828 | -0.071 | -0.149 | -1081.6901 | -515.4362 | Yes | Yes | 59.3 | 0.528 | 2021
TI_2021-01-07_002032 | 2021-01-06 18:21 | 2021-01-06 18:21 | CST | 2021-01-07 00:21 | 774 | 60.012 | 59.919 | 59.846 | -0.093 | -0.166 | -832.2581 | -466.2651 | Yes | Yes | 59.3 | 0.546 | 2021
TI_2021-01-11_190323 | 2021-01-11 13:03 | 2021-01-11 13:03 | CST | 2021-01-11 19:03 | 757 | 59.98 | 59.915 | 59.865 | -0.065 | -0.115 | -1164.6154 | -658.2609 | Yes | Yes | 59.3 | 0.565 | 2021
TI_2021-01-17_033525 | 2021-01-16 21:35 | 2021-01-16 21:35 | CST | 2021-01-17 03:35 | 453 | 60.007 | 59.935 | 59.898 | -0.072 | -0.109 | -629.1667 | -415.5963 | Yes | No | 59.3 | 0.598 | 2021
TI_2021-01-28_202116 | 2021-01-28 14:21 | 2021-01-28 14:21 | CST | 2021-01-28 20:21 | 718 | 60.008 | 59.94 | 59.874 | -0.068 | -0.134 | -1055.8824 | -535.8209 | Yes | Yes | 59.3 | 0.574 | 2021
TI_2021-02-15_105440 | 2021-02-15 04:55 | 2021-02-15 04:55 | CST | 2021-02-15 10:55 | 557 | 59.917 | 59.839 | 59.829 | -0.078 | -0.088 | -714.1026 | -632.9545 | Yes | No | 59.3 | 0.529 | 2021
TI_2021-02-15_112648 | 2021-02-15 05:27 | 2021-02-15 05:27 | CST | 2021-02-15 11:27 | 1389 | 60.022 | 59.847 | 59.771 | -0.175 | -0.251 | -793.7143 | -553.3865 | Yes | Yes | 59.3 | 0.471 | 2021
TI_2021-02-15_132926 | 2021-02-15 07:29 | 2021-02-15 07:29 | CST | 2021-02-15 13:29 | 600 | 60.013 | 59.934 | 59.905 | -0.079 | -0.108 | -759.4937 | -555.5556 | No | No | 59.3 | 0.605 | 2021
TI_2021-02-15_185515 | 2021-02-15 12:55 | 2021-02-15 12:55 | CST | 2021-02-15 18:55 | 407 | 60.009 | 59.957 | 59.934 | -0.052 | -0.075 | -782.6923 | -542.6667 | No | No | 59.3 | 0.634 | 2021
TI_2021-02-16_184643 | 2021-02-16 12:47 | 2021-02-16 12:47 | CST | 2021-02-16 18:47 | 628 | 60.017 | 59.947 | 59.93 | -0.07 | -0.087 | -897.1429 | -721.8391 | Yes | No | 59.3 | 0.63 | 2021
TI_2021-02-22_113844 | 2021-02-22 05:39 | 2021-02-22 05:39 | CST | 2021-02-22 11:39 | 717 | 60.019 | 59.934 | 59.885 | -0.085 | -0.134 | -843.5294 | -535.0746 | Yes | Yes | 59.3 | 0.585 | 2021

## QI
Initial Start Time
(From Fnet)
UTC Initial t0
Event ID (From UTC Initial t0) | Local Date / Time (MM/DD/YY HH:MM:SS) | Day | Time Zone | Date / Time (MM/DD/YY HH:MM:SS) | NERC Confirmed MW Loss | A Value Hz | B Value Hz | Point C Hz | B-A Delta Hz | C-A Delta Hz | A to B IFRM | A to C IFRM | FWG Sel. M-4 | FWG Sel. BAL-003 | 1st Step UFLS Hz | C - UFLS Margin Hz | Oper Year (Local)
QI_2012-01-13_133351 | 2012-01-13 08:34 | 2012-01-13 08:34 | EST | 2012-01-13 13:34 | 615 | 60.0174 | 59.9215 | 59.6998 | -0.095909 | -0.31756 | -641.2314 | -193.6631 | Yes | Yes | 58.5 | 1.1998 | 2012
QI_2012-02-09_141750 | 2012-02-09 09:18 | 2012-02-09 09:18 | EST | 2012-02-09 14:18 | -785.2 | 59.9925 | 60.0693 | 60.4409 | 0.076866 | 0.44842 | -1021.5141 | -175.105 | Yes | Yes | 58.5 | 1.9409 | 2012
QI_2012-03-03_185654 | 2012-03-03 13:57 | 2012-03-03 13:57 | EST | 2012-03-03 18:57 | 2060 | 60.0175 | 59.5153 | 58.7919 | -0.50224 | -1.2256 | -410.1661 | -168.077 | Yes | Yes | 58.5 | 0.2919 | 2012
QI_2012-03-15_191435 | 2012-03-15 15:15 | 2012-03-15 15:15 | EDT | 2012-03-15 19:15 | -575 | 60.0173 | 60.0625 | 60.3846 | 0.045174 | 0.36726 | -1272.8437 | -156.5646 | Yes | Yes | 58.5 | 1.8846 | 2012
QI_2012-04-12_171252 | 2012-04-12 13:13 | 2012-04-12 13:13 | EDT | 2012-04-12 17:13 | -453 | 59.9829 | 60.1051 | 60.4552 | 0.12217 | 0.47225 | -370.7824 | -95.9231 | Yes | Yes | 58.5 | 1.9552 | 2012
QI_2012-04-23_122724 | 2012-04-23 08:27 | 2012-04-23 08:27 | EDT | 2012-04-23 12:27 | 477 | 60.0042 | 59.9397 | 59.69 | -0.064473 | -0.31416 | -739.8393 | -151.8335 | Yes | Yes | 58.5 | 1.19 | 2012
QI_2012-04-27_130050 | 2012-04-27 09:01 | 2012-04-27 09:01 | EDT | 2012-04-27 13:01 | 478 | 57.866 | 60.0413 | 60.0214 | 2.1753 | 2.1554 | 21.974 | 22.1773 | No | No | 58.5 | 1.5214 | 2012
QI_2012-05-05_043347 | 2012-05-05 00:34 | 2012-05-05 00:34 | EDT | 2012-05-05 04:34 | 1293 | 59.9414 | 59.8641 | 59.5579 | -0.077259 | -0.38347 | -1673.583 | -337.1881 | Yes | Yes | 58.5 | 1.0579 | 2012
QI_2012-05-26_035210 | 2012-05-25 23:52 | 2012-05-25 23:52 | EDT | 2012-05-26 03:52 | 420 | 60.0171 | 59.9261 | 59.6582 | -0.091034 | -0.35889 | -461.3673 | -117.0278 | No | Yes | 58.5 | 1.1582 | 2012
QI_2012-06-11_213051 | 2012-06-11 17:31 | 2012-06-11 17:31 | EDT | 2012-06-11 21:31 | 1479 | 59.9848 | 59.7565 | 59.087 | -0.22829 | -0.89776 | -647.8716 | -164.7439 | Yes | Yes | 58.5 | 0.587 | 2012
QI_2012-06-18_021056 | 2012-06-17 22:11 | 2012-06-17 22:11 | EDT | 2012-06-18 02:11 | 459 | 60.0103 | 59.9449 | 59.6595 | -0.06531 | -0.35076 | -702.797 | -130.8591 | Yes | Yes | 58.5 | 1.1595 | 2012
QI_2012-06-21_140715 | 2012-06-21 10:07 | 2012-06-21 10:07 | EDT | 2012-06-21 14:07 | -605 | 60.0128 | 60.0755 | 60.4307 | 0.062679 | 0.4179 | -965.2392 | -144.7721 | Yes | Yes | 58.5 | 1.9307 | 2012
QI_2012-06-29_141922 | 2012-06-29 10:19 | 2012-06-29 10:19 | EDT | 2012-06-29 14:19 | 560 | 60.0063 | 59.9413 | 59.6508 | -0.064962 | -0.35547 | -862.0485 | -157.5371 | Yes | Yes | 58.5 | 1.1508 | 2012
QI_2012-06-30_124953 | 2012-06-30 08:50 | 2012-06-30 08:50 | EDT | 2012-06-30 12:50 | -422 | 60.0108 | 60.0603 | 60.3244 | 0.049509 | 0.31361 | -852.3762 | -134.5606 | No | Yes | 58.5 | 1.8244 | 2012
QI_2012-07-02_025214 | 2012-07-01 22:52 | 2012-07-01 22:52 | EDT | 2012-07-02 02:52 | -876 | 60.0419 | 60.1578 | 60.6215 | 0.1159 | 0.57959 | -755.8245 | -151.1409 | Yes | Yes | 58.5 | 2.1215 | 2012
QI_2012-07-15_180917 | 2012-07-15 14:09 | 2012-07-15 14:09 | EDT | 2012-07-15 18:09 | 3154 | 59.6628 | 59.0706 | 59.2826 | -0.59218 | -0.38017 | -532.6098 | -829.6187 | No | No | 58.5 | 0.7826 | 2012
QI_2012-07-24_060640 | 2012-07-24 02:07 | 2012-07-24 02:07 | EDT | 2012-07-24 06:07 | 872 | 59.9911 | 59.8041 | 59.3205 | -0.18698 | -0.67059 | -466.3717 | -130.0339 | Yes | Yes | 58.5 | 0.8205 | 2012
QI_2012-08-11_094803 | 2012-08-11 05:48 | 2012-08-11 05:48 | EDT | 2012-08-11 09:48 |  | 59.9003 | 60.0306 | 60.0579 | 0.13031 | 0.15761 |  |  | No | No | 58.5 | 1.5579 | 2012
QI_2012-08-13_003222 | 2012-08-12 20:32 | 2012-08-12 20:32 | EDT | 2012-08-13 00:32 | 618 | 60.0068 | 59.8864 | 59.5715 | -0.1204 | -0.43528 | -513.3053 | -141.9769 | Yes | Yes | 58.5 | 1.0715 | 2012
QI_2012-08-21_043553 | 2012-08-21 00:36 | 2012-08-21 00:36 | EDT | 2012-08-21 04:36 | 427 | 60.0208 | 59.9406 | 59.6281 | -0.080215 | -0.39269 | -532.3226 | -108.7366 | No | Yes | 58.5 | 1.1281 | 2012
QI_2012-08-23_181358 | 2012-08-23 14:14 | 2012-08-23 14:14 | EDT | 2012-08-23 18:14 | 461 | 59.9657 | 59.9221 | 59.6569 | -0.04368 | -0.30885 | -1055.4029 | -149.2658 | No | No | 58.5 | 1.1569 | 2012
QI_2012-08-24_072110 | 2012-08-24 03:21 | 2012-08-24 03:21 | EDT | 2012-08-24 07:21 | -459 | 60.0025 | 60.0787 | 60.4042 | 0.076165 | 0.40165 | -602.6381 | -114.2781 | No | No | 58.5 | 1.9042 | 2012
QI_2012-08-24_160136 | 2012-08-24 12:02 | 2012-08-24 12:02 | EDT | 2012-08-24 16:02 | -418 | 60.009 | 60.0578 | 60.3253 | 0.048764 | 0.3163 | -857.1917 | -132.1512 | No | No | 58.5 | 1.8253 | 2012
QI_2012-08-26_021548 | 2012-08-25 22:16 | 2012-08-25 22:16 | EDT | 2012-08-26 02:16 | 465 | 60.0105 | 59.9373 | 59.6303 | -0.073223 | -0.38024 | -635.0479 | -122.2913 | Yes | Yes | 58.5 | 1.1303 | 2012
QI_2012-08-26_040641 | 2012-08-26 00:07 | 2012-08-26 00:07 | EDT | 2012-08-26 04:07 | 944 | 60.0246 | 59.812 | 59.3041 | -0.21256 | -0.7205 | -444.102 | -131.0201 | Yes | Yes | 58.5 | 0.8041 | 2012
QI_2012-08-26_182500 | 2012-08-26 14:25 | 2012-08-26 14:25 | EDT | 2012-08-26 18:25 | 608 | 59.992 | 59.9081 | 59.5522 | -0.08394 | -0.43981 | -724.3264 | -138.2426 | Yes | Yes | 58.5 | 1.0522 | 2012
QI_2012-08-28_124541 | 2012-08-28 08:46 | 2012-08-28 08:46 | EDT | 2012-08-28 12:46 | -473 | 59.9782 | 60.0467 | 60.3227 | 0.068478 | 0.34448 | -690.7285 | -137.3076 | No | No | 58.5 | 1.8227 | 2012
QI_2012-08-30_231423 | 2012-08-30 19:14 | 2012-08-30 19:14 | EDT | 2012-08-30 23:14 | 1414 | 60.0276 | 59.8018 | 59.1421 | -0.2258 | -0.8855 | -626.2088 | -159.684 | Yes | Yes | 58.5 | 0.6421 | 2012
QI_2012-08-30_233519 | 2012-08-30 19:35 | 2012-08-30 19:35 | EDT | 2012-08-30 23:35 | 1435 | 60.0041 | 59.4078 | 59.1143 | -0.59637 | -0.88983 | -240.6211 | -161.2676 | No | No | 58.5 | 0.6143 | 2012
QI_2012-08-30_233525 | 2012-08-30 19:35 | 2012-08-30 19:35 | EDT | 2012-08-30 23:35 |  | 59.8088 | 59.3545 | 59.716 | -0.45436 | -0.092844 |  |  | No | No | 58.5 | 1.216 | 2012
QI_2012-08-30_233547 | 2012-08-30 19:36 | 2012-08-30 19:36 | EDT | 2012-08-30 23:36 | 1344 | 59.7054 | 59.5135 | 58.9761 | -0.1919 | -0.72927 | -700.3798 | -184.2929 | No | No | 58.5 | 0.4761 | 2012
QI_2012-08-30_234449 | 2012-08-30 19:45 | 2012-08-30 19:45 | EDT | 2012-08-30 23:45 | -410 | 59.5028 | 59.607 | 59.8915 | 0.10418 | 0.3887 | -393.5321 | -105.4786 | No | No | 58.5 | 1.3915 | 2012
QI_2012-08-31_014245 | 2012-08-30 21:43 | 2012-08-30 21:43 | EDT | 2012-08-31 01:43 | 1302 | 60.003 | 59.741 | 59.1178 | -0.26196 | -0.88517 | -497.0174 | -147.0909 | Yes | Yes | 58.5 | 0.6178 | 2012
QI_2012-08-31_035145 | 2012-08-30 23:52 | 2012-08-30 23:52 | EDT | 2012-08-31 03:52 | 342 | 60.0302 | 59.9816 | 59.7216 | -0.048529 | -0.30856 | -704.7283 | -110.8386 | No | No | 58.5 | 1.2216 | 2012
QI_2012-08-31_044036 | 2012-08-31 00:41 | 2012-08-31 00:41 | EDT | 2012-08-31 04:41 | 339 | 60.0162 | 59.9544 | 59.7052 | -0.061818 | -0.31099 | -548.383 | -109.0054 | No | No | 58.5 | 1.2052 | 2012
QI_2012-08-31_052336 | 2012-08-31 01:24 | 2012-08-31 01:24 | EDT | 2012-08-31 05:24 | 339 | 60.0179 | 59.9669 | 59.7067 | -0.050994 | -0.31124 | -664.7801 | -108.9199 | No | No | 58.5 | 1.2067 | 2012
QI_2012-09-04_213820 | 2012-09-04 17:38 | 2012-09-04 17:38 | EDT | 2012-09-04 21:38 | -460 | 59.9937 | 60.0345 | 60.3057 | 0.040777 | 0.31196 | -1128.0742 | -147.4544 | No | No | 58.5 | 1.8057 | 2012
QI_2012-09-07_094825 | 2012-09-07 05:48 | 2012-09-07 05:48 | EDT | 2012-09-07 09:48 | 210 | 59.9196 | 59.9924 | 60.0339 | 0.072754 | 0.11428 | 288.6448 | 183.7653 | No | No | 58.5 | 1.5339 | 2012
QI_2012-09-07_215617 | 2012-09-07 17:56 | 2012-09-07 17:56 | EDT | 2012-09-07 21:56 | 452 | 60.0455 | 59.9317 | 59.6633 | -0.11381 | -0.38223 | -397.1632 | -118.2548 | Yes | Yes | 58.5 | 1.1633 | 2012
QI_2012-09-08_080803 | 2012-09-08 04:08 | 2012-09-08 04:08 | EDT | 2012-09-08 08:08 | -682 | 60.0154 | 60.1649 | 60.6267 | 0.14945 | 0.61128 | -456.3469 | -111.5687 | Yes | Yes | 58.5 | 2.1267 | 2012
QI_2012-09-10_231156 | 2012-09-10 19:12 | 2012-09-10 19:12 | EDT | 2012-09-10 23:12 | -434 | 59.9755 | 60.0284 | 60.3487 | 0.05291 | 0.37325 | -820.2597 | -116.2775 | No | No | 58.5 | 1.8487 | 2012
QI_2012-09-15_211635 | 2012-09-15 17:17 | 2012-09-15 17:17 | EDT | 2012-09-15 21:17 | -466 | 59.989 | 60.0532 | 60.3581 | 0.064255 | 0.36912 | -725.2308 | -126.2462 | No | No | 58.5 | 1.8581 | 2012
QI_2012-09-15_225749 | 2012-09-15 18:58 | 2012-09-15 18:58 | EDT | 2012-09-15 22:58 | 452 | 60.0088 | 59.9553 | 59.6827 | -0.053519 | -0.32614 | -844.5541 | -138.5922 | Yes | Yes | 58.5 | 1.1827 | 2012
QI_2012-09-19_171913 | 2012-09-19 13:19 | 2012-09-19 13:19 | EDT | 2012-09-19 17:19 | -417 | 59.9838 | 60.0371 | 60.2814 | 0.05334 | 0.29761 | -781.781 | -140.1158 | No | No | 58.5 | 1.7814 | 2012
QI_2012-09-23_100604 | 2012-09-23 06:06 | 2012-09-23 06:06 | EDT | 2012-09-23 10:06 | 452 | 60.015 | 60.0211 | 59.6869 | 0.0060977 | -0.32807 | 7412.6753 | -137.7738 | No | No | 58.5 | 1.1869 | 2012
QI_2012-09-29_031755 | 2012-09-28 23:18 | 2012-09-28 23:18 | EDT | 2012-09-29 03:18 | 733 | 59.9483 | 59.8077 | 59.4469 | -0.14064 | -0.50141 | -521.1979 | -146.1866 | Yes | Yes | 58.5 | 0.9469 | 2012
QI_2012-10-02_081726 | 2012-10-02 04:17 | 2012-10-02 04:17 | EDT | 2012-10-02 08:17 |  | 59.9895 | 60.0441 | 60.3084 | 0.054689 | 0.31894 |  |  | No | No | 58.5 | 1.8084 | 2012
QI_2012-10-11_093541 | 2012-10-11 05:36 | 2012-10-11 05:36 | EDT | 2012-10-11 09:36 |  | 59.9909 | 60.0301 | 59.6627 | 0.039117 | -0.32824 |  |  | No | No | 58.5 | 1.1627 | 2012
QI_2012-10-19_093702 | 2012-10-19 05:37 | 2012-10-19 05:37 | EDT | 2012-10-19 09:37 |  | 60.0218 | 60.0567 | 59.731 | 0.034914 | -0.29076 |  |  | No | No | 58.5 | 1.231 | 2012
QI_2012-10-26_185846 | 2012-10-26 14:59 | 2012-10-26 14:59 | EDT | 2012-10-26 18:59 | 807 | 60.0023 | 59.8514 | 59.4343 | -0.15091 | -0.56799 | -534.7606 | -142.0789 | Yes | Yes | 58.5 | 0.9343 | 2012
QI_2012-10-28_093811 | 2012-10-28 05:38 | 2012-10-28 05:38 | EDT | 2012-10-28 09:38 |  | 60.0049 | 59.9672 | 59.6891 | -0.037678 | -0.31578 |  |  | No | No | 58.5 | 1.1891 | 2012
QI_2012-10-28_111131 | 2012-10-28 07:12 | 2012-10-28 07:12 | EDT | 2012-10-28 11:12 |  | 60.011 | 60.0161 | 59.714 | 0.0050381 | -0.29703 |  |  | No | No | 58.5 | 1.214 | 2012
QI_2012-10-28_111420 | 2012-10-28 07:14 | 2012-10-28 07:14 | EDT | 2012-10-28 11:14 |  | 60.0262 | 59.9657 | 59.7311 | -0.060459 | -0.29506 |  |  | No | No | 58.5 | 1.2311 | 2012
QI_2012-10-28_144144 | 2012-10-28 10:42 | 2012-10-28 10:42 | EDT | 2012-10-28 14:42 | 571 | 60.0175 | 59.9078 | 59.5852 | -0.10973 | -0.43231 | -520.3774 | -132.0826 | Yes | Yes | 58.5 | 1.0852 | 2012
QI_2012-10-29_223836 | 2012-10-29 18:39 | 2012-10-29 18:39 | EDT | 2012-10-29 22:39 |  | 59.9908 | 59.9511 | 59.7047 | -0.039651 | -0.28606 |  |  | No | No | 58.5 | 1.2047 | 2012
QI_2012-11-02_192615 | 2012-11-02 15:26 | 2012-11-02 15:26 | EDT | 2012-11-02 19:26 |  | 60.0103 | 59.9937 | 60.0509 | -0.016683 | 0.04055 |  |  | No | No | 58.5 | 1.5509 | 2012
QI_2012-12-12_154455 | 2012-12-12 10:45 | 2012-12-12 10:45 | EST | 2012-12-12 15:45 | 670 | 60.021 | 59.9234 | 59.6673 | -0.097561 | -0.3537 | -686.7522 | -189.4266 | Yes | Yes | 58.5 | 1.1673 | 2013
QI_2012-12-18_193143 | 2012-12-18 14:32 | 2012-12-18 14:32 | EST | 2012-12-18 19:32 | 1405 | 59.9843 | 59.781 | 59.3258 | -0.20335 | -0.6585 | -690.9311 | -213.3623 | Yes | Yes | 58.5 | 0.8258 | 2013
QI_2013-01-10_204412 | 2013-01-10 15:44 | 2013-01-10 15:44 | EST | 2013-01-10 20:44 | 1461 | 59.9938 | 59.8296 | 59.5296 | -0.16422 | -0.4642 | -889.6695 | -314.7339 | Yes | Yes | 58.5 | 1.0296 | 2013
QI_2013-01-20_135612 | 2013-01-20 08:56 | 2013-01-20 08:56 | EST | 2013-01-20 13:56 | 650 | 59.9828 | 59.9242 | 59.646 | -0.058627 | -0.33679 | -1108.7127 | -193.0002 | Yes | Yes | 58.5 | 1.146 | 2013
QI_2013-01-27_123655 | 2013-01-27 07:37 | 2013-01-27 07:37 | EST | 2013-01-27 12:37 |  | 59.9952 | 59.6388 | 59.6289 | -0.35633 | -0.36626 |  |  | No | No | 58.5 | 1.1289 | 2013
QI_2013-01-29_194015 | 2013-01-29 14:40 | 2013-01-29 14:40 | EST | 2013-01-29 19:40 | -448 | 59.9799 | 60.0407 | 60.2809 | 0.060711 | 0.30096 | -737.9239 | -148.8592 | No | No | 58.5 | 1.7809 | 2013
QI_2013-02-16_070927 | 2013-02-16 02:09 | 2013-02-16 02:09 | EST | 2013-02-16 07:09 | -448 | 59.9908 | 60.0393 | 60.2959 | 0.048508 | 0.30508 | -923.5521 | -146.8469 | No | No | 58.5 | 1.7959 | 2013
QI_2013-02-21_192857 | 2013-02-21 14:29 | 2013-02-21 14:29 | EST | 2013-02-21 19:29 | 324 | 60.0845 | 59.9554 | 59.71 | -0.12911 | -0.37451 | -250.9497 | -86.5137 | No | Yes | 58.5 | 1.21 | 2013
QI_2013-02-22_180006 | 2013-02-22 13:00 | 2013-02-22 13:00 | EST | 2013-02-22 18:00 | 1249 | 60.0218 | 59.7597 | 59.2935 | -0.26215 | -0.72831 | -476.436 | -171.4935 | Yes | Yes | 58.5 | 0.7935 | 2013
QI_2013-02-27_232259 | 2013-02-27 18:23 | 2013-02-27 18:23 | EST | 2013-02-27 23:23 | -448 | 60.0205 | 59.9774 | 60.258 | -0.043089 | 0.23748 | 1039.7008 | -188.6473 | No | No | 58.5 | 1.758 | 2013
QI_2013-03-21_142458 | 2013-03-21 10:25 | 2013-03-21 10:25 | EDT | 2013-03-21 14:25 | -820 | 59.9903 | 60.0724 | 60.4193 | 0.082161 | 0.42901 | -998.0439 | -191.1367 | Yes | Yes | 58.5 | 1.9193 | 2013
QI_2013-03-26_080034 | 2013-03-26 04:01 | 2013-03-26 04:01 | EDT | 2013-03-26 08:01 | 381 | 60.0067 | 60.0455 | 59.7223 | 0.038748 | -0.28441 | 983.2854 | -133.961 | No | No | 58.5 | 1.2223 | 2013
QI_2013-04-03_124407 | 2013-04-03 08:44 | 2013-04-03 08:44 | EDT | 2013-04-03 12:44 | 996 | 60.0037 | 59.8333 | 59.4298 | -0.1704 | -0.57391 | -584.5169 | -173.5451 | Yes | Yes | 58.5 | 0.9298 | 2013
QI_2013-04-05_124712 | 2013-04-05 08:47 | 2013-04-05 08:47 | EDT | 2013-04-05 12:47 | -642 | 60.0067 | 60.0952 | 60.448 | 0.088537 | 0.44135 | -725.1177 | -145.4622 | No | No | 58.5 | 1.948 | 2013
QI_2013-04-22_130913 | 2013-04-22 09:09 | 2013-04-22 09:09 | EDT | 2013-04-22 13:09 | -447 | 60.0019 | 60.0394 | 60.3317 | 0.0375 | 0.32982 | -1191.9943 | -135.5294 | No | No | 58.5 | 1.8317 | 2013
QI_2013-04-29_225741 | 2013-04-29 18:58 | 2013-04-29 18:58 | EDT | 2013-04-29 22:58 | -468 | 60.0146 | 60.047 | 60.3343 | 0.032383 | 0.31966 | -1445.1933 | -146.407 | No | No | 58.5 | 1.8343 | 2013
QI_2013-04-30_144658 | 2013-04-30 10:47 | 2013-04-30 10:47 | EDT | 2013-04-30 14:47 | 993 | 59.9901 | 59.7349 | 59.317 | -0.2552 | -0.67315 | -389.1045 | -147.5158 | Yes | Yes | 58.5 | 0.817 | 2013
QI_2013-05-04_073917 | 2013-05-04 03:39 | 2013-05-04 03:39 | EDT | 2013-05-04 07:39 | -889 | 60.0049 | 60.2133 | 60.7828 | 0.20844 | 0.77793 | -426.4955 | -114.2776 | Yes | Yes | 58.5 | 2.2828 | 2013
QI_2013-05-04_161245 | 2013-05-04 12:13 | 2013-05-04 12:13 | EDT | 2013-05-04 16:13 | 518 | 60.0038 | 59.908 | 59.5808 | -0.095792 | -0.42303 | -540.757 | -122.4511 | Yes | Yes | 58.5 | 1.0808 | 2013
QI_2013-05-06_133302 | 2013-05-06 09:33 | 2013-05-06 09:33 | EDT | 2013-05-06 13:33 |  | 60.007 | 60.0599 | 60.3439 | 0.05282 | 0.33687 |  |  | No | No | 58.5 | 1.8439 | 2013
QI_2013-05-06_182445 | 2013-05-06 14:25 | 2013-05-06 14:25 | EDT | 2013-05-06 18:25 | 551 | 60.0005 | 59.9205 | 59.6019 | -0.079954 | -0.39858 | -689.1469 | -138.2417 | Yes | Yes | 58.5 | 1.1019 | 2013
QI_2013-05-07_162256 | 2013-05-07 12:23 | 2013-05-07 12:23 | EDT | 2013-05-07 16:23 | 553 | 59.9829 | 59.9379 | 59.6272 | -0.04504 | -0.35571 | -1227.7983 | -155.4631 | Yes | Yes | 58.5 | 1.1272 | 2013
QI_2013-05-12_122317 | 2013-05-12 08:23 | 2013-05-12 08:23 | EDT | 2013-05-12 12:23 | 488 | 60.0055 | 59.9029 | 59.5638 | -0.10258 | -0.44171 | -475.7167 | -110.4793 | Yes | Yes | 58.5 | 1.0638 | 2013
QI_2013-05-12_171231 | 2013-05-12 13:13 | 2013-05-12 13:13 | EDT | 2013-05-12 17:13 |  | 60.0012 | 60.0943 | 60.3475 | 0.093023 | 0.34627 |  |  | No | No | 58.5 | 1.8475 | 2013
QI_2013-05-16_141535 | 2013-05-16 10:16 | 2013-05-16 10:16 | EDT | 2013-05-16 14:16 | -332 | 59.9962 | 60.0471 | 60.3456 | 0.050891 | 0.34939 | -652.3791 | -95.0218 | No | No | 58.5 | 1.8456 | 2013
QI_2013-05-27_092854 | 2013-05-27 05:29 | 2013-05-27 05:29 | EDT | 2013-05-27 09:29 |  | 60.0342 | 60.1331 | 60.4222 | 0.098814 | 0.38796 |  |  | No | No | 58.5 | 1.9222 | 2013
QI_2013-05-27_101055 | 2013-05-27 06:11 | 2013-05-27 06:11 | EDT | 2013-05-27 10:11 |  | 59.9918 | 60.0379 | 60.3344 | 0.046023 | 0.34256 |  |  | No | No | 58.5 | 1.8344 | 2013
QI_2013-06-05_145404 | 2013-06-05 10:54 | 2013-06-05 10:54 | EDT | 2013-06-05 14:54 | -462 | 59.9841 | 60.0691 | 60.4823 | 0.085 | 0.4982 | -543.5285 | -92.7339 | No | No | 58.5 | 1.9823 | 2013
QI_2013-06-06_134856 | 2013-06-06 09:49 | 2013-06-06 09:49 | EDT | 2013-06-06 13:49 |  | 59.9969 | 60.0607 | 60.3378 | 0.063856 | 0.34095 |  |  | No | No | 58.5 | 1.8378 | 2013
QI_2013-06-11_212813 | 2013-06-11 17:28 | 2013-06-11 17:28 | EDT | 2013-06-11 21:28 | 1276 | 60.0327 | 59.7832 | 59.2101 | -0.24954 | -0.82261 | -511.3415 | -155.1164 | Yes | Yes | 58.5 | 0.7101 | 2013
QI_2013-06-12_202904 | 2013-06-12 16:29 | 2013-06-12 16:29 | EDT | 2013-06-12 20:29 | 1466 | 59.9991 | 59.7675 | 59.1568 | -0.23161 | -0.84234 | -632.9686 | -174.0382 | Yes | Yes | 58.5 | 0.6568 | 2013
QI_2013-06-13_011745 | 2013-06-12 21:18 | 2013-06-12 21:18 | EDT | 2013-06-13 01:18 |  | 60.002 | 60.0634 | 60.3572 | 0.061437 | 0.35523 |  |  | No | No | 58.5 | 1.8572 | 2013
QI_2013-06-14_190016 | 2013-06-14 15:00 | 2013-06-14 15:00 | EDT | 2013-06-14 19:00 | 1004 | 59.9882 | 59.8342 | 59.3217 | -0.15402 | -0.66649 | -651.8756 | -150.6394 | Yes | Yes | 58.5 | 0.8217 | 2013
QI_2013-06-14_190337 | 2013-06-14 15:04 | 2013-06-14 15:04 | EDT | 2013-06-14 19:04 | 848 | 59.9934 | 59.829 | 59.3862 | -0.16436 | -0.60717 | -515.9317 | -139.6632 | Yes | Yes | 58.5 | 0.8862 | 2013
QI_2013-06-16_152621 | 2013-06-16 11:26 | 2013-06-16 11:26 | EDT | 2013-06-16 15:26 |  | 60.0005 | 60.0546 | 60.3766 | 0.054143 | 0.37613 |  |  | No | No | 58.5 | 1.8766 | 2013
QI_2013-06-17_154937 | 2013-06-17 11:50 | 2013-06-17 11:50 | EDT | 2013-06-17 15:50 | -377 | 59.9934 | 60.0313 | 60.3085 | 0.037917 | 0.31514 | -994.2828 | -119.6286 | No | No | 58.5 | 1.8085 | 2013
QI_2013-06-17_172332 | 2013-06-17 13:24 | 2013-06-17 13:24 | EDT | 2013-06-17 17:24 | 750 | 59.9523 | 59.8299 | 59.484 | -0.12241 | -0.4683 | -612.6707 | -160.1542 | No | No | 58.5 | 0.984 | 2013
QI_2013-06-22_201848 | 2013-06-22 16:19 | 2013-06-22 16:19 | EDT | 2013-06-22 20:19 | 1123 | 59.9946 | 59.7609 | 59.2537 | -0.23368 | -0.74092 | -480.5728 | -151.5686 | Yes | Yes | 58.5 | 0.7537 | 2013
QI_2013-06-22_212115 | 2013-06-22 17:21 | 2013-06-22 17:21 | EDT | 2013-06-22 21:21 | 1122 | 59.9856 | 59.7276 | 59.2281 | -0.25801 | -0.75753 | -434.8719 | -148.1138 | Yes | Yes | 58.5 | 0.7281 | 2013
QI_2013-06-23_193841 | 2013-06-23 15:39 | 2013-06-23 15:39 | EDT | 2013-06-23 19:39 | 506 | 60.0241 | 59.958 | 59.6791 | -0.06602 | -0.34497 | -766.4388 | -146.6801 | No | No | 58.5 | 1.1791 | 2013
QI_2013-06-26_203148 | 2013-06-26 16:32 | 2013-06-26 16:32 | EDT | 2013-06-26 20:32 |  | 59.9774 | 60.0505 | 60.3101 | 0.073051 | 0.33269 |  |  | No | No | 58.5 | 1.8101 | 2013
QI_2013-06-30_184651 | 2013-06-30 14:47 | 2013-06-30 14:47 | EDT | 2013-06-30 18:47 | 1203 | 60.0226 | 59.8022 | 59.2538 | -0.22037 | -0.76879 | -545.8927 | -156.4788 | Yes | Yes | 58.5 | 0.7538 | 2013
QI_2013-07-01_115602 | 2013-07-01 07:56 | 2013-07-01 07:56 | EDT | 2013-07-01 11:56 |  | 60.0069 | 59.9456 | 59.6748 | -0.061286 | -0.33213 |  |  | No | No | 58.5 | 1.1748 | 2013
QI_2013-07-02_162655 | 2013-07-02 12:27 | 2013-07-02 12:27 | EDT | 2013-07-02 16:27 |  | 59.9949 | 60.0356 | 60.3134 | 0.040713 | 0.31847 |  |  | No | No | 58.5 | 1.8134 | 2013
QI_2013-07-03_150503 | 2013-07-03 11:05 | 2013-07-03 11:05 | EDT | 2013-07-03 15:05 | 1176 | 59.9786 | 59.8055 | 59.2641 | -0.1731 | -0.71454 | -679.3587 | -164.5804 | Yes | Yes | 58.5 | 0.7641 | 2013
QI_2013-07-03_203329 | 2013-07-03 16:33 | 2013-07-03 16:33 | EDT | 2013-07-03 20:33 | 489 | 60.0147 | 59.7999 | 59.5965 | -0.21484 | -0.41824 | -227.6137 | -116.9193 | No | No | 58.5 | 1.0965 | 2013
QI_2013-07-04_203349 | 2013-07-04 16:34 | 2013-07-04 16:34 | EDT | 2013-07-04 20:34 | 837 | 59.9963 | 59.8559 | 59.4733 | -0.14037 | -0.52296 | -596.2895 | -160.0501 | Yes | Yes | 58.5 | 0.9733 | 2013
QI_2013-07-04_210558 | 2013-07-04 17:06 | 2013-07-04 17:06 | EDT | 2013-07-04 21:06 |  | 60.0214 | 59.911 | 59.4335 | -0.11038 | -0.58788 |  |  | No | No | 58.5 | 0.9335 | 2013
QI_2013-07-04_215255 | 2013-07-04 17:53 | 2013-07-04 17:53 | EDT | 2013-07-04 21:53 | 1900 | 60.01 | 59.6072 | 58.868 | -0.4028 | -1.142 | -471.7037 | -166.3684 | Yes | Yes | 58.5 | 0.368 | 2013
QI_2013-07-05_001609 | 2013-07-04 20:16 | 2013-07-04 20:16 | EDT | 2013-07-05 00:16 |  | 60.0128 | 59.7547 | 59.7888 | -0.25811 | -0.22404 |  |  | No | No | 58.5 | 1.2888 | 2013
QI_2013-07-05_174630 | 2013-07-05 13:46 | 2013-07-05 13:46 | EDT | 2013-07-05 17:46 | 902 | 59.9959 | 59.8231 | 59.3626 | -0.17281 | -0.63333 | -521.9504 | -142.4211 | Yes | Yes | 58.5 | 0.8626 | 2013
QI_2013-07-05_200645 | 2013-07-05 16:07 | 2013-07-05 16:07 | EDT | 2013-07-05 20:07 | 877 | 59.9954 | 59.8378 | 59.3614 | -0.15759 | -0.63402 | -556.5004 | -138.3241 | Yes | Yes | 58.5 | 0.8614 | 2013
QI_2013-07-05_200808 | 2013-07-05 16:08 | 2013-07-05 16:08 | EDT | 2013-07-05 20:08 | 447 | 59.8683 | 59.8009 | 59.5545 | -0.067369 | -0.31377 | -663.51 | -142.4619 | No | No | 58.5 | 1.0545 | 2013
QI_2013-07-05_205909 | 2013-07-05 16:59 | 2013-07-05 16:59 | EDT | 2013-07-05 20:59 |  | 60.0211 | 59.963 | 59.7664 | -0.058123 | -0.25468 |  |  | No | No | 58.5 | 1.2664 | 2013
QI_2013-07-06_012809 | 2013-07-05 21:28 | 2013-07-05 21:28 | EDT | 2013-07-06 01:28 |  | 60.0072 | 60.0279 | 60.3084 | 0.020706 | 0.30117 |  |  | No | No | 58.5 | 1.8084 | 2013
QI_2013-07-06_170649 | 2013-07-06 13:07 | 2013-07-06 13:07 | EDT | 2013-07-06 17:07 | 336 | 60.0224 | 59.9297 | 59.6452 | -0.09269 | -0.37723 | -362.5 | -89.0697 | No | No | 58.5 | 1.1452 | 2013
QI_2013-07-09_020228 | 2013-07-08 22:02 | 2013-07-08 22:02 | EDT | 2013-07-09 02:02 |  | 59.9962 | 60.0735 | 60.3613 | 0.077305 | 0.36506 |  |  | No | No | 58.5 | 1.8613 | 2013
QI_2013-07-15_215837 | 2013-07-15 17:59 | 2013-07-15 17:59 | EDT | 2013-07-15 21:59 |  | 60.0092 | 60.0474 | 60.3142 | 0.038242 | 0.30499 |  |  | No | No | 58.5 | 1.8142 | 2013
QI_2013-07-19_022141 | 2013-07-18 22:22 | 2013-07-18 22:22 | EDT | 2013-07-19 02:22 |  | 59.9894 | 60.0348 | 60.316 | 0.045477 | 0.32663 |  |  | No | No | 58.5 | 1.816 | 2013
QI_2013-07-19_170623 | 2013-07-19 13:06 | 2013-07-19 13:06 | EDT | 2013-07-19 17:06 | 854 | 59.9904 | 59.8739 | 59.5111 | -0.11647 | -0.47927 | -733.2476 | -178.1886 | Yes | Yes | 58.5 | 1.0111 | 2013
QI_2013-07-23_204710 | 2013-07-23 16:47 | 2013-07-23 16:47 | EDT | 2013-07-23 20:47 | -912 | 59.9775 | 60.1181 | 60.6423 | 0.14057 | 0.66481 | -648.7848 | -137.1816 | Yes | Yes | 58.5 | 2.1423 | 2013
QI_2013-07-24_122910 | 2013-07-24 08:29 | 2013-07-24 08:29 | EDT | 2013-07-24 12:29 |  | 59.9904 | 60.0648 | 60.3587 | 0.074402 | 0.36834 |  |  | No | No | 58.5 | 1.8587 | 2013
QI_2013-07-29_203428 | 2013-07-29 16:34 | 2013-07-29 16:34 | EDT | 2013-07-29 20:34 |  | 59.9855 | 60.0458 | 60.3642 | 0.060239 | 0.37868 |  |  | No | No | 58.5 | 1.8642 | 2013
QI_2013-07-30_144020 | 2013-07-30 10:40 | 2013-07-30 10:40 | EDT | 2013-07-30 14:40 |  | 60.0061 | 59.9552 | 59.6724 | -0.050849 | -0.33368 |  |  | No | No | 58.5 | 1.1724 | 2013
QI_2013-07-30_172156 | 2013-07-30 13:22 | 2013-07-30 13:22 | EDT | 2013-07-30 17:22 | -906 | 60.0145 | 60.1573 | 60.6513 | 0.14283 | 0.63679 | -634.3186 | -142.2769 | Yes | Yes | 58.5 | 2.1513 | 2013
QI_2013-07-30_194525 | 2013-07-30 15:45 | 2013-07-30 15:45 | EDT | 2013-07-30 19:45 |  | 59.9854 | 60.0448 | 60.3646 | 0.059362 | 0.37916 |  |  | No | No | 58.5 | 1.8646 | 2013
QI_2013-07-30_202350 | 2013-07-30 16:24 | 2013-07-30 16:24 | EDT | 2013-07-30 20:24 | 1227 | 60.0029 | 59.7572 | 59.1531 | -0.24572 | -0.84982 | -499.3514 | -144.3836 | Yes | Yes | 58.5 | 0.6531 | 2013
QI_2013-08-02_095227 | 2013-08-02 05:52 | 2013-08-02 05:52 | EDT | 2013-08-02 09:52 |  | 59.9724 | 60.0015 | 60.2925 | 0.029027 | 0.32006 |  |  | No | No | 58.5 | 1.7925 | 2013
QI_2013-08-03_104757 | 2013-08-03 06:48 | 2013-08-03 06:48 | EDT | 2013-08-03 10:48 |  | 59.9826 | 60.1998 | 60.7802 | 0.21722 | 0.79763 |  |  | No | No | 58.5 | 2.2802 | 2013
QI_2013-08-03_123743 | 2013-08-03 08:38 | 2013-08-03 08:38 | EDT | 2013-08-03 12:38 |  | 60.0169 | 60.0694 | 60.3989 | 0.052417 | 0.38196 |  |  | No | No | 58.5 | 1.8989 | 2013
QI_2013-08-05_191039 | 2013-08-05 15:11 | 2013-08-05 15:11 | EDT | 2013-08-05 19:11 |  | 60.009 | 59.5212 | 58.7994 | -0.48778 | -1.2096 |  |  | No | No | 58.5 | 0.2994 | 2013
QI_2013-08-08_002726 | 2013-08-07 20:27 | 2013-08-07 20:27 | EDT | 2013-08-08 00:27 |  | 60.0187 | 60.0452 | 60.3486 | 0.026408 | 0.32985 |  |  | No | No | 58.5 | 1.8486 | 2013
QI_2013-08-10_160930 | 2013-08-10 12:10 | 2013-08-10 12:10 | EDT | 2013-08-10 16:10 | 389 | 60.0174 | 59.9392 | 59.687 | -0.078234 | -0.33042 | -497.2264 | -117.7273 | No | No | 58.5 | 1.187 | 2013
QI_2013-08-16_012212 | 2013-08-15 21:22 | 2013-08-15 21:22 | EDT | 2013-08-16 01:22 |  | 60.029 | 60.0279 | 59.7219 | -0.0011134 | -0.30714 |  |  | No | No | 58.5 | 1.2219 | 2013
QI_2013-08-16_012323 | 2013-08-15 21:23 | 2013-08-15 21:23 | EDT | 2013-08-16 01:23 |  | 59.9887 | 60.0094 | 59.7557 | 0.020737 | -0.23297 |  |  | No | No | 58.5 | 1.2557 | 2013
QI_2013-08-16_012817 | 2013-08-15 21:28 | 2013-08-15 21:28 | EDT | 2013-08-16 01:28 |  | 59.9717 | 59.9881 | 59.7193 | 0.016407 | -0.25239 |  |  | No | No | 58.5 | 1.2193 | 2013
QI_2013-08-22_020946 | 2013-08-21 22:10 | 2013-08-21 22:10 | EDT | 2013-08-22 02:10 | 503 | 59.9988 | 59.9232 | 59.6368 | -0.075677 | -0.36205 | -664.6674 | -138.9307 | No | No | 58.5 | 1.1368 | 2013
QI_2013-08-23_211545 | 2013-08-23 17:16 | 2013-08-23 17:16 | EDT | 2013-08-23 21:16 | 769 | 59.9965 | 59.8856 | 59.5119 | -0.11089 | -0.48459 | -693.4957 | -158.6922 | Yes | Yes | 58.5 | 1.0119 | 2013
QI_2013-08-24_040330 | 2013-08-24 00:04 | 2013-08-24 00:04 | EDT | 2013-08-24 04:04 |  | 60.0065 | 60.0955 | 60.3675 | 0.089015 | 0.36099 |  |  | No | No | 58.5 | 1.8675 | 2013
QI_2013-08-24_042335 | 2013-08-24 00:24 | 2013-08-24 00:24 | EDT | 2013-08-24 04:24 |  | 59.9517 | 60.0885 | 60.4538 | 0.13684 | 0.50211 |  |  | No | No | 58.5 | 1.9538 | 2013
QI_2013-08-26_011952 | 2013-08-25 21:20 | 2013-08-25 21:20 | EDT | 2013-08-26 01:20 |  | 59.9898 | 60.0545 | 60.3417 | 0.06466 | 0.35189 |  |  | No | No | 58.5 | 1.8417 | 2013
QI_2013-08-26_134524 | 2013-08-26 09:45 | 2013-08-26 09:45 | EDT | 2013-08-26 13:45 |  | 59.9856 | 59.9324 | 59.6493 | -0.053258 | -0.33634 |  |  | No | No | 58.5 | 1.1493 | 2013
QI_2013-08-28_122152 | 2013-08-28 08:22 | 2013-08-28 08:22 | EDT | 2013-08-28 12:22 |  | 59.9747 | 60.1054 | 60.2995 | 0.13075 | 0.32481 |  |  | No | No | 58.5 | 1.7995 | 2013
QI_2013-08-29_222552 | 2013-08-29 18:26 | 2013-08-29 18:26 | EDT | 2013-08-29 22:26 |  | 59.995 | 60.0221 | 60.2795 | 0.027181 | 0.28455 |  |  | No | No | 58.5 | 1.7795 | 2013
QI_2013-09-03_140935 | 2013-09-03 10:10 | 2013-09-03 10:10 | EDT | 2013-09-03 14:10 | -741 | 59.9837 | 60.1066 | 60.4616 | 0.12292 | 0.47789 | -602.8278 | -155.0551 | Yes | Yes | 58.5 | 1.9616 | 2013
QI_2013-09-06_092924 | 2013-09-06 05:29 | 2013-09-06 05:29 | EDT | 2013-09-06 09:29 | -390 | 59.9815 | 60.0816 | 60.3243 | 0.10014 | 0.34281 | -389.4405 | -113.765 | No | No | 58.5 | 1.8243 | 2013
QI_2013-09-06_123552 | 2013-09-06 08:36 | 2013-09-06 08:36 | EDT | 2013-09-06 12:36 | 836 | 59.9822 | 59.8479 | 59.4526 | -0.13431 | -0.52961 | -622.4548 | -157.8508 | Yes | Yes | 58.5 | 0.9526 | 2013
QI_2013-09-13_165520 | 2013-09-13 12:55 | 2013-09-13 12:55 | EDT | 2013-09-13 16:55 |  | 60.0184 | 60.0596 | 60.3112 | 0.041163 | 0.29278 |  |  | No | No | 58.5 | 1.8112 | 2013
QI_2013-09-16_162051 | 2013-09-16 12:21 | 2013-09-16 12:21 | EDT | 2013-09-16 16:21 |  | 60.017 | 60.1989 | 60.7903 | 0.1819 | 0.77334 |  |  | No | No | 58.5 | 2.2903 | 2013
QI_2013-09-18_184057 | 2013-09-18 14:41 | 2013-09-18 14:41 | EDT | 2013-09-18 18:41 | 792 | 60.0073 | 59.8463 | 59.4202 | -0.16093 | -0.58706 | -492.1431 | -134.9105 | Yes | Yes | 58.5 | 0.9202 | 2013
QI_2013-10-19_055302 | 2013-10-19 01:53 | 2013-10-19 01:53 | EDT | 2013-10-19 05:53 | 427 | 60.0183 | 59.9024 | 59.5712 | -0.11583 | -0.44706 | -368.6548 | -95.5126 | No | Yes | 58.5 | 1.0712 | 2013
QI_2013-11-05_213642 | 2013-11-05 16:37 | 2013-11-05 16:37 | EST | 2013-11-05 21:37 | 777 | 59.961 | 59.8512 | 59.5598 | -0.1098 | -0.40124 | -707.6648 | -193.6508 | Yes | Yes | 58.5 | 1.0598 | 2013
QI_2013-11-26_010255 | 2013-11-25 20:03 | 2013-11-25 20:03 | EST | 2013-11-26 01:03 | 680 | 59.964 | 59.8047 | 59.5309 | -0.1593 | -0.43313 | -426.873 | -156.9959 | Yes | Yes | 58.5 | 1.0309 | 2013
QI_2013-12-03_115118 | 2013-12-03 06:51 | 2013-12-03 06:51 | EST | 2013-12-03 11:51 | -889 | 60.0529 | 60.1387 | 60.5142 | 0.085788 | 0.46129 | -1036.2736 | -192.7194 | Yes | Yes | 58.5 | 2.0142 | 2014
QI_2013-12-05_213647 | 2013-12-05 16:37 | 2013-12-05 16:37 | EST | 2013-12-05 21:37 | 752 | 60.0237 | 59.8499 | 59.4979 | -0.17387 | -0.52585 | -432.5027 | -143.0076 | Yes | Yes | 58.5 | 0.9979 | 2014
QI_2014-01-16_115455 | 2014-01-16 06:55 | 2014-01-16 06:55 | EST | 2014-01-16 11:55 | 501 | 59.9959 | 59.9269 | 59.7094 | -0.069053 | -0.28654 | -725.53 | -174.8461 | Yes | Yes | 58.5 | 1.2094 | 2014
QI_2014-01-26_105336 | 2014-01-26 05:54 | 2014-01-26 05:54 | EST | 2014-01-26 10:54 | -469 | 60.0069 | 60.045 | 60.2853 | 0.038112 | 0.27842 | -1230.5969 | -168.4511 | Yes | Yes | 58.5 | 1.7853 | 2014
QI_2014-02-19_082123 | 2014-02-19 03:21 | 2014-02-19 03:21 | EST | 2014-02-19 08:21 | -416 | 59.9912 | 60.0444 | 60.2944 | 0.05317 | 0.30318 | -782.3965 | -137.2115 | No | Yes | 58.5 | 1.7944 | 2014
QI_2014-02-28_041913 | 2014-02-27 23:19 | 2014-02-27 23:19 | EST | 2014-02-28 04:19 | -449 | 60.0031 | 60.0629 | 60.2952 | 0.0598 | 0.29213 | -750.8305 | -153.7012 | No | Yes | 58.5 | 1.7952 | 2014
QI_2014-03-09_173952 | 2014-03-09 13:40 | 2014-03-09 13:40 | EDT | 2014-03-09 17:40 | 997 | 59.992 | 59.9097 | 59.5595 | -0.082235 | -0.43245 | -1212.3762 | -230.5446 | Yes | Yes | 58.5 | 1.0595 | 2014
QI_2014-03-13_200534 | 2014-03-13 16:06 | 2014-03-13 16:06 | EDT | 2014-03-13 20:06 | 995 | 59.9778 | 59.8002 | 59.4106 | -0.17766 | -0.56724 | -560.0445 | -175.4113 | Yes | Yes | 58.5 | 0.9106 | 2014
QI_2014-04-03_123636 | 2014-04-03 08:37 | 2014-04-03 08:37 | EDT | 2014-04-03 12:37 | -409 | 60.0051 | 60.057 | 60.311 | 0.05185 | 0.30586 | -788.8066 | -133.7225 | No | Yes | 58.5 | 1.811 | 2014
QI_2014-04-10_164451 | 2014-04-10 12:45 | 2014-04-10 12:45 | EDT | 2014-04-10 16:45 | -445 | 59.998 | 60.0635 | 60.3012 | 0.065491 | 0.3032 | -679.4816 | -146.7673 | No | No | 58.5 | 1.8012 | 2014
QI_2014-04-10_235308 | 2014-04-10 19:53 | 2014-04-10 19:53 | EDT | 2014-04-10 23:53 | 473 | 59.9918 | 59.9433 | 59.6609 | -0.048561 | -0.33092 | -974.0254 | -142.9355 | No | No | 58.5 | 1.1609 | 2014
QI_2014-05-13_111157 | 2014-05-13 07:12 | 2014-05-13 07:12 | EDT | 2014-05-13 11:12 |  | 60.0105 | 60.0518 | 60.4081 | 0.041297 | 0.39759 |  |  | No | No | 58.5 | 1.9081 | 2014
QI_2014-05-14_105945 | 2014-05-14 07:00 | 2014-05-14 07:00 | EDT | 2014-05-14 11:00 |  | 59.9374 | 60.0768 | 60.4104 | 0.1394 | 0.47296 |  |  | No | No | 58.5 | 1.9104 | 2014
QI_2014-05-17_214140 | 2014-05-17 17:42 | 2014-05-17 17:42 | EDT | 2014-05-17 21:42 | 450 | 60.0004 | 59.8792 | 59.5342 | -0.12121 | -0.46623 | -371.2672 | -96.5197 | Yes | Yes | 58.5 | 1.0342 | 2014
QI_2014-05-20_183650 | 2014-05-20 14:37 | 2014-05-20 14:37 | EDT | 2014-05-20 18:37 | 484 | 60.0097 | 59.8946 | 59.632 | -0.11513 | -0.37774 | -420.3972 | -128.1291 | Yes | Yes | 58.5 | 1.132 | 2014
QI_2014-05-21_103213 | 2014-05-21 06:32 | 2014-05-21 06:32 | EDT | 2014-05-21 10:32 | -465 | 59.9824 | 60.0755 | 60.4327 | 0.093079 | 0.4503 | -499.576 | -103.2642 | No | No | 58.5 | 1.9327 | 2014
QI_2014-05-21_165731 | 2014-05-21 12:58 | 2014-05-21 12:58 | EDT | 2014-05-21 16:58 | -465 | 59.9954 | 60.0673 | 60.4344 | 0.071909 | 0.43899 | -646.6502 | -105.9243 | No | No | 58.5 | 1.9344 | 2014
QI_2014-05-22_074420 | 2014-05-22 03:44 | 2014-05-22 03:44 | EDT | 2014-05-22 07:44 | -457 | 59.9964 | 60.1171 | 60.5174 | 0.12078 | 0.52104 | -378.3849 | -87.7099 | Yes | Yes | 58.5 | 2.0174 | 2014
QI_2014-05-22_160954 | 2014-05-22 12:10 | 2014-05-22 12:10 | EDT | 2014-05-22 16:10 | -670 | 60.014 | 60.1299 | 60.5465 | 0.1159 | 0.53248 | -578.087 | -125.8258 | Yes | Yes | 58.5 | 2.0465 | 2014
QI_2014-05-26_190635 | 2014-05-26 15:07 | 2014-05-26 15:07 | EDT | 2014-05-26 19:07 |  | 59.9984 | 60.0844 | 60.4515 | 0.086009 | 0.45312 |  |  | No | No | 58.5 | 1.9515 | 2014
QI_2014-05-27_225531 | 2014-05-27 18:56 | 2014-05-27 18:56 | EDT | 2014-05-27 22:56 | 490 | 60.0081 | 59.9338 | 59.6378 | -0.07429 | -0.37031 | -659.5737 | -132.3225 | Yes | Yes | 58.5 | 1.1378 | 2014
QI_2014-06-03_000447 | 2014-06-02 20:05 | 2014-06-02 20:05 | EDT | 2014-06-03 00:05 | -500 | 60.0134 | 60.0645 | 60.3936 | 0.05113 | 0.38019 | -977.9039 | -131.514 | No | No | 58.5 | 1.8936 | 2014
QI_2014-06-08_082041 | 2014-06-08 04:21 | 2014-06-08 04:21 | EDT | 2014-06-08 08:21 | 314 | 59.9909 | 59.8858 | 59.6079 | -0.10508 | -0.38298 | -298.8118 | -81.9896 | No | Yes | 58.5 | 1.1079 | 2014
QI_2014-06-08_142852 | 2014-06-08 10:29 | 2014-06-08 10:29 | EDT | 2014-06-08 14:29 | 933 | 59.9897 | 59.7727 | 59.2682 | -0.217 | -0.72149 | -429.9479 | -129.315 | Yes | Yes | 58.5 | 0.7682 | 2014
QI_2014-06-08_182427 | 2014-06-08 14:24 | 2014-06-08 14:24 | EDT | 2014-06-08 18:24 | -405 | 60.0477 | 59.9592 | 59.6477 | -0.088445 | -0.39997 | 457.9133 | 101.2582 | No | No | 58.5 | 1.1477 | 2014
QI_2014-06-08_184458 | 2014-06-08 14:45 | 2014-06-08 14:45 | EDT | 2014-06-08 18:45 |  | 60.0369 | 60.1442 | 60.4169 | 0.10727 | 0.37996 |  |  | No | No | 58.5 | 1.9169 | 2014
QI_2014-06-11_231748 | 2014-06-11 19:18 | 2014-06-11 19:18 | EDT | 2014-06-11 23:18 | -444 | 59.9773 | 60.0939 | 60.3818 | 0.11663 | 0.40453 | -380.678 | -109.7563 | No | Yes | 58.5 | 1.8818 | 2014
QI_2014-06-12_192852 | 2014-06-12 15:29 | 2014-06-12 15:29 | EDT | 2014-06-12 19:29 | -406 | 60.0225 | 60.1153 | 60.398 | 0.092843 | 0.37554 | -437.297 | -108.1121 | No | No | 58.5 | 1.898 | 2014
QI_2014-06-15_111106 | 2014-06-15 07:11 | 2014-06-15 07:11 | EDT | 2014-06-15 11:11 | -397 | 59.9961 | 60.075 | 60.4373 | 0.078935 | 0.44125 | -502.9471 | -89.9726 | No | No | 58.5 | 1.9373 | 2014
QI_2014-06-15_233705 | 2014-06-15 19:37 | 2014-06-15 19:37 | EDT | 2014-06-15 23:37 | -465 | 60.0367 | 60.1125 | 60.4312 | 0.0758 | 0.3945 | -613.4537 | -117.8694 | Yes | Yes | 58.5 | 1.9312 | 2014
QI_2014-06-18_174748 | 2014-06-18 13:48 | 2014-06-18 13:48 | EDT | 2014-06-18 17:48 | 898 | 60.0176 | 59.7955 | 59.3732 | -0.22205 | -0.6444 | -404.4194 | -139.3555 | Yes | Yes | 58.5 | 0.8732 | 2014
QI_2014-06-18_180639 | 2014-06-18 14:07 | 2014-06-18 14:07 | EDT | 2014-06-18 18:07 | 698 | 60.0451 | 59.8692 | 59.4909 | -0.17585 | -0.5542 | -396.9189 | -125.9482 | Yes | Yes | 58.5 | 0.9909 | 2014
QI_2014-06-21_043120 | 2014-06-21 00:31 | 2014-06-21 00:31 | EDT | 2014-06-21 04:31 | 534 | 59.9811 | 59.8291 | 59.4447 | -0.15202 | -0.53641 | -351.2653 | -99.5511 | No | No | 58.5 | 0.9447 | 2014
QI_2014-06-30_143145 | 2014-06-30 10:32 | 2014-06-30 10:32 | EDT | 2014-06-30 14:32 | 519 | 60.0027 | 59.9016 | 59.6041 | -0.1011 | -0.39863 | -513.3353 | -130.1974 | Yes | Yes | 58.5 | 1.1041 | 2014
QI_2014-07-04_101830 | 2014-07-04 06:19 | 2014-07-04 06:19 | EDT | 2014-07-04 10:19 |  | 59.9859 | 60.056 | 60.3689 | 0.070059 | 0.38296 |  |  | No | No | 58.5 | 1.8689 | 2014
QI_2014-07-05_125725 | 2014-07-05 08:57 | 2014-07-05 08:57 | EDT | 2014-07-05 12:57 | -409 | 59.9899 | 60.0475 | 60.4426 | 0.057581 | 0.45269 | -710.2981 | -90.3481 | No | Yes | 58.5 | 1.9426 | 2014
QI_2014-07-09_142852 | 2014-07-09 10:29 | 2014-07-09 10:29 | EDT | 2014-07-09 14:29 |  | 59.989 | 60.0572 | 60.3702 | 0.068172 | 0.38118 |  |  | No | No | 58.5 | 1.8702 | 2014
QI_2014-07-19_031005 | 2014-07-18 23:10 | 2014-07-18 23:10 | EDT | 2014-07-19 03:10 |  | 60.009 | 60.0971 | 60.4018 | 0.088134 | 0.39284 |  |  | No | No | 58.5 | 1.9018 | 2014
QI_2014-07-28_044525 | 2014-07-28 00:45 | 2014-07-28 00:45 | EDT | 2014-07-28 04:45 |  | 60.0179 | 60.0504 | 59.7846 | 0.032583 | -0.23326 |  |  | No | No | 58.5 | 1.2846 | 2014
QI_2014-07-28_044613 | 2014-07-28 00:46 | 2014-07-28 00:46 | EDT | 2014-07-28 04:46 |  | 60.0935 | 60.0557 | 59.7823 | -0.037824 | -0.31119 |  |  | No | No | 58.5 | 1.2823 | 2014
QI_2014-07-28_054930 | 2014-07-28 01:50 | 2014-07-28 01:50 | EDT | 2014-07-28 05:50 | 460 | 60.0171 | 59.8576 | 59.5119 | -0.15954 | -0.50522 | -288.3238 | -91.05 | Yes | Yes | 58.5 | 1.0119 | 2014
QI_2014-07-29_012250 | 2014-07-28 21:23 | 2014-07-28 21:23 | EDT | 2014-07-29 01:23 | -430 | 59.9933 | 60.0734 | 60.3921 | 0.080136 | 0.39879 | -536.587 | -107.8249 | No | No | 58.5 | 1.8921 | 2014
QI_2014-07-29_093815 | 2014-07-29 05:38 | 2014-07-29 05:38 | EDT | 2014-07-29 09:38 | 492 | 59.9954 | 59.8474 | 59.5418 | -0.148 | -0.45357 | -332.4223 | -108.4721 | Yes | Yes | 58.5 | 1.0418 | 2014
QI_2014-07-29_131757 | 2014-07-29 09:18 | 2014-07-29 09:18 | EDT | 2014-07-29 13:18 | -330 | 59.9751 | 60.0682 | 60.3259 | 0.093044 | 0.35076 | -354.6712 | -94.0822 | No | No | 58.5 | 1.8259 | 2014
QI_2014-07-30_191255 | 2014-07-30 15:13 | 2014-07-30 15:13 | EDT | 2014-07-30 19:13 | 1477 | 60.0014 | 59.6863 | 58.9861 | -0.31506 | -1.0153 | -468.7944 | -145.4724 | Yes | Yes | 58.5 | 0.4861 | 2014
QI_2014-08-05_062658 | 2014-08-05 02:27 | 2014-08-05 02:27 | EDT | 2014-08-05 06:27 | 520 | 60.0149 | 59.884 | 59.5291 | -0.13086 | -0.4858 | -397.3598 | -107.0395 | Yes | Yes | 58.5 | 1.0291 | 2014
QI_2014-08-05_165252 | 2014-08-05 12:53 | 2014-08-05 12:53 | EDT | 2014-08-05 16:53 | 698 | 60.0323 | 59.8399 | 59.3396 | -0.19243 | -0.69272 | -362.7219 | -100.7624 | Yes | Yes | 58.5 | 0.8396 | 2014
QI_2014-08-05_170930 | 2014-08-05 13:10 | 2014-08-05 13:10 | EDT | 2014-08-05 17:10 | 427 | 60.0512 | 59.9349 | 59.6847 | -0.11627 | -0.36649 | -367.2402 | -116.5095 | No | Yes | 58.5 | 1.1847 | 2014
QI_2014-08-06_014039 | 2014-08-05 21:41 | 2014-08-05 21:41 | EDT | 2014-08-06 01:41 |  | 60.0009 | 60.0433 | 60.3525 | 0.042424 | 0.35159 |  |  | No | No | 58.5 | 1.8525 | 2014
QI_2014-08-06_152239 | 2014-08-06 11:23 | 2014-08-06 11:23 | EDT | 2014-08-06 15:23 | 665 | 59.9776 | 59.8796 | 59.5067 | -0.098001 | -0.47093 | -678.5611 | -141.2109 | Yes | Yes | 58.5 | 1.0067 | 2014
QI_2014-08-10_133151 | 2014-08-10 09:32 | 2014-08-10 09:32 | EDT | 2014-08-10 13:32 | 430 | 60.0189 | 59.9467 | 59.6551 | -0.072126 | -0.36375 | -596.177 | -118.2115 | No | No | 58.5 | 1.1551 | 2014
QI_2014-08-10_184217 | 2014-08-10 14:42 | 2014-08-10 14:42 | EDT | 2014-08-10 18:42 | 627 | 59.979 | 59.8939 | 59.512 | -0.085095 | -0.46702 | -736.8268 | -134.2544 | Yes | Yes | 58.5 | 1.012 | 2014
QI_2014-08-14_030036 | 2014-08-13 23:01 | 2014-08-13 23:01 | EDT | 2014-08-14 03:01 | -448 | 60.0402 | 60.1162 | 60.4237 | 0.075935 | 0.38347 | -589.978 | -116.827 | No | Yes | 58.5 | 1.9237 | 2014
QI_2014-08-14_175434 | 2014-08-14 13:55 | 2014-08-14 13:55 | EDT | 2014-08-14 17:55 | 1351 | 60.0427 | 59.7488 | 59.0492 | -0.2939 | -0.99346 | -459.6875 | -135.9888 | Yes | Yes | 58.5 | 0.5492 | 2014
QI_2014-08-14_175555 | 2014-08-14 13:56 | 2014-08-14 13:56 | EDT | 2014-08-14 17:56 | 1461 | 59.7967 | 59.3885 | 58.8878 | -0.40814 | -0.90886 | -357.964 | -160.7501 | No | No | 58.5 | 0.3878 | 2014
QI_2014-08-19_161706 | 2014-08-19 12:17 | 2014-08-19 12:17 | EDT | 2014-08-19 16:17 | 1242 | 60.0049 | 59.7434 | 59.1349 | -0.26149 | -0.86999 | -474.9729 | -142.7595 | Yes | Yes | 58.5 | 0.6349 | 2014
QI_2014-08-22_050609 | 2014-08-22 01:06 | 2014-08-22 01:06 | EDT | 2014-08-22 05:06 | 889 | 59.9708 | 59.7663 | 59.2797 | -0.20445 | -0.69106 | -434.8309 | -128.6438 | Yes | Yes | 58.5 | 0.7797 | 2014
QI_2014-09-04_102433 | 2014-09-04 06:25 | 2014-09-04 06:25 | EDT | 2014-09-04 10:25 | -467 | 60.0015 | 60.116 | 60.4215 | 0.11453 | 0.42001 | -407.7416 | -111.1885 | Yes | Yes | 58.5 | 1.9215 | 2014
QI_2014-09-04_142215 | 2014-09-04 10:22 | 2014-09-04 10:22 | EDT | 2014-09-04 14:22 | -467 | 59.9814 | 60.0378 | 60.3138 | 0.056407 | 0.33244 | -827.9177 | -140.4747 | No | No | 58.5 | 1.8138 | 2014
QI_2014-09-05_153715 | 2014-09-05 11:37 | 2014-09-05 11:37 | EDT | 2014-09-05 15:37 | 1458 | 59.9831 | 59.7314 | 59.0397 | -0.25171 | -0.9434 | -579.2343 | -154.5474 | Yes | Yes | 58.5 | 0.5397 | 2014
QI_2014-09-05_162612 | 2014-09-05 12:26 | 2014-09-05 12:26 | EDT | 2014-09-05 16:26 | 1293 | 60.0156 | 59.7476 | 59.1753 | -0.268 | -0.84034 | -482.4603 | -153.8657 | Yes | Yes | 58.5 | 0.6753 | 2014
QI_2014-09-08_204044 | 2014-09-08 16:41 | 2014-09-08 16:41 | EDT | 2014-09-08 20:41 |  | 59.9824 | 60.0603 | 60.3879 | 0.077857 | 0.40548 |  |  | No | No | 58.5 | 1.8879 | 2014
QI_2014-09-09_150141 | 2014-09-09 11:02 | 2014-09-09 11:02 | EDT | 2014-09-09 15:02 |  | 59.9873 | 60.0329 | 60.3624 | 0.045686 | 0.37514 |  |  | No | No | 58.5 | 1.8624 | 2014
QI_2014-09-09_202156 | 2014-09-09 16:22 | 2014-09-09 16:22 | EDT | 2014-09-09 20:22 |  | 59.9818 | 60.0367 | 60.3668 | 0.054863 | 0.385 |  |  | No | No | 58.5 | 1.8668 | 2014
QI_2014-09-18_214254 | 2014-09-18 17:43 | 2014-09-18 17:43 | EDT | 2014-09-18 21:43 | -483 | 60.0255 | 60.1113 | 60.5114 | 0.085791 | 0.48593 | -562.9948 | -99.3972 | Yes | Yes | 58.5 | 2.0114 | 2014
QI_2014-09-27_201730 | 2014-09-27 16:18 | 2014-09-27 16:18 | EDT | 2014-09-27 20:18 | 451 | 59.9943 | 59.8966 | 59.5857 | -0.097747 | -0.40863 | -461.3968 | -110.3686 | Yes | Yes | 58.5 | 1.0857 | 2014
QI_2014-10-12_201722 | 2014-10-12 16:17 | 2014-10-12 16:17 | EDT | 2014-10-12 20:17 | -421 | 59.982 | 60.07 | 60.4509 | 0.088043 | 0.46891 | -478.176 | -89.7832 | No | No | 58.5 | 1.9509 | 2014
QI_2014-10-16_103124 | 2014-10-16 06:31 | 2014-10-16 06:31 | EDT | 2014-10-16 10:31 | -431 | 59.9922 | 60.0842 | 60.4482 | 0.091973 | 0.45599 | -468.6164 | -94.5199 | No | Yes | 58.5 | 1.9482 | 2014
QI_2014-10-16_114400 | 2014-10-16 07:44 | 2014-10-16 07:44 | EDT | 2014-10-16 11:44 | -477 | 59.9904 | 60.1256 | 60.4159 | 0.13521 | 0.42551 | -352.7856 | -112.0998 | Yes | Yes | 58.5 | 1.9159 | 2014
QI_2014-11-04_162340 | 2014-11-04 11:24 | 2014-11-04 11:24 | EST | 2014-11-04 16:24 | -500 | 59.9974 | 60.0537 | 60.3871 | 0.056364 | 0.38974 | -887.0849 | -128.2914 | Yes | Yes | 58.5 | 1.8871 | 2014
QI_2014-11-10_045003 | 2014-11-09 23:50 | 2014-11-09 23:50 | EST | 2014-11-10 04:50 |  | 60.0027 | 59.948 | 59.7204 | -0.054665 | -0.28225 |  |  | No | No | 58.5 | 1.2204 | 2014
QI_2014-11-18_182639 | 2014-11-18 13:27 | 2014-11-18 13:27 | EST | 2014-11-18 18:27 |  | 59.9633 | 60.0174 | 60.2193 | 0.054068 | 0.25596 |  |  | No | No | 58.5 | 1.7193 | 2014
QI_2014-11-30_082933 | 2014-11-30 03:30 | 2014-11-30 03:30 | EST | 2014-11-30 08:30 |  | 59.995 | 60.0569 | 60.3341 | 0.061953 | 0.33914 |  |  | No | No | 58.5 | 1.8341 | 2014
QI_2014-12-04_200550 | 2014-12-04 15:06 | 2014-12-04 15:06 | EST | 2014-12-04 20:06 | 1019 | 60.0221 | 59.8894 | 59.6416 | -0.13272 | -0.38047 | -767.8 | -267.8248 | Yes | Yes | 58.5 | 1.1416 | 2015
QI_2014-12-05_112543 | 2014-12-05 06:26 | 2014-12-05 06:26 | EST | 2014-12-05 11:26 | -640 | 60.0033 | 60.0776 | 60.3653 | 0.074275 | 0.362 | -861.6598 | -176.7962 | Yes | Yes | 58.5 | 1.8653 | 2015
QI_2014-12-06_123731 | 2014-12-06 07:38 | 2014-12-06 07:38 | EST | 2014-12-06 12:38 | 1033 | 60.0011 | 59.8068 | 59.4996 | -0.19425 | -0.50148 | -531.8022 | -205.9894 | Yes | Yes | 58.5 | 0.9996 | 2015
QI_2015-01-13_124236 | 2015-01-13 07:43 | 2015-01-13 07:43 | EST | 2015-01-13 12:43 | -1787 | 60.0247 | 60.2714 | 60.5618 | 0.24675 | 0.53712 | -724.2154 | -332.7019 | Yes | Yes | 58.5 | 2.0618 | 2015
QI_2015-01-09_100529 | 2015-01-09 05:05 | 2015-01-09 05:05 | EST | 2015-01-09 10:05 | -464 | 59.9999 | 60.054 | 60.2734 | 0.054035 | 0.27346 | -858.704 | -169.6803 | No | No | 58.5 | 1.7734 | 2015
QI_2015-01-13_121411 | 2015-01-13 07:14 | 2015-01-13 07:14 | EST | 2015-01-13 12:14 |  | 59.9775 | 59.9701 | 60.226 | -0.0074683 | 0.24845 |  |  | No | No | 58.5 | 1.726 | 2015
QI_2015-01-20_183751 | 2015-01-20 13:38 | 2015-01-20 13:38 | EST | 2015-01-20 18:38 | -442 | 59.9922 | 60.0575 | 60.2938 | 0.065292 | 0.30163 | -676.957 | -146.5391 | No | No | 58.5 | 1.7938 | 2015
QI_2015-01-22_090140 | 2015-01-22 04:02 | 2015-01-22 04:02 | EST | 2015-01-22 09:02 | 489 | 59.988 | 59.9162 | 59.722 | -0.07178 | -0.26602 | -681.2468 | -183.8214 | Yes | Yes | 58.5 | 1.222 | 2015
QI_2015-02-16_055806 | 2015-02-16 00:58 | 2015-02-16 00:58 | EST | 2015-02-16 05:58 | -500 | 59.9903 | 60.0474 | 60.27 | 0.057101 | 0.27971 | -875.6485 | -178.7584 | No | No | 58.5 | 1.77 | 2015
QI_2015-03-10_091107 | 2015-03-10 05:11 | 2015-03-10 05:11 | EDT | 2015-03-10 09:11 | 600 | 60.0355 | 59.9841 | 59.6953 | -0.051397 | -0.34018 | -1167.3897 | -176.377 | Yes | Yes | 58.5 | 1.1953 | 2015
QI_2015-03-19_013221 | 2015-03-18 21:32 | 2015-03-18 21:32 | EDT | 2015-03-19 01:32 | 521 | 59.9825 | 59.9402 | 59.7214 | -0.04227 | -0.26112 | -1232.542 | -199.5269 | No | No | 58.5 | 1.2214 | 2015
QI_2015-03-23_223951 | 2015-03-23 18:40 | 2015-03-23 18:40 | EDT | 2015-03-23 22:40 |  | 59.9646 | 60.0505 | 60.2452 | 0.085912 | 0.28061 |  |  | No | No | 58.5 | 1.7452 | 2015
QI_2015-04-06_120555 | 2015-04-06 08:06 | 2015-04-06 08:06 | EDT | 2015-04-06 12:06 | 781 | 60.0122 | 59.8567 | 59.5392 | -0.15552 | -0.47303 | -502.1982 | -165.1074 | Yes | Yes | 58.5 | 1.0392 | 2015
QI_2015-04-11_130343 | 2015-04-11 09:04 | 2015-04-11 09:04 | EDT | 2015-04-11 13:04 | -625 | 59.9885 | 60.0434 | 60.2351 | 0.054901 | 0.24662 | -1138.4038 | -253.4274 | No | No | 58.5 | 1.7351 | 2015
QI_2015-04-13_195448 | 2015-04-13 15:55 | 2015-04-13 15:55 | EDT | 2015-04-13 19:55 | -390 | 59.9902 | 60.0417 | 60.3443 | 0.051463 | 0.35409 | -757.8198 | -110.1406 | No | No | 58.5 | 1.8443 | 2015
QI_2015-04-21_231517 | 2015-04-21 19:15 | 2015-04-21 19:15 | EDT | 2015-04-21 23:15 | 392 | 59.9916 | 59.8931 | 59.6072 | -0.098551 | -0.38442 | -397.7624 | -101.9724 | No | No | 58.5 | 1.1072 | 2015
QI_2015-05-15_200211 | 2015-05-15 16:02 | 2015-05-15 16:02 | EDT | 2015-05-15 20:02 | 416 | 60.024 | 59.9067 | 59.6329 | -0.11728 | -0.39106 | -354.6948 | -106.3785 | No | No | 58.5 | 1.1329 | 2015
QI_2015-05-25_215821 | 2015-05-25 17:58 | 2015-05-25 17:58 | EDT | 2015-05-25 21:58 | -441 | 60.0105 | 60.085 | 60.3781 | 0.074524 | 0.3676 | -591.7587 | -119.9671 | No | No | 58.5 | 1.8781 | 2015
QI_2015-05-28_083003 | 2015-05-28 04:30 | 2015-05-28 04:30 | EDT | 2015-05-28 08:30 | -455 | 59.9796 | 60.0915 | 60.4446 | 0.11194 | 0.46501 | -406.4777 | -97.8482 | Yes | Yes | 58.5 | 1.9446 | 2015
QI_2015-06-24_080841 | 2015-06-24 04:09 | 2015-06-24 04:09 | EDT | 2015-06-24 08:09 | -455 | 59.9902 | 60.0585 | 60.3549 | 0.068339 | 0.3647 | -665.7948 | -124.76 | Yes | Yes | 58.5 | 1.8549 | 2015
QI_2015-06-26_111513 | 2015-06-26 07:15 | 2015-06-26 07:15 | EDT | 2015-06-26 11:15 |  | 60.0536 | 59.9758 | 59.7116 | -0.077778 | -0.34196 |  |  | No | No | 58.5 | 1.2116 | 2015
QI_2015-06-27_201247 | 2015-06-27 16:13 | 2015-06-27 16:13 | EDT | 2015-06-27 20:13 | 456 | 60.003 | 59.9331 | 59.6268 | -0.069908 | -0.37624 | -652.2857 | -121.1982 | Yes | Yes | 58.5 | 1.1268 | 2015
QI_2015-06-27_224636 | 2015-06-27 18:47 | 2015-06-27 18:47 | EDT | 2015-06-27 22:47 | 580 | 59.9947 | 59.9036 | 59.5694 | -0.091014 | -0.42526 | -637.2641 | -136.3886 | Yes | Yes | 58.5 | 1.0694 | 2015
QI_2015-06-28_094004 | 2015-06-28 05:40 | 2015-06-28 05:40 | EDT | 2015-06-28 09:40 | 848 | 60.0057 | 59.7408 | 59.2733 | -0.26489 | -0.7324 | -320.136 | -115.7838 | Yes | Yes | 58.5 | 0.7733 | 2015
QI_2015-06-28_222743 | 2015-06-28 18:28 | 2015-06-28 18:28 | EDT | 2015-06-28 22:28 |  | 60.0148 | 59.925 | 59.6736 | -0.089839 | -0.34119 |  |  | No | No | 58.5 | 1.1736 | 2015
QI_2015-06-29_150359 | 2015-06-29 11:04 | 2015-06-29 11:04 | EDT | 2015-06-29 15:04 | 513 | 60.0215 | 59.9217 | 59.6707 | -0.099792 | -0.3508 | -514.0709 | -146.2372 | Yes | Yes | 58.5 | 1.1707 | 2015
QI_2015-06-29_184207 | 2015-06-29 14:42 | 2015-06-29 14:42 | EDT | 2015-06-29 18:42 | 630 | 59.9987 | 59.8756 | 59.567 | -0.12314 | -0.4317 | -511.6279 | -145.9352 | Yes | Yes | 58.5 | 1.067 | 2015
QI_2015-06-30_065339 | 2015-06-30 02:54 | 2015-06-30 02:54 | EDT | 2015-06-30 06:54 | -790 | 60.022 | 60.2132 | 60.5111 | 0.19127 | 0.48913 | -413.0343 | -161.5107 | Yes | Yes | 58.5 | 2.0111 | 2015
QI_2015-07-02_144741 | 2015-07-02 10:48 | 2015-07-02 10:48 | EDT | 2015-07-02 14:48 | 467 | 60.0052 | 59.9427 | 59.6496 | -0.06253 | -0.3556 | -746.8364 | -131.3276 | Yes | Yes | 58.5 | 1.1496 | 2015
QI_2015-07-03_012428 | 2015-07-02 21:24 | 2015-07-02 21:24 | EDT | 2015-07-03 01:24 | 461 | 60.0041 | 59.9228 | 59.6592 | -0.081314 | -0.34495 | -566.9408 | -133.6421 | Yes | Yes | 58.5 | 1.1592 | 2015
QI_2015-07-10_063410 | 2015-07-10 02:34 | 2015-07-10 02:34 | EDT | 2015-07-10 06:34 |  | 60.0032 | 59.9367 | 59.6428 | -0.066527 | -0.3604 |  |  | No | No | 58.5 | 1.1428 | 2015
QI_2015-07-18_134335 | 2015-07-18 09:44 | 2015-07-18 09:44 | EDT | 2015-07-18 13:44 | 496 | 60.0025 | 59.9526 | 59.6511 | -0.049968 | -0.35144 | -992.6296 | -141.1346 | Yes | Yes | 58.5 | 1.1511 | 2015
QI_2015-07-20_042135 | 2015-07-20 00:22 | 2015-07-20 00:22 | EDT | 2015-07-20 04:22 |  | 60.0012 | 60.0632 | 60.4112 | 0.06197 | 0.41 |  |  | No | No | 58.5 | 1.9112 | 2015
QI_2015-07-27_061405 | 2015-07-27 02:14 | 2015-07-27 02:14 | EDT | 2015-07-27 06:14 |  | 59.9909 | 60.0922 | 60.3772 | 0.10131 | 0.38633 |  |  | No | No | 58.5 | 1.8772 | 2015
QI_2015-07-30_232103 | 2015-07-30 19:21 | 2015-07-30 19:21 | EDT | 2015-07-30 23:21 | 880 | 59.9915 | 59.8482 | 59.5546 | -0.14325 | -0.43689 | -614.2921 | -201.4246 | Yes | Yes | 58.5 | 1.0546 | 2015
QI_2015-07-31_002550 | 2015-07-30 20:26 | 2015-07-30 20:26 | EDT | 2015-07-31 00:26 | 958 | 60.0121 | 59.7872 | 59.3897 | -0.22491 | -0.62238 | -425.9509 | -153.9254 | Yes | Yes | 58.5 | 0.8897 | 2015
QI_2015-07-31_162405 | 2015-07-31 12:24 | 2015-07-31 12:24 | EDT | 2015-07-31 16:24 | 450 | 60.0387 | 59.9424 | 59.7002 | -0.096349 | -0.3385 | -467.05 | -132.9391 | No | No | 58.5 | 1.2002 | 2015
QI_2015-08-04_182756 | 2015-08-04 14:28 | 2015-08-04 14:28 | EDT | 2015-08-04 18:28 | 635 | 60.0062 | 59.8833 | 59.549 | -0.12287 | -0.45716 | -516.8249 | -138.9021 | Yes | Yes | 58.5 | 1.049 | 2015
QI_2015-08-10_145935 | 2015-08-10 11:00 | 2015-08-10 11:00 | EDT | 2015-08-10 15:00 | 521 | 60.0218 | 59.8892 | 59.6178 | -0.13262 | -0.40404 | -392.844 | -128.9469 | Yes | Yes | 58.5 | 1.1178 | 2015
QI_2015-08-31_095713 | 2015-08-31 05:57 | 2015-08-31 05:57 | EDT | 2015-08-31 09:57 |  | 60.0496 | 60.1288 | 60.4601 | 0.079139 | 0.41047 |  |  | No | No | 58.5 | 1.9601 | 2015
QI_2015-09-22_091701 | 2015-09-22 05:17 | 2015-09-22 05:17 | EDT | 2015-09-22 09:17 | 564 | 59.983 | 59.8586 | 59.5178 | -0.12438 | -0.46518 | -453.4449 | -121.243 | Yes | Yes | 58.5 | 1.0178 | 2015
QI_2015-10-03_134913 | 2015-10-03 09:49 | 2015-10-03 09:49 | EDT | 2015-10-03 13:49 | 672 | 60.0094 | 59.8514 | 59.5114 | -0.15799 | -0.49801 | -425.3383 | -134.9358 | Yes | Yes | 58.5 | 1.0114 | 2015
QI_2015-10-04_151520 | 2015-10-04 11:15 | 2015-10-04 11:15 | EDT | 2015-10-04 15:15 | 340 | 60.0098 | 59.879 | 59.608 | -0.13074 | -0.40175 | -260.0676 | -84.63 | No | No | 58.5 | 1.108 | 2015
QI_2015-10-06_204422 | 2015-10-06 16:44 | 2015-10-06 16:44 | EDT | 2015-10-06 20:44 | 515 | 59.9948 | 59.8915 | 59.6216 | -0.10327 | -0.37316 | -498.6694 | -138.0101 | Yes | Yes | 58.5 | 1.1216 | 2015
QI_2015-10-06_215331 | 2015-10-06 17:54 | 2015-10-06 17:54 | EDT | 2015-10-06 21:54 |  | 60.0032 | 60.0731 | 59.6737 | 0.069933 | -0.32948 |  |  | No | No | 58.5 | 1.1737 | 2015
QI_2015-10-06_231917 | 2015-10-06 19:19 | 2015-10-06 19:19 | EDT | 2015-10-06 23:19 |  | 60.0111 | 60.0731 | 59.6957 | 0.062016 | -0.31537 |  |  | No | No | 58.5 | 1.1957 | 2015
QI_2015-10-21_151621 | 2015-10-21 11:16 | 2015-10-21 11:16 | EDT | 2015-10-21 15:16 | 939 | 60.0144 | 59.8578 | 59.3786 | -0.1566 | -0.63583 | -599.6265 | -147.6811 | Yes | Yes | 58.5 | 0.8786 | 2015
QI_2015-10-21_165541 | 2015-10-21 12:56 | 2015-10-21 12:56 | EDT | 2015-10-21 16:56 |  | 60.0008 | 60.0701 | 59.7868 | 0.069299 | -0.21404 |  |  | No | No | 58.5 | 1.2868 | 2015
QI_2015-11-05_213005 | 2015-11-05 16:30 | 2015-11-05 16:30 | EST | 2015-11-05 21:30 | 960 | 59.9829 | 59.7647 | 59.4087 | -0.2182 | -0.57417 | -439.9594 | -167.198 | Yes | Yes | 58.5 | 0.9087 | 2015
QI_2015-11-06_184302 | 2015-11-06 13:43 | 2015-11-06 13:43 | EST | 2015-11-06 18:43 | 682 | 59.9926 | 59.8738 | 59.5314 | -0.1188 | -0.46123 | -574.0551 | -147.8647 | Yes | Yes | 58.5 | 1.0314 | 2015
QI_2015-11-20_112920 | 2015-11-20 06:29 | 2015-11-20 06:29 | EST | 2015-11-20 11:29 | 810 | 59.97 | 59.8109 | 59.4859 | -0.15908 | -0.4841 | -509.1731 | -167.3191 | No | No | 58.5 | 0.9859 | 2015
QI_2015-11-22_150559 | 2015-11-22 10:06 | 2015-11-22 10:06 | EST | 2015-11-22 15:06 | 793 | 59.976 | 59.7751 | 59.4793 | -0.20088 | -0.4967 | -394.7721 | -159.6544 | Yes | Yes | 58.5 | 0.9793 | 2015
QI_2015-12-03_102712 | 2015-12-03 05:27 | 2015-12-03 05:27 | EST | 2015-12-03 10:27 | 808 | 59.99 | 59.832 | 59.485 | -0.158 | -0.505 | -511.3924 | -160 | Yes | Yes | 58.5 | 0.985 | 2016
QI_2015-12-28_130418 | 2015-12-28 08:04 | 2015-12-28 08:04 | EST | 2015-12-28 13:04 | 1709 | 59.983 | 59.659 | 59.072 | -0.324 | -0.911 | -527.4691 | -187.596 | Yes | Yes | 58.5 | 0.572 | 2016
QI_2016-01-03_202032 | 2016-01-03 15:21 | 2016-01-03 15:21 | EST | 2016-01-03 20:21 |  | 60.002 | 59.937 | 59.808 | -0.065 | -0.194 |  |  | No | No | 58.5 | 1.308 | 2016
QI_2016-01-11_102924 | 2016-01-11 05:29 | 2016-01-11 05:29 | EST | 2016-01-11 10:29 |  | 60.024 | 59.973 | 59.787 | -0.051 | -0.237 |  |  | No | No | 58.5 | 1.287 | 2016
QI_2016-01-11_223531 | 2016-01-11 17:36 | 2016-01-11 17:36 | EST | 2016-01-11 22:36 |  | 60.013 | 59.921 | 59.788 | -0.092 | -0.225 |  |  | No | No | 58.5 | 1.288 | 2016
QI_2016-01-14_110312 | 2016-01-14 06:03 | 2016-01-14 06:03 | EST | 2016-01-14 11:03 |  | 59.9437 | 60.0143 | 60.1896 | 0.070655 | 0.24595 |  |  | No | No | 58.5 | 1.6896 | 2016
QI_2016-01-18_212451 | 2016-01-18 16:25 | 2016-01-18 16:25 | EST | 2016-01-18 21:25 | 620 | 60.002 | 59.912 | 59.69 | -0.09 | -0.312 | -688.8889 | -198.7179 | Yes | Yes | 58.5 | 1.19 | 2016
QI_2016-01-20_132511 | 2016-01-20 08:25 | 2016-01-20 08:25 | EST | 2016-01-20 13:25 |  | 59.995 | 59.957 | 59.755 | -0.038 | -0.24 |  |  | No | No | 58.5 | 1.255 | 2016
QI_2016-01-22_111153 | 2016-01-22 06:12 | 2016-01-22 06:12 | EST | 2016-01-22 11:12 |  | 60.0126 | 60.0774 | 60.2727 | 0.064834 | 0.26011 |  |  | No | No | 58.5 | 1.7727 | 2016
QI_2016-01-28_194744 | 2016-01-28 14:48 | 2016-01-28 14:48 | EST | 2016-01-28 19:48 |  | 60.0047 | 59.9922 | 60.3014 | -0.012507 | 0.29669 |  |  | No | No | 58.5 | 1.8014 | 2016
QI_2016-01-31_102426 | 2016-01-31 05:24 | 2016-01-31 05:24 | EST | 2016-01-31 10:24 | -436 | 60.0367 | 60.0755 | 60.3573 | 0.038844 | 0.32064 | -1122.437 | -135.979 | No | No | 58.5 | 1.8573 | 2016
QI_2016-02-05_133045 | 2016-02-05 08:31 | 2016-02-05 08:31 | EST | 2016-02-05 13:31 |  | 60.004 | 59.981 | 59.832 | -0.023 | -0.172 |  |  | No | No | 58.5 | 1.332 | 2016
QI_2016-02-08_015136 | 2016-02-07 20:52 | 2016-02-07 20:52 | EST | 2016-02-08 01:52 | -474 | 60.004 | 60.059 | 60.303 | 0.055 | 0.299 | -861.8182 | -158.5284 | Yes | Yes | 58.5 | 1.803 | 2016
QI_2016-02-08_035424 | 2016-02-07 22:54 | 2016-02-07 22:54 | EST | 2016-02-08 03:54 | -435 | 60.0018 | 60.0465 | 60.3052 | 0.044651 | 0.3034 | -974.2292 | -143.376 | No | No | 58.5 | 1.8052 | 2016
QI_2016-02-14_160519 | 2016-02-14 11:05 | 2016-02-14 11:05 | EST | 2016-02-14 16:05 | 498 | 60.013 | 59.9 | 59.717 | -0.113 | -0.296 | -440.708 | -168.2432 | Yes | Yes | 58.5 | 1.217 | 2016
QI_2016-03-08_173235 | 2016-03-08 12:33 | 2016-03-08 12:33 | EST | 2016-03-08 17:33 |  | 60.018 | 59.967 | 59.826 | -0.051 | -0.192 |  |  | No | No | 58.5 | 1.326 | 2016
QI_2016-03-08_164833 | 2016-03-08 11:49 | 2016-03-08 11:49 | EST | 2016-03-08 16:49 | -962 | 60.003 | 60.107 | 60.624 | 0.104 | 0.621 | -925 | -154.9114 | Yes | Yes | 58.5 | 2.124 | 2016
QI_2016-03-15_182857 | 2016-03-15 14:29 | 2016-03-15 14:29 | EDT | 2016-03-15 18:29 | 446 | 59.982 | 59.8446 | 59.5658 | -0.13741 | -0.41621 | -324.5643 | -107.1584 | No | No | 58.5 | 1.0658 | 2016
QI_2016-03-10_071011 | 2016-03-10 02:10 | 2016-03-10 02:10 | EST | 2016-03-10 07:10 | 760 | 59.976 | 59.938 | 59.665 | -0.038 | -0.311 | -2000 | -244.373 | Yes | Yes | 58.5 | 1.165 | 2016
QI_2016-03-16_112908 | 2016-03-16 07:29 | 2016-03-16 07:29 | EDT | 2016-03-16 11:29 |  | 59.983 | 59.97 | 59.806 | -0.013 | -0.177 |  |  | No | No | 58.5 | 1.306 | 2016
QI_2016-03-18_135208 | 2016-03-18 09:52 | 2016-03-18 09:52 | EDT | 2016-03-18 13:52 | 395 | 60.0113 | 59.9635 | 59.745 | -0.047825 | -0.26635 | -825.9198 | -148.3007 | No | No | 58.5 | 1.245 | 2016
QI_2016-03-20_064548 | 2016-03-20 02:46 | 2016-03-20 02:46 | EDT | 2016-03-20 06:46 |  | 59.985 | 59.945 | 59.772 | -0.04 | -0.213 |  |  | No | No | 58.5 | 1.272 | 2016
QI_2016-03-31_150127 | 2016-03-31 11:01 | 2016-03-31 11:01 | EDT | 2016-03-31 15:01 | -355 | 59.9933 | 60.0396 | 60.2521 | 0.046328 | 0.25882 | -766.2707 | -137.1603 | No | No | 58.5 | 1.7521 | 2016
QI_2016-04-02_004830 | 2016-04-01 20:49 | 2016-04-01 20:49 | EDT | 2016-04-02 00:48 | 603 | 59.99 | 59.878 | 59.569 | -0.112 | -0.421 | -538.3929 | -143.2304 | Yes | Yes | 58.5 | 1.069 | 2016
QI_2016-04-13_185231 | 2016-04-13 14:53 | 2016-04-13 14:53 | EDT | 2016-04-13 18:53 | -960 | 60.015 | 60.154 | 60.639 | 0.139 | 0.624 | -690.6475 | -153.8462 | Yes | Yes | 58.5 | 2.139 | 2016
QI_2016-04-22_033108 | 2016-04-21 23:31 | 2016-04-21 23:31 | EDT | 2016-04-22 03:31 | -710 |  |  |  | 0 | 0 |  |  |  | No | 58.5 | -58.5 | 2016
QI_2016-04-28_022739 | 2016-04-27 22:28 | 2016-04-27 22:28 | EDT | 2016-04-28 02:28 | 482 | 60.004 | 59.923 | 59.627 | -0.081 | -0.377 | -595.0617 | -127.8515 | Yes | Yes | 58.5 | 1.127 | 2016
QI_2016-05-03_130350 | 2016-05-03 09:04 | 2016-05-03 09:04 | EDT | 2016-05-03 13:04 | 455 | 60.031 | 59.956 | 59.642 | -0.075 | -0.389 | -606.6667 | -116.9666 | Yes | Yes | 58.5 | 1.142 | 2016
QI_2016-05-03_174436 | 2016-05-03 13:45 | 2016-05-03 13:45 | EDT | 2016-05-03 17:45 | 884 | 60.002 | 59.835 | 59.273 | -0.167 | -0.729 | -529.3413 | -121.262 | Yes | Yes | 58.5 | 0.773 | 2016
QI_2016-05-10_065006 | 2016-05-10 02:50 | 2016-05-10 02:50 | EDT | 2016-05-10 06:50 | -471 | 59.987 | 60.081 | 60.493 | 0.094 | 0.506 | -501.0638 | -93.083 | Yes | Yes | 58.5 | 1.993 | 2016
QI_2016-05-16_203421 | 2016-05-16 16:34 | 2016-05-16 16:34 | EDT | 2016-05-16 20:34 | -468 | 59.985 | 60.041 | 60.412 | 0.056 | 0.427 | -835.7143 | -109.6019 | Yes | Yes | 58.5 | 1.912 | 2016
QI_2016-05-19_053410 | 2016-05-19 01:34 | 2016-05-19 01:34 | EDT | 2016-05-19 05:34 | -476 | 60.017 | 60.116 | 60.529 | 0.099 | 0.512 | -480.8081 | -92.9687 | Yes | Yes | 58.5 | 2.029 | 2016
QI_2016-05-21_195451 | 2016-05-21 15:55 | 2016-05-21 15:55 | EDT | 2016-05-21 19:55 | -392 | 60.0076 | 59.932 | 59.6625 | -0.075674 | -0.34515 | 518.0125 | 113.5754 | No | No | 58.5 | 1.1625 | 2016
QI_2016-05-22_100042 | 2016-05-22 06:01 | 2016-05-22 06:01 | EDT | 2016-05-22 10:01 | -257 | 59.9833 | 60.0312 | 60.3606 | 0.047925 | 0.37733 | -536.2523 | -68.11 | No | No | 58.5 | 1.8606 | 2016
QI_2016-05-24_202305 | 2016-05-24 16:23 | 2016-05-24 16:23 | EDT | 2016-05-24 20:23 | 523 |  |  |  | 0 | 0 |  |  |  | No | 58.5 | -58.5 | 2016
QI_2016-05-24_223702 | 2016-05-24 18:37 | 2016-05-24 18:37 | EDT | 2016-05-24 22:37 | 765 | 59.988 | 59.842 | 59.476 | -0.146 | -0.512 | -523.9726 | -149.4141 | Yes | Yes | 58.5 | 0.976 | 2016
QI_2016-05-26_055400 | 2016-05-26 01:54 | 2016-05-26 01:54 | EDT | 2016-05-26 05:54 | -453 | 60.002 | 60.117 | 60.597 | 0.115 | 0.595 | -393.913 | -76.1345 | Yes | Yes | 58.5 | 2.097 | 2016
QI_2016-05-27_152211 | 2016-05-27 11:22 | 2016-05-27 11:22 | EDT | 2016-05-27 15:22 | -392 | 59.9792 | 60.0034 | 60.3136 | 0.024156 | 0.33436 | -1622.792 | -117.2386 | No | No | 58.5 | 1.8136 | 2016
QI_2016-05-31_002116 | 2016-05-30 20:21 | 2016-05-30 20:21 | EDT | 2016-05-31 00:21 | -447 | 59.9856 | 60.0739 | 60.418 | 0.088362 | 0.43244 | -505.8732 | -103.3662 | No | No | 58.5 | 1.918 | 2016
QI_2016-06-02_235132 | 2016-06-02 19:52 | 2016-06-02 19:52 | EDT | 2016-06-02 23:52 | 1022 | 60.006 | 59.789 | 59.306 | -0.217 | -0.7 | -470.9677 | -146 | Yes | Yes | 58.5 | 0.806 | 2016
QI_2016-06-03_044600 | 2016-06-03 00:46 | 2016-06-03 00:46 | EDT | 2016-06-03 04:46 | -473 | 60.005 | 60.069 | 60.467 | 0.064 | 0.462 | -739.0625 | -102.381 | Yes | Yes | 58.5 | 1.967 | 2016
QI_2016-06-19_142606 | 2016-06-19 10:26 | 2016-06-19 10:26 | EDT | 2016-06-19 14:26 | 356 | 60.0211 | 59.962 | 59.6566 | -0.0591 | -0.36449 | -602.3717 | -97.6715 | No | No | 58.5 | 1.1566 | 2016
QI_2016-06-19_194616 | 2016-06-19 15:46 | 2016-06-19 15:46 | EDT | 2016-06-19 19:46 | -510 | 59.976 | 60.128 | 60.55 | 0.152 | 0.574 | -335.5263 | -88.8502 | Yes | Yes | 58.5 | 2.05 | 2016
QI_2016-06-20_024836 | 2016-06-19 22:49 | 2016-06-19 22:49 | EDT | 2016-06-20 02:49 | -518 | 59.992 | 60.12 | 60.442 | 0.128 | 0.45 | -404.6875 | -115.1111 | Yes | Yes | 58.5 | 1.942 | 2016
QI_2016-06-27_172627 | 2016-06-27 13:26 | 2016-06-27 13:26 | EDT | 2016-06-27 17:26 | 592 | 59.974 | 59.901 | 59.517 | -0.073 | -0.457 | -810.9589 | -129.5405 | Yes | Yes | 58.5 | 1.017 | 2016
QI_2016-06-27_182446 | 2016-06-27 14:25 | 2016-06-27 14:25 | EDT | 2016-06-27 18:25 | -449 | 59.986 | 60.084 | 60.4092 | 0.09797 | 0.42322 | -458.3021 | -106.0921 | No | No | 58.5 | 1.9092 | 2016
QI_2016-07-02_003458 | 2016-07-01 20:35 | 2016-07-01 20:35 | EDT | 2016-07-02 00:35 | 281 | 60.013 | 59.948 | 59.725 | -0.065 | -0.288 | -432.3077 | -97.5694 | No | No | 58.5 | 1.225 | 2016
QI_2016-07-02_212754 | 2016-07-02 17:28 | 2016-07-02 17:28 | EDT | 2016-07-02 21:28 | 226 | 60.016 | 59.982 | 59.764 | -0.034 | -0.252 | -664.7059 | -89.6825 | No | No | 58.5 | 1.264 | 2016
QI_2016-07-14_062349 | 2016-07-14 02:24 | 2016-07-14 02:24 | EDT | 2016-07-14 06:24 | 254 | 60.008 | 59.955 | 59.751 | -0.053 | -0.257 | -479.2453 | -98.8327 | No | No | 58.5 | 1.251 | 2016
QI_2016-07-14_224720 | 2016-07-14 18:47 | 2016-07-14 18:47 | EDT | 2016-07-14 22:47 | 215 | 60.021 | 59.977 | 59.783 | -0.044 | -0.238 | -488.6364 | -90.3361 | No | No | 58.5 | 1.283 | 2016
QI_2016-07-16_000252 | 2016-07-15 20:03 | 2016-07-15 20:03 | EDT | 2016-07-16 00:03 | 227 | 60.001 | 59.968 | 59.793 | -0.033 | -0.208 | -687.8788 | -109.1346 | No | No | 58.5 | 1.293 | 2016
QI_2016-07-16_010123 | 2016-07-15 21:01 | 2016-07-15 21:01 | EDT | 2016-07-16 01:01 | 227 | 60.031 | 59.954 | 59.787 | -0.077 | -0.244 | -294.8052 | -93.0328 | No | No | 58.5 | 1.287 | 2016
QI_2016-07-20_014907 | 2016-07-19 21:49 | 2016-07-19 21:49 | EDT | 2016-07-20 01:49 | 200 | 59.996 | 59.977 | 59.778 | -0.019 | -0.218 | -1052.6316 | -91.7431 | No | No | 58.5 | 1.278 | 2016
QI_2016-07-20_140217 | 2016-07-20 10:02 | 2016-07-20 10:02 | EDT | 2016-07-20 14:02 | 206 | 60.024 | 59.974 | 59.779 | -0.05 | -0.245 | -412 | -84.0816 | No | No | 58.5 | 1.279 | 2016
QI_2016-07-21_042351 | 2016-07-21 00:24 | 2016-07-21 00:24 | EDT | 2016-07-21 04:24 | 334 | 59.988 | 59.989 | 59.664 | 0.001 | -0.324 | 33400 | -103.0864 | No | No | 58.5 | 1.164 | 2016
QI_2016-07-21_185949 | 2016-07-21 15:00 | 2016-07-21 15:00 | EDT | 2016-07-21 19:00 | 0 | 60.011 | 60.002 | 59.827 | -0.009 | -0.184 |  |  | No | No | 58.5 | 1.327 | 2016
QI_2016-07-22_030907 | 2016-07-21 23:09 | 2016-07-21 23:09 | EDT | 2016-07-22 03:09 | 282 | 60.025 | 59.967 | 59.75 | -0.058 | -0.275 | -486.2069 | -102.5455 | No | No | 58.5 | 1.25 | 2016
QI_2016-07-22_232826 | 2016-07-22 19:28 | 2016-07-22 19:28 | EDT | 2016-07-22 23:28 | 322 | 59.995 | 59.988 | 59.794 | -0.007 | -0.201 | -4600 | -160.199 | No | No | 58.5 | 1.294 | 2016
QI_2016-07-24_131641 | 2016-07-24 09:17 | 2016-07-24 09:17 | EDT | 2016-07-24 13:17 | 274 | 59.97 | 59.966 | 59.772 | -0.004 | -0.198 | -6850 | -138.3838 | No | No | 58.5 | 1.272 | 2016
QI_2016-07-26_181932 | 2016-07-26 14:20 | 2016-07-26 14:20 | EDT | 2016-07-26 18:20 | 433 | 59.973 | 59.937 | 59.688 | -0.036 | -0.285 | -1202.7778 | -151.9298 | No | No | 58.5 | 1.188 | 2016
QI_2016-07-27_163959 | 2016-07-27 12:40 | 2016-07-27 12:40 | EDT | 2016-07-27 16:40 | 439 | 59.987 | 59.907 | 59.603 | -0.08 | -0.384 | -548.75 | -114.3229 | Yes | Yes | 58.5 | 1.103 | 2016
QI_2016-08-04_060740 | 2016-08-04 02:08 | 2016-08-04 02:08 | EDT | 2016-08-04 06:08 | 881 | 60.061 | 59.872 | 59.274 | -0.189 | -0.787 | -466.1376 | -111.9441 | Yes | Yes | 58.5 | 0.774 | 2016
QI_2016-08-04_185629 | 2016-08-04 14:56 | 2016-08-04 14:56 | EDT | 2016-08-04 18:56 | 928 | 60.012 | 59.842 | 59.244 | -0.17 | -0.768 | -545.8824 | -120.8333 | Yes | Yes | 58.5 | 0.744 | 2016
QI_2016-08-05_111412 | 2016-08-05 07:14 | 2016-08-05 07:14 | EDT | 2016-08-05 11:14 | 309 | 60.007 | 59.988 | 59.751 | -0.019 | -0.256 | -1626.3158 | -120.7031 | No | No | 58.5 | 1.251 | 2016
QI_2016-08-05_142405 | 2016-08-05 10:24 | 2016-08-05 10:24 | EDT | 2016-08-05 14:24 | 342 | 59.97 | 59.938 | 59.711 | -0.032 | -0.259 | -1068.75 | -132.0463 | No | No | 58.5 | 1.211 | 2016
QI_2016-08-07_022535 | 2016-08-06 22:26 | 2016-08-06 22:26 | EDT | 2016-08-07 02:26 | 471 | 60.027 | 59.908 | 59.834 | -0.119 | -0.193 | -395.7983 | -244.0415 | No | No | 58.5 | 1.334 | 2016
QI_2016-08-09_210044 | 2016-08-09 17:01 | 2016-08-09 17:01 | EDT | 2016-08-09 21:01 | 471 | 59.982 | 59.962 | 59.655 | -0.02 | -0.327 | -2355 | -144.0367 | No | No | 58.5 | 1.155 | 2016
QI_2016-08-10_165438 | 2016-08-10 12:55 | 2016-08-10 12:55 | EDT | 2016-08-10 16:55 | 309 | 60.004 | 59.948 | 59.629 | -0.056 | -0.375 | -551.7857 | -82.4 | Yes | Yes | 58.5 | 1.129 | 2016
QI_2016-08-10_215255 | 2016-08-10 17:53 | 2016-08-10 17:53 | EDT | 2016-08-10 21:53 | 394 | 59.981 | 59.946 | 59.715 | -0.035 | -0.266 | -1125.7143 | -148.1203 | No | No | 58.5 | 1.215 | 2016
QI_2016-08-11_131246 | 2016-08-11 09:13 | 2016-08-11 09:13 | EDT | 2016-08-11 13:13 | 706 | 60.013 | 59.87 | 59.504 | -0.143 | -0.509 | -493.7063 | -138.7033 | Yes | Yes | 58.5 | 1.004 | 2016
QI_2016-08-16_002202 | 2016-08-15 20:22 | 2016-08-15 20:22 | EDT | 2016-08-16 00:22 | 529 | 60.001 | 59.913 | 59.628 | -0.088 | -0.373 | -601.1364 | -141.8231 | Yes | Yes | 58.5 | 1.128 | 2016
QI_2016-08-20_040940 | 2016-08-20 00:10 | 2016-08-20 00:10 | EDT | 2016-08-20 04:10 | 329 | 60.009 | 59.937 | 59.796 | -0.072 | -0.213 | -456.9444 | -154.4601 | No | No | 58.5 | 1.296 | 2016
QI_2016-08-26_051156 | 2016-08-26 01:12 | 2016-08-26 01:12 | EDT | 2016-08-26 05:12 | 258 | 60.006 | 59.936 | 59.995 | -0.07 | -0.011 | -368.5714 | -2345.4545 | No | No | 58.5 | 1.495 | 2016
QI_2016-08-27_142837 | 2016-08-27 10:29 | 2016-08-27 10:29 | EDT | 2016-08-27 14:29 | 323 | 59.999 | 59.95 | 59.732 | -0.049 | -0.267 | -659.1837 | -120.9738 | No | No | 58.5 | 1.232 | 2016
QI_2016-08-29_132057 | 2016-08-29 09:21 | 2016-08-29 09:21 | EDT | 2016-08-29 13:21 | 514 | 59.989 | 59.918 | 59.649 | -0.071 | -0.34 | -723.9437 | -151.1765 | Yes | Yes | 58.5 | 1.149 | 2016
QI_2016-09-02_215041 | 2016-09-02 17:51 | 2016-09-02 17:51 | EDT | 2016-09-02 21:51 | 1177 | 60.012 | 59.764 | 59.213 | -0.248 | -0.799 | -474.5968 | -147.3091 | Yes | Yes | 58.5 | 0.713 | 2016
QI_2016-09-04_221111 | 2016-09-04 18:11 | 2016-09-04 18:11 | EDT | 2016-09-04 22:11 | 302 | 60 | 59.976 | 59.731 | -0.024 | -0.269 | -1258.3333 | -112.2677 | No | No | 58.5 | 1.231 | 2016
QI_2016-09-05_143543 | 2016-09-05 10:36 | 2016-09-05 10:36 | EDT | 2016-09-05 14:36 | 277 | 60.016 | 59.982 | 59.775 | -0.034 | -0.241 | -814.7059 | -114.9378 | No | No | 58.5 | 1.275 | 2016
QI_2016-09-06_085608 | 2016-09-06 04:56 | 2016-09-06 04:56 | EDT | 2016-09-06 08:56 | 294 | 60.073 | 59.96 | 59.685 | -0.113 | -0.388 | -260.177 | -75.7732 | No | No | 58.5 | 1.185 | 2016
QI_2016-09-06_174941 | 2016-09-06 13:50 | 2016-09-06 13:50 | EDT | 2016-09-06 17:50 | 433 | 59.98 | 59.961 | 59.675 | -0.019 | -0.305 | -2278.9474 | -141.9672 | No | No | 58.5 | 1.175 | 2016
QI_2016-09-07_202440 | 2016-09-07 16:25 | 2016-09-07 16:25 | EDT | 2016-09-07 20:25 | 221 | 60.047 | 59.983 | 59.838 | -0.064 | -0.209 | -345.3125 | -105.7416 | No | No | 58.5 | 1.338 | 2016
QI_2016-09-10_152340 | 2016-09-10 11:24 | 2016-09-10 11:24 | EDT | 2016-09-10 15:24 | 444 | 60.012 | 59.916 | 59.598 | -0.096 | -0.414 | -462.5 | -107.2464 | No | No | 58.5 | 1.098 | 2016
QI_2016-09-11_190953 | 2016-09-11 15:10 | 2016-09-11 15:10 | EDT | 2016-09-11 19:10 | 327 | 60.012 | 59.953 | 59.673 | -0.059 | -0.339 | -554.2373 | -96.4602 | No | No | 58.5 | 1.173 | 2016
QI_2016-09-11_191934 | 2016-09-11 15:20 | 2016-09-11 15:20 | EDT | 2016-09-11 19:20 | 271 | 59.988 | 59.954 | 59.782 | -0.034 | -0.206 | -797.0588 | -131.5534 | No | No | 58.5 | 1.282 | 2016
QI_2016-09-12_024824 | 2016-09-11 22:48 | 2016-09-11 22:48 | EDT | 2016-09-12 02:48 | 286 | 59.974 | 59.957 | 59.716 | -0.017 | -0.258 | -1682.3529 | -110.8527 | No | No | 58.5 | 1.216 | 2016
QI_2016-09-12_051213 | 2016-09-12 01:12 | 2016-09-12 01:12 | EDT | 2016-09-12 05:12 | 258 | 60.012 | 59.95 | 59.692 | -0.062 | -0.32 | -416.129 | -80.625 | No | No | 58.5 | 1.192 | 2016
QI_2016-09-12_225436 | 2016-09-12 18:55 | 2016-09-12 18:55 | EDT | 2016-09-12 22:55 |  | 59.988 | 59.978 | 59.801 | -0.01 | -0.187 |  |  |  |  | 58.5 | 1.301 | 2016
QI_2016-09-13_151146 | 2016-09-13 11:12 | 2016-09-13 11:12 | EDT | 2016-09-13 15:12 | 249 | 59.996 | 59.94 | 59.774 | -0.056 | -0.222 | -444.6429 | -112.1622 | No | No | 58.5 | 1.274 | 2016
QI_2016-09-15_133518 | 2016-09-15 09:35 | 2016-09-15 09:35 | EDT | 2016-09-15 13:35 | 932 | 60 | 59.794 | 59.239 | -0.206 | -0.761 | -452.4272 | -122.4704 | Yes | Yes | 58.5 | 0.739 | 2016
QI_2016-09-16_235036 | 2016-09-16 19:51 | 2016-09-16 19:51 | EDT | 2016-09-16 23:51 | 846 | 59.969 | 59.805 | 59.366 | -0.164 | -0.603 | -515.8537 | -140.2985 | Yes | Yes | 58.5 | 0.866 | 2016
QI_2016-09-18_031238 | 2016-09-17 23:13 | 2016-09-17 23:13 | EDT | 2016-09-18 03:13 | 269 | 60.02 | 59.957 | 59.747 | -0.063 | -0.273 | -426.9841 | -98.5348 | No | No | 58.5 | 1.247 | 2016
QI_2016-09-20_192704 | 2016-09-20 15:27 | 2016-09-20 15:27 | EDT | 2016-09-20 19:27 | 152 | 60.039 | 59.973 | 59.864 | -0.066 | -0.175 | -230.303 | -86.8571 | No | No | 58.5 | 1.364 | 2016
QI_2016-10-01_135345 | 2016-10-01 09:54 | 2016-10-01 09:54 | EDT | 2016-10-01 13:54 | -253 | 60.003 | 60.045 | 59.969 | 0.042 | -0.034 | -602.381 | 744.1176 | No | No | 58.5 | 1.469 | 2016
QI_2016-10-05_155732 | 2016-10-05 11:58 | 2016-10-05 11:58 | EDT | 2016-10-05 15:58 | 495 | 60.009 | 59.919 | 59.586 | -0.09 | -0.423 | -550 | -117.0213 | Yes | Yes | 58.5 | 1.086 | 2016
QI_2016-10-12_215205 | 2016-10-12 17:52 | 2016-10-12 17:52 | EDT | 2016-10-12 21:52 | -451 | 60.01 | 60.117 | 60.451 | 0.107 | 0.441 | -421.4953 | -102.2676 | Yes | Yes | 58.5 | 1.951 | 2016
QI_2016-10-26_112451 | 2016-10-26 07:25 | 2016-10-26 07:25 | EDT | 2016-10-26 11:25 | -484 | 59.981 | 60.07 | 60.443 | 0.089 | 0.462 | -543.8202 | -104.7619 | Yes | Yes | 58.5 | 1.943 | 2016
QI_2016-10-26_180825 | 2016-10-26 14:08 | 2016-10-26 14:08 | EDT | 2016-10-26 18:08 | 1141 | 59.948 | 59.728 | 59.229 | -0.22 | -0.719 | -518.6364 | -158.6926 | Yes | Yes | 58.5 | 0.729 | 2016
QI_2016-10-26_214901 | 2016-10-26 17:49 | 2016-10-26 17:49 | EDT | 2016-10-26 21:49 | 859 | 59.996 | 59.817 | 59.44 | -0.179 | -0.556 | -479.8883 | -154.4964 | Yes | Yes | 58.5 | 0.94 | 2016
QI_2016-10-27_160538 | 2016-10-27 12:06 | 2016-10-27 12:06 | EDT | 2016-10-27 16:06 | 485 | 59.99 | 59.908 | 59.683 | -0.082 | -0.307 | -591.4634 | -157.9805 | Yes | Yes | 58.5 | 1.183 | 2016
QI_2016-11-04_063042 | 2016-11-04 02:31 | 2016-11-04 02:31 | EDT | 2016-11-04 06:31 | 785 | 59.998 | 59.821 | 59.422 | -0.177 | -0.576 | -443.5028 | -136.2847 | Yes | Yes | 58.5 | 0.922 | 2016
QI_2016-11-11_140715 | 2016-11-11 09:07 | 2016-11-11 09:07 | EST | 2016-11-11 14:07 | -730 | 60.009 | 60.13 | 60.629 | 0.121 | 0.62 | -603.3058 | -117.7419 | Yes | Yes | 58.5 | 2.129 | 2016
QI_2016-11-12_084721 | 2016-11-12 03:47 | 2016-11-12 03:47 | EST | 2016-11-12 08:47 | 457 | 60.004 | 59.922 | 59.66 | -0.082 | -0.344 | -557.3171 | -132.8488 | Yes | Yes | 58.5 | 1.16 | 2016
QI_2016-11-16_125240 | 2016-11-16 07:53 | 2016-11-16 07:53 | EST | 2016-11-16 12:53 | 439 | 59.987 | 59.943 | 59.6796 | -0.044 | -0.3074 | -997.7273 | -142.8107 | No | No | 58.5 | 1.1796 | 2016
QI_2016-11-22_112442 | 2016-11-22 06:25 | 2016-11-22 06:25 | EST | 2016-11-22 11:25 | -483 | 59.982 | 60.042 | 60.328 | 0.06 | 0.346 | -805 | -139.5954 | Yes | No | 58.5 | 1.828 | 2016
QI_2016-11-23_144809 | 2016-11-23 09:48 | 2016-11-23 09:48 | EST | 2016-11-23 14:48 | 1637 | 60.009 | 59.625 | 59.019 | -0.384 | -0.99 | -426.3021 | -165.3535 | Yes | Yes | 58.5 | 0.519 | 2016
QI_2016-11-23_175453 | 2016-11-23 12:55 | 2016-11-23 12:55 | EST | 2016-11-23 17:55 | 478 | 60.004 | 59.949 | 59.69 | -0.055 | -0.314 | -869.0909 | -152.2293 | Yes | Yes | 58.5 | 1.19 | 2016
QI_2016-11-25_024832 | 2016-11-24 21:49 | 2016-11-24 21:49 | EST | 2016-11-25 02:49 | -483 | 59.997 | 60.069 | 60.305 | 0.072 | 0.308 | -670.8333 | -156.8182 | Yes | No | 58.5 | 1.805 | 2016
QI_2016-11-25_031749 | 2016-11-24 22:18 | 2016-11-24 22:18 | EST | 2016-11-25 03:18 | -487 | 59.997 | 60.049 | 60.376 | 0.052 | 0.379 | -936.5385 | -128.496 | Yes | No | 58.5 | 1.876 | 2016
QI_2016-11-30_184730 | 2016-11-30 13:47 | 2016-11-30 13:47 | EST | 2016-11-30 18:48 | 706 | 60.001 | 59.874 | 59.539 | -0.127 | -0.462 | -555.9055 | -152.8139 | Yes | Yes | 58.5 | 1.039 | 2016
QI_2016-12-01_195638 | 2016-12-01 14:57 | 2016-12-01 14:57 | EST | 2016-12-01 19:57 | 582 | 60.008 | 59.895 | 59.626 | -0.113 | -0.382 | -515.0442 | -152.356 | Yes | Yes | 58.5 | 1.126 | 2017
QI_2016-12-12_152252 | 2016-12-12 10:23 | 2016-12-12 10:23 | EST | 2016-12-12 15:23 | 696 | 60.003 | 59.89 | 59.596 | -0.113 | -0.407 | -615.9292 | -171.0074 | Yes | Yes | 58.5 | 1.096 | 2017
QI_2016-12-14_204448 | 2016-12-14 15:45 | 2016-12-14 15:45 | EST | 2016-12-14 20:45 | 691 | 59.985 | 59.886 | 59.596 | -0.099 | -0.389 | -697.9798 | -177.635 | Yes | Yes | 58.5 | 1.096 | 2017
QI_2016-12-19_015648 | 2016-12-18 20:57 | 2016-12-18 20:57 | EST | 2016-12-19 01:57 | 439 | 59.9994 | 59.9283 | 59.758 | -0.071102 | -0.2414 | -617.4216 | -181.8546 | No | No | 58.5 | 1.258 | 2017
QI_2016-12-21_094411 | 2016-12-21 04:44 | 2016-12-21 04:44 | EST | 2016-12-21 09:44 | -480 | 59.9957 | 60.0555 | 60.3152 | 0.059799 | 0.3195 | -802.6864 | -150.2348 | No | No | 58.5 | 1.8152 | 2017
QI_2017-01-04_030815 | 2017-01-03 22:08 | 2017-01-03 22:08 | EST | 2017-01-04 03:08 | -550 | 60.021 | 60.083 | 60.348 | 0.062 | 0.327 | -887.0968 | -168.1957 | Yes | Yes | 58.5 | 1.848 | 2017
QI_2017-01-04_034557 | 2017-01-03 22:46 | 2017-01-03 22:46 | EST | 2017-01-04 03:46 | -348 | 59.994 | 60.033 | 60.0039 | 0.039 | 0.0099019 | -892.3077 | -3514.4662 | No | No | 58.5 | 1.5039 | 2017
QI_2017-01-05_005629 | 2017-01-04 19:56 | 2017-01-04 19:56 | EST | 2017-01-05 00:56 | 502 | 59.982 | 59.956 | 59.746 | -0.026 | -0.236 | -1930.7692 | -212.7119 | Yes | No | 58.5 | 1.246 | 2017
QI_2017-01-05_184829 | 2017-01-05 13:48 | 2017-01-05 13:48 | EST | 2017-01-05 18:48 |  | 60.025 | 59.964 | 59.74 | -0.061 | -0.285 |  |  | No | No | 58.5 | 1.24 | 2017
QI_2017-01-12_155000 | 2017-01-12 10:50 | 2017-01-12 10:50 | EST | 2017-01-12 15:50 |  | 60.012 | 59.992 | 59.679 | -0.02 | -0.333 |  |  | No | No | 58.5 | 1.179 | 2017
QI_2017-01-12_230200 | 2017-01-12 18:02 | 2017-01-12 18:02 | EST | 2017-01-12 23:02 |  | 60.011 | 60 | 59.69 | -0.011 | -0.321 |  |  | No | No | 58.5 | 1.19 | 2017
QI_2017-01-17_185400 | 2017-01-17 13:54 | 2017-01-17 13:54 | EST | 2017-01-17 18:54 |  | 59.993 | 60.007 | 59.98 | 0.014 | -0.013 |  |  | No | No | 58.5 | 1.48 | 2017
QI_2017-01-25_201200 | 2017-01-25 15:12 | 2017-01-25 15:12 | EST | 2017-01-25 20:12 |  | 60.018 | 60.003 | 59.615 | -0.015 | -0.403 |  |  | No | No | 58.5 | 1.115 | 2017
QI_2017-02-08_151741 | 2017-02-08 10:18 | 2017-02-08 10:18 | EST | 2017-02-08 15:18 | -479 | 59.992 | 60.003 | 60.348 | 0.011 | 0.356 | -4354.5455 | -134.5506 | Yes | Yes | 58.5 | 1.848 | 2017
QI_2017-02-08_211000 | 2017-02-08 16:10 | 2017-02-08 16:10 | EST | 2017-02-08 21:10 |  | 60.028 | 60.006 | 59.961 | -0.022 | -0.067 |  |  | No | No | 58.5 | 1.461 | 2017
QI_2017-02-17_084000 | 2017-02-17 03:40 | 2017-02-17 03:40 | EST | 2017-02-17 08:40 |  | 59.995 | 59.959 | 59.475 | -0.036 | -0.52 |  |  | No | No | 58.5 | 0.975 | 2017
QI_2017-02-24_210129 | 2017-02-24 16:01 | 2017-02-24 16:01 | EST | 2017-02-24 21:01 |  | 59.964 | 60.035 | 59.967 | 0.071 | 0.003 |  |  | No | No | 58.5 | 1.467 | 2017
QI_2017-02-25_040819 | 2017-02-24 23:08 | 2017-02-24 23:08 | EST | 2017-02-25 04:08 | -449 | 60.003 | 60.072 | 60.337 | 0.069 | 0.334 | -650.7246 | -134.4311 | Yes | Yes | 58.5 | 1.837 | 2017
QI_2017-02-26_145442 | 2017-02-26 09:55 | 2017-02-26 09:55 | EST | 2017-02-26 14:55 | 920 | 59.996 | 59.815 | 59.459 | -0.181 | -0.537 | -508.2873 | -171.3222 | Yes | Yes | 58.5 | 0.959 | 2017
QI_2017-02-26_214345 | 2017-02-26 16:44 | 2017-02-26 16:44 | EST | 2017-02-26 21:44 | -437 | 60.003 | 60.064 | 60.335 | 0.061 | 0.332 | -716.3934 | -131.6265 | Yes | Yes | 58.5 | 1.835 | 2017
QI_2017-03-19_134139 | 2017-03-19 09:42 | 2017-03-19 09:42 | EDT | 2017-03-19 13:42 | -242 | 59.998 | 60.023 | 60.205 | 0.025 | 0.207 | -968 | -116.9082 | No | No | 58.5 | 1.705 | 2017
QI_2017-03-20_035237 | 2017-03-19 23:53 | 2017-03-19 23:53 | EDT | 2017-03-20 03:53 | -474 | 59.996 | 60.04 | 60.31 | 0.044 | 0.314 | -1077.2727 | -150.9554 | Yes | Yes | 58.5 | 1.81 | 2017
QI_2017-03-20_045442 | 2017-03-20 00:55 | 2017-03-20 00:55 | EDT | 2017-03-20 04:55 | -438 | 59.998 | 60.039 | 60.309 | 0.041 | 0.311 | -1068.2927 | -140.836 | No | No | 58.5 | 1.809 | 2017
QI_2017-03-24_080553 | 2017-03-24 04:06 | 2017-03-24 04:06 | EDT | 2017-03-24 08:06 |  | 60.013 | 60.041 | 60.025 | 0.028 | 0.012 |  |  | No | No | 58.5 | 1.525 | 2017
QI_2017-03-30_082745 | 2017-03-30 04:28 | 2017-03-30 04:28 | EDT | 2017-03-30 08:28 | -1 | 59.989 | 60.041 | 60.244 | 0.052 | 0.255 | -1.9231 | -0.39216 | No | No | 58.5 | 1.744 | 2017
QI_2017-04-06_030225 | 2017-04-05 23:02 | 2017-04-05 23:02 | EDT | 2017-04-06 03:02 | 420 | 59.999 | 59.93 | 59.693 | -0.069 | -0.306 | -608.6957 | -137.2549 | Yes | Yes | 58.5 | 1.193 | 2017
QI_2017-04-07_101805 | 2017-04-07 06:18 | 2017-04-07 06:18 | EDT | 2017-04-07 10:18 | -481 | 60.012 | 60.024 | 60.317 | 0.012 | 0.305 | -4008.3333 | -157.7049 | Yes | No | 58.5 | 1.817 | 2017
QI_2017-04-11_025251 | 2017-04-10 22:53 | 2017-04-10 22:53 | EDT | 2017-04-11 02:53 | -470 | 59.934 | 60.045 | 60.38 | 0.111 | 0.446 | -423.4234 | -105.3812 | Yes | No | 58.5 | 1.88 | 2017
QI_2017-04-11_040312 | 2017-04-11 00:03 | 2017-04-11 00:03 | EDT | 2017-04-11 04:03 | -439 | 60.005 | 60.116 | 60.43 | 0.111 | 0.425 | -395.4955 | -103.2941 | Yes | Yes | 58.5 | 1.93 | 2017
QI_2017-04-11_231854 | 2017-04-11 19:19 | 2017-04-11 19:19 | EDT | 2017-04-11 23:19 | -474 | 60.003 | 60.076 | 60.344 | 0.073 | 0.341 | -649.3151 | -139.0029 | Yes | Yes | 58.5 | 1.844 | 2017
QI_2017-04-19_022017 | 2017-04-18 22:20 | 2017-04-18 22:20 | EDT | 2017-04-19 02:20 | 827 | 59.993 | 59.85 | 59.469 | -0.143 | -0.524 | -578.3217 | -157.8244 | No | No | 58.5 | 0.969 | 2017
QI_2017-04-19_114208 | 2017-04-19 07:42 | 2017-04-19 07:42 | EDT | 2017-04-19 11:42 | -465 | 60.015 | 60.075 | 60.381 | 0.06 | 0.366 | -775 | -127.0492 | Yes | Yes | 58.5 | 1.881 | 2017
QI_2017-04-19_133902 | 2017-04-19 09:39 | 2017-04-19 09:39 | EDT | 2017-04-19 13:39 | 1329 | 60.002 | 59.671 | 59.134 | -0.331 | -0.868 | -401.5106 | -153.1106 |  |  | 58.5 | 0.634 | 2017
QI_2017-04-21_211300 | 2017-04-21 17:13 | 2017-04-21 17:13 | EDT | 2017-04-21 21:13 | 405 | 60.007 | 59.958 | 59.704 | -0.049 | -0.303 | -826.5306 | -133.6634 |  |  | 58.5 | 1.204 | 2017
QI_2017-04-30_015932 | 2017-04-29 22:00 | 2017-04-29 22:00 | EDT | 2017-04-30 02:00 | -425 | 59.992 | 60.063 | 60.412 | 0.071 | 0.42 | -598.5915 | -101.1905 | Yes | Yes | 58.5 | 1.912 | 2017
QI_2017-04-30_123832 | 2017-04-30 08:39 | 2017-04-30 08:39 | EDT | 2017-04-30 12:39 | 300 | 60.021 | 59.961 | 59.766 | -0.06 | -0.255 | -500 | -117.6471 | No | No | 58.5 | 1.266 | 2017
QI_2017-04-30_142713 | 2017-04-30 10:27 | 2017-04-30 10:27 | EDT | 2017-04-30 14:27 | -406 | 60.004 | 60.049 | 60.351 | 0.045 | 0.347 | -902.2222 | -117.0029 | Yes | Yes | 58.5 | 1.851 | 2017
QI_2017-05-05_131829 | 2017-05-05 09:18 | 2017-05-05 09:18 | EDT | 2017-05-05 13:18 | -447 | 60.014 | 60.058 | 60.381 | 0.044 | 0.367 | -1015.9091 | -121.7984 | Yes | Yes | 58.5 | 1.881 | 2017
QI_2017-05-06_003219 | 2017-05-05 20:32 | 2017-05-05 20:32 | EDT | 2017-05-06 00:32 | -570 | 59.995 | 60.068 | 60.439 | 0.073 | 0.444 | -780.8219 | -128.3784 | Yes | Yes | 58.5 | 1.939 | 2017
QI_2017-05-06_043409 | 2017-05-06 00:34 | 2017-05-06 00:34 | EDT | 2017-05-06 04:34 | -460 | 59.997 | 60.086 | 60.43 | 0.089 | 0.433 | -516.8539 | -106.2356 | Yes | Yes | 58.5 | 1.93 | 2017
QI_2017-05-06_174749 | 2017-05-06 13:48 | 2017-05-06 13:48 | EDT | 2017-05-06 17:48 | -455 | 59.959 | 60.072 | 60.392 | 0.113 | 0.433 | -402.6549 | -105.0808 | Yes | Yes | 58.5 | 1.892 | 2017
QI_2017-05-09_005509 | 2017-05-08 20:55 | 2017-05-08 20:55 | EDT | 2017-05-09 00:55 | -435 | 60.052 | 60.072 | 60.34 | 0.02 | 0.288 | -2175 | -151.0417 | Yes | No | 58.5 | 1.84 | 2017
QI_2017-05-10_113703 | 2017-05-10 07:37 | 2017-05-10 07:37 | EDT | 2017-05-10 11:37 | 1016 | 60.01 | 59.759 | 59.36 | -0.251 | -0.65 | -404.7809 | -156.3077 | No | No | 58.5 | 0.86 | 2017
QI_2017-05-12_023403 | 2017-05-11 22:34 | 2017-05-11 22:34 | EDT | 2017-05-12 02:34 | -467 | 59.998 | 60.063 | 60.365 | 0.065 | 0.367 | -718.4615 | -127.248 | Yes | Yes | 58.5 | 1.865 | 2017
QI_2017-05-13_210847 | 2017-05-13 17:09 | 2017-05-13 17:09 | EDT | 2017-05-13 21:09 | -474 | 60.015 | 60.07 | 60.39 | 0.055 | 0.375 | -861.8182 | -126.4 | Yes | Yes | 58.5 | 1.89 | 2017
QI_2017-05-22_165959 | 2017-05-22 13:00 | 2017-05-22 13:00 | EDT | 2017-05-22 17:00 | -474 | 60.021 | 60.106 | 60.424 | 0.085 | 0.403 | -557.6471 | -117.6179 | Yes | Yes | 58.5 | 1.924 | 2017
QI_2017-05-24_171813 | 2017-05-24 13:18 | 2017-05-24 13:18 | EDT | 2017-05-24 17:18 | -850 | 60.001 | 60.159 | 60.734 | 0.158 | 0.733 | -537.9747 | -115.9618 | Yes | Yes | 58.5 | 2.234 | 2017
QI_2017-05-25_082830 | 2017-05-25 04:29 | 2017-05-25 04:29 | EDT | 2017-05-25 08:28 | -210 | 59.959 | 60.02 | 60.291 | 0.061 | 0.332 | -344.2623 | -63.253 | No | No | 58.5 | 1.791 | 2017
QI_2017-05-25_235824 | 2017-05-25 19:58 | 2017-05-25 19:58 | EDT | 2017-05-25 23:58 | -448 | 59.985 | 60.086 | 60.448 | 0.101 | 0.463 | -443.5644 | -96.7603 | Yes | Yes | 58.5 | 1.948 | 2017
QI_2017-05-30_193734 | 2017-05-30 15:38 | 2017-05-30 15:38 | EDT | 2017-05-30 19:38 | -419 | 60.016 | 60.056 | 60.357 | 0.04 | 0.341 | -1047.5 | -122.8739 | Yes | Yes | 58.5 | 1.857 | 2017
QI_2017-05-31_180656 | 2017-05-31 14:07 | 2017-05-31 14:07 | EDT | 2017-05-31 18:07 | -700 | 60.041 | 60.157 | 60.606 | 0.116 | 0.565 | -603.4483 | -123.8938 | Yes | Yes | 58.5 | 2.106 | 2017
QI_2017-05-31_220146 | 2017-05-31 18:02 | 2017-05-31 18:02 | EDT | 2017-05-31 22:02 | 823 | 60.034 | 59.713 | 59.368 | -0.321 | -0.666 | -256.3863 | -123.5736 | Yes | No | 58.5 | 0.868 | 2017
QI_2017-06-04_121339 | 2017-06-04 08:14 | 2017-06-04 08:14 | EDT | 2017-06-04 12:14 | 438 | 60.03 | 59.861 | 59.616 | -0.169 | -0.414 | -259.1716 | -105.7971 | Yes | Yes | 58.5 | 1.116 | 2017
QI_2017-06-09_025807 | 2017-06-08 22:58 | 2017-06-08 22:58 | EDT | 2017-06-09 02:58 | -399 | 60.018 | 60.118 | 60.422 | 0.1 | 0.404 | -399 | -98.7624 | No | No | 58.5 | 1.922 | 2017
QI_2017-06-10_033717 | 2017-06-09 23:37 | 2017-06-09 23:37 | EDT | 2017-06-10 03:37 | 314 | 60.063 | 59.921 | 59.699 | -0.142 | -0.364 | -221.1268 | -86.2637 | Yes | No | 58.5 | 1.199 | 2017
QI_2017-06-11_182406 | 2017-06-11 14:24 | 2017-06-11 14:24 | EDT | 2017-06-11 18:24 | -435 | 60.014 | 60.069 | 60.394 | 0.055 | 0.38 | -790.9091 | -114.4737 | Yes | Yes | 58.5 | 1.894 | 2017
QI_2017-06-14_062917 | 2017-06-14 02:29 | 2017-06-14 02:29 | EDT | 2017-06-14 06:29 | -419 | 60.027 | 60.068 | 60.407 | 0.041 | 0.38 | -1021.9512 | -110.2632 | Yes | Yes | 58.5 | 1.907 | 2017
QI_2017-06-20_203123 | 2017-06-20 16:31 | 2017-06-20 16:31 | EDT | 2017-06-20 20:31 | 906 | 60.024 | 59.776 | 59.362 | -0.248 | -0.662 | -365.3226 | -136.858 | Yes | Yes | 58.5 | 0.862 | 2017
QI_2017-06-24_172448 | 2017-06-24 13:25 | 2017-06-24 13:25 | EDT | 2017-06-24 17:25 | -423 | 59.974 | 60.109 | 60.445 | 0.135 | 0.471 | -313.3333 | -89.8089 | Yes | Yes | 58.5 | 1.945 | 2017
QI_2017-06-27_145644 | 2017-06-27 10:57 | 2017-06-27 10:57 | EDT | 2017-06-27 14:57 | -269 | 59.992 | 60.025 | 60.295 | 0.033 | 0.303 | -815.1515 | -88.7789 | No | No | 58.5 | 1.795 | 2017
QI_2017-06-28_224956 | 2017-06-28 18:50 | 2017-06-28 18:50 | EDT | 2017-06-28 22:50 | 904 | 60.003 | 59.395 | 59.624 | -0.608 | -0.379 | -148.6842 | -238.5224 | No | No | 58.5 | 1.124 | 2017
QI_2017-07-03_213835 | 2017-07-03 17:39 | 2017-07-03 17:39 | EDT | 2017-07-03 21:39 | -471 | 60.001 | 60.091 | 60.408 | 0.09 | 0.407 | -523.3333 | -115.7248 | Yes | Yes | 58.5 | 1.908 | 2017
QI_2017-07-04_044031 | 2017-07-04 00:41 | 2017-07-04 00:41 | EDT | 2017-07-04 04:41 | -419 | 60.006 | 60.122 | 60.486 | 0.116 | 0.48 | -361.2069 | -87.2917 | Yes | Yes | 58.5 | 1.986 | 2017
QI_2017-07-06_105622 | 2017-07-06 06:56 | 2017-07-06 06:56 | EDT | 2017-07-06 10:56 | 671 | 59.989 | 59.86 | 59.463 | -0.129 | -0.526 | -520.155 | -127.5665 | Yes | Yes | 58.5 | 0.963 | 2017
QI_2017-07-06_173336 | 2017-07-06 13:34 | 2017-07-06 13:34 | EDT | 2017-07-06 17:34 | 794 | 60.012 | 59.851 | 59.456 | -0.161 | -0.556 | -493.1677 | -142.8058 | No | No | 58.5 | 0.956 | 2017
QI_2017-07-06_222049 | 2017-07-06 18:21 | 2017-07-06 18:21 | EDT | 2017-07-06 22:21 | 403 | 60.01 | 59.939 | 59.682 | -0.071 | -0.328 | -567.6056 | -122.8659 | Yes | Yes | 58.5 | 1.182 | 2017
QI_2017-07-10_162649 | 2017-07-10 12:27 | 2017-07-10 12:27 | EDT | 2017-07-10 16:27 | -796 | 60.016 | 60.129 | 60.625 | 0.113 | 0.609 | -704.4248 | -130.7061 | Yes | Yes | 58.5 | 2.125 | 2017
QI_2017-07-12_204900 | 2017-07-12 16:49 | 2017-07-12 16:49 | EDT | 2017-07-12 20:49 | -292 | 59.984 | 60.013 | 60.283 | 0.029 | 0.299 | -1006.8966 | -97.6589 | No | No | 58.5 | 1.783 | 2017
QI_2017-07-14_171651 | 2017-07-14 13:17 | 2017-07-14 13:17 | EDT | 2017-07-14 17:17 | -470 | 60.009 | 60.109 | 60.428 | 0.1 | 0.419 | -470 | -112.1718 | Yes | Yes | 58.5 | 1.928 | 2017
QI_2017-07-19_165659 | 2017-07-19 12:57 | 2017-07-19 12:57 | EDT | 2017-07-19 16:57 | -489 | 60.002 | 60.076 | 60.38 | 0.074 | 0.378 | -660.8108 | -129.3651 | Yes | Yes | 58.5 | 1.88 | 2017
QI_2017-07-28_113644 | 2017-07-28 07:37 | 2017-07-28 07:37 | EDT | 2017-07-28 11:37 | -440 | 60.011 | 60.07 | 60.397 | 0.059 | 0.386 | -745.7627 | -113.9896 | Yes | Yes | 58.5 | 1.897 | 2017
QI_2017-08-05_021419 | 2017-08-04 22:14 | 2017-08-04 22:14 | EDT | 2017-08-05 02:14 | 390 | 60.008 | 59.947 | 59.677 | -0.061 | -0.331 | -639.3443 | -117.8248 | Yes | Yes | 58.5 | 1.177 | 2017
QI_2017-08-12_105022 | 2017-08-12 06:50 | 2017-08-12 06:50 | EDT | 2017-08-12 10:50 | -429 | 59.978 | 60.076 | 60.477 | 0.098 | 0.499 | -437.7551 | -85.9719 | Yes | Yes | 58.5 | 1.977 | 2017
QI_2017-08-15_212901 | 2017-08-15 17:29 | 2017-08-15 17:29 | EDT | 2017-08-15 21:29 | 637 | 59.96 | 59.874 | 59.525 | -0.086 | -0.435 | -740.6977 | -146.4368 | Yes | Yes | 58.5 | 1.025 | 2017
QI_2017-08-19_030813 | 2017-08-18 23:08 | 2017-08-18 23:08 | EDT | 2017-08-19 03:08 | 457 | 60.026 | 59.891 | 59.58 | -0.135 | -0.446 | -338.5185 | -102.4664 | Yes | Yes | 58.5 | 1.08 | 2017
QI_2017-08-19_040117 | 2017-08-19 00:01 | 2017-08-19 00:01 | EDT | 2017-08-19 04:01 | 439 | 60.001 | 59.944 | 59.606 | -0.057 | -0.395 | -770.1754 | -111.1392 | Yes | Yes | 58.5 | 1.106 | 2017
QI_2017-08-21_222221 | 2017-08-21 18:22 | 2017-08-21 18:22 | EDT | 2017-08-21 22:22 | 698 | 60.029 | 59.908 | 59.503 | -0.121 | -0.526 | -576.8595 | -132.6996 | Yes | Yes | 58.5 | 1.003 | 2017
QI_2017-08-21_235713 | 2017-08-21 19:57 | 2017-08-21 19:57 | EDT | 2017-08-21 23:57 | 697 | 59.993 | 59.891 | 59.512 | -0.102 | -0.481 | -683.3333 | -144.9064 | Yes | Yes | 58.5 | 1.012 | 2017
QI_2017-08-22_014538 | 2017-08-21 21:46 | 2017-08-21 21:46 | EDT | 2017-08-22 01:46 | 954 | 59.947 | 59.81 | 59.373 | -0.137 | -0.574 | -696.3504 | -166.2021 | Yes | Yes | 58.5 | 0.873 | 2017
QI_2017-08-22_142307 | 2017-08-22 10:23 | 2017-08-22 10:23 | EDT | 2017-08-22 14:23 | 414 | 60.002 | 59.97 | 59.705 | -0.032 | -0.297 | -1293.75 | -139.3939 | No | No | 58.5 | 1.205 | 2017
QI_2017-08-24_142023 | 2017-08-24 10:20 | 2017-08-24 10:20 | EDT | 2017-08-24 14:20 | 498 | 60.003 | 59.919 | 59.603 | -0.084 | -0.4 | -592.8571 | -124.5 | Yes | Yes | 58.5 | 1.103 | 2017
QI_2017-08-24_173639 | 2017-08-24 13:37 | 2017-08-24 13:37 | EDT | 2017-08-24 17:37 | 627 | 60.019 | 59.934 | 59.593 | -0.085 | -0.426 | -737.6471 | -147.1831 | Yes | Yes | 58.5 | 1.093 | 2017
QI_2017-08-30_144020 | 2017-08-30 10:40 | 2017-08-30 10:40 | EDT | 2017-08-30 14:40 | -713 | 59.978 | 60.101 | 60.554 | 0.123 | 0.576 | -579.6748 | -123.7847 | Yes | Yes | 58.5 | 2.054 | 2017
QI_2017-09-06_110519 | 2017-09-06 07:05 | 2017-09-06 07:05 | EDT | 2017-09-06 11:05 | 438 | 60.007 | 59.933 | 59.652 | -0.074 | -0.355 | -591.8919 | -123.3803 | Yes | Yes | 58.5 | 1.152 | 2017
QI_2017-09-08_035631 | 2017-09-07 23:57 | 2017-09-07 23:57 | EDT | 2017-09-08 03:57 | 442 | 60.052 | 59.885 | 59.571 | -0.167 | -0.481 | -264.6707 | -91.8919 | Yes | Yes | 58.5 | 1.071 | 2017
QI_2017-09-08_105005 | 2017-09-08 06:50 | 2017-09-08 06:50 | EDT | 2017-09-08 10:50 | 329 | 59.969 | 59.947 | 59.706 | -0.022 | -0.263 | -1495.4545 | -125.0951 | No | No | 58.5 | 1.206 | 2017
QI_2017-09-13_061207 | 2017-09-13 02:12 | 2017-09-13 02:12 | EDT | 2017-09-13 06:12 | -485 | 60.008 | 60.122 | 60.464 | 0.114 | 0.456 | -425.4386 | -106.3596 | Yes | Yes | 58.5 | 1.964 | 2017
QI_2017-09-17_111752 | 2017-09-17 07:18 | 2017-09-17 07:18 | EDT | 2017-09-17 11:18 | 333 | 60 | 59.993 | 59.672 | -0.007 | -0.328 | -4757.1429 | -101.5244 | No | No | 58.5 | 1.172 | 2017
QI_2017-09-22_184131 | 2017-09-22 14:42 | 2017-09-22 14:42 | EDT | 2017-09-22 18:42 | -449 | 60.001 | 60.069 | 60.403 | 0.068 | 0.402 | -660.2941 | -111.6915 | Yes | Yes | 58.5 | 1.903 | 2017
QI_2017-10-04_143404 | 2017-10-04 10:34 | 2017-10-04 10:34 | EDT | 2017-10-04 14:34 | -404 | 59.983 | 60.057 | 60.387 | 0.074 | 0.404 | -545.9459 | -100 | Yes | Yes | 58.5 | 1.887 | 2017
QI_2017-10-09_032413 | 2017-10-08 23:24 | 2017-10-08 23:24 | EDT | 2017-10-09 03:24 | 503 | 59.997 | 59.843 | 59.508 | -0.154 | -0.489 | -326.6234 | -102.863 | Yes | Yes | 58.5 | 1.008 | 2017
QI_2017-10-15_185313 | 2017-10-15 14:53 | 2017-10-15 14:53 | EDT | 2017-10-15 18:53 | 356 | 60.006 | 59.986 | 59.691 | -0.02 | -0.315 | -1780 | -113.0159 | Yes | No | 58.5 | 1.191 | 2017
QI_2017-10-18_052408 | 2017-10-18 01:24 | 2017-10-18 01:24 | EDT | 2017-10-18 05:24 | 335 | 60.005 | 59.874 | 59.647 | -0.131 | -0.358 | -255.7252 | -93.5754 | Yes | Yes | 58.5 | 1.147 | 2017
QI_2017-10-19_035104 | 2017-10-18 23:51 | 2017-10-18 23:51 | EDT | 2017-10-19 03:51 | 336 | 60.009 | 59.96 | 59.702 | -0.049 | -0.307 | -685.7143 | -109.4463 | Yes | No | 58.5 | 1.202 | 2017
QI_2017-10-20_225454 | 2017-10-20 18:55 | 2017-10-20 18:55 | EDT | 2017-10-20 22:55 | 475 | 60 | 59.903 | 59.592 | -0.097 | -0.408 | -489.6907 | -116.4216 | Yes | Yes | 58.5 | 1.092 | 2017
QI_2017-10-23_005045 | 2017-10-22 20:51 | 2017-10-22 20:51 | EDT | 2017-10-23 00:51 | 307 | 60.02 | 59.884 | 59.695 | -0.136 | -0.325 | -225.7353 | -94.4615 | Yes | Yes | 58.5 | 1.195 | 2017
QI_2017-10-24_124154 | 2017-10-24 08:42 | 2017-10-24 08:42 | EDT | 2017-10-24 12:42 | -617 | 59.983 | 60.12 | 60.528 | 0.137 | 0.545 | -450.365 | -113.211 | Yes | Yes | 58.5 | 2.028 | 2017
QI_2017-10-26_122641 | 2017-10-26 08:27 | 2017-10-26 08:27 | EDT | 2017-10-26 12:27 | 451 | 60.008 | 59.929 | 59.647 | -0.079 | -0.361 | -570.8861 | -124.9307 | Yes | Yes | 58.5 | 1.147 | 2017
QI_2017-10-29_023541 | 2017-10-28 22:36 | 2017-10-28 22:36 | EDT | 2017-10-29 02:36 | 279 | 60.01 | 59.987 | 59.699 | -0.023 | -0.311 | -1213.0435 | -89.7106 | Yes | No | 58.5 | 1.199 | 2017
QI_2017-10-30_211914 | 2017-10-30 17:19 | 2017-10-30 17:19 | EDT | 2017-10-30 21:19 | 438 | 59.999 | 59.866 | 59.575 | -0.133 | -0.424 | -329.3233 | -103.3019 | Yes | Yes | 58.5 | 1.075 | 2017
QI_2017-11-06_195115 | 2017-11-06 14:51 | 2017-11-06 14:51 | EST | 2017-11-06 19:51 | -480 | 60.055 | 60.164 | 60.541 | 0.109 | 0.486 | -440.367 | -98.7654 | Yes | Yes | 58.5 | 2.041 | 2017
QI_2017-11-08_004005 | 2017-11-07 19:40 | 2017-11-07 19:40 | EST | 2017-11-08 00:40 | 435 | 59.998 | 59.941 | 59.665 | -0.057 | -0.333 | -763.1579 | -130.6306 | Yes | Yes | 58.5 | 1.165 | 2017
QI_2017-11-11_153300 | 2017-11-11 10:33 | 2017-11-11 10:33 | EST | 2017-11-11 15:33 | 380 | 59.975 | 59.926 | 59.691 | -0.049 | -0.284 | -775.5102 | -133.8028 | No | No | 58.5 | 1.191 | 2017
QI_2017-11-11_121134 | 2017-11-11 07:12 | 2017-11-11 07:12 | EST | 2017-11-11 12:12 | 972 | 59.997 | 59.807 | 59.35 | -0.19 | -0.647 | -511.5789 | -150.2318 | No | No | 58.5 | 0.85 | 2017
QI_2017-11-11_155651 | 2017-11-11 10:57 | 2017-11-11 10:57 | EST | 2017-11-11 15:57 | 837 | 59.988 | 59.841 | 59.411 | -0.147 | -0.577 | -569.3878 | -145.0607 | No | No | 58.5 | 0.911 | 2017
QI_2017-11-11_180417 | 2017-11-11 13:04 | 2017-11-11 13:04 | EST | 2017-11-11 18:04 | 801 | 59.988 | 59.856 | 59.456 | -0.132 | -0.532 | -606.8182 | -150.5639 | No | No | 58.5 | 0.956 | 2017
QI_2017-12-07_200118 | 2017-12-07 15:01 | 2017-12-07 15:01 | EST | 2017-12-07 20:01 | -517 | 59.998 | 60.072 | 60.381 | 0.074 | 0.383 | -698.6486 | -134.9869 | Yes | Yes | 58.5 | 1.881 | 2018
QI_2017-12-13_190559 | 2017-12-13 14:06 | 2017-12-13 14:06 | EST | 2017-12-13 19:06 | -524 | 60.049 | 60.055 | 60.298 | 0.006 | 0.249 | -8733.3333 | -210.4418 | Yes | No | 58.5 | 1.798 | 2018
QI_2017-12-15_151055 | 2017-12-15 10:11 | 2017-12-15 10:11 | EST | 2017-12-15 15:11 | 898 | 60.013 | 59.85 | 59.444 | -0.163 | -0.569 | -550.9202 | -157.8207 | No | No | 58.5 | 0.944 | 2018
QI_2017-12-15_174554 | 2017-12-15 12:46 | 2017-12-15 12:46 | EST | 2017-12-15 17:46 | 896 | 60.006 | 59.834 | 59.491 | -0.172 | -0.515 | -520.9302 | -173.9806 | No | No | 58.5 | 0.991 | 2018
QI_2017-12-16_054559 | 2017-12-16 00:46 | 2017-12-16 00:46 | EST | 2017-12-16 05:46 | -472 | 60.006 | 60.059 | 60.273 | 0.053 | 0.267 | -890.566 | -176.779 | Yes | No | 58.5 | 1.773 | 2018
QI_2017-12-20_035720 | 2017-12-19 22:57 | 2017-12-19 22:57 | EST | 2017-12-20 03:57 | -500 | 60.014 | 60.074 | 60.286 | 0.06 | 0.272 | -833.3333 | -183.8235 | Yes | No | 58.5 | 1.786 | 2018
QI_2017-12-20_095429 | 2017-12-20 04:54 | 2017-12-20 04:54 | EST | 2017-12-20 09:54 | -500 | 60.015 | 60.07 | 60.365 | 0.055 | 0.35 | -909.0909 | -142.8571 | Yes | Yes | 58.5 | 1.865 | 2018
QI_2017-12-20_233618 | 2017-12-20 18:36 | 2017-12-20 18:36 | EST | 2017-12-20 23:36 | 590 | 60.027 | 59.932 | 59.675 | -0.095 | -0.352 | -621.0526 | -167.6136 | Yes | Yes | 58.5 | 1.175 | 2018
QI_2017-12-22_130113 | 2017-12-22 08:01 | 2017-12-22 08:01 | EST | 2017-12-22 13:01 | 989 | 59.995 | 59.786 | 59.43 | -0.209 | -0.565 | -473.2057 | -175.0442 | Yes | Yes | 58.5 | 0.93 | 2018
QI_2017-12-22_132146 | 2017-12-22 08:22 | 2017-12-22 08:22 | EST | 2017-12-22 13:22 | 953 | 60.031 | 59.769 | 59.436 | -0.262 | -0.595 | -363.7405 | -160.1681 | Yes | Yes | 58.5 | 0.936 | 2018
QI_2018-01-11_183311 | 2018-01-11 13:33 | 2018-01-11 13:33 | EST | 2018-01-11 18:33 | 491 | 60 | 59.946 | 59.711 | -0.054 | -0.289 | -909.2593 | -169.8962 | Yes | No | 58.5 | 1.211 | 2018
QI_2018-01-12_123615 | 2018-01-12 07:36 | 2018-01-12 07:36 | EST | 2018-01-12 12:36 | 471 | 59.995 | 59.934 | 59.673 | -0.061 | -0.322 | -772.1311 | -146.2733 | Yes | Yes | 58.5 | 1.173 | 2018
QI_2018-01-25_212121 | 2018-01-25 16:21 | 2018-01-25 16:21 | EST | 2018-01-25 21:21 | 925 | 59.986 | 59.897 | 59.524 | -0.089 | -0.462 | -1039.3258 | -200.2165 | No | No | 58.5 | 1.024 | 2018
QI_2018-01-25_212135 | 2018-01-25 16:22 | 2018-01-25 16:22 | EST | 2018-01-25 21:22 |  | 59.986 | 59.896 | 59.524 | -0.09 | -0.462 |  |  | No | No | 58.5 | 1.024 | 2018
QI_2018-02-03_133521 | 2018-02-03 08:35 | 2018-02-03 08:35 | EST | 2018-02-03 13:35 | -666 | 60.007 | 60.1 | 60.369 | 0.093 | 0.362 | -716.129 | -183.9779 | Yes | No | 58.5 | 1.869 | 2018
QI_2018-02-03_141538 | 2018-02-03 09:16 | 2018-02-03 09:16 | EST | 2018-02-03 14:16 | -478 | 59.967 | 60.047 | 60.312 | 0.08 | 0.345 | -597.5 | -138.5507 | Yes | No | 58.5 | 1.812 | 2018
QI_2018-02-08_190919 | 2018-02-08 14:09 | 2018-02-08 14:09 | EST | 2018-02-08 19:09 | 488 | 59.998 | 59.911 | 59.684 | -0.087 | -0.314 | -560.9195 | -155.414 | Yes | Yes | 58.5 | 1.184 | 2018
QI_2018-02-17_214010 | 2018-02-17 16:40 | 2018-02-17 16:40 | EST | 2018-02-17 21:40 | -478 | 59.999 | 60.029 | 60.338 | 0.03 | 0.339 | -1593.3333 | -141.0029 | Yes | No | 58.5 | 1.838 | 2018
QI_2018-03-05_025157 | 2018-03-04 21:52 | 2018-03-04 21:52 | EST | 2018-03-05 02:52 | 499 | 59.958 | 59.888 | 59.641 | -0.07 | -0.317 | -712.8571 | -157.4132 | Yes | Yes | 58.5 | 1.141 | 2018
QI_2018-03-05_074153 | 2018-03-05 02:42 | 2018-03-05 02:42 | EST | 2018-03-05 07:42 | 455 | 59.997 | 59.953 | 59.64 | -0.044 | -0.357 | -1034.0909 | -127.451 | Yes | Yes | 58.5 | 1.14 | 2018
QI_2018-03-10_183317 | 2018-03-10 13:33 | 2018-03-10 13:33 | EST | 2018-03-10 18:33 | -481 | 59.961 | 60.048 | 60.343 | 0.087 | 0.382 | -552.8736 | -125.9162 | Yes | Yes | 58.5 | 1.843 | 2018
QI_2018-03-12_011543 | 2018-03-11 21:16 | 2018-03-11 21:16 | EDT | 2018-03-12 01:16 | 989 | 59.996 | 59.826 | 59.382 | -0.17 | -0.614 | -581.7647 | -161.0749 | No | No | 58.5 | 0.882 | 2018
QI_2018-03-12_011650 | 2018-03-11 21:17 | 2018-03-11 21:17 | EDT | 2018-03-12 01:17 | 516 | 59.916 | 59.894 | 59.583 | -0.022 | -0.333 | -2345.4545 | -154.955 | No | No | 58.5 | 1.083 | 2018
QI_2018-03-14_175603 | 2018-03-14 13:56 | 2018-03-14 13:56 | EDT | 2018-03-14 17:56 | 1000 | 59.996 | 59.787 | 59.345 | -0.209 | -0.651 | -478.4689 | -153.6098 | Yes | Yes | 58.5 | 0.845 | 2018
QI_2018-03-27_105518 | 2018-03-27 06:55 | 2018-03-27 06:55 | EDT | 2018-03-27 10:55 | -617 | 59.996 | 60.091 | 60.375 | 0.095 | 0.379 | -649.4737 | -162.7968 | Yes | Yes | 58.5 | 1.875 | 2018
QI_2018-03-30_083057 | 2018-03-30 04:31 | 2018-03-30 04:31 | EDT | 2018-03-30 08:31 | -469 | 59.992 | 60.052 | 60.36 | 0.06 | 0.368 | -781.6667 | -127.4457 | Yes | Yes | 58.5 | 1.86 | 2018
QI_2018-04-04_112405 | 2018-04-04 07:24 | 2018-04-04 07:24 | EDT | 2018-04-04 11:24 | -492 | 60.027 | 60.074 | 60.318 | 0.047 | 0.291 | -1046.8085 | -169.0722 | Yes | Yes | 58.5 | 1.818 | 2018
QI_2018-04-12_042651 | 2018-04-12 00:27 | 2018-04-12 00:27 | EDT | 2018-04-12 04:27 | -354 | 60.022 | 60.027 | 60.305 | 0.005 | 0.283 | -7080 | -125.0883 | No | No | 58.5 | 1.805 | 2018
QI_2018-04-21_190857 | 2018-04-21 15:09 | 2018-04-21 15:09 | EDT | 2018-04-21 19:09 | 759 | 60.027 | 59.825 | 59.435 | -0.202 | -0.592 | -375.7426 | -128.2095 | Yes | Yes | 58.5 | 0.935 | 2018
QI_2018-04-28_010138 | 2018-04-27 21:02 | 2018-04-27 21:02 | EDT | 2018-04-28 01:02 | -437 | 60.018 | 60.063 | 60.369 | 0.045 | 0.351 | -971.1111 | -124.5014 | Yes | Yes | 58.5 | 1.869 | 2018
QI_2018-05-01_202642 | 2018-05-01 16:27 | 2018-05-01 16:27 | EDT | 2018-05-01 20:27 | 1189 | 60.011 | 59.745 | 59.178 | -0.266 | -0.833 | -446.9925 | -142.7371 | Yes | Yes | 58.5 | 0.678 | 2018
QI_2018-05-02_032703 | 2018-05-01 23:27 | 2018-05-01 23:27 | EDT | 2018-05-02 03:27 | -454 | 60.016 | 60.084 | 60.428 | 0.068 | 0.412 | -667.6471 | -110.1942 | Yes | Yes | 58.5 | 1.928 | 2018
QI_2018-05-11_133734 | 2018-05-11 09:38 | 2018-05-11 09:38 | EDT | 2018-05-11 13:38 | -407 | 60.01 | 60.048 | 60.354 | 0.038 | 0.344 | -1071.0526 | -118.314 | Yes | Yes | 58.5 | 1.854 | 2018
QI_2018-05-15_060040 | 2018-05-15 02:01 | 2018-05-15 02:01 | EDT | 2018-05-15 06:01 | -439 | 60.014 | 60.122 | 60.527 | 0.108 | 0.513 | -406.4815 | -85.575 | Yes | No | 58.5 | 2.027 | 2018
QI_2018-05-17_223703 | 2018-05-17 18:37 | 2018-05-17 18:37 | EDT | 2018-05-17 22:37 | 494 | 59.987 | 59.92 | 59.632 | -0.067 | -0.355 | -737.3134 | -139.1549 | Yes | Yes | 58.5 | 1.132 | 2018
QI_2018-06-04_112613 | 2018-06-04 07:26 | 2018-06-04 07:26 | EDT | 2018-06-04 11:26 | -475 | 60.018 | 60.086 | 60.395 | 0.068 | 0.377 | -698.5294 | -125.9947 | Yes | Yes | 58.5 | 1.895 | 2018
QI_2018-06-05_155013 | 2018-06-05 11:50 | 2018-06-05 11:50 | EDT | 2018-06-05 15:50 | -467 | 60.004 | 60.083 | 60.397 | 0.079 | 0.393 | -591.1392 | -118.8295 | Yes | Yes | 58.5 | 1.897 | 2018
QI_2018-06-06_012924 | 2018-06-05 21:29 | 2018-06-05 21:29 | EDT | 2018-06-06 01:29 | -464 | 59.969 | 60.056 | 60.331 | 0.087 | 0.362 | -533.3333 | -128.1768 | Yes | Yes | 58.5 | 1.831 | 2018
QI_2018-06-13_164229 | 2018-06-13 12:42 | 2018-06-13 12:42 | EDT | 2018-06-13 16:42 | -424 | 59.98 | 60.046 | 60.357 | 0.066 | 0.377 | -642.4242 | -112.4668 | Yes | Yes | 58.5 | 1.857 | 2018
QI_2018-06-14_235329 | 2018-06-14 19:53 | 2018-06-14 19:53 | EDT | 2018-06-14 23:53 | 521 | 60.008 | 59.913 | 59.588 | -0.095 | -0.42 | -548.4211 | -124.0476 | Yes | Yes | 58.5 | 1.088 | 2018
QI_2018-06-25_132245 | 2018-06-25 09:23 | 2018-06-25 09:23 | EDT | 2018-06-25 13:23 | 412 | 59.989 | 59.922 | 59.666 | -0.067 | -0.323 | -614.9254 | -127.5542 | Yes | Yes | 58.5 | 1.166 | 2018
QI_2018-06-26_172019 | 2018-06-26 13:20 | 2018-06-26 13:20 | EDT | 2018-06-26 17:20 | -374 | 60.001 | 60.046 | 60.32 | 0.045 | 0.319 | -831.1111 | -117.2414 | Yes | Yes | 58.5 | 1.82 | 2018
QI_2018-06-29_210040 | 2018-06-29 17:01 | 2018-06-29 17:01 | EDT | 2018-06-29 21:01 | 390 | 59.988 | 59.92 | 59.689 | -0.068 | -0.299 | -573.5294 | -130.4348 | No | No | 58.5 | 1.189 | 2018
QI_2018-07-04_185548 | 2018-07-04 14:56 | 2018-07-04 14:56 | EDT | 2018-07-04 18:56 | 484 | 60.001 | 59.93 | 59.635 | -0.071 | -0.366 | -681.6901 | -132.2404 | Yes | Yes | 58.5 | 1.135 | 2018
QI_2018-07-05_093310 | 2018-07-05 05:33 | 2018-07-05 05:33 | EDT | 2018-07-05 09:33 | -350 | 59.987 | 60.04 | 60.306 | 0.053 | 0.319 | -660.3774 | -109.7179 | Yes | Yes | 58.5 | 1.806 | 2018
QI_2018-07-09_005829 | 2018-07-08 20:58 | 2018-07-08 20:58 | EDT | 2018-07-09 00:58 | 320 | 59.987 | 59.952 | 59.698 | -0.035 | -0.289 | -914.2857 | -110.7266 | No | No | 58.5 | 1.198 | 2018
QI_2018-07-09_011344 | 2018-07-08 21:14 | 2018-07-08 21:14 | EDT | 2018-07-09 01:14 | 338 | 60.008 | 59.967 | 59.697 | -0.041 | -0.311 | -824.3902 | -108.6817 | Yes | No | 58.5 | 1.197 | 2018
QI_2018-07-09_022744 | 2018-07-08 22:28 | 2018-07-08 22:28 | EDT | 2018-07-09 02:28 | 348 | 59.988 | 59.952 | 59.689 | -0.036 | -0.299 | -966.6667 | -116.388 | No | No | 58.5 | 1.189 | 2018
QI_2018-07-16_140526 | 2018-07-16 10:05 | 2018-07-16 10:05 | EDT | 2018-07-16 14:05 | 460 | 60.002 | 59.904 | 59.625 | -0.098 | -0.377 | -469.3878 | -122.0159 | Yes | Yes | 58.5 | 1.125 | 2018
QI_2018-07-16_203008 | 2018-07-16 16:30 | 2018-07-16 16:30 | EDT | 2018-07-16 20:30 | 1231 | 60.011 | 59.761 | 59.186 | -0.25 | -0.825 | -492.4 | -149.2121 | Yes | Yes | 58.5 | 0.686 | 2018
QI_2018-07-19_011140 | 2018-07-18 21:12 | 2018-07-18 21:12 | EDT | 2018-07-19 01:12 | 487 | 60 | 59.951 | 59.628 | -0.049 | -0.372 | -993.8776 | -130.914 | Yes | Yes | 58.5 | 1.128 | 2018
QI_2018-07-21_105747 | 2018-07-21 06:58 | 2018-07-21 06:58 | EDT | 2018-07-21 10:58 | -468 | 60.001 | 60.075 | 60.425 | 0.074 | 0.424 | -632.4324 | -110.3774 | Yes | Yes | 58.5 | 1.925 | 2018
QI_2018-07-21_144828 | 2018-07-21 10:48 | 2018-07-21 10:48 | EDT | 2018-07-21 14:48 | 470 | 60.051 | 59.947 | 59.628 | -0.104 | -0.423 | -451.9231 | -111.1111 | Yes | Yes | 58.5 | 1.128 | 2018
QI_2018-07-21_160439 | 2018-07-21 12:05 | 2018-07-21 12:05 | EDT | 2018-07-21 16:05 | 470 | 59.986 | 59.943 | 59.66 | -0.043 | -0.326 | -1093.0233 | -144.1718 | Yes | Yes | 58.5 | 1.16 | 2018
QI_2018-07-21_205359 | 2018-07-21 16:54 | 2018-07-21 16:54 | EDT | 2018-07-21 20:54 | 920 | 60.014 | 59.835 | 59.292 | -0.179 | -0.722 | -513.9665 | -127.4238 | Yes | Yes | 58.5 | 0.792 | 2018
QI_2018-07-24_034623 | 2018-07-23 23:46 | 2018-07-23 23:46 | EDT | 2018-07-24 03:46 | 438 | 60.022 | 59.949 | 59.659 | -0.073 | -0.363 | -600 | -120.6612 | Yes | Yes | 58.5 | 1.159 | 2018
QI_2018-07-24_144132 | 2018-07-24 10:42 | 2018-07-24 10:42 | EDT | 2018-07-24 14:42 | 439 | 60.038 | 59.933 | 59.607 | -0.105 | -0.431 | -418.0952 | -101.8561 | Yes | Yes | 58.5 | 1.107 | 2018
QI_2018-07-28_021150 | 2018-07-27 22:12 | 2018-07-27 22:12 | EDT | 2018-07-28 02:12 | 411 | 59.966 | 59.941 | 59.655 | -0.025 | -0.311 | -1644 | -132.1543 | Yes | No | 58.5 | 1.155 | 2018
QI_2018-07-28_124536 | 2018-07-28 08:46 | 2018-07-28 08:46 | EDT | 2018-07-28 12:46 | -467 | 60.013 | 60.069 | 60.374 | 0.056 | 0.361 | -833.9286 | -129.3629 | Yes | Yes | 58.5 | 1.874 | 2018
QI_2018-07-30_154656 | 2018-07-30 11:47 | 2018-07-30 11:47 | EDT | 2018-07-30 15:47 | 418 | 60.009 | 59.953 | 59.668 | -0.056 | -0.341 | -746.4286 | -122.5806 | Yes | Yes | 58.5 | 1.168 | 2018
QI_2018-08-05_013252 | 2018-08-04 21:33 | 2018-08-04 21:33 | EDT | 2018-08-05 01:33 | -456 | 60 | 60.064 | 60.39 | 0.064 | 0.39 | -712.5 | -116.9231 | Yes | Yes | 58.5 | 1.89 | 2018
QI_2018-08-12_080207 | 2018-08-12 04:02 | 2018-08-12 04:02 | EDT | 2018-08-12 08:02 | -442 | 59.988 | 60.058 | 60.384 | 0.07 | 0.396 | -631.4286 | -111.6162 | Yes | Yes | 58.5 | 1.884 | 2018
QI_2018-08-26_183958 | 2018-08-26 14:40 | 2018-08-26 14:40 | EDT | 2018-08-26 18:40 | 574 | 59.976 | 59.899 | 59.535 | -0.077 | -0.441 | -745.4545 | -130.1587 | Yes | Yes | 58.5 | 1.035 | 2018
QI_2018-08-27_200846 | 2018-08-27 16:09 | 2018-08-27 16:09 | EDT | 2018-08-27 20:09 | 397 | 60.029 | 60.03 | 59.692 | 0.001 | -0.337 | 39700 | -117.8042 | No | No | 58.5 | 1.192 | 2018
QI_2018-08-29_131620 | 2018-08-29 09:16 | 2018-08-29 09:16 | EDT | 2018-08-29 13:16 | 486 | 59.957 | 59.941 | 59.621 | -0.016 | -0.336 | -3037.5 | -144.6429 | Yes | No | 58.5 | 1.121 | 2018
QI_2018-08-29_222857 | 2018-08-29 18:29 | 2018-08-29 18:29 | EDT | 2018-08-29 22:29 | 447 | 60.008 | 59.93 | 59.613 | -0.078 | -0.395 | -573.0769 | -113.1646 | Yes | Yes | 58.5 | 1.113 | 2018
QI_2018-08-30_133901 | 2018-08-30 09:39 | 2018-08-30 09:39 | EDT | 2018-08-30 13:39 | 461 | 60.003 | 59.944 | 59.617 | -0.059 | -0.386 | -781.3559 | -119.4301 | Yes | Yes | 58.5 | 1.117 | 2018
QI_2018-08-31_104350 | 2018-08-31 06:44 | 2018-08-31 06:44 | EDT | 2018-08-31 10:44 | -102 | 60.012 | 60.03 | 60.216 | 0.018 | 0.204 | -566.6667 | -50 | No | No | 58.5 | 1.716 | 2018
QI_2018-08-31_130621 | 2018-08-31 09:06 | 2018-08-31 09:06 | EDT | 2018-08-31 13:06 | -473 | 60 | 60.068 | 60.399 | 0.068 | 0.399 | -695.5882 | -118.5464 | Yes | Yes | 58.5 | 1.899 | 2018
QI_2018-09-02_234535 | 2018-09-02 19:46 | 2018-09-02 19:46 | EDT | 2018-09-02 23:46 | 472 | 59.985 | 59.937 | 59.6 | -0.048 | -0.385 | -983.3333 | -122.5974 | No | No | 58.5 | 1.1 | 2018
QI_2018-09-04_120442 | 2018-09-04 08:05 | 2018-09-04 08:05 | EDT | 2018-09-04 12:05 | -477 | 60.008 | 60.065 | 60.422 | 0.057 | 0.414 | -836.8421 | -115.2174 | Yes | Yes | 58.5 | 1.922 | 2018
QI_2018-09-04_120923 | 2018-09-04 08:09 | 2018-09-04 08:09 | EDT | 2018-09-04 12:09 | 480 | 60.006 | 59.948 | 59.612 | -0.058 | -0.394 | -827.5862 | -121.8274 | No | No | 58.5 | 1.112 | 2018
QI_2018-09-11_144104 | 2018-09-11 10:41 | 2018-09-11 10:41 | EDT | 2018-09-11 14:41 | 476 | 59.998 | 59.887 | 59.61 | -0.111 | -0.388 | -428.8288 | -122.6804 | No | No | 58.5 | 1.11 | 2018
QI_2018-09-15_001247 | 2018-09-14 20:13 | 2018-09-14 20:13 | EDT | 2018-09-15 00:13 | 414 | 59.999 | 59.953 | 59.669 | -0.046 | -0.33 | -900 | -125.4545 | No | No | 58.5 | 1.169 | 2018
QI_2018-09-18_013014 | 2018-09-17 21:30 | 2018-09-17 21:30 | EDT | 2018-09-18 01:30 | 418 | 60.014 | 59.974 | 59.654 | -0.04 | -0.36 | -1045 | -116.1111 | No | No | 58.5 | 1.154 | 2018
QI_2018-09-18_111527 | 2018-09-18 07:15 | 2018-09-18 07:15 | EDT | 2018-09-18 11:15 | 397 | 59.966 | 59.936 | 59.676 | -0.03 | -0.29 | -1323.3333 | -136.8966 | No | No | 58.5 | 1.176 | 2018
QI_2018-09-18_164137 | 2018-09-18 12:42 | 2018-09-18 12:42 | EDT | 2018-09-18 16:42 | 403 | 59.993 | 59.966 | 59.646 | -0.027 | -0.347 | -1492.5926 | -116.1383 | No | No | 58.5 | 1.146 | 2018
QI_2018-09-20_124150 | 2018-09-20 08:42 | 2018-09-20 08:42 | EDT | 2018-09-20 12:42 | -700 | 59.992 | 60.113 | 60.555 | 0.121 | 0.563 | -578.5124 | -124.3339 | Yes | Yes | 58.5 | 2.055 | 2018
QI_2018-09-21_203027 | 2018-09-21 16:30 | 2018-09-21 16:30 | EDT | 2018-09-21 20:30 | 871 | 60.004 | 59.775 | 59.321 | -0.229 | -0.683 | -380.3493 | -127.5256 | No | No | 58.5 | 0.821 | 2018
QI_2018-09-22_173108 | 2018-09-22 13:31 | 2018-09-22 13:31 | EDT | 2018-09-22 17:31 | 418 | 59.959 | 59.92 | 59.586 | -0.039 | -0.373 | -1071.7949 | -112.0643 | No | No | 58.5 | 1.086 | 2018
QI_2018-09-23_085510 | 2018-09-23 04:55 | 2018-09-23 04:55 | EDT | 2018-09-23 08:55 | -302 | 59.992 | 60.041 | 60.34 | 0.049 | 0.348 | -616.3265 | -86.7816 | No | No | 58.5 | 1.84 | 2018
QI_2018-09-23_174146 | 2018-09-23 13:42 | 2018-09-23 13:42 | EDT | 2018-09-23 17:42 | -481 | 60.01 | 60.078 | 60.421 | 0.068 | 0.411 | -707.3529 | -117.0316 | No | No | 58.5 | 1.921 | 2018
QI_2018-09-29_000546 | 2018-09-28 20:06 | 2018-09-28 20:06 | EDT | 2018-09-29 00:06 | 551 | 60.006 | 59.888 | 59.548 | -0.118 | -0.458 | -466.9492 | -120.3057 | Yes | Yes | 58.5 | 1.048 | 2018
QI_2018-10-03_111359 | 2018-10-03 07:14 | 2018-10-03 07:14 | EDT | 2018-10-03 11:14 | -465 | 59.973 | 60.076 | 60.428 | 0.103 | 0.455 | -451.4563 | -102.1978 | Yes | Yes | 58.5 | 1.928 | 2018
QI_2018-10-04_183744 | 2018-10-04 14:38 | 2018-10-04 14:38 | EDT | 2018-10-04 18:38 | 447 | 59.992 | 59.923 | 59.619 | -0.069 | -0.373 | -647.8261 | -119.8391 | No | No | 58.5 | 1.119 | 2018
QI_2018-10-11_175130 | 2018-10-11 13:52 | 2018-10-11 13:52 | EDT | 2018-10-11 17:52 | 850 | 60 | 59.777 | 59.332 | -0.223 | -0.668 | -381.1659 | -127.2455 | Yes | Yes | 58.5 | 0.832 | 2018
QI_2018-10-19_065356 | 2018-10-19 02:54 | 2018-10-19 02:54 | EDT | 2018-10-19 06:54 | 291 | 60.014 | 59.933 | 59.715 | -0.081 | -0.299 | -359.2593 | -97.3244 | No | No | 58.5 | 1.215 | 2018
QI_2018-10-20_134949 | 2018-10-20 09:50 | 2018-10-20 09:50 | EDT | 2018-10-20 13:50 | -430 | 59.9992 | 60.0631 | 60.3601 | 0.0639 | 0.3609 | -672.9264 | -119.1466 | Yes | Yes | 58.5 | 1.8601 | 2018
QI_2018-10-22_220650 | 2018-10-22 18:07 | 2018-10-22 18:07 | EDT | 2018-10-22 22:07 | -435 | 59.967 | 60.072 | 60.302 | 0.105 | 0.335 | -414.2857 | -129.8507 | No | No | 58.5 | 1.802 | 2018
QI_2018-10-23_234218 | 2018-10-23 19:42 | 2018-10-23 19:42 | EDT | 2018-10-23 23:42 | 477 | 60.004 | 59.948 | 59.666 | -0.056 | -0.338 | -851.7857 | -141.1243 | No | No | 58.5 | 1.166 | 2018
QI_2018-10-31_105237 | 2018-10-31 06:53 | 2018-10-31 06:53 | EDT | 2018-10-31 10:53 | -460 | 59.999 | 60.054 | 60.391 | 0.055 | 0.392 | -836.3636 | -117.3469 | No | No | 58.5 | 1.891 | 2018
QI_2018-10-31_220005 | 2018-10-31 18:00 | 2018-10-31 18:00 | EDT | 2018-10-31 22:00 | -497 | 60.055 | 60.144 | 60.553 | 0.089 | 0.498 | -558.427 | -99.7992 | No | No | 58.5 | 2.053 | 2018
QI_2018-11-06_031631 | 2018-11-05 22:17 | 2018-11-05 22:17 | EST | 2018-11-06 03:17 | 394 | 59.984 | 59.945 | 59.696 | -0.039 | -0.288 | -1010.2564 | -136.8056 | No | No | 58.5 | 1.196 | 2018
QI_2018-11-07_001940 | 2018-11-06 19:20 | 2018-11-06 19:20 | EST | 2018-11-07 00:20 | -464 | 60.003 | 60.064 | 60.328 | 0.061 | 0.325 | -760.6557 | -142.7692 | No | No | 58.5 | 1.828 | 2018
QI_2018-11-08_081151 | 2018-11-08 03:12 | 2018-11-08 03:12 | EST | 2018-11-08 08:12 | -498 | 59.974 | 60.047 | 60.356 | 0.073 | 0.382 | -682.1918 | -130.3665 | Yes | Yes | 58.5 | 1.856 | 2018
QI_2018-11-09_191125 | 2018-11-09 14:11 | 2018-11-09 14:11 | EST | 2018-11-09 19:11 | 815 | 60.013 | 59.868 | 59.457 | -0.145 | -0.556 | -562.069 | -146.5827 | Yes | Yes | 58.5 | 0.957 | 2018
QI_2018-11-13_104040 | 2018-11-13 05:41 | 2018-11-13 05:41 | EST | 2018-11-13 10:41 | 900 | 59.985 | 59.915 | 59.648 | -0.07 | -0.337 | -1285.7143 | -267.0623 | Yes | Yes | 58.5 | 1.148 | 2018
QI_2018-11-19_032858 | 2018-11-18 22:29 | 2018-11-18 22:29 | EST | 2018-11-19 03:29 | -498 | 60.011 | 60.052 | 60.272 | 0.041 | 0.261 | -1214.6341 | -190.8046 | No | No | 58.5 | 1.772 | 2018
QI_2018-11-22_015709 | 2018-11-21 20:57 | 2018-11-21 20:57 | EST | 2018-11-22 01:57 | -472 | 59.974 | 60.047 | 60.286 | 0.073 | 0.312 | -646.5753 | -151.2821 | No | No | 58.5 | 1.786 | 2018
QI_2018-11-30_000000 | 2018-11-29 19:00 | 2018-11-29 19:00 | EST | 2018-11-30 | -430 | 60.004 | 60.068 | 60.362 | 0.064 | 0.358 | -671.875 | -120.1117 | No | No | 58.5 | 1.862 | 2018
QI_2018-12-03_163143 | 2018-12-03 11:32 | 2018-12-03 11:32 | EST | 2018-12-03 16:32 | 744 | 60.005 | 59.866 | 59.498 | -0.139 | -0.507 | -535.2518 | -146.7456 | Yes | Yes | 58.5 | 0.998 | 2019
QI_2018-12-10_144156 | 2018-12-10 09:42 | 2018-12-10 09:42 | EST | 2018-12-10 14:42 | 452 | 59.999 | 59.945 | 59.731 | -0.054 | -0.268 | -837.037 | -168.6567 | No | No | 58.5 | 1.231 | 2019
QI_2018-12-11_070019 | 2018-12-11 02:00 | 2018-12-11 02:00 | EST | 2018-12-11 07:00 | -477 | 59.984 | 60.04 | 60.262 | 0.056 | 0.278 | -851.7857 | -171.5827 | Yes | No | 58.5 | 1.762 | 2019
QI_2018-12-20_231135 | 2018-12-20 18:12 | 2018-12-20 18:12 | EST | 2018-12-20 23:12 | -485 | 59.975 | 60.054 | 60.268 | 0.079 | 0.293 | -613.9241 | -165.529 | Yes | No | 58.5 | 1.768 | 2019
QI_2019-02-01_235513 | 2019-02-01 18:55 | 2019-02-01 18:55 | EST | 2019-02-01 23:55 | -498 | 60.021 | 60.057 | 60.217 | 0.036 | 0.196 | -1383.3333 | -254.0816 | Yes | No | 58.5 | 1.717 | 2019
QI_2019-02-06_234901 | 2019-02-06 18:49 | 2019-02-06 18:49 | EST | 2019-02-06 23:49 | -476 | 60.024 | 60.081 | 60.334 | 0.057 | 0.31 | -835.0877 | -153.5484 | Yes | Yes | 58.5 | 1.834 | 2019
QI_2019-02-09_065517 | 2019-02-09 01:55 | 2019-02-09 01:55 | EST | 2019-02-09 06:55 | 495 | 60.023 | 59.941 | 59.707 | -0.082 | -0.316 | -603.6585 | -156.6456 | Yes | Yes | 58.5 | 1.207 | 2019
QI_2019-02-16_174223 | 2019-02-16 12:42 | 2019-02-16 12:42 | EST | 2019-02-16 17:42 | -478 | 59.986 | 60.053 | 60.341 | 0.067 | 0.355 | -713.4328 | -134.6479 | Yes | Yes | 58.5 | 1.841 | 2019
QI_2019-03-07_142643 | 2019-03-07 09:27 | 2019-03-07 09:27 | EST | 2019-03-07 14:27 | -445 | 59.984 | 60.042 | 60.274 | 0.058 | 0.29 | -767.2414 | -153.4483 | No | No | 58.5 | 1.774 | 2019
QI_2019-03-08_193334 | 2019-03-08 14:34 | 2019-03-08 14:34 | EST | 2019-03-08 19:34 | 517 | 60.007 | 59.933 | 59.69 | -0.074 | -0.317 | -698.6486 | -163.0915 | Yes | Yes | 58.5 | 1.19 | 2019
QI_2019-03-17_202305 | 2019-03-17 16:23 | 2019-03-17 16:23 | EDT | 2019-03-17 20:23 | 547 | 60.027 | 59.928 | 59.679 | -0.099 | -0.348 | -552.5253 | -157.1839 | Yes | Yes | 58.5 | 1.179 | 2019
QI_2019-03-18_164613 | 2019-03-18 12:46 | 2019-03-18 12:46 | EDT | 2019-03-18 16:46 | 503 | 60.008 | 59.95 | 59.715 | -0.058 | -0.293 | -867.2414 | -171.6724 | Yes | No | 58.5 | 1.215 | 2019
QI_2019-03-18_193535 | 2019-03-18 15:36 | 2019-03-18 15:36 | EDT | 2019-03-18 19:36 | 2109 | 60.009 | 59.471 | 58.932 | -0.538 | -1.077 | -392.0074 | -195.8217 | Yes | Yes | 58.5 | 0.432 | 2019
QI_2019-03-29_082615 | 2019-03-29 04:26 | 2019-03-29 04:26 | EDT | 2019-03-29 08:26 | -492 | 59.966 | 60.059 | 60.367 | 0.093 | 0.401 | -529.0323 | -122.6933 | Yes | Yes | 58.5 | 1.867 | 2019
QI_2019-03-29_161537 | 2019-03-29 12:16 | 2019-03-29 12:16 | EDT | 2019-03-29 16:16 | -744 | 60.017 | 60.132 | 60.544 | 0.115 | 0.527 | -646.9565 | -141.1765 | No | No | 58.5 | 2.044 | 2019
QI_2019-03-29_234014 | 2019-03-29 19:40 | 2019-03-29 19:40 | EDT | 2019-03-29 23:40 | 495 | 59.982 | 59.935 | 59.684 | -0.047 | -0.298 | -1053.1915 | -166.1074 | Yes | No | 58.5 | 1.184 | 2019
QI_2019-03-30_050722 | 2019-03-30 01:07 | 2019-03-30 01:07 | EDT | 2019-03-30 05:07 | 485 | 60 | 59.94 | 59.692 | -0.06 | -0.308 | -808.3333 | -157.4675 | Yes | Yes | 58.5 | 1.192 | 2019
QI_2019-03-30_134138 | 2019-03-30 09:42 | 2019-03-30 09:42 | EDT | 2019-03-30 13:42 | 495 | 59.996 | 59.904 | 59.679 | -0.092 | -0.317 | -538.0435 | -156.1514 | Yes | Yes | 58.5 | 1.179 | 2019
QI_2019-04-16_200210 | 2019-04-16 16:02 | 2019-04-16 16:02 | EDT | 2019-04-16 20:02 | 1520 | 59.97 | 59.621 | 59.001 | -0.349 | -0.969 | -435.5301 | -156.8627 | Yes | Yes | 58.5 | 0.501 | 2019
QI_2019-04-25_105323 | 2019-04-25 06:53 | 2019-04-25 06:53 | EDT | 2019-04-25 10:53 | -458 | 59.996 | 60.057 | 60.404 | 0.061 | 0.408 | -750.8197 | -112.2549 | Yes | No | 58.5 | 1.904 | 2019
QI_2019-04-28_130759 | 2019-04-28 09:08 | 2019-04-28 09:08 | EDT | 2019-04-28 13:08 | 868 | 59.993 | 59.737 | 59.376 | -0.256 | -0.617 | -339.0625 | -140.6807 | Yes | Yes | 58.5 | 0.876 | 2019
QI_2019-04-28_131625 | 2019-04-28 09:16 | 2019-04-28 09:16 | EDT | 2019-04-28 13:16 | 456 | 59.991 | 59.843 | 59.614 | -0.148 | -0.377 | -308.1081 | -120.9549 | Yes | Yes | 58.5 | 1.114 | 2019
QI_2019-04-28_152435 | 2019-04-28 11:25 | 2019-04-28 11:25 | EDT | 2019-04-28 15:25 | 877 | 59.989 | 59.798 | 59.406 | -0.191 | -0.583 | -459.1623 | -150.4288 | Yes | Yes | 58.5 | 0.906 | 2019
QI_2019-04-28_153532 | 2019-04-28 11:36 | 2019-04-28 11:36 | EDT | 2019-04-28 15:36 | 877 | 60.016 | 59.823 | 59.357 | -0.193 | -0.659 | -454.4041 | -133.0804 | Yes | Yes | 58.5 | 0.857 | 2019
QI_2019-04-28_154220 | 2019-04-28 11:42 | 2019-04-28 11:42 | EDT | 2019-04-28 15:42 | 791 | 60.011 | 59.83 | 59.415 | -0.181 | -0.596 | -437.0166 | -132.7181 | Yes | Yes | 58.5 | 0.915 | 2019
QI_2019-04-28_155250 | 2019-04-28 11:53 | 2019-04-28 11:53 | EDT | 2019-04-28 15:53 | 803 | 59.983 | 59.832 | 59.427 | -0.151 | -0.556 | -531.7881 | -144.4245 | Yes | Yes | 58.5 | 0.927 | 2019
QI_2019-04-28_161212 | 2019-04-28 12:12 | 2019-04-28 12:12 | EDT | 2019-04-28 16:12 | 831 | 59.959 | 59.764 | 59.376 | -0.195 | -0.583 | -426.1538 | -142.5386 | Yes | No | 58.5 | 0.876 | 2019
QI_2019-05-09_155347 | 2019-05-09 11:54 | 2019-05-09 11:54 | EDT | 2019-05-09 15:54 | 482 | 59.999 | 59.894 | 59.611 | -0.105 | -0.388 | -459.0476 | -124.2268 | Yes | Yes | 58.5 | 1.111 | 2019
QI_2019-05-22_185729 | 2019-05-22 14:57 | 2019-05-22 14:57 | EDT | 2019-05-22 18:57 | 464 | 59.983 | 59.865 | 59.557 | -0.118 | -0.426 | -393.2203 | -108.9202 | Yes | Yes | 58.5 | 1.057 | 2019
QI_2019-05-24_231413 | 2019-05-24 19:14 | 2019-05-24 19:14 | EDT | 2019-05-24 23:14 | -433 | 60.031 | 60.055 | 60.344 | 0.024 | 0.313 | -1804.1667 | -138.3387 | Yes | No | 58.5 | 1.844 | 2019
QI_2019-05-27_082721 | 2019-05-27 04:27 | 2019-05-27 04:27 | EDT | 2019-05-27 08:27 | -512 | 59.99 | 60.165 | 60.584 | 0.175 | 0.594 | -292.5714 | -86.1953 | Yes | Yes | 58.5 | 2.084 | 2019
QI_2019-06-18_035230 | 2019-06-17 23:53 | 2019-06-17 23:53 | EDT | 2019-06-18 03:52 | -480 | 60.003 | 60.122 | 60.474 | 0.119 | 0.471 | -403.3613 | -101.9108 | Yes | Yes | 58.5 | 1.974 | 2019
QI_2019-06-19_044725 | 2019-06-19 00:47 | 2019-06-19 00:47 | EDT | 2019-06-19 04:47 | 411 | 59.984 | 59.926 | 59.623 | -0.058 | -0.361 | -708.6207 | -113.8504 | Yes | Yes | 58.5 | 1.123 | 2019
QI_2019-06-19_173725 | 2019-06-19 13:37 | 2019-06-19 13:37 | EDT | 2019-06-19 17:37 | 426 | 60.023 | 59.938 | 59.624 | -0.085 | -0.399 | -501.1765 | -106.7669 | Yes | Yes | 58.5 | 1.124 | 2019
QI_2019-06-20_202607 | 2019-06-20 16:26 | 2019-06-20 16:26 | EDT | 2019-06-20 20:26 | 615 | 59.996 | 59.893 | 59.474 | -0.103 | -0.522 | -597.0874 | -117.8161 | Yes | Yes | 58.5 | 0.974 | 2019
QI_2019-06-21_184102 | 2019-06-21 14:41 | 2019-06-21 14:41 | EDT | 2019-06-21 18:41 | -246 | 60.002 | 60.001 | 60.308 | -0.001 | 0.306 | 24600 | -80.3922 | No | No | 58.5 | 1.808 | 2019
QI_2019-06-25_140044 | 2019-06-25 10:01 | 2019-06-25 10:01 | EDT | 2019-06-25 14:01 | -313 | 60.004 | 60.061 | 60.414 | 0.057 | 0.41 | -549.1228 | -76.3415 | Yes | Yes | 58.5 | 1.914 | 2019
QI_2019-06-29_175456 | 2019-06-29 13:55 | 2019-06-29 13:55 | EDT | 2019-06-29 17:55 | 403 | 60.007 | 59.956 | 59.66 | -0.051 | -0.347 | -790.1961 | -116.1383 | Yes | No | 58.5 | 1.16 | 2019
QI_2019-07-01_213959 | 2019-07-01 17:40 | 2019-07-01 17:40 | EDT | 2019-07-01 21:40 | 1291 | 59.978 | 59.732 | 59.143 | -0.246 | -0.835 | -524.7967 | -154.6108 | No | No | 58.5 | 0.643 | 2019
QI_2019-07-12_004519 | 2019-07-11 20:45 | 2019-07-11 20:45 | EDT | 2019-07-12 00:45 | -1505 | 59.989 | 60.141 | 60.602 | 0.152 | 0.613 | -990.1316 | -245.5139 | Yes | Yes | 58.5 | 2.102 | 2019
QI_2019-07-13_213359 | 2019-07-13 17:34 | 2019-07-13 17:34 | EDT | 2019-07-13 21:34 | 400 | 59.982 | 59.949 | 59.673 | -0.033 | -0.309 | -1212.1212 | -129.4498 | Yes | Yes | 58.5 | 1.173 | 2019
QI_2019-07-26_221122 | 2019-07-26 18:11 | 2019-07-26 18:11 | EDT | 2019-07-26 22:11 | -1505 | 60.024 | 60.153 | 60.661 | 0.129 | 0.637 | -1166.6667 | -236.2637 | Yes | Yes | 58.5 | 2.161 | 2019
QI_2019-07-27_171837 | 2019-07-27 13:19 | 2019-07-27 13:19 | EDT | 2019-07-27 17:19 | 854 | 59.968 | 59.794 | 59.328 | -0.174 | -0.64 | -490.8046 | -133.4375 | Yes | Yes | 58.5 | 0.828 | 2019
QI_2019-07-28_203520 | 2019-07-28 16:35 | 2019-07-28 16:35 | EDT | 2019-07-28 20:35 | 419 | 59.988 | 59.93 | 59.652 | -0.058 | -0.336 | -722.4138 | -124.7024 | No | No | 58.5 | 1.152 | 2019
QI_2019-07-30_134448 | 2019-07-30 09:45 | 2019-07-30 09:45 | EDT | 2019-07-30 13:45 | 315 | 60.036 | 59.983 | 59.705 | -0.053 | -0.331 | -594.3396 | -95.1662 | Yes | No | 58.5 | 1.205 | 2019
QI_2019-08-04_015424 | 2019-08-03 21:54 | 2019-08-03 21:54 | EDT | 2019-08-04 01:54 | -442 | 60.003 | 60.213 | 60.38 | 0.21 | 0.377 | -210.4762 | -117.2414 | No | No | 58.5 | 1.88 | 2019
QI_2019-08-04_015453 | 2019-08-03 21:55 | 2019-08-03 21:55 | EDT | 2019-08-04 01:55 | -498 | 60.221 | 60.098 | 60.501 | -0.123 | 0.28 | 404.878 | -177.8571 | No | No | 58.5 | 2.001 | 2019
QI_2019-08-05_170818 | 2019-08-05 13:08 | 2019-08-05 13:08 | EDT | 2019-08-05 17:08 | 409 | 60.025 | 60.034 | 59.698 | 0.009 | -0.327 | 4544.4444 | -125.0765 | No | No | 58.5 | 1.198 | 2019
QI_2019-08-05_175556 | 2019-08-05 13:56 | 2019-08-05 13:56 | EDT | 2019-08-05 17:56 | 363 | 60.012 | 60.041 | 59.74 | 0.029 | -0.272 | 1251.7241 | -133.4559 | No | No | 58.5 | 1.24 | 2019
QI_2019-09-03_133529 | 2019-09-03 09:35 | 2019-09-03 09:35 | EDT | 2019-09-03 13:35 | -1208 | 60.012 | 60.078 | 60.425 | 0.066 | 0.413 | -1830.303 | -292.4939 | Yes | No | 58.5 | 1.925 | 2019
QI_2019-09-05_145232 | 2019-09-05 10:53 | 2019-09-05 10:53 | EDT | 2019-09-05 14:53 | 440 | 59.992 | 59.92 | 59.604 | -0.072 | -0.388 | -611.1111 | -113.4021 | No | No | 58.5 | 1.104 | 2019
QI_2019-09-05_195747 | 2019-09-05 15:58 | 2019-09-05 15:58 | EDT | 2019-09-05 19:58 | 428 | 60.033 | 59.911 | 59.62 | -0.122 | -0.413 | -350.8197 | -103.632 | No | No | 58.5 | 1.12 | 2019
QI_2019-09-06_085632 | 2019-09-06 04:57 | 2019-09-06 04:57 | EDT | 2019-09-06 08:57 | 393 | 59.995 | 59.926 | 59.635 | -0.069 | -0.36 | -569.5652 | -109.1667 | Yes | Yes | 58.5 | 1.135 | 2019
QI_2019-09-08_075750 | 2019-09-08 03:58 | 2019-09-08 03:58 | EDT | 2019-09-08 07:58 | 326 | 60.015 | 59.948 | 59.685 | -0.067 | -0.33 | -486.5672 | -98.7879 | No | No | 58.5 | 1.185 | 2019
QI_2019-09-09_210900 | 2019-09-09 17:09 | 2019-09-09 17:09 | EDT | 2019-09-09 21:09 | 439 | 60.023 | 59.96 | 59.643 | -0.063 | -0.38 | -696.8254 | -115.5263 | Yes | Yes | 58.5 | 1.143 | 2019
QI_2019-09-11_210645 | 2019-09-11 17:07 | 2019-09-11 17:07 | EDT | 2019-09-11 21:07 | 397 | 60.011 | 59.947 | 59.644 | -0.064 | -0.367 | -620.3125 | -108.1744 | No | No | 58.5 | 1.144 | 2019
QI_2019-09-11_233134 | 2019-09-11 19:32 | 2019-09-11 19:32 | EDT | 2019-09-11 23:32 | 380 | 59.988 | 59.941 | 59.7 | -0.047 | -0.288 | -808.5106 | -131.9444 | No | No | 58.5 | 1.2 | 2019
QI_2019-09-16_132234 | 2019-09-16 09:23 | 2019-09-16 09:23 | EDT | 2019-09-16 13:23 | 1013 | 59.974 | 60.015 | 59.589 | 0.041 | -0.385 | 2470.7317 | -263.1169 | No | No | 58.5 | 1.089 | 2019
QI_2019-09-19_145450 | 2019-09-19 10:55 | 2019-09-19 10:55 | EDT | 2019-09-19 14:55 | 825 | 60.013 | 59.833 | 59.366 | -0.18 | -0.647 | -458.3333 | -127.5116 | Yes | Yes | 58.5 | 0.866 | 2019
QI_2019-09-21_230149 | 2019-09-21 19:02 | 2019-09-21 19:02 | EDT | 2019-09-21 23:02 | 391 | 60.005 | 59.945 | 59.647 | -0.06 | -0.358 | -651.6667 | -109.2179 | Yes | No | 58.5 | 1.147 | 2019
QI_2019-09-22_193912 | 2019-09-22 15:39 | 2019-09-22 15:39 | EDT | 2019-09-22 19:39 | 1090 | 60.026 | 59.758 | 59.214 | -0.268 | -0.812 | -406.7164 | -134.2365 | Yes | Yes | 58.5 | 0.714 | 2019
QI_2019-09-22_195652 | 2019-09-22 15:57 | 2019-09-22 15:57 | EDT | 2019-09-22 19:57 | 551 | 60.04 | 59.923 | 59.55 | -0.117 | -0.49 | -470.9402 | -112.449 | Yes | Yes | 58.5 | 1.05 | 2019
QI_2019-09-25_131908 | 2019-09-25 09:19 | 2019-09-25 09:19 | EDT | 2019-09-25 13:19 | 368 | 60.014 | 59.979 | 59.684 | -0.035 | -0.33 | -1051.4286 | -111.5152 | Yes | No | 58.5 | 1.184 | 2019
QI_2019-09-27_012613 | 2019-09-26 21:26 | 2019-09-26 21:26 | EDT | 2019-09-27 01:26 | 1616 | 59.961 | 59.611 | 58.938 | -0.35 | -1.023 | -461.7143 | -157.9668 | Yes | Yes | 58.5 | 0.438 | 2019
QI_2019-09-29_114928 | 2019-09-29 07:49 | 2019-09-29 07:49 | EDT | 2019-09-29 11:49 | 415 | 60.088 | 59.96 | 59.639 | -0.128 | -0.449 | -324.2187 | -92.4276 | Yes | Yes | 58.5 | 1.139 | 2019
QI_2019-10-02_170048 | 2019-10-02 13:01 | 2019-10-02 13:01 | EDT | 2019-10-02 17:01 | 430 | 60.012 | 59.94 | 59.654 | -0.072 | -0.358 | -597.2222 | -120.1117 | Yes | Yes | 58.5 | 1.154 | 2019
QI_2019-10-11_145548 | 2019-10-11 10:56 | 2019-10-11 10:56 | EDT | 2019-10-11 14:56 | -458 | 59.958 | 60.052 | 60.401 | 0.094 | 0.443 | -487.234 | -103.386 | Yes | Yes | 58.5 | 1.901 | 2019
QI_2019-10-20_144829 | 2019-10-20 10:48 | 2019-10-20 10:48 | EDT | 2019-10-20 14:48 | 416 | 59.994 | 59.972 | 59.629 | -0.022 | -0.365 | -1890.9091 | -113.9726 | Yes | No | 58.5 | 1.129 | 2019
QI_2019-10-31_142243 | 2019-10-31 10:23 | 2019-10-31 10:23 | EDT | 2019-10-31 14:23 | 901 | 60.046 | 59.843 | 59.359 | -0.203 | -0.687 | -443.8424 | -131.1499 | Yes | Yes | 58.5 | 0.859 | 2019
QI_2019-11-15_055304 | 2019-11-15 00:53 | 2019-11-15 00:53 | EST | 2019-11-15 05:53 | 526 | 60.003 | 59.946 | 59.682 | -0.057 | -0.321 | -922.807 | -163.8629 | Yes | No | 58.5 | 1.182 | 2019
QI_2019-11-15_203004 | 2019-11-15 15:30 | 2019-11-15 15:30 | EST | 2019-11-15 20:30 | 956 | 60.018 | 59.809 | 59.391 | -0.209 | -0.627 | -457.4163 | -152.4721 | Yes | Yes | 58.5 | 0.891 | 2019
QI_2019-11-16_021456 | 2019-11-15 21:15 | 2019-11-15 21:15 | EST | 2019-11-16 02:15 | -634 | 59.99 | 60.074 | 60.453 | 0.084 | 0.463 | -754.7619 | -136.933 | Yes | Yes | 58.5 | 1.953 | 2019
QI_2019-11-22_225004 | 2019-11-22 17:50 | 2019-11-22 17:50 | EST | 2019-11-22 22:50 | 479 | 60.032 | 59.963 | 59.682 | -0.069 | -0.35 | -694.2029 | -136.8571 | Yes | Yes | 58.5 | 1.182 | 2019
QI_2019-12-02_140740 | 2019-12-02 09:08 | 2019-12-02 09:08 | EST | 2019-12-02 14:08 | 343 | 60.04 | 59.901 | 59.792 | -0.139 | -0.248 | -246.7626 | -138.3065 | No | No | 58.5 | 1.292 | 2020
QI_2019-12-02_141242 | 2019-12-02 09:13 | 2019-12-02 09:13 | EST | 2019-12-02 14:13 | 319 | 59.988 | 59.968 | 59.778 | -0.02 | -0.21 | -1595 | -151.9048 | No | No | 58.5 | 1.278 | 2020
QI_2019-12-02_141609 | 2019-12-02 09:16 | 2019-12-02 09:16 | EST | 2019-12-02 14:16 | 355 | 59.996 | 59.944 | 59.779 | -0.052 | -0.217 | -682.6923 | -163.5945 | No | No | 58.5 | 1.279 | 2020
QI_2019-12-08_043810 | 2019-12-07 23:38 | 2019-12-07 23:38 | EST | 2019-12-08 04:38 | 511 | 59.991 | 59.949 | 59.721 | -0.042 | -0.27 | -1216.6667 | -189.2593 | Yes | No | 58.5 | 1.221 | 2020
QI_2019-12-26_232332 | 2019-12-26 18:24 | 2019-12-26 18:24 | EST | 2019-12-26 23:24 | -495 | 60.029 | 60.032 | 60.28 | 0.003 | 0.251 | -16500 | -197.2112 | Yes | No | 58.5 | 1.78 | 2020
QI_2020-01-16_152718 | 2020-01-16 10:27 | 2020-01-16 10:27 | EST | 2020-01-16 15:27 | -349 | 60 | 60.033 | 60.224 | 0.033 | 0.224 | -1057.5758 | -155.8036 | No | No | 58.5 | 1.724 | 2020
QI_2020-01-18_033219 | 2020-01-17 22:32 | 2020-01-17 22:32 | EST | 2020-01-18 03:32 | -455 | 60.001 | 60.038 | 60.312 | 0.037 | 0.311 | -1229.7297 | -146.3023 | Yes | No | 58.5 | 1.812 | 2020
QI_2020-02-08_163651 | 2020-02-08 11:37 | 2020-02-08 11:37 | EST | 2020-02-08 16:37 | -541 | 59.998 | 60.055 | 60.344 | 0.057 | 0.346 | -949.1228 | -156.3584 | Yes | Yes | 58.5 | 1.844 | 2020
QI_2020-02-27_154226 | 2020-02-27 10:42 | 2020-02-27 10:42 | EST | 2020-02-27 15:42 | 327 | 60.015 | 59.975 | 59.792 | -0.04 | -0.223 | -817.5 | -146.6368 | No | No | 58.5 | 1.292 | 2020
QI_2020-02-28_211020 | 2020-02-28 16:10 | 2020-02-28 16:10 | EST | 2020-02-28 21:10 | 522 | 60.004 | 59.95 | 59.721 | -0.054 | -0.283 | -966.6667 | -184.4523 | Yes | No | 58.5 | 1.221 | 2020
QI_2020-03-02_113811 | 2020-03-02 06:38 | 2020-03-02 06:38 | EST | 2020-03-02 11:38 | 481 | 60.009 | 59.947 | 59.722 | -0.062 | -0.287 | -775.8065 | -167.5958 | Yes | No | 58.5 | 1.222 | 2020
QI_2020-03-12_003256 | 2020-03-11 20:33 | 2020-03-11 20:33 | EDT | 2020-03-12 00:33 | -473 | 60.016 | 60.039 | 60.32 | 0.023 | 0.304 | -2056.5217 | -155.5921 | Yes | No | 58.5 | 1.82 | 2020
QI_2020-03-12_044310 | 2020-03-12 00:43 | 2020-03-12 00:43 | EDT | 2020-03-12 04:43 | -496 | 59.992 | 60.051 | 60.35 | 0.059 | 0.358 | -840.678 | -138.5475 | Yes | No | 58.5 | 1.85 | 2020
QI_2020-03-12_190029 | 2020-03-12 15:00 | 2020-03-12 15:00 | EDT | 2020-03-12 19:00 | 976 | 60.001 | 59.88 | 59.402 | -0.121 | -0.599 | -806.6116 | -162.9382 | Yes | Yes | 58.5 | 0.902 | 2020
QI_2020-05-20_005004 | 2020-05-19 20:50 | 2020-05-19 20:50 | EDT | 2020-05-20 00:50 | -504 | 59.987 | 60.038 | 60.427 | 0.051 | 0.44 | -988.2353 | -114.5455 | Yes | No | 58.5 | 1.927 | 2020
QI_2020-05-25_143456 | 2020-05-25 10:35 | 2020-05-25 10:35 | EDT | 2020-05-25 14:35 | 318 | 60.013 | 59.964 | 59.743 | -0.049 | -0.27 | -648.9796 | -117.7778 | No | No | 58.5 | 1.243 | 2020
QI_2020-05-27_184752 | 2020-05-27 14:48 | 2020-05-27 14:48 | EDT | 2020-05-27 18:48 | 343 | 59.971 | 60.252 | 59.708 | 0.281 | -0.263 | 122.0641 | -130.4183 | No | No | 58.5 | 1.208 | 2020
QI_2020-05-27_184820 | 2020-05-27 14:48 | 2020-05-27 14:48 | EDT | 2020-05-27 18:48 | -1093 | 59.82 | 60.115 | 60.726 | 0.295 | 0.906 | -370.5085 | -120.6402 | No | No | 58.5 | 2.226 | 2020
QI_2020-05-30_002339 | 2020-05-29 20:24 | 2020-05-29 20:24 | EDT | 2020-05-30 00:24 | -685 | 59.984 | 60.119 | 60.611 | 0.135 | 0.627 | -507.4074 | -109.2504 | Yes | Yes | 58.5 | 2.111 | 2020
QI_2020-05-30_003440 | 2020-05-29 20:35 | 2020-05-29 20:35 | EDT | 2020-05-30 00:35 | -730 | 60.033 | 60.151 | 60.587 | 0.118 | 0.554 | -618.6441 | -131.769 | Yes | Yes | 58.5 | 2.087 | 2020
QI_2020-06-02_001826 | 2020-06-01 20:18 | 2020-06-01 20:18 | EDT | 2020-06-02 00:18 | 510 | 60.001 | 59.872 | 59.53 | -0.129 | -0.471 | -395.3488 | -108.2803 | Yes | Yes | 58.5 | 1.03 | 2020
QI_2020-06-17_163930 | 2020-06-17 12:40 | 2020-06-17 12:40 | EDT | 2020-06-17 16:40 | 400 | 59.971 | 59.959 | 59.688 | -0.012 | -0.283 | -3333.3333 | -141.3428 | No | No | 58.5 | 1.188 | 2020
QI_2020-06-18_001131 | 2020-06-17 20:12 | 2020-06-17 20:12 | EDT | 2020-06-18 00:12 | -612 | 59.993 | 60.075 | 60.481 | 0.082 | 0.488 | -746.3415 | -125.4098 | Yes | No | 58.5 | 1.981 | 2020
QI_2020-06-24_180415 | 2020-06-24 14:04 | 2020-06-24 14:04 | EDT | 2020-06-24 18:04 | -573 | 59.984 | 60.098 | 60.598 | 0.114 | 0.614 | -502.6316 | -93.3225 | Yes | Yes | 58.5 | 2.098 | 2020
QI_2020-06-28_185957 | 2020-06-28 15:00 | 2020-06-28 15:00 | EDT | 2020-06-28 19:00 | 346 | 59.985 | 59.946 | 59.71 | -0.039 | -0.275 | -887.1795 | -125.8182 | No | No | 58.5 | 1.21 | 2020
QI_2020-07-01_192237 | 2020-07-01 15:23 | 2020-07-01 15:23 | EDT | 2020-07-01 19:23 | 663 | 59.989 | 59.902 | 59.466 | -0.087 | -0.523 | -762.069 | -126.7686 | Yes | No | 58.5 | 0.966 | 2020
QI_2020-07-05_112536 | 2020-07-05 07:26 | 2020-07-05 07:26 | EDT | 2020-07-05 11:26 | 835 | 60.007 | 59.79 | 59.287 | -0.217 | -0.72 | -384.7926 | -115.9722 | Yes | Yes | 58.5 | 0.787 | 2020
QI_2020-07-05_221854 | 2020-07-05 18:19 | 2020-07-05 18:19 | EDT | 2020-07-05 22:19 | 416 | 60.02 | 60.002 | 59.666 | -0.018 | -0.354 | -2311.1111 | -117.5141 | Yes | No | 58.5 | 1.166 | 2020
QI_2020-07-09_172809 | 2020-07-09 13:28 | 2020-07-09 13:28 | EDT | 2020-07-09 17:28 | 792 | 60.016 | 59.869 | 59.453 | -0.147 | -0.563 | -538.7755 | -140.675 | Yes | Yes | 58.5 | 0.953 | 2020
QI_2020-07-09_225354 | 2020-07-09 18:54 | 2020-07-09 18:54 | EDT | 2020-07-09 22:54 | 530 | 59.972 | 59.893 | 59.531 | -0.079 | -0.441 | -670.8861 | -120.1814 | Yes | No | 58.5 | 1.031 | 2020
QI_2020-07-11_113811 | 2020-07-11 07:38 | 2020-07-11 07:38 | EDT | 2020-07-11 11:38 | -473 | 59.992 | 60.05 | 60.399 | 0.058 | 0.407 | -815.5172 | -116.2162 | Yes | No | 58.5 | 1.899 | 2020
QI_2020-07-12_224422 | 2020-07-12 18:44 | 2020-07-12 18:44 | EDT | 2020-07-12 22:44 | 460 | 60 | 59.95 | 59.688 | -0.05 | -0.312 | -920 | -147.4359 | Yes | Yes | 58.5 | 1.188 | 2020
QI_2020-07-13_194158 | 2020-07-13 15:42 | 2020-07-13 15:42 | EDT | 2020-07-13 19:42 | -213 | 60 | 60.049 | 60.397 | 0.049 | 0.397 | -434.6939 | -53.6524 | Yes | No | 58.5 | 1.897 | 2020
QI_2020-07-13_195508 | 2020-07-13 15:55 | 2020-07-13 15:55 | EDT | 2020-07-13 19:55 | -703 | 60.012 | 60.108 | 60.6 | 0.096 | 0.588 | -732.2917 | -119.5578 | Yes | No | 58.5 | 2.1 | 2020
QI_2020-07-17_094044 | 2020-07-17 05:41 | 2020-07-17 05:41 | EDT | 2020-07-17 09:41 | 948 | 59.978 | 59.773 | 59.269 | -0.205 | -0.709 | -462.439 | -133.7094 | Yes | Yes | 58.5 | 0.769 | 2020
QI_2020-07-20_044852 | 2020-07-20 00:49 | 2020-07-20 00:49 | EDT | 2020-07-20 04:49 | 570 | 60.006 | 59.889 | 59.492 | -0.117 | -0.514 | -487.1795 | -110.8949 | Yes | Yes | 58.5 | 0.992 | 2020
QI_2020-07-21_114904 | 2020-07-21 07:49 | 2020-07-21 07:49 | EDT | 2020-07-21 11:49 | -720 | 59.963 | 60.121 | 60.491 | 0.158 | 0.528 | -455.6962 | -136.3636 | No | No | 58.5 | 1.991 | 2020
QI_2020-08-03_193434 | 2020-08-03 15:35 | 2020-08-03 15:35 | EDT | 2020-08-03 19:35 | 442 | 60.016 | 59.936 | 59.684 | -0.08 | -0.332 | -552.5 | -133.1325 | Yes | Yes | 58.5 | 1.184 | 2020
QI_2020-08-08_174248 | 2020-08-08 13:43 | 2020-08-08 13:43 | EDT | 2020-08-08 17:43 | 540 | 59.994 | 59.9 | 59.566 | -0.094 | -0.428 | -574.4681 | -126.1682 | Yes | Yes | 58.5 | 1.066 | 2020
QI_2020-08-12_132120 | 2020-08-12 09:21 | 2020-08-12 09:21 | EDT | 2020-08-12 13:21 | -394 | 59.989 | 60.058 | 60.344 | 0.069 | 0.355 | -571.0145 | -110.9859 | Yes | No | 58.5 | 1.844 | 2020
QI_2020-08-18_122153 | 2020-08-18 08:22 | 2020-08-18 08:22 | EDT | 2020-08-18 12:22 | -310 | 60.007 | 60.121 | 60.568 | 0.114 | 0.561 | -271.9298 | -55.2585 | Yes | No | 58.5 | 2.068 | 2020
QI_2020-08-23_102418 | 2020-08-23 06:24 | 2020-08-23 06:24 | EDT | 2020-08-23 10:24 | 305 | 59.962 | 59.984 | 59.695 | 0.022 | -0.267 | 1386.3636 | -114.2322 | No | No | 58.5 | 1.195 | 2020
QI_2020-08-29_155031 | 2020-08-29 11:51 | 2020-08-29 11:51 | EDT | 2020-08-29 15:51 | 458 | 60.013 | 59.929 | 59.571 | -0.084 | -0.442 | -545.2381 | -103.6199 | Yes | Yes | 58.5 | 1.071 | 2020
QI_2020-08-29_155203 | 2020-08-29 11:52 | 2020-08-29 11:52 | EDT | 2020-08-29 15:52 | 478 | 60.03 | 59.964 | 59.596 | -0.066 | -0.434 | -724.2424 | -110.1382 | Yes | Yes | 58.5 | 1.096 | 2020
QI_2020-09-08_134035 | 2020-09-08 09:41 | 2020-09-08 09:41 | EDT | 2020-09-08 13:41 | -711 | 60.012 | 60.119 | 60.542 | 0.107 | 0.53 | -664.486 | -134.1509 | Yes | No | 58.5 | 2.042 | 2020
QI_2020-09-11_233924 | 2020-09-11 19:39 | 2020-09-11 19:39 | EDT | 2020-09-11 23:39 | -353 | 60.028 | 60.022 | 60.325 | -0.006 | 0.297 | 5883.3333 | -118.8552 | No | No | 58.5 | 1.825 | 2020
QI_2020-09-17_114456 | 2020-09-17 07:45 | 2020-09-17 07:45 | EDT | 2020-09-17 11:45 | -504 | 60.002 | 60.135 | 60.544 | 0.133 | 0.542 | -378.9474 | -92.9889 | Yes | No | 58.5 | 2.044 | 2020
QI_2020-09-18_151411 | 2020-09-18 11:14 | 2020-09-18 11:14 | EDT | 2020-09-18 15:14 | -498 | 60.042 | 60.052 | 60.337 | 0.01 | 0.295 | -4980 | -168.8136 | Yes | No | 58.5 | 1.837 | 2020
QI_2020-09-21_132726 | 2020-09-21 09:27 | 2020-09-21 09:27 | EDT | 2020-09-21 13:27 | 918 | 59.956 | 59.77 | 59.312 | -0.186 | -0.644 | -493.5484 | -142.5466 | Yes | Yes | 58.5 | 0.812 | 2020
QI_2020-09-25_170756 | 2020-09-25 13:08 | 2020-09-25 13:08 | EDT | 2020-09-25 17:08 | 641 | 60.034 | 59.948 | 59.501 | -0.086 | -0.533 | -745.3488 | -120.2627 | Yes | No | 58.5 | 1.001 | 2020
QI_2020-09-30_010741 | 2020-09-29 21:08 | 2020-09-29 21:08 | EDT | 2020-09-30 01:08 | 407 | 60.016 | 59.925 | 59.641 | -0.091 | -0.375 | -447.2527 | -108.5333 | Yes | Yes | 58.5 | 1.141 | 2020
QI_2020-09-30_052036 | 2020-09-30 01:21 | 2020-09-30 01:21 | EDT | 2020-09-30 05:21 | 620 | 59.974 | 59.831 | 59.437 | -0.143 | -0.537 | -433.5664 | -115.4562 | Yes | Yes | 58.5 | 0.937 | 2020
QI_2020-10-02_025429 | 2020-10-01 22:54 | 2020-10-01 22:54 | EDT | 2020-10-02 02:54 | 400 | 59.918 | 59.902 | 59.619 | -0.016 | -0.299 | -2500 | -133.7793 | No | No | 58.5 | 1.119 | 2020
QI_2020-10-10_192651 | 2020-10-10 15:27 | 2020-10-10 15:27 | EDT | 2020-10-10 19:27 | -495 | 60.028 | 60.076 | 60.398 | 0.048 | 0.37 | -1031.25 | -133.7838 | Yes | Yes | 58.5 | 1.898 | 2020
QI_2020-10-11_020932 | 2020-10-10 22:10 | 2020-10-10 22:10 | EDT | 2020-10-11 02:10 | 361 | 60.005 | 59.943 | 59.664 | -0.062 | -0.341 | -582.2581 | -105.8651 | Yes | No | 58.5 | 1.164 | 2020
QI_2020-10-18_224729 | 2020-10-18 18:47 | 2020-10-18 18:47 | EDT | 2020-10-18 22:47 | -504 | 59.983 | 60.081 | 60.44 | 0.098 | 0.457 | -514.2857 | -110.2845 | Yes | Yes | 58.5 | 1.94 | 2020
QI_2020-10-27_032853 | 2020-10-26 23:29 | 2020-10-26 23:29 | EDT | 2020-10-27 03:29 | 826 | 59.988 | 59.83 | 59.432 | -0.158 | -0.556 | -522.7848 | -148.5612 | Yes | Yes | 58.5 | 0.932 | 2020
QI_2020-10-29_230422 | 2020-10-29 19:04 | 2020-10-29 19:04 | EDT | 2020-10-29 23:04 | 787 | 59.989 | 59.858 | 59.497 | -0.131 | -0.492 | -600.7634 | -159.9593 | Yes | Yes | 58.5 | 0.997 | 2020
QI_2020-11-10_030058 | 2020-11-09 22:01 | 2020-11-09 22:01 | EST | 2020-11-10 03:01 | 906 | 59.994 | 59.737 | 59.238 | -0.257 | -0.756 | -352.5292 | -119.8413 | Yes | Yes | 58.5 | 0.738 | 2020
QI_2020-11-14_090028 | 2020-11-14 04:00 | 2020-11-14 04:00 | EST | 2020-11-14 09:00 | 499 | 60.004 | 59.932 | 59.632 | -0.072 | -0.372 | -693.0556 | -134.1398 | Yes | Yes | 58.5 | 1.132 | 2020
QI_2020-11-19_112457 | 2020-11-19 06:25 | 2020-11-19 06:25 | EST | 2020-11-19 11:25 | -507 | 59.981 | 60.065 | 60.381 | 0.084 | 0.4 | -603.5714 | -126.75 | Yes | Yes | 58.5 | 1.881 | 2020
QI_2020-11-21_052124 | 2020-11-21 00:21 | 2020-11-21 00:21 | EST | 2020-11-21 05:21 | 520 | 60 | 59.935 | 59.596 | -0.065 | -0.404 | -800 | -128.7129 | Yes | Yes | 58.5 | 1.096 | 2020
QI_2020-11-21_144939 | 2020-11-21 09:50 | 2020-11-21 09:50 | EST | 2020-11-21 14:50 | 898 | 59.998 | 59.815 | 59.349 | -0.183 | -0.649 | -490.7104 | -138.3667 | Yes | Yes | 58.5 | 0.849 | 2020
QI_2020-11-21_190156 | 2020-11-21 14:02 | 2020-11-21 14:02 | EST | 2020-11-21 19:02 | -474 | 59.982 | 60.045 | 60.381 | 0.063 | 0.399 | -752.381 | -118.797 | Yes | Yes | 58.5 | 1.881 | 2020
QI_2020-11-27_182652 | 2020-11-27 13:27 | 2020-11-27 13:27 | EST | 2020-11-27 18:27 | 891 | 60.005 | 59.833 | 59.41 | -0.172 | -0.595 | -518.0233 | -149.7479 | Yes | Yes | 58.5 | 0.91 | 2020
QI_2020-12-03_033040 | 2020-12-02 22:31 | 2020-12-02 22:31 | EST | 2020-12-03 03:31 | -530 | 60.005 | 60.079 | 60.371 | 0.074 | 0.366 | -716.2162 | -144.8087 | Yes | No | 58.5 | 1.871 | 2021
QI_2020-12-17_143639 | 2020-12-17 09:37 | 2020-12-17 09:37 | EST | 2020-12-17 14:37 | 410 | 59.994 | 59.858 | 59.518 | -0.136 | -0.476 | -301.4706 | -86.1345 | Yes | Yes | 58.5 | 1.018 | 2021
QI_2021-01-17_030408 | 2021-01-16 22:04 | 2021-01-16 22:04 | EST | 2021-01-17 03:04 | -568 | 60.018 | 60.088 | 60.417 | 0.07 | 0.399 | -811.4286 | -142.3559 | Yes | Yes | 58.5 | 1.917 | 2021
QI_2021-01-28_061624 | 2021-01-28 01:16 | 2021-01-28 01:16 | EST | 2021-01-28 06:16 | 477 | 60.011 | 59.963 | 59.693 | -0.048 | -0.318 | -993.75 | -150 | Yes | Yes | 58.5 | 1.193 | 2021
QI_2021-02-02_160539 | 2021-02-02 11:06 | 2021-02-02 11:06 | EST | 2021-02-02 16:06 | 503 | 59.992 | 59.962 | 59.718 | -0.03 | -0.274 | -1676.6667 | -183.5766 | Yes | No | 58.5 | 1.218 | 2021
QI_2021-02-06_122936 | 2021-02-06 07:30 | 2021-02-06 07:30 | EST | 2021-02-06 12:30 | -488 | 59.998 | 60.08 | 60.345 | 0.082 | 0.347 | -595.122 | -140.634 | Yes | Yes | 58.5 | 1.845 | 2021
QI_2021-02-23_160309 | 2021-02-23 11:03 | 2021-02-23 11:03 | EST | 2021-02-23 16:03 | 948 | 59.995 | 59.864 | 59.399 | -0.131 | -0.596 | -723.6641 | -159.0604 | Yes | Yes | 58.5 | 0.899 | 2021
QI_2021-02-26_084148 | 2021-02-26 03:42 | 2021-02-26 03:42 | EST | 2021-02-26 08:42 | -491 | 59.998 | 60.016 | 60.3 | 0.018 | 0.302 | -2727.7778 | -162.5828 | Yes | No | 58.5 | 1.8 | 2021

## Update_History
Date | Updates
2015-04-22 | Frequency Working Group made the selection and confirmed MW loss. Column E, F, W and X for all interconnects are updated.
2015-04-27 | HQ updated the column E and F Selections
2015-05-15 | EPG added april 2015 events for all four interconnections.
2015-06-19 | EPG added May 2015 events for all four interconnections.
2015-07-16 | Verified HQ events for BAL-003-1 from Form 1s. Updated selections.
2015-07-17 | EPG added June 2015 events for all four interconnections.
2015-07-22 | Frequency Working Group made event selections and confirmed MW loss. Column E, F, W and X for all interconnections Mar Apr and May.
2015-07-22 | Changed to a formula in column Z to calculate the Estimated Frequency Response using the NERC SA MW data column. This column will be updated by the Region if more accurate MW loss data is found.
2015-07-23 | Updated Region information and MW loss for the Western Interconnection.
2015-08-18 | EPG added July 2015 events for all four interconnections.
2015-09-11 | Added C' Frequency columns for the Eastern Interconnection. Updated MW loss data from Form 1s.
2015-09-16 | EPG added August 2015 events for all four interconnections.
2015-10-07 | EPG added September 2015 events for all four interconnections.
2015-10-27 | Frequency Working Group made event selections and confirmed MW loss. Column E, F, W and X for all interconnections Jun, Jul and Aug (Sept for EI and ERCOT)
2016-01-27 | FWG updated with approval of December 2015 events.
2016-04-06 | Corrected the MW Loss for the WI event on 5/26/2014 at 17:31:32 PDT from 2,636 MW to 2,826 MW, as verified by Jim Burns from BPA.
2016-04-27 | Added 2016 1st quarter events, corrected M4 formula, and revised format for quicker data entry in FWG meetings.
2016-08-08 | Added 2016 2nd quarter events, added CPT calculation to EI and WI.
2016-11-15 | Added 2016 3rd quarter events.
∆