## Instructions
Steps | To be completed for each event evaluated.
1 | Set-up Data collection in exact same order as the "Data" sheet of this work book. Data should be in this order:
Column A: Date and Time in this format, mm/dd/yy HH:MM:SS
Column B: Frequency Hz
Column C: Net Actual Interchange
Column D: Joint Owned Unit dynamic schedule
Column E: Non Conforming Load
Column F: Pumped Hydro
Column G: Ramping units
Column H: Transferred Frequency Response
Column I: Contingent BA Lost load or generation
Column J: BA Bias Setting
Column K: BA Load
2 | Note: Columns D, E, F, G and H are optional data. If you choose not to use these, leave the columns blank. Do not delete the columns. Use the sign (+/-) convention defined in FRS Form 1.
3 | Data compression must be turned off for each data point. Quality data will give you quality results in the evaluation.
4 | Data must be at 2 second sample rate for the full 25 minute minimum collection period that starts a minimum of two (2) minutes before the event begins and includes a minimum of 15 minutes after the beginning of the event.
The spreadsheet will work with up to 60 minutes of data. Be sure "Data" worksheet is clear of any old data.
If using PI historian as your data source, use "PasteSpecial/Values" to enter data into the spreadsheet. Do not include historian data collection formulas in the data.
5 | Once data is in place in the "Data" worksheet, determine when the beginning of the event occurred. This is accomplished by knowing the UTC event time from the master event list.
Convert the UTC event time to your PI data time and then scroll through the Data worksheet column B data of frequency and observe when frequency moves from the normal, pre-event frequency.
This will usually be a single change in frequency of 0.008 to 0.010 Hz more or less. Note the row number in the worksheet that this change occurs. In this sample data spreadsheet this occurs in row 313 of the data.
6 | Edit cell "C8" of the "Entry Data" worksheet, change the formula in the cell "C8" to reference the row number identified in step 5 above. In the sample data of this workbook this formula is: "=Data!A313"
If the correct row is selected, the "Graph 20 to 52s" worksheet will indicate the first change in frequency of the event on the center vertical grid line of the graph (Red Trend).
7 | Determine the end of the event to be evaluated. Use the same rules that are used for DCS only look at frequency instead of ACE. Scroll down the frequency data in column B of the "Data" worksheet until frequency reaches 60 Hz or the
pre-disturbance value. Note the row number in the worksheet that this occurs. In this sample data spreadsheet this occurs in row 427.
8 | Edit cell "C11" of the "Evaluation" worksheet, change the formula in the cell "C11" to reference the row number identified in step 7 above. In the sample data of this workbook this formula is: "=Data!A427"
9 | In cell "R41" of the "Evaluation" spreadsheet, enter the MW value of the unit(s) that tripped (from the Master Event List). This is only necessary for the "Interconnection" evaluation if you're interested.
It is not necessary to do this for the BA evaluation but it will provide a comparison of the BA frequency response as compared to the Interconnection frequency response.
10 | Use the "copy" button provided to copy the evaluation and event specific data for the "FRS Form 1" of this field trial. This data is summarized in the correct order on worksheet "Form 1 Summary Data" of this workbook.
Use PasteSpecial/Values when pasting the data into FRS Form 1 on the appropriate event row.
Steps | To be completed once at the initial setup of the evaluation spreadsheet for your BA.
A | Enter the Balancing Authority name as you want it to appear on the graphs in cell "B1" of the "Entry Data" worksheet. For example: "NYISO".
B | Enter your Balancing Authorities Frequency Response Obligation in cell "B2" of the "Entry Data" worksheet. For example: -80 MW/0.1 Hz (This value could change annually)
C | For informational and educational purposes, a "Sustained" performance evaluation is provided in the "Evaluation" worksheet and in the "Sustained" Graph. This evaluation uses a Time Constant (TC) to model the frequency response of your BA.
The time constant is located in cell "L13" of the "Evaluation" spreadsheet and should be edited for the types of generators in your BA. Presently this time constant is set at 0.35.
The higher the value of the time constant, the faster the delivery of frequency response is expected. Setting the TC to 1.0 effectively turns off the delay and instantaneous frequency response will be modeled. Do not set higher than 1.0.
This time constant is only used in the "Sustained" evaluation and is not used for the Field Trial evaluation of performance to the FRO.
A typical setting for this time constant is 0.08 to 0.15 for hydro units, 0.10 to 0.20 for large steam turbines and 0.20 to 0.40 for combustion turbines.
By observing the slope of your "Interchange Actual" on the "Sustained" Graph, adjust the time constant until the initial slope of the "Target" is similar.
When set appropriately, the "Target" trend on the "Sustained" graph will model what Interchange Actual should have done during the event recovery period based on your minimum FRO.
Note: For ease of use, only the necessary worksheets are displayed. If you are interested in viewing graphs and other hidden worksheets, select the "tab" at the bottom, right click, select unhide and select the worksheet you wish to unhide.

## Data
|  |  | JOU | Non- |  |  | Transferred | Contingent
|  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA
|  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load
|  | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting
Time (T) | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW
2009-10-12 02:12 | 59.98 | 3669.8784 | 350 | -351.3615 | 0 | 0 | 10 | 15 | -103 | 7500
2009-10-12 02:12 | 59.981 | 3672.385 | 350 | -351.3615 | 0 | 0.5 | 10 | 15 | -103 | 7500.33
2009-10-12 02:12 | 59.98 | 3669.8784 | 350 | -351.3615 | 0 | 1 | 10 | 15 | -103 | 7500.66
2009-10-12 02:12 | 59.981 | 3672.385 | 350 | -357.9475 | 0 | 1.5 | 10 | 15 | -103 | 7500.99
2009-10-12 02:12 | 59.98 | 3671.6997 | 350 | -357.9475 | 0 | 2 | 10 | 15 | -103 | 7501.32
2009-10-12 02:12 | 59.98 | 3670.9492 | 350 | -357.9475 | 0 | 2.5 | 10 | 15 | -103 | 7501.65
2009-10-12 02:12 | 59.982 | 3671.6985 | 350 | -357.9475 | 0 | 3 | 10 | 15 | -103 | 7501.98
2009-10-12 02:12 | 59.981 | 3671.5481 | 350 | -357.9475 | 0 | 3.5 | 10 | 15 | -103 | 7502.31
2009-10-12 02:12 | 59.979 | 3672.3103 | 350 | -360.2347 | 0 | 4 | 10 | 15 | -103 | 7502.64
2009-10-12 02:12 | 59.981 | 3672.7754 | 350 | -360.2347 | 0 | 4.5 | 10 | 15 | -103 | 7502.97
2009-10-12 02:12 | 59.982 | 3672.1741 | 350 | -360.2347 | 0 | 5 | 10 | 15 | -103 | 7503.3
2009-10-12 02:12 | 59.979 | 3672.2761 | 350 | -360.2347 | 0 | 5.5 | 10 | 15 | -103 | 7503.63
2009-10-12 02:12 | 59.979 | 3674.2634 | 350 | -360.2347 | 0 | 6 | 10 | 15 | -103 | 7503.96
2009-10-12 02:12 | 59.98 | 3674.5081 | 350 | -346.5259 | 0 | 6.5 | 10 | 15 | -103 | 7504.29
2009-10-12 02:12 | 59.98 | 3673.8438 | 350 | -346.5259 | 0 | 7 | 10 | 15 | -103 | 7504.62
2009-10-12 02:12 | 59.983 | 3675.0916 | 350 | -346.5259 | 0 | 7.5 | 10 | 15 | -103 | 7504.95
2009-10-12 02:13 | 59.986 | 3672.1062 | 350 | -346.5259 | 0 | 8 | 10 | 15 | -103 | 7505.28
2009-10-12 02:13 | 59.986 | 3669.3303 | 350 | -346.5259 | 0 | 8.5 | 10 | 15 | -103 | 7505.61
2009-10-12 02:13 | 59.98 | 3669.168 | 350 | -296.4434 | 0 | 9 | 10 | 15 | -103 | 7505.94
2009-10-12 02:13 | 59.976 | 3671.5005 | 350 | -296.4434 | 0 | 9.5 | 10 | 15 | -103 | 7506.27
2009-10-12 02:13 | 59.975 | 3673.5603 | 350 | -296.4434 | 0 | 10 | 10 | 15 | -103 | 7506.6
2009-10-12 02:13 | 59.979 | 3673.8975 | 350 | -296.4434 | 0 | 10.5 | 10 | 15 | -103 | 7506.93
2009-10-12 02:13 | 59.981 | 3673.8342 | 350 | -296.4434 | 0 | 11 | 10 | 15 | -103 | 7507.26
2009-10-12 02:13 | 59.982 | 3671.8872 | 350 | -341.0612 | 0 | 11.5 | 10 | 15 | -103 | 7507.59
2009-10-12 02:13 | 59.987 | 3671.6345 | 350 | -341.0612 | 0 | 12 | 10 | 15 | -103 | 7507.92
2009-10-12 02:13 | 59.99 | 3671.2205 | 350 | -341.0612 | 0 | 12.5 | 10 | 15 | -103 | 7508.25
2009-10-12 02:13 | 59.993 | 3671.5603 | 350 | -341.0612 | 0 | 13 | 10 | 15 | -103 | 7508.58
2009-10-12 02:13 | 59.994 | 3671.2832 | 350 | -341.0612 | 0 | 13.5 | 10 | 15 | -103 | 7508.91
2009-10-12 02:13 | 59.995 | 3670.772 | 350 | -322.8263 | 0 | 14 | 10 | 15 | -103 | 7509.24
2009-10-12 02:13 | 59.995 | 3668.3621 | 350 | -322.8263 | 0 | 14.5 | 10 | 15 | -103 | 7509.57
2009-10-12 02:13 | 59.995 | 3668.1289 | 350 | -322.8263 | 0 | 15 | 10 | 15 | -103 | 7509.9
2009-10-12 02:13 | 59.995 | 3668.2446 | 350 | -322.8263 | 0 | 15.5 | 10 | 15 | -103 | 7510.23
2009-10-12 02:13 | 59.995 | 3669.2913 | 350 | -322.8263 | 0 | 16 | 10 | 15 | -103 | 7510.56
2009-10-12 02:13 | 59.994 | 3670.4937 | 350 | -321.5444 | 0 | 16.5 | 10 | 15 | -103 | 7510.89
2009-10-12 02:13 | 59.994 | 3671.2539 | 350 | -321.5444 | 0 | 17 | 10 | 15 | -103 | 7511.22
2009-10-12 02:13 | 59.995 | 3670.6833 | 350 | -321.5444 | 0 | 17.5 | 10 | 15 | -103 | 7511.55
2009-10-12 02:13 | 59.997 | 3670.1558 | 350 | -321.5444 | 0 | 18 | 10 | 15 | -103 | 7511.88
2009-10-12 02:13 | 60.001 | 3670.2117 | 350 | -321.5444 | 0 | 18.5 | 10 | 15 | -103 | 7512.21
2009-10-12 02:13 | 60.002 | 3670.7124 | 350 | -362.1363 | 0 | 19 | 10 | 15 | -103 | 7512.54
2009-10-12 02:13 | 60.001 | 3670.3291 | 350 | -362.1363 | 0 | 19.5 | 10 | 15 | -103 | 7512.87
2009-10-12 02:13 | 60.003 | 3671.1836 | 350 | -362.1363 | 0 | 20 | 10 | 15 | -103 | 7513.2
2009-10-12 02:13 | 60.003 | 3671.2271 | 350 | -362.1363 | 0 | 20.5 | 10 | 15 | -103 | 7513.53
2009-10-12 02:13 | 60.005 | 3670.2671 | 350 | -362.1363 | 0 | 21 | 10 | 15 | -103 | 7513.86
2009-10-12 02:13 | 60.003 | 3670.1897 | 350 | -336.3118 | 0 | 21.5 | 10 | 15 | -103 | 7514.19
2009-10-12 02:13 | 60 | 3671.0923 | 350 | -336.3118 | 0 | 22 | 10 | 15 | -103 | 7514.52
2009-10-12 02:13 | 60.001 | 3670.2485 | 350 | -336.3118 | 0 | 22.5 | 10 | 15 | -103 | 7514.85
2009-10-12 02:14 | 60.003 | 3670.6699 | 350 | -336.3118 | 0 | 23 | 10 | 15 | -103 | 7515.18
2009-10-12 02:14 | 60.004 | 3669.8992 | 350 | -336.3118 | 0 | 23.5 | 10 | 15 | -103 | 7515.51
2009-10-12 02:14 | 60.005 | 3669.5342 | 350 | -316.4431 | 0 | 24 | 10 | 15 | -103 | 7515.84
2009-10-12 02:14 | 60.001 | 3670.1995 | 350 | -316.4431 | 0 | 24.5 | 10 | 15 | -103 | 7516.17
2009-10-12 02:14 | 59.999 | 3671.6284 | 350 | -316.4431 | 0 | 25 | 10 | 15 | -103 | 7516.5
2009-10-12 02:14 | 60.001 | 3671.1228 | 350 | -316.4431 | 0 | 25.5 | 10 | 15 | -103 | 7516.83
2009-10-12 02:14 | 60.004 | 3671.9683 | 350 | -316.4431 | 0 | 26 | 10 | 15 | -103 | 7517.16
2009-10-12 02:14 | 60.004 | 3671.4443 | 350 | -325.4643 | 0 | 26.5 | 10 | 15 | -103 | 7517.49
2009-10-12 02:14 | 60.004 | 3671.8716 | 350 | -325.4643 | 0 | 27 | 10 | 15 | -103 | 7517.82
2009-10-12 02:14 | 60.004 | 3671.8752 | 350 | -325.4643 | 0 | 27.5 | 10 | 15 | -103 | 7518.15
2009-10-12 02:14 | 60.005 | 3671.0657 | 350 | -325.4643 | 0 | 28 | 10 | 15 | -103 | 7518.48
2009-10-12 02:14 | 60.003 | 3672.8728 | 350 | -325.4643 | 0 | 28.5 | 10 | 15 | -103 | 7518.81
2009-10-12 02:14 | 60.002 | 3673.2351 | 350 | -336.6142 | 0 | 29 | 10 | 15 | -103 | 7519.14
2009-10-12 02:14 | 60.003 | 3673.4978 | 350 | -336.6142 | 0 | 29.5 | 10 | 15 | -103 | 7519.47
2009-10-12 02:14 | 60.001 | 3673.5305 | 350 | -336.6142 | 0 | 30 | 10 | 15 | -103 | 7519.8
2009-10-12 02:14 | 59.999 | 3672.75 | 350 | -336.6142 | 0 | 30.5 | 10 | 15 | -103 | 7520.13
2009-10-12 02:14 | 59.999 | 3673.1863 | 350 | -336.6142 | 0 | 31 | 10 | 15 | -103 | 7520.46
2009-10-12 02:14 | 59.997 | 3674.3218 | 350 | -316.7262 | 0 | 31.5 | 10 | 15 | -103 | 7520.79
2009-10-12 02:14 | 59.998 | 3673.5764 | 350 | -316.7262 | 0 | 32 | 10 | 15 | -103 | 7521.12
2009-10-12 02:14 | 59.996 | 3673.365 | 350 | -316.7262 | 0 | 32.5 | 10 | 15 | -103 | 7521.45
2009-10-12 02:14 | 59.995 | 3671.8206 | 350 | -316.7262 | 0 | 33 | 10 | 15 | -103 | 7521.78
2009-10-12 02:14 | 59.993 | 3672.093 | 350 | -316.7262 | 0 | 33.5 | 10 | 15 | -103 | 7522.11
2009-10-12 02:14 | 59.993 | 3671.998 | 350 | -320.1955 | 0 | 34 | 10 | 15 | -103 | 7522.44
2009-10-12 02:14 | 59.996 | 3671.5684 | 350 | -320.1955 | 0 | 34.5 | 10 | 15 | -103 | 7522.77
2009-10-12 02:14 | 59.999 | 3671.0725 | 350 | -320.1955 | 0 | 35 | 10 | 15 | -103 | 7523.1
2009-10-12 02:14 | 60.001 | 3670.9568 | 350 | -320.1955 | 0 | 35.5 | 10 | 15 | -103 | 7523.43
2009-10-12 02:14 | 60.005 | 3671.4414 | 350 | -320.1955 | 0 | 36 | 10 | 15 | -103 | 7523.76
2009-10-12 02:14 | 60.007 | 3670.8928 | 350 | -341.8661 | 0 | 36.5 | 10 | 15 | -103 | 7524.09
2009-10-12 02:14 | 60.007 | 3670.1619 | 350 | -341.8661 | 0 | 37 | 10 | 15 | -103 | 7524.42
2009-10-12 02:14 | 60.005 | 3670.5129 | 350 | -341.8661 | 0 | 37.5 | 10 | 15 | -103 | 7524.75
2009-10-12 02:15 | 60.002 | 3670.6199 | 350 | -341.8661 | 0 | 38 | 10 | 15 | -103 | 7525.08
2009-10-12 02:15 | 59.999 | 3672.7129 | 350 | -341.8661 | 0 | 38.5 | 10 | 15 | -103 | 7525.41
2009-10-12 02:15 | 59.997 | 3672.0857 | 350 | -348.5978 | 0 | 39 | 10 | 15 | -103 | 7525.74
2009-10-12 02:15 | 59.999 | 3671.0703 | 350 | -348.5978 | 0 | 39.5 | 10 | 15 | -103 | 7526.07
2009-10-12 02:15 | 60.002 | 3670.8257 | 350 | -348.5978 | 0 | 40 | 10 | 15 | -103 | 7526.4
2009-10-12 02:15 | 60.007 | 3670.8235 | 350 | -348.5978 | 0 | 40.5 | 10 | 15 | -103 | 7526.73
2009-10-12 02:15 | 60.01 | 3671.8091 | 350 | -348.5978 | 0 | 41 | 10 | 15 | -103 | 7527.06
2009-10-12 02:15 | 60.011 | 3673.3633 | 350 | -329.085 | 0 | 41.5 | 10 | 15 | -103 | 7527.39
2009-10-12 02:15 | 60.009 | 3672.7358 | 350 | -329.085 | 0 | 42 | 10 | 15 | -103 | 7527.72
2009-10-12 02:15 | 60.003 | 3673.2554 | 350 | -329.085 | 0 | 42.5 | 10 | 15 | -103 | 7528.05
2009-10-12 02:15 | 59.997 | 3674.4146 | 350 | -329.085 | 0 | 43 | 10 | 15 | -103 | 7528.38
2009-10-12 02:15 | 59.995 | 3675.4258 | 350 | -329.085 | 0 | 43.5 | 10 | 15 | -103 | 7528.71
2009-10-12 02:15 | 59.994 | 3674.7546 | 350 | -342.4182 | 0 | 44 | 10 | 15 | -103 | 7529.04
2009-10-12 02:15 | 59.994 | 3674.29 | 350 | -342.4182 | 0 | 44.5 | 10 | 15 | -103 | 7529.37
2009-10-12 02:15 | 60 | 3675.3105 | 350 | -342.4182 | 0 | 45 | 10 | 15 | -103 | 7529.7
2009-10-12 02:15 | 60.001 | 3675.1572 | 350 | -342.4182 | 0 | 45.5 | 10 | 15 | -103 | 7530.03
2009-10-12 02:15 | 59.998 | 3675.1655 | 350 | -342.4182 | 0 | 46 | 10 | 15 | -103 | 7530.36
2009-10-12 02:15 | 59.998 | 3674.4417 | 350 | -338.7946 | 0 | 46.5 | 10 | 15 | -103 | 7530.69
2009-10-12 02:15 | 59.995 | 3674.3191 | 350 | -338.7946 | 0 | 47 | 10 | 15 | -103 | 7531.02
2009-10-12 02:15 | 59.992 | 3674.9065 | 350 | -338.7946 | 0 | 47.5 | 10 | 15 | -103 | 7531.35
2009-10-12 02:15 | 59.986 | 3676.3286 | 350 | -338.7946 | 0 | 48 | 10 | 15 | -103 | 7531.68
2009-10-12 02:15 | 59.986 | 3676.7144 | 350 | -338.7946 | 0 | 48.5 | 10 | 15 | -103 | 7532.01
2009-10-12 02:15 | 59.986 | 3677.791 | 350 | -335.931 | 0 | 49 | 10 | 15 | -103 | 7532.34
2009-10-12 02:15 | 59.988 | 3675.9724 | 350 | -335.931 | 0 | 49.5 | 10 | 15 | -103 | 7532.67
2009-10-12 02:15 | 59.989 | 3675.543 | 350 | -335.931 | 0 | 50 | 10 | 15 | -103 | 7533
2009-10-12 02:15 | 59.988 | 3676.593 | 350 | -335.931 | 0 | 50.5 | 10 | 15 | -103 | 7533.33
2009-10-12 02:15 | 59.987 | 3676.9314 | 350 | -335.931 | 0 | 51 | 10 | 15 | -103 | 7533.66
2009-10-12 02:15 | 59.985 | 3677.2234 | 350 | -339.7124 | 0 | 51.5 | 10 | 15 | -103 | 7533.99
2009-10-12 02:15 | 59.984 | 3677.0671 | 350 | -339.7124 | 0 | 52 | 10 | 15 | -103 | 7534.32
2009-10-12 02:16 | 59.983 | 3677.3611 | 350 | -339.7124 | 0 | 52.5 | 10 | 15 | -103 | 7534.65
2009-10-12 02:16 | 59.982 | 3678.4553 | 350 | -339.7124 | 0 | 53 | 10 | 15 | -103 | 7534.98
2009-10-12 02:16 | 59.984 | 3679.2278 | 350 | -339.7124 | 0 | 53.5 | 10 | 15 | -103 | 7535.31
2009-10-12 02:16 | 59.984 | 3679.7314 | 350 | -332.0247 | 0 | 54 | 10 | 15 | -103 | 7535.64
2009-10-12 02:16 | 59.985 | 3679.0591 | 350 | -332.0247 | 0 | 54.5 | 10 | 15 | -103 | 7535.97
2009-10-12 02:16 | 59.986 | 3677.627 | 350 | -332.0247 | 0 | 55 | 10 | 15 | -103 | 7536.3
2009-10-12 02:16 | 59.987 | 3677.4822 | 350 | -332.0247 | 0 | 55.5 | 10 | 15 | -103 | 7536.63
2009-10-12 02:16 | 59.99 | 3676.4094 | 350 | -332.0247 | 0 | 56 | 10 | 15 | -103 | 7536.96
2009-10-12 02:16 | 59.99 | 3677.5281 | 350 | -330.759 | 0 | 56.5 | 10 | 15 | -103 | 7537.29
2009-10-12 02:16 | 59.987 | 3677.3711 | 350 | -330.759 | 0 | 57 | 10 | 15 | -103 | 7537.62
2009-10-12 02:16 | 59.983 | 3676.9148 | 350 | -330.759 | 0 | 57.5 | 10 | 15 | -103 | 7537.95
2009-10-12 02:16 | 59.98 | 3678.0864 | 350 | -330.759 | 0 | 58 | 10 | 15 | -103 | 7538.28
2009-10-12 02:16 | 59.979 | 3679.2329 | 350 | -330.759 | 0 | 58.5 | 10 | 15 | -103 | 7538.61
2009-10-12 02:16 | 59.983 | 3680.1631 | 350 | -323.42 | 0 | 59 | 10 | 15 | -103 | 7538.94
2009-10-12 02:16 | 59.987 | 3679.2134 | 350 | -323.42 | 0 | 59.5 | 10 | 15 | -103 | 7539.27
2009-10-12 02:16 | 59.986 | 3678.3442 | 350 | -323.42 | 0 | 60 | 10 | 15 | -103 | 7539.6
2009-10-12 02:16 | 59.988 | 3677.6528 | 350 | -323.42 | 0 | 60.5 | 10 | 15 | -103 | 7539.93
2009-10-12 02:16 | 59.987 | 3677.6777 | 350 | -323.42 | 0 | 61 | 10 | 15 | -103 | 7540.26
2009-10-12 02:16 | 59.983 | 3678.9507 | 350 | -342.3509 | 0 | 61.5 | 10 | 15 | -103 | 7540.59
2009-10-12 02:16 | 59.978 | 3679.2791 | 350 | -342.3509 | 0 | 62 | 10 | 15 | -103 | 7540.92
2009-10-12 02:16 | 59.979 | 3678.7295 | 350 | -342.3509 | 0 | 62.5 | 10 | 15 | -103 | 7541.25
2009-10-12 02:16 | 59.979 | 3679.6057 | 350 | -342.3509 | 0 | 63 | 10 | 15 | -103 | 7541.58
2009-10-12 02:16 | 59.989 | 3680.2869 | 350 | -342.3509 | 0 | 63.5 | 10 | 15 | -103 | 7541.91
2009-10-12 02:16 | 59.991 | 3679.0259 | 350 | -345.0818 | 0 | 64 | 10 | 15 | -103 | 7542.24
2009-10-12 02:16 | 59.988 | 3678.8125 | 350 | -345.0818 | 0 | 64.5 | 10 | 15 | -103 | 7542.57
2009-10-12 02:16 | 59.983 | 3678.4885 | 350 | -345.0818 | 0 | 65 | 10 | 15 | -103 | 7542.9
2009-10-12 02:16 | 59.989 | 3678.7202 | 350 | -345.0818 | 0 | 65.5 | 10 | 15 | -103 | 7543.23
2009-10-12 02:16 | 59.991 | 3678.7402 | 350 | -345.0818 | 0 | 66 | 10 | 15 | -103 | 7543.56
2009-10-12 02:16 | 59.989 | 3678.9707 | 350 | -346.5374 | 0 | 66.5 | 10 | 15 | -103 | 7543.89
2009-10-12 02:16 | 59.992 | 3679.3901 | 350 | -346.5374 | 0 | 67 | 10 | 15 | -103 | 7544.22
2009-10-12 02:17 | 59.993 | 3677.0625 | 350 | -346.5374 | 0 | 67.5 | 10 | 15 | -103 | 7544.55
2009-10-12 02:17 | 59.995 | 3678.3301 | 350 | -346.5374 | 0 | 68 | 10 | 15 | -103 | 7544.88
2009-10-12 02:17 | 59.996 | 3678.4905 | 350 | -346.5374 | 0 | 68.5 | 10 | 15 | -103 | 7545.21
2009-10-12 02:17 | 59.998 | 3677.9443 | 350 | -342.9058 | 0 | 69 | 10 | 15 | -103 | 7545.54
2009-10-12 02:17 | 59.998 | 3676.7632 | 350 | -342.9058 | 0 | 69.5 | 10 | 15 | -103 | 7545.87
2009-10-12 02:17 | 60 | 3678.9509 | 350 | -342.9058 | 0 | 70 | 10 | 15 | -103 | 7546.2
2009-10-12 02:17 | 59.999 | 3678.4556 | 350 | -342.9058 | 0 | 70.5 | 10 | 15 | -103 | 7546.53
2009-10-12 02:17 | 59.995 | 3679.1484 | 350 | -342.9058 | 0 | 71 | 10 | 15 | -103 | 7546.86
2009-10-12 02:17 | 59.991 | 3679.9033 | 350 | -340.0944 | 0 | 71.5 | 10 | 15 | -103 | 7547.19
2009-10-12 02:17 | 59.992 | 3680.041 | 350 | -340.0944 | 0 | 72 | 10 | 15 | -103 | 7547.52
2009-10-12 02:17 | 59.995 | 3678.9966 | 350 | -340.0944 | 0 | 72.5 | 10 | 15 | -103 | 7547.85
2009-10-12 02:17 | 59.998 | 3677.8604 | 350 | -340.0944 | 0 | 73 | 10 | 15 | -103 | 7548.18
2009-10-12 02:17 | 60.001 | 3678.4934 | 350 | -340.0944 | 0 | 73.5 | 10 | 15 | -103 | 7548.51
2009-10-12 02:17 | 60.003 | 3678.2668 | 350 | -342.7712 | 0 | 74 | 10 | 15 | -103 | 7548.84
2009-10-12 02:17 | 60.006 | 3677.6855 | 350 | -342.7712 | 0 | 74.5 | 10 | 15 | -103 | 7549.17
2009-10-12 02:17 | 60.009 | 3677.8987 | 350 | -342.7712 | 0 | 75 | 10 | 15 | -103 | 7549.5
2009-10-12 02:17 | 60.009 | 3678.3638 | 350 | -342.7712 | 0 | 75.5 | 10 | 15 | -103 | 7549.83
2009-10-12 02:17 | 60.011 | 3679.2087 | 350 | -342.7712 | 0 | 76 | 10 | 15 | -103 | 7550.16
2009-10-12 02:17 | 60.012 | 3678.6589 | 350 | -342.9099 | 0 | 76.5 | 10 | 15 | -103 | 7550.49
2009-10-12 02:17 | 60.011 | 3678.6526 | 350 | -342.9099 | 0 | 77 | 10 | 15 | -103 | 7550.82
2009-10-12 02:17 | 60.01 | 3679.0566 | 350 | -342.9099 | 0 | 77.5 | 10 | 15 | -103 | 7551.15
2009-10-12 02:17 | 60.008 | 3679.7026 | 350 | -342.9099 | 0 | 78 | 10 | 15 | -103 | 7551.48
2009-10-12 02:17 | 60.007 | 3680.6042 | 350 | -342.9099 | 0 | 78.5 | 10 | 15 | -103 | 7551.81
2009-10-12 02:17 | 60.011 | 3679.8059 | 350 | -343.286 | 0 | 79 | 10 | 15 | -103 | 7552.14
2009-10-12 02:17 | 60.012 | 3680.6255 | 350 | -343.286 | 0 | 79.5 | 10 | 15 | -103 | 7552.47
2009-10-12 02:17 | 60.013 | 3680.2627 | 350 | -343.286 | 0 | 80 | 10 | 15 | -103 | 7552.8
2009-10-12 02:17 | 60.01 | 3679.8511 | 350 | -343.286 | 0 | 80.5 | 10 | 15 | -103 | 7553.13
2009-10-12 02:17 | 60.01 | 3679.5608 | 350 | -343.286 | 0 | 81 | 10 | 15 | -103 | 7553.46
2009-10-12 02:17 | 60.007 | 3679.946 | 350 | -331.853 | 0 | 81.5 | 10 | 15 | -103 | 7553.79
2009-10-12 02:17 | 60.009 | 3679.4399 | 350 | -331.853 | 0 | 82 | 10 | 15 | -103 | 7554.12
2009-10-12 02:18 | 60.009 | 3679.9119 | 350 | -331.853 | 0 | 82.5 | 10 | 15 | -103 | 7554.45
2009-10-12 02:18 | 60.006 | 3679.5166 | 350 | -331.853 | 0 | 83 | 10 | 15 | -103 | 7554.78
2009-10-12 02:18 | 60.006 | 3679.8879 | 350 | -331.853 | 0 | 83.5 | 10 | 15 | -103 | 7555.11
2009-10-12 02:18 | 60.009 | 3679.6082 | 350 | -329.9882 | 0 | 84 | 10 | 15 | -103 | 7555.44
2009-10-12 02:18 | 60.009 | 3679.0596 | 350 | -329.9882 | 0 | 84.5 | 10 | 15 | -103 | 7555.77
2009-10-12 02:18 | 60.008 | 3679.2607 | 350 | -329.9882 | 0 | 85 | 10 | 15 | -103 | 7556.1
2009-10-12 02:18 | 60.009 | 3679.1641 | 350 | -329.9882 | 0 | 85.5 | 10 | 15 | -103 | 7556.43
2009-10-12 02:18 | 60.009 | 3679.0247 | 350 | -329.9882 | 0 | 86 | 10 | 15 | -103 | 7556.76
2009-10-12 02:18 | 60.005 | 3679.1521 | 350 | -255.4442 | 0 | 86.5 | 10 | 15 | -103 | 7557.09
2009-10-12 02:18 | 60.004 | 3678.5723 | 350 | -255.4442 | 0 | 87 | 10 | 15 | -103 | 7557.42
2009-10-12 02:18 | 60.001 | 3678.2952 | 350 | -255.4442 | 0 | 87.5 | 10 | 15 | -103 | 7557.75
2009-10-12 02:18 | 59.999 | 3678.2488 | 350 | -255.4442 | 0 | 88 | 10 | 15 | -103 | 7558.08
2009-10-12 02:18 | 59.993 | 3678.2358 | 350 | -255.4442 | 0 | 88.5 | 10 | 15 | -103 | 7558.41
2009-10-12 02:18 | 59.991 | 3677.8296 | 350 | -254.8383 | 0 | 89 | 10 | 15 | -103 | 7558.74
2009-10-12 02:18 | 59.994 | 3677.9548 | 350 | -254.8383 | 0 | 89.5 | 10 | 15 | -103 | 7559.07
2009-10-12 02:18 | 59.992 | 3677.7722 | 350 | -254.8383 | 0 | 90 | 10 | 15 | -103 | 7559.4
2009-10-12 02:18 | 59.994 | 3676.6658 | 350 | -254.8383 | 0 | 90.5 | 10 | 15 | -103 | 7559.73
2009-10-12 02:18 | 59.992 | 3677.0933 | 350 | -254.8383 | 0 | 91 | 10 | 15 | -103 | 7560.06
2009-10-12 02:18 | 59.994 | 3677.1406 | 350 | -257.147 | 0 | 91.5 | 10 | 15 | -103 | 7560.39
2009-10-12 02:18 | 59.995 | 3676.4006 | 350 | -257.147 | 0 | 92 | 10 | 15 | -103 | 7560.72
2009-10-12 02:18 | 59.993 | 3678.5156 | 350 | -257.147 | 0 | 92.5 | 10 | 15 | -103 | 7561.05
2009-10-12 02:18 | 59.99 | 3679.8721 | 350 | -257.147 | 0 | 93 | 10 | 15 | -103 | 7561.38
2009-10-12 02:18 | 59.99 | 3680.1965 | 350 | -257.147 | 0 | 93.5 | 10 | 15 | -103 | 7561.71
2009-10-12 02:18 | 59.987 | 3678.7432 | 350 | -262.2894 | 0 | 94 | 10 | 15 | -103 | 7562.04
2009-10-12 02:18 | 59.983 | 3678.428 | 350 | -262.2894 | 0 | 94.5 | 10 | 15 | -103 | 7562.37
2009-10-12 02:18 | 59.977 | 3677.9211 | 350 | -262.2894 | 0 | 95 | 10 | 15 | -103 | 7562.7
2009-10-12 02:18 | 59.977 | 3680.2537 | 350 | -262.2894 | 0 | 95.5 | 10 | 15 | -103 | 7563.03
2009-10-12 02:18 | 59.989 | 3682.0701 | 350 | -262.2894 | 0 | 96 | 10 | 15 | -103 | 7563.36
2009-10-12 02:18 | 59.995 | 3681.3293 | 350 | -256.6479 | 0 | 96.5 | 10 | 15 | -103 | 7563.69
2009-10-12 02:18 | 59.999 | 3678.6555 | 350 | -256.6479 | 0 | 97 | 10 | 15 | -103 | 7564.02
2009-10-12 02:18 | 59.994 | 3678.0767 | 350 | -256.6479 | 0 | 97.5 | 10 | 15 | -103 | 7564.35
2009-10-12 02:19 | 59.989 | 3677.78 | 350 | -256.6479 | 0 | 98 | 10 | 15 | -103 | 7564.68
2009-10-12 02:19 | 59.987 | 3678.4268 | 350 | -256.6479 | 0 | 98.5 | 10 | 15 | -103 | 7565.01
2009-10-12 02:19 | 59.986 | 3678.4731 | 350 | -256.3073 | 0 | 99 | 10 | 15 | -103 | 7565.34
2009-10-12 02:19 | 59.984 | 3678.2778 | 350 | -256.3073 | 0 | 99.5 | 10 | 15 | -103 | 7565.67
2009-10-12 02:19 | 59.983 | 3677.8223 | 350 | -256.3073 | 0 | 100 | 10 | 15 | -103 | 7566
2009-10-12 02:19 | 59.985 | 3676.615 | 350 | -256.3073 | 0 | 100.5 | 10 | 15 | -103 | 7566.33
2009-10-12 02:19 | 59.986 | 3677.3975 | 350 | -256.3073 | 0 | 101 | 10 | 15 | -103 | 7566.66
2009-10-12 02:19 | 59.985 | 3677.917 | 350 | -249.0864 | 0 | 101.5 | 10 | 15 | -103 | 7566.99
2009-10-12 02:19 | 59.986 | 3677.9497 | 350 | -249.0864 | 0 | 102 | 10 | 15 | -103 | 7567.32
2009-10-12 02:19 | 59.98 | 3678.6167 | 350 | -249.0864 | 0 | 102.5 | 10 | 15 | -103 | 7567.65
2009-10-12 02:19 | 59.981 | 3678.9626 | 350 | -249.0864 | 0 | 103 | 10 | 15 | -103 | 7567.98
2009-10-12 02:19 | 59.981 | 3681.2522 | 350 | -249.0864 | 0 | 103.5 | 10 | 15 | -103 | 7568.31
2009-10-12 02:19 | 59.989 | 3680.7373 | 350 | -253.7425 | 0 | 104 | 10 | 15 | -103 | 7568.64
2009-10-12 02:19 | 59.998 | 3680.0449 | 350 | -253.7425 | 0 | 104.5 | 10 | 15 | -103 | 7568.97
2009-10-12 02:19 | 60.007 | 3678.1614 | 350 | -253.7425 | 0 | 105 | 10 | 15 | -103 | 7569.3
2009-10-12 02:19 | 60.007 | 3674.0762 | 350 | -253.7425 | 0 | 105.5 | 10 | 15 | -103 | 7569.63
2009-10-12 02:19 | 59.997 | 3676.2222 | 350 | -253.7425 | 0 | 106 | 10 | 15 | -103 | 7569.96
2009-10-12 02:19 | 59.986 | 3676.6694 | 350 | -257.4212 | 0 | 106.5 | 10 | 15 | -103 | 7570.29
2009-10-12 02:19 | 59.981 | 3677.4971 | 350 | -257.4212 | 0 | 107 | 10 | 15 | -103 | 7570.62
2009-10-12 02:19 | 59.977 | 3677.49 | 350 | -257.4212 | 0 | 107.5 | 10 | 15 | -103 | 7570.95
2009-10-12 02:19 | 59.974 | 3675.1858 | 350 | -257.4212 | 0 | 108 | 10 | 15 | -103 | 7571.28
2009-10-12 02:19 | 59.976 | 3675.437 | 350 | -257.4212 | 0 | 108.5 | 10 | 15 | -103 | 7571.61
2009-10-12 02:19 | 59.974 | 3680.4509 | 350 | -261.7382 | 0 | 109 | 10 | 15 | -103 | 7571.94
2009-10-12 02:19 | 59.974 | 3682.0317 | 350 | -261.7382 | 0 | 109.5 | 10 | 15 | -103 | 7572.27
2009-10-12 02:19 | 59.977 | 3683.8286 | 350 | -261.7382 | 0 | 110 | 10 | 15 | -103 | 7572.6
2009-10-12 02:19 | 59.979 | 3682.8433 | 350 | -261.7382 | 0 | 110.5 | 10 | 15 | -103 | 7572.93
2009-10-12 02:19 | 59.979 | 3681.1084 | 350 | -261.7382 | 0 | 111 | 10 | 15 | -103 | 7573.26
2009-10-12 02:19 | 59.982 | 3680.5657 | 350 | -271.876 | 0 | 111.5 | 10 | 15 | -103 | 7573.59
2009-10-12 02:19 | 59.984 | 3678.229 | 350 | -271.876 | 0 | 112 | 10 | 15 | -103 | 7573.92
2009-10-12 02:20 | 59.987 | 3676.752 | 350 | -271.876 | 0 | 112.5 | 10 | 15 | -103 | 7574.25
2009-10-12 02:20 | 59.988 | 3675.7593 | 350 | -271.876 | 0 | 113 | 10 | 15 | -103 | 7574.58
2009-10-12 02:20 | 59.988 | 3671.9424 | 350 | -271.876 | 0 | 113.5 | 10 | 15 | -103 | 7574.91
2009-10-12 02:20 | 59.987 | 3671.1655 | 350 | -262.0735 | 0 | 114 | 10 | 15 | -103 | 7575.24
2009-10-12 02:20 | 59.987 | 3670.4758 | 350 | -262.0735 | 0 | 114.5 | 10 | 15 | -103 | 7575.57
2009-10-12 02:20 | 59.987 | 3670.1287 | 350 | -262.0735 | 0 | 115 | 10 | 15 | -103 | 7575.9
2009-10-12 02:20 | 59.985 | 3671.5415 | 350 | -262.0735 | 0 | 115.5 | 10 | 15 | -103 | 7576.23
2009-10-12 02:20 | 59.984 | 3672.0479 | 350 | -262.0735 | 0 | 116 | 10 | 15 | -103 | 7576.56
2009-10-12 02:20 | 59.982 | 3671.5757 | 350 | -260.3644 | 0 | 116.5 | 10 | 15 | -103 | 7576.89
2009-10-12 02:20 | 59.983 | 3672.1035 | 350 | -260.3644 | 0 | 117 | 10 | 15 | -103 | 7577.22
2009-10-12 02:20 | 59.989 | 3672.4136 | 350 | -260.3644 | 0 | 117.5 | 10 | 15 | -103 | 7577.55
2009-10-12 02:20 | 59.989 | 3671.8823 | 350 | -260.3644 | 0 | 118 | 10 | 15 | -103 | 7577.88
2009-10-12 02:20 | 59.988 | 3671.8372 | 350 | -260.3644 | 0 | 118.5 | 10 | 15 | -103 | 7578.21
2009-10-12 02:20 | 59.984 | 3671.3359 | 350 | -352.6444 | 0 | 119 | 10 | 15 | -103 | 7578.54
2009-10-12 02:20 | 59.982 | 3670.7258 | 350 | -352.6444 | 0 | 119.5 | 10 | 15 | -103 | 7578.87
2009-10-12 02:20 | 59.983 | 3670.3721 | 350 | -352.6444 | 0 | 120 | 10 | 15 | -103 | 7579.2
2009-10-12 02:20 | 59.981 | 3671.364 | 350 | -352.6444 | 0 | 120.5 | 10 | 15 | -103 | 7579.53
2009-10-12 02:20 | 59.982 | 3671.4009 | 350 | -352.6444 | 0 | 121 | 10 | 15 | -103 | 7579.86
2009-10-12 02:20 | 59.983 | 3672.1562 | 350 | -354.8957 | 0 | 121.5 | 10 | 15 | -103 | 7580.19
2009-10-12 02:20 | 59.986 | 3672.1814 | 350 | -354.8957 | 0 | 122 | 10 | 15 | -103 | 7580.52
2009-10-12 02:20 | 59.989 | 3670.2964 | 350 | -354.8957 | 0 | 122.5 | 10 | 15 | -103 | 7580.85
2009-10-12 02:20 | 59.987 | 3668.0708 | 350 | -354.8957 | 0 | 123 | 10 | 15 | -103 | 7581.18
2009-10-12 02:20 | 59.985 | 3668.5896 | 350 | -354.8957 | 0 | 123.5 | 10 | 15 | -103 | 7581.51
2009-10-12 02:20 | 59.98 | 3669.9082 | 350 | -340.4694 | 0 | 124 | 10 | 15 | -103 | 7581.84
2009-10-12 02:20 | 59.98 | 3670.3994 | 350 | -340.4694 | 0 | 124.5 | 10 | 15 | -103 | 7582.17
2009-10-12 02:20 | 59.983 | 3670.2627 | 350 | -340.4694 | 0 | 125 | 10 | 15 | -103 | 7582.5
2009-10-12 02:20 | 59.98 | 3669.3823 | 350 | -340.4694 | 0 | 125.5 | 10 | 15 | -103 | 7582.83
2009-10-12 02:20 | 59.979 | 3670.1021 | 350 | -340.4694 | 0 | 126 | 10 | 15 | -103 | 7583.16
2009-10-12 02:20 | 59.979 | 3670.4375 | 350 | -337.6429 | 0 | 126.5 | 10 | 15 | -103 | 7583.49
2009-10-12 02:20 | 59.981 | 3671.4026 | 350 | -337.6429 | 0 | 127 | 10 | 15 | -103 | 7583.82
2009-10-12 02:20 | 59.981 | 3672.4424 | 350 | -337.6429 | 0 | 127.5 | 10 | 15 | -103 | 7584.15
2009-10-12 02:21 | 59.98 | 3672.3718 | 350 | -337.6429 | 0 | 128 | 10 | 15 | -103 | 7584.48
2009-10-12 02:21 | 59.98 | 3671.947 | 350 | -337.6429 | 0 | 128.5 | 10 | 15 | -103 | 7584.81
2009-10-12 02:21 | 59.981 | 3670.9375 | 350 | -284.3608 | 0 | 129 | 10 | 15 | -103 | 7585.14
2009-10-12 02:21 | 59.98 | 3670.7046 | 350 | -284.3608 | 0 | 129.5 | 10 | 15 | -103 | 7585.47
2009-10-12 02:21 | 59.98 | 3670.1372 | 350 | -284.3608 | 0 | 130 | 10 | 15 | -103 | 7585.8
2009-10-12 02:21 | 59.977 | 3669.2793 | 350 | -284.3608 | 0 | 130.5 | 10 | 15 | -103 | 7586.13
2009-10-12 02:21 | 59.979 | 3672.3909 | 350 | -284.3608 | 0 | 131 | 10 | 15 | -103 | 7586.46
2009-10-12 02:21 | 59.981 | 3672.5579 | 350 | -260.468 | 0 | 131.5 | 10 | 15 | -103 | 7586.79
2009-10-12 02:21 | 59.979 | 3674.0518 | 350 | -260.468 | 0 | 132 | 10 | 15 | -103 | 7587.12
2009-10-12 02:21 | 59.976 | 3672.6265 | 350 | -260.468 | 0 | 132.5 | 10 | 15 | -103 | 7587.45
2009-10-12 02:21 | 59.977 | 3671.8003 | 350 | -260.468 | 0 | 133 | 10 | 15 | -103 | 7587.78
2009-10-12 02:21 | 59.972 | 3673.1829 | 350 | -260.468 | 0 | 133.5 | 10 | 15 | -103 | 7588.11
2009-10-12 02:21 | 59.971 | 3673.8735 | 350 | -253.1415 | 0 | 134 | 10 | 15 | -103 | 7588.44
2009-10-12 02:21 | 59.973 | 3676.2627 | 350 | -253.1415 | 0 | 134.5 | 10 | 15 | -103 | 7588.77
2009-10-12 02:21 | 59.973 | 3676.6233 | 350 | -253.1415 | 0 | 135 | 10 | 15 | -103 | 7589.1
2009-10-12 02:21 | 59.973 | 3676.8699 | 350 | -253.1415 | 0 | 135.5 | 10 | 15 | -103 | 7589.43
2009-10-12 02:21 | 59.974 | 3676.543 | 350 | -253.1415 | 0 | 136 | 10 | 15 | -103 | 7589.76
2009-10-12 02:21 | 59.971 | 3675.4641 | 350 | -251.9299 | 0 | 136.5 | 10 | 15 | -103 | 7590.09
2009-10-12 02:21 | 59.975 | 3675.7524 | 350 | -251.9299 | 0 | 137 | 10 | 15 | -103 | 7590.42
2009-10-12 02:21 | 59.977 | 3675.2559 | 350 | -251.9299 | 0 | 137.5 | 10 | 15 | -103 | 7590.75
2009-10-12 02:21 | 59.977 | 3674.8696 | 350 | -251.9299 | 0 | 138 | 10 | 15 | -103 | 7591.08
2009-10-12 02:21 | 59.975 | 3671.2769 | 350 | -251.9299 | 0 | 138.5 | 10 | 15 | -103 | 7591.41
2009-10-12 02:21 | 59.976 | 3671.5933 | 350 | -250.6742 | 0 | 139 | 10 | 15 | -103 | 7591.74
2009-10-12 02:21 | 59.98 | 3670.5869 | 350 | -250.6742 | 0 | 139.5 | 10 | 15 | -103 | 7592.07
2009-10-12 02:21 | 59.979 | 3669.9629 | 350 | -250.6742 | 0 | 140 | 10 | 15 | -103 | 7592.4
2009-10-12 02:21 | 59.981 | 3669.54 | 350 | -250.6742 | 0 | 140.5 | 10 | 15 | -103 | 7592.73
2009-10-12 02:21 | 59.982 | 3669.4968 | 350 | -250.6742 | 0 | 141 | 10 | 15 | -103 | 7593.06
2009-10-12 02:21 | 59.982 | 3668.7056 | 350 | -253.6319 | 0 | 141.5 | 10 | 15 | -103 | 7593.39
2009-10-12 02:21 | 59.982 | 3667.6765 | 350 | -253.6319 | 0 | 142 | 10 | 15 | -103 | 7593.72
2009-10-12 02:22 | 59.982 | 3666.4817 | 350 | -253.6319 | 0 | 142.5 | 10 | 15 | -103 | 7594.05
2009-10-12 02:22 | 59.981 | 3666.5994 | 350 | -253.6319 | 0 | 143 | 10 | 15 | -103 | 7594.38
2009-10-12 02:22 | 59.982 | 3666.9106 | 350 | -253.6319 | 0 | 143.5 | 10 | 15 | -103 | 7594.71
2009-10-12 02:22 | 59.984 | 3666.4417 | 350 | -246.9573 | 0 | 144 | 10 | 15 | -103 | 7595.04
2009-10-12 02:22 | 59.985 | 3666.4048 | 350 | -246.9573 | 0 | 144.5 | 10 | 15 | -103 | 7595.37
2009-10-12 02:22 | 59.987 | 3667.4563 | 350 | -246.9573 | 0 | 145 | 10 | 15 | -103 | 7595.7
2009-10-12 02:22 | 59.989 | 3666.3804 | 350 | -246.9573 | 0 | 145.5 | 10 | 15 | -103 | 7596.03
2009-10-12 02:22 | 59.993 | 3665.2617 | 350 | -246.9573 | 0 | 146 | 10 | 15 | -103 | 7596.36
2009-10-12 02:22 | 59.996 | 3664.031 | 350 | -254.5418 | 0 | 146.5 | 10 | 15 | -103 | 7596.69
2009-10-12 02:22 | 59.998 | 3663.825 | 350 | -254.5418 | 0 | 147 | 10 | 15 | -103 | 7597.02
2009-10-12 02:22 | 59.998 | 3663.2288 | 350 | -254.5418 | 0 | 147.5 | 10 | 15 | -103 | 7597.35
2009-10-12 02:22 | 60.004 | 3662.0549 | 350 | -254.5418 | 0 | 148 | 10 | 15 | -103 | 7597.68
2009-10-12 02:22 | 60.007 | 3661.6953 | 350 | -254.5418 | 0 | 148.5 | 10 | 15 | -103 | 7598.01
2009-10-12 02:22 | 60.01 | 3662.0762 | 350 | -256.5716 | 0 | 149 | 10 | 15 | -103 | 7598.34
2009-10-12 02:22 | 60.013 | 3662.2239 | 350 | -256.5716 | 0 | 149.5 | 10 | 15 | -103 | 7598.67
2009-10-12 02:22 | 60.014 | 3662.9595 | 350 | -256.5716 | 0 | 150 | 10 | 15 | -103 | 7599
2009-10-12 02:22 | 60.013 | 3663.7944 | 350 | -256.5716 | 0 | 150.5 | 10 | 15 | -103 | 7599.33
2009-10-12 02:22 | 60.008 | 3664.1392 | 350 | -256.5716 | 0 | 151 | 10 | 15 | -103 | 7599.66
2009-10-12 02:22 | 60.008 | 3665.2778 | 350 | -258.3726 | 0 | 151.5 | 10 | 15 | -103 | 7599.99
2009-10-12 02:22 | 60.01 | 3664.1587 | 350 | -258.3726 | 0 | 152 | 10 | 15 | -103 | 7600.32
2009-10-12 02:22 | 60.019 | 3663.2646 | 350 | -258.3726 | 0 | 152.5 | 10 | 15 | -103 | 7600.65
2009-10-12 02:22 | 60.019 | 3663.1836 | 350 | -258.3726 | 0 | 153 | 10 | 15 | -103 | 7600.98
2009-10-12 02:22 | 60.023 | 3661.9292 | 350 | -258.3726 | 0 | 153.5 | 10 | 15 | -103 | 7601.31
2009-10-12 02:22 | 60.021 | 3661.5122 | 350 | -263.0474 | 0 | 154 | 10 | 15 | -103 | 7601.64
2009-10-12 02:22 | 60.02 | 3659.1724 | 350 | -263.0474 | 0 | 154.5 | 10 | 15 | -103 | 7601.97
2009-10-12 02:22 | 60.021 | 3658.6614 | 350 | -263.0474 | 0 | 155 | 10 | 15 | -103 | 7602.3
2009-10-12 02:22 | 60.021 | 3656.7854 | 350 | -263.0474 | 0 | 155.5 | 10 | 15 | -103 | 7602.63
2009-10-12 02:22 | 60.02 | 3657.571 | 350 | -263.0474 | 0 | 156 | 10 | 15 | -103 | 7602.96
2009-10-12 02:22 | 60.019 | 3658.126 | 350 | -260.9844 | 0 | 156.5 | 10 | 15 | -103 | 7603.29
2009-10-12 02:22 | 60.019 | 3657.7104 | 350 | -260.9844 | 0 | 157 | 10 | 15 | -103 | 7603.62
2009-10-12 02:22 | 60.022 | 3658.0146 | 350 | -260.9844 | 0 | 157.5 | 10 | 15 | -103 | 7603.95
2009-10-12 02:23 | 60.025 | 3660.2275 | 350 | -260.9844 | 0 | 158 | 10 | 15 | -103 | 7604.28
2009-10-12 02:23 | 60.025 | 3659.2236 | 350 | -260.9844 | 0 | 158.5 | 10 | 15 | -103 | 7604.61
2009-10-12 02:23 | 60.026 | 3658.6982 | 350 | -261.3183 | 0 | 159 | 10 | 15 | -103 | 7604.94
2009-10-12 02:23 | 60.02 | 3658.6687 | 350 | -261.3183 | 0 | 159.5 | 10 | 15 | -103 | 7605.27
2009-10-12 02:23 | 60.02 | 3658.1545 | 350 | -261.3183 | 0 | 160 | 10 | 15 | -103 | 7605.6
2009-10-12 02:23 | 60.018 | 3659.1296 | 350 | -261.3183 | 0 | 160.5 | 10 | 15 | -103 | 7605.93
2009-10-12 02:23 | 60.018 | 3659.7776 | 350 | -261.3183 | 0 | 161 | 10 | 15 | -103 | 7606.26
2009-10-12 02:23 | 60.02 | 3660.8196 | 350 | -262.1026 | 0 | 161.5 | 10 | 15 | -103 | 7606.59
2009-10-12 02:23 | 60.019 | 3662.5315 | 350 | -262.1026 | 0 | 162 | 10 | 15 | -103 | 7606.92
2009-10-12 02:23 | 60.019 | 3662.3872 | 350 | -262.1026 | 0 | 162.5 | 10 | 15 | -103 | 7607.25
2009-10-12 02:23 | 60.023 | 3662.0789 | 350 | -262.1026 | 0 | 163 | 10 | 15 | -103 | 7607.58
2009-10-12 02:23 | 60.022 | 3662.3901 | 350 | -262.1026 | 0 | 163.5 | 10 | 15 | -103 | 7607.91
2009-10-12 02:23 | 60.022 | 3662.6782 | 350 | -262.717 | 0 | 164 | 10 | 15 | -103 | 7608.24
2009-10-12 02:23 | 60.025 | 3663.5767 | 350 | -262.717 | 0 | 164.5 | 10 | 15 | -103 | 7608.57
2009-10-12 02:23 | 60.02 | 3663.5386 | 350 | -262.717 | 0 | 165 | 10 | 15 | -103 | 7608.9
2009-10-12 02:23 | 60.02 | 3662.9592 | 350 | -262.717 | 0 | 165.5 | 10 | 15 | -103 | 7609.23
2009-10-12 02:23 | 60.02 | 3662.5525 | 350 | -262.717 | 0 | 166 | 10 | 15 | -103 | 7609.56
2009-10-12 02:23 | 60.02 | 3662.543 | 350 | -260.0165 | 0 | 166.5 | 10 | 15 | -103 | 7609.89
2009-10-12 02:23 | 60.02 | 3663.6006 | 350 | -260.0165 | 0 | 167 | 10 | 15 | -103 | 7610.22
2009-10-12 02:23 | 60.021 | 3663.9097 | 350 | -260.0165 | 0 | 167.5 | 10 | 15 | -103 | 7610.55
2009-10-12 02:23 | 60.021 | 3663.6899 | 350 | -260.0165 | 0 | 168 | 10 | 15 | -103 | 7610.88
2009-10-12 02:23 | 60.018 | 3662.7913 | 350 | -260.0165 | 0 | 168.5 | 10 | 15 | -103 | 7611.21
2009-10-12 02:23 | 60.014 | 3663.3958 | 350 | -263.8732 | 0 | 169 | 10 | 15 | -103 | 7611.54
2009-10-12 02:23 | 60.014 | 3663.6978 | 350 | -263.8732 | 0 | 169.5 | 10 | 15 | -103 | 7611.87
2009-10-12 02:23 | 60.014 | 3664.3154 | 350 | -263.8732 | 0 | 170 | 10 | 15 | -103 | 7612.2
2009-10-12 02:23 | 60.013 | 3665.313 | 350 | -263.8732 | 0 | 170.5 | 10 | 15 | -103 | 7612.53
2009-10-12 02:23 | 60.013 | 3665.7976 | 350 | -263.8732 | 0 | 171 | 10 | 15 | -103 | 7612.86
2009-10-12 02:23 | 60.01 | 3666.1411 | 350 | -264.5979 | 0 | 171.5 | 10 | 15 | -103 | 7613.19
2009-10-12 02:23 | 60.008 | 3666.7258 | 350 | -264.5979 | 0 | 172 | 10 | 15 | -103 | 7613.52
2009-10-12 02:24 | 60.011 | 3667.6768 | 350 | -264.5979 | 0 | 172.5 | 10 | 15 | -103 | 7613.85
2009-10-12 02:24 | 60.011 | 3667.5454 | 350 | -264.5979 | 0 | 173 | 10 | 15 | -103 | 7614.18
2009-10-12 02:24 | 60.012 | 3666.6882 | 350 | -264.5979 | 0 | 173.5 | 10 | 15 | -103 | 7614.51
2009-10-12 02:24 | 60.012 | 3666.4487 | 350 | -262.4159 | 0 | 174 | 10 | 15 | -103 | 7614.84
2009-10-12 02:24 | 60.009 | 3666.7104 | 350 | -262.4159 | 0 | 174.5 | 10 | 15 | -103 | 7615.17
2009-10-12 02:24 | 60.009 | 3667.696 | 350 | -262.4159 | 0 | 175 | 10 | 15 | -103 | 7615.5
2009-10-12 02:24 | 60.009 | 3667.3982 | 350 | -262.4159 | 0 | 175.5 | 10 | 15 | -103 | 7615.83
2009-10-12 02:24 | 60.009 | 3667.043 | 350 | -262.4159 | 0 | 176 | 10 | 15 | -103 | 7616.16
2009-10-12 02:24 | 60.005 | 3666.6235 | 350 | -259.6852 | 0 | 176.5 | 10 | 15 | -103 | 7616.49
2009-10-12 02:24 | 60.002 | 3666.2227 | 350 | -259.6852 | 0 | 177 | 10 | 15 | -103 | 7616.82
2009-10-12 02:24 | 59.999 | 3665.8796 | 350 | -259.6852 | 0 | 177.5 | 10 | 15 | -103 | 7617.15
2009-10-12 02:24 | 59.996 | 3665.4033 | 350 | -259.6852 | 0 | 178 | 10 | 15 | -103 | 7617.48
2009-10-12 02:24 | 59.995 | 3665.8015 | 350 | -259.6852 | 0 | 178.5 | 10 | 15 | -103 | 7617.81
2009-10-12 02:24 | 59.997 | 3665.6797 | 350 | -255.911 | 0 | 179 | 10 | 15 | -103 | 7618.14
2009-10-12 02:24 | 59.998 | 3665.3521 | 350 | -255.911 | 0 | 179.5 | 10 | 15 | -103 | 7618.47
2009-10-12 02:24 | 59.998 | 3664.9475 | 350 | -255.911 | 0 | 180 | 10 | 15 | -103 | 7618.8
2009-10-12 02:24 | 59.998 | 3665.0649 | 350 | -255.911 | 0 | 180.5 | 10 | 15 | -103 | 7619.13
2009-10-12 02:24 | 59.998 | 3666.1333 | 350 | -255.911 | 0 | 181 | 10 | 15 | -103 | 7619.46
2009-10-12 02:24 | 59.995 | 3666.6396 | 350 | -258.1482 | 0 | 181.5 | 10 | 15 | -103 | 7619.79
2009-10-12 02:24 | 59.995 | 3666.7346 | 350 | -258.1482 | 0 | 182 | 10 | 15 | -103 | 7620.12
2009-10-12 02:24 | 59.992 | 3667.084 | 350 | -258.1482 | 0 | 182.5 | 10 | 15 | -103 | 7620.45
2009-10-12 02:24 | 59.993 | 3667.5574 | 350 | -258.1482 | 0 | 183 | 10 | 15 | -103 | 7620.78
2009-10-12 02:24 | 59.988 | 3667.3367 | 350 | -258.1482 | 0 | 183.5 | 10 | 15 | -103 | 7621.11
2009-10-12 02:24 | 59.988 | 3667.8533 | 350 | -258.8736 | 0 | 184 | 10 | 15 | -103 | 7621.44
2009-10-12 02:24 | 59.982 | 3668.1165 | 350 | -258.8736 | 0 | 184.5 | 10 | 15 | -103 | 7621.77
2009-10-12 02:24 | 59.982 | 3668.6909 | 350 | -258.8736 | 0 | 185 | 10 | 15 | -103 | 7622.1
2009-10-12 02:24 | 59.982 | 3669.3992 | 350 | -258.8736 | 0 | 185.5 | 10 | 15 | -103 | 7622.43
2009-10-12 02:24 | 59.982 | 3669.6062 | 350 | -258.8736 | 0 | 186 | 10 | 15 | -103 | 7622.76
2009-10-12 02:24 | 59.984 | 3671.228 | 350 | -249.3376 | 0 | 186.5 | 10 | 15 | -103 | 7623.09
2009-10-12 02:24 | 59.982 | 3670.25 | 350 | -249.3376 | 0 | 187 | 10 | 15 | -103 | 7623.42
2009-10-12 02:24 | 59.978 | 3670.2646 | 350 | -249.3376 | 0 | 187.5 | 10 | 15 | -103 | 7623.75
2009-10-12 02:25 | 59.978 | 3671.5488 | 350 | -249.3376 | 0 | 188 | 10 | 15 | -103 | 7624.08
2009-10-12 02:25 | 59.976 | 3673.2432 | 350 | -249.3376 | 0 | 188.5 | 10 | 15 | -103 | 7624.41
2009-10-12 02:25 | 59.975 | 3674.2629 | 350 | -258.2782 | 0 | 189 | 10 | 15 | -103 | 7624.74
2009-10-12 02:25 | 59.974 | 3675.8245 | 350 | -258.2782 | 0 | 189.5 | 10 | 15 | -103 | 7625.07
2009-10-12 02:25 | 59.974 | 3676.4182 | 350 | -258.2782 | 0 | 190 | 10 | 15 | -103 | 7625.4
2009-10-12 02:25 | 59.979 | 3676.3057 | 350 | -258.2782 | 0 | 190.5 | 10 | 15 | -103 | 7625.73
2009-10-12 02:25 | 59.98 | 3674.6375 | 350 | -258.2782 | 0 | 191 | 10 | 15 | -103 | 7626.06
2009-10-12 02:25 | 59.981 | 3675.3289 | 350 | -258.4064 | 0 | 191.5 | 10 | 15 | -103 | 7626.39
2009-10-12 02:25 | 59.98 | 3675.2261 | 350 | -258.4064 | 0 | 192 | 10 | 15 | -103 | 7626.72
2009-10-12 02:25 | 59.984 | 3674.7681 | 350 | -258.4064 | 0 | 192.5 | 10 | 15 | -103 | 7627.05
2009-10-12 02:25 | 59.987 | 3674.3994 | 350 | -258.4064 | 0 | 193 | 10 | 15 | -103 | 7627.38
2009-10-12 02:25 | 59.988 | 3673.5142 | 350 | -258.4064 | 0 | 193.5 | 10 | 15 | -103 | 7627.71
2009-10-12 02:25 | 59.988 | 3673.0396 | 350 | -260.5389 | 0 | 194 | 10 | 15 | -103 | 7628.04
2009-10-12 02:25 | 59.99 | 3672.4417 | 350 | -260.5389 | 0 | 194.5 | 10 | 15 | -103 | 7628.37
2009-10-12 02:25 | 59.992 | 3673.0564 | 350 | -260.5389 | 0 | 195 | 10 | 15 | -103 | 7628.7
2009-10-12 02:25 | 59.991 | 3671.6802 | 350 | -260.5389 | 0 | 195.5 | 10 | 15 | -103 | 7629.03
2009-10-12 02:25 | 59.991 | 3671.4932 | 350 | -260.5389 | 0 | 196 | 10 | 15 | -103 | 7629.36
2009-10-12 02:25 | 59.991 | 3669.53 | 350 | -257.8821 | 0 | 196.5 | 10 | 15 | -103 | 7629.69
2009-10-12 02:25 | 59.993 | 3670.0662 | 350 | -257.8821 | 0 | 197 | 10 | 15 | -103 | 7630.02
2009-10-12 02:25 | 59.993 | 3670.0278 | 350 | -257.8821 | 0 | 197.5 | 10 | 15 | -103 | 7630.35
2009-10-12 02:25 | 59.996 | 3671.7441 | 350 | -257.8821 | 0 | 198 | 10 | 15 | -103 | 7630.68
2009-10-12 02:25 | 60.002 | 3671.5781 | 350 | -257.8821 | 0 | 198.5 | 10 | 15 | -103 | 7631.01
2009-10-12 02:25 | 60.002 | 3672.6255 | 350 | -258.5887 | 0 | 199 | 10 | 15 | -103 | 7631.34
2009-10-12 02:25 | 60.003 | 3672.6741 | 350 | -258.5887 | 0 | 199.5 | 10 | 15 | -103 | 7631.67
2009-10-12 02:25 | 60.004 | 3673.8186 | 350 | -258.5887 | 0 | 200 | 10 | 15 | -103 | 7632
2009-10-12 02:25 | 60.005 | 3673.2495 | 350 | -258.5887 | 0 | 200.5 | 10 | 15 | -103 | 7632.33
2009-10-12 02:25 | 60.004 | 3673.1821 | 350 | -258.5887 | 0 | 201 | 10 | 15 | -103 | 7632.66
2009-10-12 02:25 | 60.002 | 3673.4963 | 350 | -261.9062 | 0 | 201.5 | 10 | 15 | -103 | 7632.99
2009-10-12 02:25 | 60.004 | 3672.418 | 350 | -261.9062 | 0 | 202 | 10 | 15 | -103 | 7633.32
2009-10-12 02:26 | 60.008 | 3672.363 | 350 | -261.9062 | 0 | 202.5 | 10 | 15 | -103 | 7633.65
2009-10-12 02:26 | 60.01 | 3672.2168 | 350 | -261.9062 | 0 | 203 | 10 | 15 | -103 | 7633.98
2009-10-12 02:26 | 60.01 | 3672.2607 | 350 | -261.9062 | 0 | 203.5 | 10 | 15 | -103 | 7634.31
2009-10-12 02:26 | 60.01 | 3673.1821 | 350 | -256.7478 | 0 | 204 | 10 | 15 | -103 | 7634.64
2009-10-12 02:26 | 60.011 | 3673.6033 | 350 | -256.7478 | 0 | 204.5 | 10 | 15 | -103 | 7634.97
2009-10-12 02:26 | 60.013 | 3673.5535 | 350 | -256.7478 | 0 | 205 | 10 | 15 | -103 | 7635.3
2009-10-12 02:26 | 60.014 | 3674.312 | 350 | -256.7478 | 0 | 205.5 | 10 | 15 | -103 | 7635.63
2009-10-12 02:26 | 60.013 | 3674.5371 | 350 | -256.7478 | 0 | 206 | 10 | 15 | -103 | 7635.96
2009-10-12 02:26 | 60.012 | 3673.8125 | 350 | -167.432 | 0 | 206.5 | 10 | 15 | -103 | 7636.29
2009-10-12 02:26 | 60.011 | 3673.2036 | 350 | -167.432 | 0 | 207 | 10 | 15 | -103 | 7636.62
2009-10-12 02:26 | 60.011 | 3672.5632 | 350 | -167.432 | 0 | 207.5 | 10 | 15 | -103 | 7636.95
2009-10-12 02:26 | 60.017 | 3673.0676 | 350 | -167.432 | 0 | 208 | 10 | 15 | -103 | 7637.28
2009-10-12 02:26 | 60.022 | 3672.3882 | 350 | -167.432 | 0 | 208.5 | 10 | 15 | -103 | 7637.61
2009-10-12 02:26 | 60.017 | 3672.5195 | 350 | -164.9734 | 0 | 209 | 10 | 15 | -103 | 7637.94
2009-10-12 02:26 | 60.014 | 3671.25 | 350 | -164.9734 | 0 | 209.5 | 10 | 15 | -103 | 7638.27
2009-10-12 02:26 | 60.013 | 3671.2881 | 350 | -164.9734 | 0 | 210 | 10 | 15 | -103 | 7638.6
2009-10-12 02:26 | 60.014 | 3672.989 | 350 | -164.9734 | 0 | 210.5 | 10 | 15 | -103 | 7638.93
2009-10-12 02:26 | 60.017 | 3672.9817 | 350 | -164.9734 | 0 | 211 | 10 | 15 | -103 | 7639.26
2009-10-12 02:26 | 60.017 | 3672.9153 | 350 | -157.6281 | 0 | 211.5 | 10 | 15 | -103 | 7639.59
2009-10-12 02:26 | 60.019 | 3671.9517 | 350 | -157.6281 | 0 | 212 | 10 | 15 | -103 | 7639.92
2009-10-12 02:26 | 60.019 | 3671.1931 | 350 | -157.6281 | 0 | 212.5 | 10 | 15 | -103 | 7640.25
2009-10-12 02:26 | 60.019 | 3671.6272 | 350 | -157.6281 | 0 | 213 | 10 | 15 | -103 | 7640.58
2009-10-12 02:26 | 60.027 | 3671.189 | 350 | -157.6281 | 0 | 213.5 | 10 | 15 | -103 | 7640.91
2009-10-12 02:26 | 60.026 | 3668.6106 | 350 | -155.5317 | 0 | 214 | 10 | 15 | -103 | 7641.24
2009-10-12 02:26 | 60.026 | 3665.2322 | 350 | -155.5317 | 0 | 214.5 | 10 | 15 | -103 | 7641.57
2009-10-12 02:26 | 60.022 | 3664.4951 | 350 | -155.5317 | 0 | 215 | 10 | 15 | -103 | 7641.9
2009-10-12 02:26 | 60.019 | 3666.0618 | 350 | -155.5317 | 0 | 215.5 | 10 | 15 | -103 | 7642.23
2009-10-12 02:26 | 60.017 | 3666.8208 | 350 | -155.5317 | 0 | 216 | 10 | 15 | -103 | 7642.56
2009-10-12 02:26 | 60.019 | 3666.7874 | 350 | -160.4472 | 0 | 216.5 | 10 | 15 | -103 | 7642.89
2009-10-12 02:26 | 60.02 | 3670.4536 | 350 | -160.4472 | 0 | 217 | 10 | 15 | -103 | 7643.22
2009-10-12 02:26 | 60.019 | 3670.2668 | 350 | -160.4472 | 0 | 217.5 | 10 | 15 | -103 | 7643.55
2009-10-12 02:27 | 60.021 | 3671.668 | 350 | -160.4472 | 0 | 218 | 10 | 15 | -103 | 7643.88
2009-10-12 02:27 | 60.021 | 3672.4932 | 350 | -160.4472 | 0 | 218.5 | 10 | 15 | -103 | 7644.21
2009-10-12 02:27 | 60.021 | 3672.6851 | 350 | -163.9586 | 0 | 219 | 10 | 15 | -103 | 7644.54
2009-10-12 02:27 | 60.019 | 3672.8574 | 350 | -163.9586 | 0 | 219.5 | 10 | 15 | -103 | 7644.87
2009-10-12 02:27 | 60.018 | 3672.1641 | 350 | -163.9586 | 0 | 220 | 10 | 15 | -103 | 7645.2
2009-10-12 02:27 | 60.022 | 3671.4131 | 350 | -163.9586 | 0 | 220.5 | 10 | 15 | -103 | 7645.53
2009-10-12 02:27 | 60.031 | 3669.9829 | 350 | -163.9586 | 0 | 221 | 10 | 15 | -103 | 7645.86
2009-10-12 02:27 | 60.037 | 3666.4673 | 350 | -166.0724 | 0 | 221.5 | 10 | 15 | -103 | 7646.19
2009-10-12 02:27 | 60.037 | 3663.7581 | 350 | -166.0724 | 0 | 222 | 10 | 15 | -103 | 7646.52
2009-10-12 02:27 | 60.036 | 3661.5991 | 350 | -166.0724 | 0 | 222.5 | 10 | 15 | -103 | 7646.85
2009-10-12 02:27 | 60.037 | 3660.6724 | 350 | -166.0724 | 0 | 223 | 10 | 15 | -103 | 7647.18
2009-10-12 02:27 | 60.046 | 3651.4917 | 350 | -166.0724 | 0 | 223.5 | 10 | 15 | -103 | 7647.51
2009-10-12 02:27 | 60.048 | 3649.1904 | 350 | -163.7666 | 0 | 224 | 10 | 15 | -103 | 7647.84
2009-10-12 02:27 | 60.048 | 3650.0251 | 350 | -163.7666 | 0 | 224.5 | 10 | 15 | -103 | 7648.17
2009-10-12 02:27 | 60.043 | 3648.2463 | 350 | -163.7666 | 0 | 225 | 10 | 15 | -103 | 7648.5
2009-10-12 02:27 | 60.041 | 3649.512 | 350 | -163.7666 | 0 | 225.5 | 10 | 15 | -103 | 7648.83
2009-10-12 02:27 | 60.041 | 3654.2944 | 350 | -163.7666 | 0 | 226 | 10 | 15 | -103 | 7649.16
2009-10-12 02:27 | 60.041 | 3655.0068 | 350 | -165.1017 | 0 | 226.5 | 10 | 15 | -103 | 7649.49
2009-10-12 02:27 | 60.039 | 3651.8743 | 350 | -165.1017 | 0 | 227 | 10 | 15 | -103 | 7649.82
2009-10-12 02:27 | 60.041 | 3651.0593 | 350 | -165.1017 | 0 | 227.5 | 10 | 15 | -103 | 7650.15
2009-10-12 02:27 | 60.043 | 3649.187 | 350 | -165.1017 | 0 | 228 | 10 | 15 | -103 | 7650.48
2009-10-12 02:27 | 60.045 | 3648.2363 | 350 | -165.1017 | 0 | 228.5 | 10 | 15 | -103 | 7650.81
2009-10-12 02:27 | 60.046 | 3645.387 | 350 | -165.4764 | 0 | 229 | 10 | 15 | -103 | 7651.14
2009-10-12 02:27 | 60.041 | 3644.6277 | 350 | -165.4764 | 0 | 229.5 | 10 | 15 | -103 | 7651.47
2009-10-12 02:27 | 60.041 | 3645.4458 | 350 | -165.4764 | 0 | 230 | 10 | 15 | -103 | 7651.8
2009-10-12 02:27 | 60.041 | 3640.6821 | 350 | -165.4764 | 0 | 230.5 | 10 | 15 | -103 | 7652.13
2009-10-12 02:27 | 60.039 | 3641.1912 | 350 | -165.4764 | 0 | 231 | 10 | 15 | -103 | 7652.46
2009-10-12 02:27 | 59.978 | 3659.4648 | 350 | -206.4591 | 0 | 231.5 | 10 | 15 | -103 | 7652.79
2009-10-12 02:27 | 59.852 | 3696.3623 | 350 | -206.4591 | 0 | 232 | 10 | 0 | -103 | 7616
2009-10-12 02:28 | 59.836 | 3734.9043 | 335 | -206.4591 | 0 | 232.5 | 10 | 0 | -103 | 7626
2009-10-12 02:28 | 59.869 | 3734.6726 | 335 | -206.4591 | 0 | 233 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.892 | 3737.1567 | 335 | -206.4591 | 0 | 233.5 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.891 | 3761.2495 | 335 | -211.256 | 0 | 234 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.88 | 3766.113 | 335 | -211.256 | 1 | 234.5 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.876 | 3766.1938 | 335 | -211.256 | 1 | 235 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.875 | 3768.877 | 335 | -211.256 | 1 | 235.5 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.883 | 3769.925 | 335 | -211.256 | 1 | 236 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.887 | 3780.6206 | 335 | -214.3467 | 1 | 236.5 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.886 | 3781.5918 | 335 | -214.3467 | 1 | 237 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.885 | 3782.4995 | 335 | -214.3467 | 1 | 237.5 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.887 | 3784.9619 | 335 | -214.3467 | 2 | 238 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.888 | 3784.7297 | 335 | -214.3467 | 3 | 238.5 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.89 | 3784.4189 | 335 | -212.1727 | 4 | 239 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.895 | 3788.0723 | 335 | -212.1727 | 5 | 239.5 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.894 | 3788.3276 | 335 | -212.1727 | 6 | 240 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.893 | 3788.8684 | 335 | -212.1727 | 7 | 240.5 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.894 | 3788.4719 | 335 | -212.1727 | 8 | 241 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.894 | 3792.2756 | 335 | -215.5982 | 9 | 241.5 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.891 | 3793.0745 | 335 | -215.5982 | 10 | 242 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.89 | 3794.3743 | 335 | -215.5982 | 11 | 242.5 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.885 | 3799.4277 | 335 | -215.5982 | 12 | 243 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.885 | 3800.4275 | 335 | -215.5982 | 13 | 243.5 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.888 | 3799.9592 | 335 | -218.3273 | 14 | 244 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.887 | 3803.625 | 335 | -218.3273 | 15 | 244.5 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.888 | 3802.925 | 335 | -218.3273 | 16 | 245 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.888 | 3802.9509 | 335 | -218.3273 | 16 | 245.5 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.89 | 3804.3879 | 335 | -218.3273 | 16 | 246 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.889 | 3805.4961 | 335 | -217.3794 | 16 | 246.5 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.882 | 3805.6167 | 335 | -217.3794 | 16 | 247 | 10 | 0 | -103 | 7632
2009-10-12 02:28 | 59.873 | 3809.2373 | 335 | -217.3794 | 16 | 247.5 | 10 | 0 | -103 | 7631
2009-10-12 02:29 | 59.857 | 3811.5029 | 335 | -217.3794 | 16 | 248 | 10 | 0 | -103 | 7625
2009-10-12 02:29 | 59.849 | 3814.8623 | 335 | -217.3794 | 16 | 248.5 | 10 | 0 | -103 | 7623
2009-10-12 02:29 | 59.852 | 3815.8889 | 335 | -214.8304 | 16 | 249 | 10 | 0 | -103 | 7621
2009-10-12 02:29 | 59.858 | 3825.6426 | 335 | -214.8304 | 16 | 249.5 | 10 | 0 | -103 | 7623
2009-10-12 02:29 | 59.863 | 3826.0532 | 335 | -214.8304 | 16 | 250 | 10 | 0 | -103 | 7625
2009-10-12 02:29 | 59.866 | 3826.0024 | 335 | -214.8304 | 16 | 250.5 | 10 | 0 | -103 | 7627
2009-10-12 02:29 | 59.865 | 3827.5239 | 335 | -214.8304 | 16 | 251 | 10 | 0 | -103 | 7628
2009-10-12 02:29 | 59.867 | 3826.7532 | 335 | -227.6559 | 16 | 251.5 | 10 | 0 | -103 | 7628
2009-10-12 02:29 | 59.866 | 3826.7834 | 335 | -227.6559 | 16 | 252 | 10 | 0 | -103 | 7629
2009-10-12 02:29 | 59.871 | 3826.4536 | 335 | -227.6559 | 16 | 252.5 | 10 | 0 | -103 | 7630
2009-10-12 02:29 | 59.874 | 3825.7134 | 335 | -227.6559 | 16 | 253 | 10 | 0 | -103 | 7631
2009-10-12 02:29 | 59.879 | 3823.8257 | 335 | -227.6559 | 16 | 253.5 | 10 | 0 | -103 | 7635
2009-10-12 02:29 | 59.88 | 3822.5054 | 335 | -225.0181 | 16 | 254 | 10 | 0 | -103 | 7638
2009-10-12 02:29 | 59.883 | 3819.0811 | 335 | -225.0181 | 16 | 254.5 | 10 | 0 | -103 | 7639
2009-10-12 02:29 | 59.886 | 3818.0552 | 335 | -225.0181 | 16 | 255 | 10 | 0 | -103 | 7642
2009-10-12 02:29 | 59.89 | 3816.8147 | 335 | -225.0181 | 16 | 255.5 | 10 | 0 | -103 | 7644
2009-10-12 02:29 | 59.892 | 3815.0098 | 335 | -225.0181 | 16 | 256 | 10 | 0 | -103 | 7645
2009-10-12 02:29 | 59.889 | 3813.7827 | 335 | -228.3652 | 16 | 256.5 | 10 | 0 | -103 | 7647
2009-10-12 02:29 | 59.893 | 3811.8384 | 335 | -228.3652 | 16 | 257 | 10 | 0 | -103 | 7648
2009-10-12 02:29 | 59.899 | 3809.6519 | 335 | -228.3652 | 16 | 257.5 | 10 | 0 | -103 | 7649
2009-10-12 02:29 | 59.903 | 3806.9722 | 335 | -228.3652 | 16 | 258 | 10 | 0 | -103 | 7650
2009-10-12 02:29 | 59.902 | 3805.5933 | 335 | -228.3652 | 16 | 258.5 | 10 | 0 | -103 | 7651
2009-10-12 02:29 | 59.902 | 3804.1885 | 335 | -234.0753 | 16 | 259 | 10 | 0 | -103 | 7652
2009-10-12 02:29 | 59.904 | 3796.0776 | 335 | -234.0753 | 16 | 259.5 | 10 | 0 | -103 | 7653
2009-10-12 02:29 | 59.907 | 3793.9751 | 335 | -234.0753 | 16 | 260 | 10 | 0 | -103 | 7654
2009-10-12 02:29 | 59.911 | 3792.1694 | 335 | -234.0753 | 16 | 260.5 | 10 | 0 | -103 | 7655
2009-10-12 02:29 | 59.916 | 3791.502 | 335 | -234.0753 | 16 | 261 | 10 | 0 | -103 | 7655
2009-10-12 02:29 | 59.916 | 3789.5337 | 335 | -228.7982 | 16 | 261.5 | 10 | 0 | -103 | 7656
2009-10-12 02:29 | 59.917 | 3788.1321 | 335 | -228.7982 | 16 | 262 | 10 | 0 | -103 | 7656
2009-10-12 02:29 | 59.918 | 3784.5635 | 335 | -228.7982 | 16 | 262.5 | 10 | 0 | -103 | 7657
2009-10-12 02:30 | 59.92 | 3783.0283 | 335 | -228.7982 | 16 | 263 | 10 | 0 | -103 | 7657
2009-10-12 02:30 | 59.921 | 3781.7012 | 335 | -228.7982 | 16 | 263.5 | 10 | 0 | -103 | 7658
2009-10-12 02:30 | 59.92 | 3776.3584 | 335 | -229.467 | 16 | 264 | 10 | 0 | -103 | 7658
2009-10-12 02:30 | 59.917 | 3775.6355 | 335 | -229.467 | 16 | 264.5 | 10 | 0 | -103 | 7659
2009-10-12 02:30 | 59.92 | 3774.6042 | 335 | -229.467 | 16 | 265 | 10 | 0 | -103 | 7659
2009-10-12 02:30 | 59.921 | 3773.3337 | 335 | -229.467 | 16 | 265.5 | 10 | 0 | -103 | 7659
2009-10-12 02:30 | 59.923 | 3773.9578 | 335 | -229.467 | 16 | 266 | 10 | 0 | -103 | 7660
2009-10-12 02:30 | 59.926 | 3772.7224 | 335 | -228.9802 | 16 | 266.5 | 10 | 0 | -103 | 7660
2009-10-12 02:30 | 59.925 | 3771.6704 | 335 | -228.9802 | 16 | 267 | 10 | 0 | -103 | 7661
2009-10-12 02:30 | 59.928 | 3769.6296 | 335 | -228.9802 | 16 | 267.5 | 10 | 0 | -103 | 7661
2009-10-12 02:30 | 59.927 | 3768.707 | 335 | -228.9802 | 16 | 268 | 10 | 0 | -103 | 7662
2009-10-12 02:30 | 59.932 | 3767.6428 | 335 | -228.9802 | 16 | 268.5 | 10 | 0 | -103 | 7662
2009-10-12 02:30 | 59.927 | 3767.021 | 335 | -219.9756 | 16 | 269 | 10 | 0 | -103 | 7663
2009-10-12 02:30 | 59.928 | 3767.408 | 335 | -219.9756 | 16 | 269.5 | 10 | 0 | -103 | 7663
2009-10-12 02:30 | 59.931 | 3766.7881 | 335 | -219.9756 | 16 | 270 | 10 | 0 | -103 | 7664
2009-10-12 02:30 | 59.929 | 3766.259 | 335 | -219.9756 | 16 | 270.5 | 10 | 0 | -103 | 7664
2009-10-12 02:30 | 59.931 | 3765.6716 | 335 | -219.9756 | 16 | 271 | 10 | 0 | -103 | 7665
2009-10-12 02:30 | 59.933 | 3766.1226 | 335 | -229.0892 | 16 | 271.5 | 10 | 0 | -103 | 7666
2009-10-12 02:30 | 59.937 | 3764.2427 | 335 | -229.0892 | 16 | 272 | 10 | 0 | -103 | 7666
2009-10-12 02:30 | 59.937 | 3765.105 | 335 | -229.0892 | 16 | 272.5 | 10 | 0 | -103 | 7667
2009-10-12 02:30 | 59.945 | 3762.9353 | 335 | -229.0892 | 16 | 273 | 10 | 0 | -103 | 7668
2009-10-12 02:30 | 59.949 | 3758.3872 | 335 | -229.0892 | 16 | 273.5 | 10 | 0 | -103 | 7668
2009-10-12 02:30 | 59.947 | 3753.9224 | 335 | -229.6633 | 16 | 274 | 10 | 0 | -103 | 7669
2009-10-12 02:30 | 59.942 | 3749.8672 | 335 | -229.6633 | 16 | 274.5 | 10 | 0 | -103 | 7669
2009-10-12 02:30 | 59.941 | 3746.8887 | 335 | -229.6633 | 16 | 275 | 10 | 0 | -103 | 7670
2009-10-12 02:30 | 59.942 | 3747.8755 | 335 | -229.6633 | 16 | 275.5 | 10 | 0 | -103 | 7670
2009-10-12 02:30 | 59.945 | 3749.5933 | 335 | -229.6633 | 16 | 276 | 10 | 0 | -103 | 7671
2009-10-12 02:30 | 59.948 | 3748.6611 | 335 | -229.2339 | 16 | 276.5 | 10 | 0 | -103 | 7671
2009-10-12 02:30 | 59.947 | 3746.7061 | 335 | -229.2339 | 16 | 277 | 10 | 0 | -103 | 7672
2009-10-12 02:30 | 59.949 | 3749.0769 | 335 | -229.2339 | 16 | 277.5 | 10 | 0 | -103 | 7673
2009-10-12 02:31 | 59.951 | 3742.7415 | 335 | -229.2339 | 16 | 278 | 10 | 0 | -103 | 7673
2009-10-12 02:31 | 59.952 | 3740.259 | 350 | -229.2339 | 16 | 278.5 | 10 | 0 | -103 | 7673
2009-10-12 02:31 | 59.953 | 3736.1392 | 350 | -231.4099 | 16 | 279 | 10 | 0 | -103 | 7673
2009-10-12 02:31 | 59.951 | 3731.3821 | 350 | -231.4099 | 16 | 279.5 | 10 | 0 | -103 | 7673
2009-10-12 02:31 | 59.952 | 3727.8384 | 350 | -231.4099 | 16 | 280 | 10 | 0 | -103 | 7673
2009-10-12 02:31 | 59.952 | 3725.9517 | 350 | -231.4099 | 16 | 280.5 | 10 | 0 | -103 | 7673
2009-10-12 02:31 | 59.952 | 3722.6489 | 350 | -231.4099 | 16 | 281 | 10 | 0 | -103 | 7673
2009-10-12 02:31 | 59.955 | 3720.5781 | 350 | -218.6223 | 16 | 281.5 | 10 | 0 | -103 | 7673
2009-10-12 02:31 | 59.952 | 3717.9961 | 350 | -218.6223 | 16 | 282 | 10 | 0 | -103 | 7673
2009-10-12 02:31 | 59.954 | 3718.1418 | 350 | -218.6223 | 16 | 282.5 | 10 | 0 | -103 | 7673
2009-10-12 02:31 | 59.952 | 3715.7527 | 350 | -218.6223 | 16 | 283 | 10 | 0 | -103 | 7673
2009-10-12 02:31 | 59.953 | 3713.6938 | 350 | -218.6223 | 16 | 283.5 | 10 | 0 | -103 | 7673
2009-10-12 02:31 | 59.953 | 3713.4836 | 350 | -213.5359 | 16 | 284 | 10 | 0 | -103 | 7673
2009-10-12 02:31 | 59.952 | 3710.8481 | 350 | -213.5359 | 16 | 284.5 | 10 | 0 | -103 | 7673
2009-10-12 02:31 | 59.954 | 3710.8101 | 350 | -213.5359 | 16 | 285 | 10 | 0 | -103 | 7673
2009-10-12 02:31 | 59.954 | 3712.0918 | 350 | -213.5359 | 16 | 285.5 | 10 | 0 | -103 | 7674
2009-10-12 02:31 | 59.959 | 3714.6226 | 350 | -213.5359 | 16 | 286 | 10 | 0 | -103 | 7675
2009-10-12 02:31 | 59.957 | 3715.1296 | 350 | -225.6519 | 16 | 286.5 | 10 | 0 | -103 | 7676
2009-10-12 02:31 | 59.956 | 3716.1682 | 350 | -225.6519 | 16 | 287 | 10 | 0 | -103 | 7677
2009-10-12 02:31 | 59.954 | 3716.4614 | 350 | -225.6519 | 16 | 287.5 | 10 | 0 | -103 | 7678
2009-10-12 02:31 | 59.956 | 3716.98 | 350 | -225.6519 | 16 | 288 | 10 | 0 | -103 | 7679
2009-10-12 02:31 | 59.955 | 3717.759 | 350 | -225.6519 | 16 | 288.5 | 10 | 0 | -103 | 7680
2009-10-12 02:31 | 59.958 | 3722.3613 | 350 | -212.5736 | 16 | 289 | 10 | 0 | -103 | 7681
2009-10-12 02:31 | 59.961 | 3721.9731 | 350 | -212.5736 | 16 | 289.5 | 10 | 0 | -103 | 7682
2009-10-12 02:31 | 59.962 | 3722.658 | 350 | -212.5736 | 16 | 290 | 10 | 0 | -103 | 7684
2009-10-12 02:31 | 59.962 | 3722.2666 | 350 | -212.5736 | 16 | 290.5 | 10 | 0 | -103 | 7685
2009-10-12 02:31 | 59.968 | 3722.2776 | 350 | -212.5736 | 16 | 291 | 10 | 0 | -103 | 7687
2009-10-12 02:31 | 59.966 | 3721.7866 | 350 | -219.8973 | 16 | 291.5 | 10 | 0 | -103 | 7689
2009-10-12 02:31 | 59.966 | 3723.0908 | 350 | -219.8973 | 16 | 292 | 10 | 0 | -103 | 7690
2009-10-12 02:32 | 59.968 | 3723.9839 | 350 | -219.8973 | 16 | 292.5 | 10 | 0 | -103 | 7692
2009-10-12 02:32 | 59.97 | 3723.4346 | 350 | -219.8973 | 16 | 293 | 10 | 0 | -103 | 7692
2009-10-12 02:32 | 59.974 | 3723.8931 | 350 | -219.8973 | 16 | 293.5 | 10 | 0 | -103 | 7693
2009-10-12 02:32 | 59.97 | 3725.4028 | 350 | -231.1754 | 16 | 294 | 10 | 0 | -103 | 7693
2009-10-12 02:32 | 59.969 | 3727.1211 | 350 | -231.1754 | 16 | 294.5 | 10 | 0 | -103 | 7694
2009-10-12 02:32 | 59.969 | 3728.053 | 350 | -231.1754 | 16 | 295 | 10 | 0 | -103 | 7694
2009-10-12 02:32 | 59.97 | 3731.1299 | 350 | -231.1754 | 16 | 295.5 | 10 | 0 | -103 | 7695
2009-10-12 02:32 | 59.971 | 3732.53 | 350 | -231.1754 | 16 | 296 | 10 | 0 | -103 | 7695
2009-10-12 02:32 | 59.973 | 3733.3271 | 350 | -226.6341 | 16 | 296.5 | 10 | 0 | -103 | 7695
2009-10-12 02:32 | 59.973 | 3736.5352 | 350 | -226.6341 | 16 | 297 | 10 | 0 | -103 | 7696
2009-10-12 02:32 | 59.976 | 3736.9075 | 350 | -226.6341 | 16 | 297.5 | 10 | 0 | -103 | 7696
2009-10-12 02:32 | 59.978 | 3736.8218 | 350 | -226.6341 | 16 | 298 | 10 | 0 | -103 | 7697
2009-10-12 02:32 | 59.978 | 3738.6992 | 350 | -226.6341 | 16 | 298.5 | 10 | 0 | -103 | 7697
2009-10-12 02:32 | 59.976 | 3739.9438 | 350 | -227.2551 | 16 | 299 | 10 | 0 | -103 | 7697
2009-10-12 02:32 | 59.978 | 3740.877 | 350 | -227.2551 | 16 | 299.5 | 10 | 0 | -103 | 7698
2009-10-12 02:32 | 59.976 | 3741.7937 | 350 | -227.2551 | 16 | 300 | 10 | 0 | -103 | 7698
2009-10-12 02:32 | 59.978 | 3745.2336 | 350 | -227.2551 | 16 | 300.5 | 10 | 0 | -103 | 7698.33
2009-10-12 02:32 | 59.977 | 3746.6079 | 350 | -227.2551 | 16 | 301 | 10 | 0 | -103 | 7698.66
2009-10-12 02:32 | 59.98 | 3748.2998 | 350 | -229.2902 | 16 | 301.5 | 10 | 0 | -103 | 7698.99
2009-10-12 02:32 | 59.982 | 3750.7163 | 350 | -229.2902 | 16 | 302 | 10 | 0 | -103 | 7699.32
2009-10-12 02:32 | 59.981 | 3751.5576 | 350 | -229.2902 | 16 | 302.5 | 10 | 0 | -103 | 7699.65
2009-10-12 02:32 | 59.98 | 3752.7476 | 350 | -229.2902 | 16 | 303 | 10 | 0 | -103 | 7699.98
2009-10-12 02:32 | 59.979 | 3755.5986 | 350 | -229.2902 | 16 | 303.5 | 10 | 0 | -103 | 7700.31
2009-10-12 02:32 | 59.98 | 3756.4072 | 350 | -221.4614 | 16 | 304 | 10 | 0 | -103 | 7700.64
2009-10-12 02:32 | 59.979 | 3756.9753 | 350 | -221.4614 | 16 | 304.5 | 10 | 0 | -103 | 7700.97
2009-10-12 02:32 | 59.983 | 3760.4053 | 350 | -221.4614 | 16 | 305 | 10 | 0 | -103 | 7701.3
2009-10-12 02:32 | 59.983 | 3760.9822 | 350 | -221.4614 | 16 | 305.5 | 10 | 0 | -103 | 7701.63
2009-10-12 02:32 | 59.984 | 3761.407 | 350 | -221.4614 | 16 | 306 | 10 | 0 | -103 | 7701.96
2009-10-12 02:32 | 59.988 | 3762.7373 | 350 | -241.2744 | 16 | 306.5 | 10 | 0 | -103 | 7702.29
2009-10-12 02:32 | 59.989 | 3763.2122 | 350 | -241.2744 | 16 | 307 | 10 | 0 | -103 | 7702.62
2009-10-12 02:33 | 59.987 | 3764.9575 | 350 | -241.2744 | 16 | 307.5 | 10 | 0 | -103 | 7702.95
2009-10-12 02:33 | 59.987 | 3766.0852 | 350 | -241.2744 | 16 | 308 | 10 | 0 | -103 | 7703.28
2009-10-12 02:33 | 59.991 | 3766.4331 | 350 | -241.2744 | 16 | 308.5 | 10 | 0 | -103 | 7703.61
2009-10-12 02:33 | 59.993 | 3767.251 | 350 | -243.0719 | 16 | 309 | 10 | 0 | -103 | 7703.94
2009-10-12 02:33 | 59.992 | 3767.7925 | 350 | -243.0719 | 16 | 309.5 | 10 | 0 | -103 | 7704.27
2009-10-12 02:33 | 59.991 | 3768.6335 | 350 | -243.0719 | 16 | 310 | 10 | 0 | -103 | 7704.6
2009-10-12 02:33 | 59.989 | 3771.1465 | 350 | -243.0719 | 16 | 310.5 | 10 | 0 | -103 | 7704.93
2009-10-12 02:33 | 59.986 | 3772.4446 | 350 | -243.0719 | 16 | 311 | 10 | 0 | -103 | 7705.26
2009-10-12 02:33 | 59.983 | 3773.6948 | 350 | -241.6702 | 16 | 311.5 | 10 | 0 | -103 | 7705.59
2009-10-12 02:33 | 59.983 | 3774.6685 | 350 | -241.6702 | 16 | 312 | 10 | 0 | -103 | 7705.92
2009-10-12 02:33 | 59.988 | 3775.8408 | 350 | -241.6702 | 16 | 312.5 | 10 | 0 | -103 | 7706.25
2009-10-12 02:33 | 59.993 | 3775.3633 | 350 | -241.6702 | 16 | 313 | 10 | 0 | -103 | 7706.58
2009-10-12 02:33 | 59.996 | 3774.8662 | 350 | -241.6702 | 16 | 313.5 | 10 | 0 | -103 | 7706.91
2009-10-12 02:33 | 59.998 | 3775.4917 | 350 | -228.1493 | 16 | 314 | 10 | 0 | -103 | 7707.24
2009-10-12 02:33 | 59.999 | 3776.4202 | 350 | -228.1493 | 16 | 314.5 | 10 | 0 | -103 | 7707.57
2009-10-12 02:33 | 60.001 | 3778.5537 | 350 | -228.1493 | 16 | 315 | 10 | 0 | -103 | 7707.9
2009-10-12 02:33 | 59.999 | 3779.6919 | 350 | -228.1493 | 16 | 315.5 | 10 | 0 | -103 | 7708.23
2009-10-12 02:33 | 59.999 | 3781.2559 | 350 | -228.1493 | 16 | 316 | 10 | 0 | -103 | 7708.56
2009-10-12 02:33 | 59.999 | 3780.595 | 350 | -235.129 | 16 | 316.5 | 10 | 0 | -103 | 7708.89
2009-10-12 02:33 | 60.002 | 3783.092 | 350 | -235.129 | 16 | 317 | 10 | 0 | -103 | 7709.22
2009-10-12 02:33 | 60.005 | 3783.8955 | 350 | -235.129 | 16 | 317.5 | 10 | 0 | -103 | 7709.55
2009-10-12 02:33 | 60.007 | 3784.4209 | 350 | -235.129 | 16 | 318 | 10 | 0 | -103 | 7709.88
2009-10-12 02:33 | 60.008 | 3785.7681 | 350 | -235.129 | 16 | 318.5 | 10 | 0 | -103 | 7710.21
2009-10-12 02:33 | 60.011 | 3785.4626 | 350 | -246.4331 | 16 | 319 | 10 | 0 | -103 | 7710.54
2009-10-12 02:33 | 60.014 | 3786.8503 | 350 | -246.4331 | 16 | 319.5 | 10 | 0 | -103 | 7710.87
2009-10-12 02:33 | 60.017 | 3786.3042 | 350 | -246.4331 | 16 | 320 | 10 | 0 | -103 | 7711.2
2009-10-12 02:33 | 60.019 | 3787.2593 | 350 | -246.4331 | 16 | 320.5 | 10 | 0 | -103 | 7711.53
2009-10-12 02:33 | 60.021 | 3787.5159 | 350 | -246.4331 | 16 | 321 | 10 | 0 | -103 | 7711.86
2009-10-12 02:33 | 60.017 | 3787.9551 | 350 | -236.5535 | 16 | 321.5 | 10 | 0 | -103 | 7712.19
2009-10-12 02:33 | 60.017 | 3788.0303 | 350 | -236.5535 | 16 | 322 | 10 | 0 | -103 | 7712.52
2009-10-12 02:34 | 60.019 | 3788.6067 | 350 | -236.5535 | 16 | 322.5 | 10 | 0 | -103 | 7712.85
2009-10-12 02:34 | 60.023 | 3789.2158 | 350 | -236.5535 | 16 | 323 | 10 | 0 | -103 | 7713.18
2009-10-12 02:34 | 60.024 | 3787.5366 | 350 | -236.5535 | 16 | 323.5 | 10 | 0 | -103 | 7713.51
2009-10-12 02:34 | 60.025 | 3785.8418 | 350 | -230.2976 | 16 | 324 | 10 | 0 | -103 | 7713.84
2009-10-12 02:34 | 60.021 | 3786.0767 | 350 | -230.2976 | 16 | 324.5 | 10 | 0 | -103 | 7714.17
2009-10-12 02:34 | 60.019 | 3787.9304 | 350 | -230.2976 | 16 | 325 | 10 | 0 | -103 | 7714.5
2009-10-12 02:34 | 60.024 | 3788.7603 | 350 | -230.2976 | 16 | 325.5 | 10 | 0 | -103 | 7714.83
2009-10-12 02:34 | 60.024 | 3786.8748 | 350 | -230.2976 | 16 | 326 | 10 | 0 | -103 | 7715.16
2009-10-12 02:34 | 60.021 | 3786.5498 | 350 | -231.1755 | 16 | 326.5 | 10 | 0 | -103 | 7715.49
2009-10-12 02:34 | 60.02 | 3787.3577 | 350 | -231.1755 | 16 | 327 | 10 | 0 | -103 | 7715.82
2009-10-12 02:34 | 60.025 | 3785.0181 | 350 | -231.1755 | 16 | 327.5 | 10 | 0 | -103 | 7716.15
2009-10-12 02:34 | 60.024 | 3785.614 | 350 | -231.1755 | 16 | 328 | 10 | 0 | -103 | 7716.48
2009-10-12 02:34 | 60.02 | 3785.9492 | 350 | -231.1755 | 16 | 328.5 | 10 | 0 | -103 | 7716.81
2009-10-12 02:34 | 60.02 | 3785.8037 | 350 | -225.6176 | 16 | 329 | 10 | 0 | -103 | 7717.14
2009-10-12 02:34 | 60.022 | 3786.8643 | 350 | -225.6176 | 16 | 329.5 | 10 | 0 | -103 | 7717.47
2009-10-12 02:34 | 60.022 | 3786.8772 | 350 | -225.6176 | 16 | 330 | 10 | 0 | -103 | 7717.8
2009-10-12 02:34 | 60.022 | 3785.2539 | 350 | -225.6176 | 16 | 330.5 | 10 | 0 | -103 | 7718.13
2009-10-12 02:34 | 60.021 | 3785.7261 | 350 | -225.6176 | 16 | 331 | 10 | 0 | -103 | 7718.46
2009-10-12 02:34 | 60.021 | 3786.3469 | 350 | -230.7344 | 16 | 331.5 | 10 | 0 | -103 | 7718.79
2009-10-12 02:34 | 60.023 | 3785.821 | 350 | -230.7344 | 16 | 332 | 10 | 0 | -103 | 7719.12
2009-10-12 02:34 | 60.023 | 3785.7983 | 350 | -230.7344 | 16 | 332.5 | 10 | 0 | -103 | 7719.45
2009-10-12 02:34 | 60.022 | 3786.2842 | 350 | -230.7344 | 16 | 333 | 10 | 0 | -103 | 7719.78
2009-10-12 02:34 | 60.019 | 3786.9392 | 350 | -230.7344 | 16 | 333.5 | 10 | 0 | -103 | 7720.11
2009-10-12 02:34 | 60.016 | 3787.6274 | 350 | -234.8471 | 16 | 334 | 10 | 0 | -103 | 7720.44
2009-10-12 02:34 | 60.018 | 3789.4443 | 350 | -234.8471 | 16 | 334.5 | 10 | 0 | -103 | 7720.77
2009-10-12 02:34 | 60.018 | 3789.6733 | 350 | -234.8471 | 16 | 335 | 10 | 0 | -103 | 7721.1
2009-10-12 02:34 | 60.018 | 3789.4043 | 350 | -234.8471 | 16 | 335.5 | 10 | 0 | -103 | 7721.43
2009-10-12 02:34 | 60.019 | 3788.4788 | 350 | -234.8471 | 16 | 336 | 10 | 0 | -103 | 7721.76
2009-10-12 02:34 | 60.019 | 3789.1833 | 350 | -228.9609 | 16 | 336.5 | 10 | 0 | -103 | 7722.09
2009-10-12 02:34 | 60.016 | 3789.3689 | 350 | -228.9609 | 16 | 337 | 10 | 0 | -103 | 7722.42
2009-10-12 02:34 | 60.015 | 3789.0049 | 350 | -228.9609 | 16 | 337.5 | 10 | 0 | -103 | 7722.75
2009-10-12 02:35 | 60.016 | 3788.6646 | 350 | -228.9609 | 16 | 338 | 10 | 0 | -103 | 7723.08
2009-10-12 02:35 | 60.014 | 3788.9329 | 350 | -228.9609 | 16 | 338.5 | 10 | 0 | -103 | 7723.41
2009-10-12 02:35 | 60.013 | 3790.667 | 350 | -231.1779 | 16 | 339 | 10 | 0 | -103 | 7723.74
2009-10-12 02:35 | 60.012 | 3790.8052 | 350 | -231.1779 | 16 | 339.5 | 10 | 0 | -103 | 7724.07
2009-10-12 02:35 | 60.012 | 3790.4111 | 350 | -231.1779 | 16 | 340 | 10 | 0 | -103 | 7724.4
2009-10-12 02:35 | 60.01 | 3789.7686 | 350 | -231.1779 | 16 | 340.5 | 10 | 0 | -103 | 7724.73
2009-10-12 02:35 | 60.007 | 3791.5398 | 350 | -231.1779 | 16 | 341 | 10 | 0 | -103 | 7725.06
2009-10-12 02:35 | 60.007 | 3792.9453 | 350 | -236.4893 | 16 | 341.5 | 10 | 0 | -103 | 7725.39
2009-10-12 02:35 | 60.009 | 3791.0271 | 350 | -236.4893 | 16 | 342 | 10 | 0 | -103 | 7725.72
2009-10-12 02:35 | 60.009 | 3791.4431 | 350 | -236.4893 | 16 | 342.5 | 10 | 0 | -103 | 7726.05
2009-10-12 02:35 | 60.01 | 3791.426 | 350 | -236.4893 | 16 | 343 | 10 | 0 | -103 | 7726.38
2009-10-12 02:35 | 60.003 | 3790.603 | 350 | -236.4893 | 16 | 343.5 | 10 | 0 | -103 | 7726.71
2009-10-12 02:35 | 59.999 | 3790.4573 | 350 | -245.0389 | 16 | 344 | 10 | 0 | -103 | 7727.04
2009-10-12 02:35 | 59.995 | 3790.2163 | 350 | -245.0389 | 16 | 344.5 | 10 | 0 | -103 | 7727.37
2009-10-12 02:35 | 59.992 | 3789.585 | 350 | -245.0389 | 16 | 345 | 10 | 0 | -103 | 7727.7
2009-10-12 02:35 | 59.991 | 3788.457 | 350 | -245.0389 | 16 | 345.5 | 10 | 0 | -103 | 7728.03
2009-10-12 02:35 | 59.992 | 3788.105 | 350 | -245.0389 | 16 | 346 | 10 | 0 | -103 | 7728.36
2009-10-12 02:35 | 59.992 | 3788.0571 | 350 | -223.6057 | 16 | 346.5 | 10 | 0 | -103 | 7728.69
2009-10-12 02:35 | 59.988 | 3788.1895 | 350 | -223.6057 | 16 | 347 | 10 | 0 | -103 | 7729.02
2009-10-12 02:35 | 59.986 | 3788.4973 | 350 | -223.6057 | 16 | 347.5 | 10 | 0 | -103 | 7729.35
2009-10-12 02:35 | 59.985 | 3788.54 | 350 | -223.6057 | 16 | 348 | 10 | 0 | -103 | 7729.68
2009-10-12 02:35 | 59.984 | 3788.5708 | 350 | -223.6057 | 16 | 348.5 | 10 | 0 | -103 | 7730.01
2009-10-12 02:35 | 59.985 | 3788.1011 | 350 | -231.1194 | 16 | 349 | 10 | 0 | -103 | 7730.34
2009-10-12 02:35 | 59.984 | 3787.1333 | 350 | -231.1194 | 16 | 349.5 | 10 | 0 | -103 | 7730.67
2009-10-12 02:35 | 59.982 | 3786.4529 | 350 | -231.1194 | 16 | 350 | 10 | 0 | -103 | 7731
2009-10-12 02:35 | 59.981 | 3787.7324 | 350 | -231.1194 | 16 | 350.5 | 10 | 0 | -103 | 7731.33
2009-10-12 02:35 | 59.982 | 3788.8135 | 350 | -231.1194 | 16 | 351 | 10 | 0 | -103 | 7731.66
2009-10-12 02:35 | 59.979 | 3789.2852 | 350 | -237.2066 | 16 | 351.5 | 10 | 0 | -103 | 7731.99
2009-10-12 02:35 | 59.977 | 3788.2563 | 350 | -237.2066 | 16 | 352 | 10 | 0 | -103 | 7732.32
2009-10-12 02:36 | 59.976 | 3788.4097 | 350 | -237.2066 | 16 | 352.5 | 10 | 0 | -103 | 7732.65
2009-10-12 02:36 | 59.976 | 3790.4673 | 350 | -237.2066 | 16 | 353 | 10 | 0 | -103 | 7732.98
2009-10-12 02:36 | 59.979 | 3790.6646 | 350 | -237.2066 | 16 | 353.5 | 10 | 0 | -103 | 7733.31
2009-10-12 02:36 | 59.982 | 3790.4204 | 350 | -240.5164 | 16 | 354 | 10 | 0 | -103 | 7733.64
2009-10-12 02:36 | 59.978 | 3789.6738 | 350 | -240.5164 | 16 | 354.5 | 10 | 0 | -103 | 7733.97
2009-10-12 02:36 | 59.976 | 3789.2671 | 350 | -240.5164 | 16 | 355 | 10 | 0 | -103 | 7734.3
2009-10-12 02:36 | 59.974 | 3789.1479 | 350 | -240.5164 | 16 | 355.5 | 10 | 0 | -103 | 7734.63
2009-10-12 02:36 | 59.976 | 3790.4304 | 350 | -240.5164 | 16 | 356 | 10 | 0 | -103 | 7734.96
2009-10-12 02:36 | 59.977 | 3789.9143 | 350 | -237.5661 | 16 | 356.5 | 10 | 0 | -103 | 7735.29
2009-10-12 02:36 | 59.977 | 3786.2432 | 350 | -237.5661 | 16 | 357 | 10 | 0 | -103 | 7735.62
2009-10-12 02:36 | 59.975 | 3787.4421 | 350 | -237.5661 | 16 | 357.5 | 10 | 0 | -103 | 7735.95
2009-10-12 02:36 | 59.973 | 3788.9629 | 350 | -237.5661 | 16 | 358 | 10 | 0 | -103 | 7736.28
2009-10-12 02:36 | 59.969 | 3790.6016 | 350 | -237.5661 | 16 | 358.5 | 10 | 0 | -103 | 7736.61
2009-10-12 02:36 | 59.97 | 3791.877 | 350 | -231.5814 | 16 | 359 | 10 | 0 | -103 | 7736.94
2009-10-12 02:36 | 59.971 | 3792.9106 | 350 | -231.5814 | 16 | 359.5 | 10 | 0 | -103 | 7737.27
2009-10-12 02:36 | 59.973 | 3792.3113 | 350 | -231.5814 | 16 | 360 | 10 | 0 | -103 | 7737.6
2009-10-12 02:36 | 59.978 | 3789.125 | 350 | -231.5814 | 16 | 360.5 | 10 | 0 | -103 | 7737.93
2009-10-12 02:36 | 59.981 | 3788.0796 | 350 | -231.5814 | 16 | 361 | 10 | 0 | -103 | 7738.26
2009-10-12 02:36 | 59.978 | 3787.844 | 350 | -235.8508 | 16 | 361.5 | 10 | 0 | -103 | 7738.59
2009-10-12 02:36 | 59.975 | 3787.135 | 350 | -235.8508 | 16 | 362 | 10 | 0 | -103 | 7738.92
2009-10-12 02:36 | 59.972 | 3787.1643 | 350 | -235.8508 | 16 | 362.5 | 10 | 0 | -103 | 7739.25
2009-10-12 02:36 | 59.976 | 3786.9961 | 350 | -235.8508 | 16 | 363 | 10 | 0 | -103 | 7739.58
2009-10-12 02:36 | 59.975 | 3787.4048 | 350 | -235.8508 | 16 | 363.5 | 10 | 0 | -103 | 7739.91
2009-10-12 02:36 | 59.973 | 3786.4868 | 350 | -233.56 | 16 | 364 | 10 | 0 | -103 | 7740.24
2009-10-12 02:36 | 59.969 | 3787.0791 | 350 | -233.56 | 16 | 364.5 | 10 | 0 | -103 | 7740.57
2009-10-12 02:36 | 59.966 | 3789.2139 | 350 | -233.56 | 16 | 365 | 10 | 0 | -103 | 7740.9
2009-10-12 02:36 | 59.965 | 3790.5117 | 350 | -233.56 | 16 | 365.5 | 10 | 0 | -103 | 7741.23
2009-10-12 02:36 | 59.966 | 3791.2212 | 350 | -233.56 | 16 | 366 | 10 | 0 | -103 | 7741.56
2009-10-12 02:36 | 59.969 | 3792.2183 | 350 | -219.01 | 16 | 366.5 | 10 | 0 | -103 | 7741.89
2009-10-12 02:36 | 59.97 | 3790.9595 | 350 | -219.01 | 16 | 367 | 10 | 0 | -103 | 7742.22
2009-10-12 02:36 | 59.968 | 3788.8242 | 350 | -219.01 | 16 | 367.5 | 10 | 0 | -103 | 7742.55
2009-10-12 02:37 | 59.965 | 3789.0264 | 350 | -219.01 | 16 | 368 | 10 | 0 | -103 | 7742.88
2009-10-12 02:37 | 59.964 | 3789.1675 | 350 | -219.01 | 16 | 368.5 | 10 | 0 | -103 | 7743.21
2009-10-12 02:37 | 59.97 | 3787.394 | 350 | -205.3389 | 16 | 369 | 10 | 0 | -103 | 7743.54
2009-10-12 02:37 | 59.972 | 3785.6899 | 350 | -205.3389 | 16 | 369.5 | 10 | 0 | -103 | 7743.87
2009-10-12 02:37 | 59.967 | 3784.8306 | 350 | -205.3389 | 16 | 370 | 10 | 0 | -103 | 7744.2
2009-10-12 02:37 | 59.967 | 3785.0095 | 350 | -205.3389 | 16 | 370.5 | 10 | 0 | -103 | 7744.53
2009-10-12 02:37 | 59.969 | 3784.3203 | 350 | -205.3389 | 16 | 371 | 10 | 0 | -103 | 7744.86
2009-10-12 02:37 | 59.968 | 3782.8086 | 350 | -236.2854 | 16 | 371.5 | 10 | 0 | -103 | 7745.19
2009-10-12 02:37 | 59.969 | 3782.1099 | 350 | -236.2854 | 16 | 372 | 10 | 0 | -103 | 7745.52
2009-10-12 02:37 | 59.967 | 3779.3516 | 350 | -236.2854 | 16 | 372.5 | 10 | 0 | -103 | 7745.85
2009-10-12 02:37 | 59.967 | 3779.0562 | 350 | -236.2854 | 16 | 373 | 10 | 0 | -103 | 7746.18
2009-10-12 02:37 | 59.966 | 3778.6333 | 350 | -236.2854 | 16 | 373.5 | 10 | 0 | -103 | 7746.51
2009-10-12 02:37 | 59.965 | 3779.2117 | 350 | -223.0157 | 16 | 374 | 10 | 0 | -103 | 7746.84
2009-10-12 02:37 | 59.971 | 3779.3347 | 350 | -223.0157 | 16 | 374.5 | 10 | 0 | -103 | 7747.17
2009-10-12 02:37 | 59.967 | 3776.4292 | 350 | -223.0157 | 16 | 375 | 10 | 0 | -103 | 7747.5
2009-10-12 02:37 | 59.965 | 3775.6467 | 350 | -223.0157 | 16 | 375.5 | 10 | 0 | -103 | 7747.83
2009-10-12 02:37 | 59.962 | 3776.5967 | 350 | -223.0157 | 16 | 376 | 10 | 0 | -103 | 7748.16
2009-10-12 02:37 | 59.964 | 3776.5591 | 350 | -223.0157 | 16 | 376.5 | 10 | 0 | -103 | 7748.49
2009-10-12 02:37 | 59.97 | 3776.0229 | 350 | -223.0157 | 16 | 377 | 10 | 0 | -103 | 7748.82
2009-10-12 02:37 | 59.967 | 3773.1699 | 350 | -223.0157 | 16 | 377.5 | 10 | 0 | -103 | 7749.15
2009-10-12 02:37 | 59.969 | 3771.7305 | 350 | -223.0157 | 16 | 378 | 10 | 0 | -103 | 7749.48
2009-10-12 02:37 | 59.968 | 3768.793 | 350 | -223.0157 | 16 | 378.5 | 10 | 0 | -103 | 7749.81
2009-10-12 02:37 | 59.963 | 3768.5029 | 350 | -223.0157 | 16 | 379 | 10 | 0 | -103 | 7750.14
2009-10-12 02:37 | 59.965 | 3768.9175 | 350 | -223.0157 | 16 | 379.5 | 10 | 0 | -103 | 7750.47
2009-10-12 02:37 | 59.97 | 3767.3662 | 350 | -223.0157 | 16 | 380 | 10 | 0 | -103 | 7750.8
2009-10-12 02:37 | 59.973 | 3764.7861 | 350 | -223.0157 | 16 | 380.5 | 10 | 0 | -103 | 7751.13
2009-10-12 02:37 | 59.968 | 3760.2954 | 350 | -223.0157 | 16 | 381 | 10 | 0 | -103 | 7751.46
2009-10-12 02:37 | 59.965 | 3759.5918 | 350 | -223.0157 | 16 | 381.5 | 10 | 0 | -103 | 7751.79
2009-10-12 02:37 | 59.968 | 3761.8938 | 350 | -223.0157 | 16 | 382 | 10 | 0 | -103 | 7752.12
2009-10-12 02:38 | 59.969 | 3761.7766 | 350 | -223.0157 | 16 | 382.5 | 10 | 0 | -103 | 7752.45
2009-10-12 02:38 | 59.967 | 3760.5825 | 350 | -223.0157 | 16 | 383 | 10 | 0 | -103 | 7752.78
2009-10-12 02:38 | 59.964 | 3760.1575 | 350 | -223.0157 | 16 | 383.5 | 10 | 0 | -103 | 7753.11
2009-10-12 02:38 | 59.966 | 3759.781 | 350 | -223.0157 | 16 | 384 | 10 | 0 | -103 | 7753.44
2009-10-12 02:38 | 59.979 | 3759.4949 | 350 | -223.0157 | 16 | 384.5 | 10 | 0 | -103 | 7753.77
2009-10-12 02:38 | 59.99 | 3757.7729 | 350 | -223.0157 | 16 | 385 | 10 | 0 | -103 | 7754.1
2009-10-12 02:38 | 59.983 | 3753.2771 | 350 | -223.0157 | 16 | 385.5 | 10 | 0 | -103 | 7754.43
2009-10-12 02:38 | 59.974 | 3753.0874 | 350 | -223.0157 | 16 | 386 | 10 | 0 | -103 | 7754.76
2009-10-12 02:38 | 59.967 | 3751.6367 | 350 | -223.0157 | 16 | 386.5 | 10 | 0 | -103 | 7755.09
2009-10-12 02:38 | 59.965 | 3753.751 | 350 | -223.0157 | 16 | 387 | 10 | 0 | -103 | 7755.42
2009-10-12 02:38 | 59.962 | 3758.2246 | 350 | -223.0157 | 16 | 387.5 | 10 | 0 | -103 | 7755.75
2009-10-12 02:38 | 59.962 | 3759.2498 | 350 | -223.0157 | 16 | 388 | 10 | 0 | -103 | 7756.08
2009-10-12 02:38 | 59.961 | 3758.041 | 350 | -223.0157 | 16 | 388.5 | 10 | 0 | -103 | 7756.41
2009-10-12 02:38 | 59.961 | 3760.9648 | 350 | -223.0157 | 16 | 389 | 10 | 0 | -103 | 7756.74
2009-10-12 02:38 | 59.96 | 3762.0222 | 350 | -223.0157 | 16 | 389.5 | 10 | 0 | -103 | 7757.07
2009-10-12 02:38 | 59.963 | 3763.8223 | 350 | -223.0157 | 16 | 390 | 10 | 0 | -103 | 7757.4
2009-10-12 02:38 | 59.959 | 3763.1001 | 350 | -223.0157 | 16 | 390.5 | 10 | 0 | -103 | 7757.73
2009-10-12 02:38 | 59.956 | 3763.8582 | 350 | -223.0157 | 16 | 391 | 10 | 0 | -103 | 7758.06
2009-10-12 02:38 | 59.951 | 3764.1577 | 350 | -223.0157 | 16 | 391.5 | 10 | 0 | -103 | 7758.39
2009-10-12 02:38 | 59.953 | 3766.1267 | 350 | -223.0157 | 16 | 392 | 10 | 0 | -103 | 7758.72
2009-10-12 02:38 | 59.954 | 3768.3389 | 350 | -223.0157 | 16 | 392.5 | 10 | 0 | -103 | 7759.05
2009-10-12 02:38 | 59.957 | 3767.9722 | 350 | -223.0157 | 16 | 393 | 10 | 0 | -103 | 7759.38
2009-10-12 02:38 | 59.956 | 3767.4375 | 350 | -223.0157 | 16 | 393.5 | 10 | 0 | -103 | 7759.71
2009-10-12 02:38 | 59.961 | 3765.6064 | 350 | -223.0157 | 16 | 394 | 10 | 0 | -103 | 7760.04
2009-10-12 02:38 | 59.963 | 3762.688 | 350 | -223.0157 | 16 | 394.5 | 10 | 0 | -103 | 7760.37
2009-10-12 02:38 | 59.961 | 3761.5703 | 350 | -223.0157 | 16 | 395 | 10 | 0 | -103 | 7760.7
2009-10-12 02:38 | 59.959 | 3761.9199 | 350 | -223.0157 | 16 | 395.5 | 10 | 0 | -103 | 7761.03
2009-10-12 02:38 | 59.963 | 3759.627 | 350 | -223.0157 | 16 | 396 | 10 | 0 | -103 | 7761.36
2009-10-12 02:38 | 59.963 | 3758.522 | 350 | -223.0157 | 16 | 396.5 | 10 | 0 | -103 | 7761.69
2009-10-12 02:38 | 59.965 | 3752.4287 | 350 | -223.0157 | 16 | 397 | 10 | 0 | -103 | 7762.02
2009-10-12 02:38 | 59.968 | 3750.1016 | 350 | -223.0157 | 16 | 397.5 | 10 | 0 | -103 | 7762.35
2009-10-12 02:39 | 59.968 | 3753.8296 | 350 | -223.0157 | 16 | 398 | 10 | 0 | -103 | 7762.68
2009-10-12 02:39 | 59.968 | 3753.5103 | 350 | -223.0157 | 16 | 398.5 | 10 | 0 | -103 | 7763.01
2009-10-12 02:39 | 59.97 | 3753.5229 | 350 | -223.0157 | 16 | 399 | 10 | 0 | -103 | 7763.34
2009-10-12 02:39 | 59.973 | 3752.7407 | 350 | -223.0157 | 16 | 399.5 | 10 | 0 | -103 | 7763.67
2009-10-12 02:39 | 59.971 | 3753.1782 | 350 | -223.0157 | 16 | 400 | 10 | 0 | -103 | 7764
2009-10-12 02:39 | 59.965 | 3752.729 | 350 | -223.0157 | 16 | 400.5 | 10 | 0 | -103 | 7764.33
2009-10-12 02:39 | 59.967 | 3753.2905 | 350 | -223.0157 | 16 | 401 | 10 | 0 | -103 | 7764.66
2009-10-12 02:39 | 59.967 | 3752.8716 | 350 | -223.0157 | 16 | 401.5 | 10 | 0 | -103 | 7764.99
2009-10-12 02:39 | 59.972 | 3752.3586 | 350 | -223.0157 | 16 | 402 | 10 | 0 | -103 | 7765.32
2009-10-12 02:39 | 59.976 | 3749.3979 | 350 | -223.0157 | 16 | 402.5 | 10 | 0 | -103 | 7765.65
2009-10-12 02:39 | 59.975 | 3747.4758 | 350 | -223.0157 | 16 | 403 | 10 | 0 | -103 | 7765.98
2009-10-12 02:39 | 59.969 | 3740.3704 | 350 | -223.0157 | 16 | 403.5 | 10 | 0 | -103 | 7766.31
2009-10-12 02:39 | 59.973 | 3741.2852 | 350 | -223.0157 | 16 | 404 | 10 | 0 | -103 | 7766.64
2009-10-12 02:39 | 59.974 | 3746.6509 | 350 | -223.0157 | 16 | 404.5 | 10 | 0 | -103 | 7766.97
2009-10-12 02:39 | 59.978 | 3745.7383 | 350 | -223.0157 | 16 | 405 | 10 | 0 | -103 | 7767.3
2009-10-12 02:39 | 59.981 | 3743.3506 | 350 | -223.0157 | 16 | 405.5 | 10 | 0 | -103 | 7767.63
2009-10-12 02:39 | 59.981 | 3741.6182 | 350 | -223.0157 | 16 | 406 | 10 | 0 | -103 | 7767.96
2009-10-12 02:39 | 59.981 | 3740.3064 | 350 | -223.0157 | 16 | 406.5 | 10 | 0 | -103 | 7768.29
2009-10-12 02:39 | 59.982 | 3738.4844 | 350 | -223.0157 | 16 | 407 | 10 | 0 | -103 | 7768.62
2009-10-12 02:39 | 59.982 | 3738.9014 | 350 | -223.0157 | 16 | 407.5 | 10 | 0 | -103 | 7768.95
2009-10-12 02:39 | 59.984 | 3737.4036 | 350 | -223.0157 | 16 | 408 | 10 | 0 | -103 | 7769.28
2009-10-12 02:39 | 59.982 | 3737.2732 | 350 | -223.0157 | 16 | 408.5 | 10 | 0 | -103 | 7769.61
2009-10-12 02:39 | 59.981 | 3736.3083 | 350 | -223.0157 | 16 | 409 | 10 | 0 | -103 | 7769.94
2009-10-12 02:39 | 59.979 | 3736.272 | 350 | -223.0157 | 16 | 409.5 | 10 | 0 | -103 | 7770.27
2009-10-12 02:39 | 59.98 | 3735.4482 | 350 | -223.0157 | 16 | 410 | 10 | 0 | -103 | 7770.6
2009-10-12 02:39 | 59.978 | 3735.6497 | 350 | -223.0157 | 16 | 410.5 | 10 | 0 | -103 | 7770.93
2009-10-12 02:39 | 59.978 | 3737.5405 | 350 | -223.0157 | 16 | 411 | 10 | 0 | -103 | 7771.26
2009-10-12 02:39 | 59.98 | 3738.012 | 350 | -223.0157 | 16 | 411.5 | 10 | 0 | -103 | 7771.59
2009-10-12 02:39 | 59.981 | 3736.7476 | 350 | -223.0157 | 16 | 412 | 10 | 0 | -103 | 7771.92
2009-10-12 02:40 | 59.98 | 3736.6931 | 350 | -223.0157 | 16 | 412.5 | 10 | 0 | -103 | 7772.25
2009-10-12 02:40 | 59.978 | 3736.0674 | 350 | -223.0157 | 16 | 413 | 10 | 0 | -103 | 7772.58
2009-10-12 02:40 | 59.976 | 3736.0942 | 350 | -223.0157 | 16 | 413.5 | 10 | 0 | -103 | 7772.91
2009-10-12 02:40 | 59.972 | 3736.575 | 350 | -223.0157 | 16 | 414 | 10 | 0 | -103 | 7773.24
2009-10-12 02:40 | 59.971 | 3738.571 | 350 | -223.0157 | 16 | 414.5 | 10 | 0 | -103 | 7773.57
2009-10-12 02:40 | 59.969 | 3738.8748 | 350 | -223.0157 | 16 | 415 | 10 | 0 | -103 | 7773.9
2009-10-12 02:40 | 59.974 | 3738.9346 | 350 | -223.0157 | 16 | 415.5 | 10 | 0 | -103 | 7774.23
2009-10-12 02:40 | 59.975 | 3738.647 | 350 | -223.0157 | 16 | 416 | 10 | 0 | -103 | 7774.56
2009-10-12 02:40 | 59.976 | 3737.6841 | 350 | -223.0157 | 16 | 416.5 | 10 | 0 | -103 | 7774.89
2009-10-12 02:40 | 59.972 | 3737.3821 | 350 | -223.0157 | 16 | 417 | 10 | 0 | -103 | 7775.22
2009-10-12 02:40 | 59.969 | 3737.8921 | 350 | -223.0157 | 16 | 417.5 | 10 | 0 | -103 | 7775.55
2009-10-12 02:40 | 59.971 | 3740.0168 | 350 | -223.0157 | 16 | 418 | 10 | 0 | -103 | 7775.88
2009-10-12 02:40 | 59.974 | 3740.3289 | 350 | -223.0157 | 16 | 418.5 | 10 | 0 | -103 | 7776.21
2009-10-12 02:40 | 59.972 | 3742.0527 | 350 | -223.0157 | 16 | 419 | 10 | 0 | -103 | 7776.54
2009-10-12 02:40 | 59.972 | 3742.4238 | 350 | -223.0157 | 16 | 419.5 | 10 | 0 | -103 | 7776.87
2009-10-12 02:40 | 59.972 | 3742.5244 | 350 | -223.0157 | 16 | 420 | 10 | 0 | -103 | 7777.2
2009-10-12 02:40 | 59.977 | 3742.2451 | 350 | -223.0157 | 16 | 420.5 | 10 | 0 | -103 | 7777.53
2009-10-12 02:40 | 59.982 | 3741.7231 | 350 | -223.0157 | 16 | 421 | 10 | 0 | -103 | 7777.86
2009-10-12 02:40 | 59.978 | 3740.0854 | 350 | -223.0157 | 16 | 421.5 | 10 | 0 | -103 | 7778.19
2009-10-12 02:40 | 59.976 | 3740.6292 | 350 | -223.0157 | 16 | 422 | 10 | 0 | -103 | 7778.52
2009-10-12 02:40 | 59.973 | 3739.9644 | 350 | -223.0157 | 16 | 422.5 | 10 | 0 | -103 | 7778.85
2009-10-12 02:40 | 59.974 | 3740.7751 | 350 | -223.0157 | 16 | 423 | 10 | 0 | -103 | 7779.18
2009-10-12 02:40 | 59.977 | 3742.8325 | 350 | -223.0157 | 16 | 423.5 | 10 | 0 | -103 | 7779.51
2009-10-12 02:40 | 59.977 | 3741.2678 | 350 | -223.0157 | 16 | 424 | 10 | 0 | -103 | 7779.84
2009-10-12 02:40 | 59.978 | 3739.7761 | 350 | -223.0157 | 16 | 424.5 | 10 | 0 | -103 | 7780.17
2009-10-12 02:40 | 59.979 | 3738.9658 | 350 | -223.0157 | 16 | 425 | 10 | 0 | -103 | 7780.5
2009-10-12 02:40 | 59.981 | 3738.7061 | 350 | -223.0157 | 16 | 425.5 | 10 | 0 | -103 | 7780.83
2009-10-12 02:40 | 59.977 | 3738.8787 | 350 | -223.0157 | 16 | 426 | 10 | 0 | -103 | 7781.16
2009-10-12 02:40 | 59.974 | 3739.8596 | 350 | -223.0157 | 16 | 426.5 | 10 | 0 | -103 | 7781.49
2009-10-12 02:40 | 59.971 | 3738.1016 | 350 | -223.0157 | 16 | 427 | 10 | 0 | -103 | 7781.82
2009-10-12 02:40 | 59.971 | 3738.5579 | 350 | -223.0157 | 16 | 427.5 | 10 | 0 | -103 | 7782.15
2009-10-12 02:41 | 59.971 | 3743.5068 | 350 | -223.0157 | 16 | 428 | 10 | 0 | -103 | 7782.48
2009-10-12 02:41 | 59.972 | 3743.4187 | 350 | -223.0157 | 16 | 428.5 | 10 | 0 | -103 | 7782.81
2009-10-12 02:41 | 59.968 | 3745.2507 | 350 | -223.0157 | 16 | 429 | 10 | 0 | -103 | 7783.14
2009-10-12 02:41 | 59.966 | 3745.7441 | 350 | -223.0157 | 16 | 429.5 | 10 | 0 | -103 | 7783.47
2009-10-12 02:41 | 59.966 | 3747.3396 | 350 | -223.0157 | 16 | 430 | 10 | 0 | -103 | 7783.8
2009-10-12 02:41 | 59.971 | 3750.7002 | 350 | -223.0157 | 16 | 430.5 | 10 | 0 | -103 | 7784.13
2009-10-12 02:41 | 59.973 | 3749.75 | 350 | -223.0157 | 16 | 431 | 10 | 0 | -103 | 7784.46
2009-10-12 02:41 | 59.972 | 3746.2166 | 350 | -223.0157 | 16 | 431.5 | 10 | 0 | -103 | 7784.79
2009-10-12 02:41 | 59.969 | 3744.6826 | 350 | -223.0157 | 16 | 432 | 10 | 0 | -103 | 7785.12
2009-10-12 02:41 | 59.972 | 3743.7451 | 350 | -223.0157 | 16 | 432.5 | 10 | 0 | -103 | 7785.45
2009-10-12 02:41 | 59.974 | 3743.1489 | 350 | -223.0157 | 16 | 433 | 10 | 0 | -103 | 7785.78
2009-10-12 02:41 | 59.973 | 3740.2986 | 350 | -223.0157 | 16 | 433.5 | 10 | 0 | -103 | 7786.11
2009-10-12 02:41 | 59.97 | 3739.4526 | 350 | -223.0157 | 16 | 434 | 10 | 0 | -103 | 7786.44
2009-10-12 02:41 | 59.971 | 3733.376 | 350 | -223.0157 | 16 | 434.5 | 10 | 0 | -103 | 7786.77
2009-10-12 02:41 | 59.974 | 3731.8296 | 350 | -223.0157 | 16 | 435 | 10 | 0 | -103 | 7787.1
2009-10-12 02:41 | 59.982 | 3737.5825 | 350 | -223.0157 | 16 | 435.5 | 10 | 0 | -103 | 7787.43
2009-10-12 02:41 | 59.985 | 3736.2295 | 350 | -223.0157 | 16 | 436 | 10 | 0 | -103 | 7787.76
2009-10-12 02:41 | 59.985 | 3734.8967 | 350 | -223.0157 | 16 | 436.5 | 10 | 0 | -103 | 7788.09
2009-10-12 02:41 | 59.985 | 3733.4338 | 350 | -223.0157 | 16 | 437 | 10 | 0 | -103 | 7788.42
2009-10-12 02:41 | 59.987 | 3733.1152 | 350 | -223.0157 | 16 | 437.5 | 10 | 0 | -103 | 7788.75
2009-10-12 02:41 | 59.989 | 3730.5098 | 350 | -223.0157 | 16 | 438 | 10 | 0 | -103 | 7789.08
2009-10-12 02:41 | 59.989 | 3729.1802 | 350 | -223.0157 | 16 | 438.5 | 10 | 0 | -103 | 7789.41
2009-10-12 02:41 | 59.986 | 3725.4587 | 350 | -223.0157 | 16 | 439 | 10 | 0 | -103 | 7789.74
2009-10-12 02:41 | 59.987 | 3724.7847 | 350 | -223.0157 | 16 | 439.5 | 10 | 0 | -103 | 7790.07
2009-10-12 02:41 | 59.99 | 3720.1079 | 350 | -223.0157 | 16 | 440 | 10 | 0 | -103 | 7790.4
2009-10-12 02:41 | 59.994 | 3720.9382 | 350 | -223.0157 | 16 | 440.5 | 10 | 0 | -103 | 7790.73
2009-10-12 02:41 | 59.996 | 3725.6614 | 350 | -223.0157 | 16 | 441 | 10 | 0 | -103 | 7791.06
2009-10-12 02:41 | 60.001 | 3725.6768 | 350 | -223.0157 | 16 | 441.5 | 10 | 0 | -103 | 7791.39
2009-10-12 02:41 | 60.003 | 3727.7542 | 350 | -223.0157 | 16 | 442 | 10 | 0 | -103 | 7791.72
2009-10-12 02:42 | 60.004 | 3727.8247 | 350 | -223.0157 | 16 | 442.5 | 10 | 0 | -103 | 7792.05
2009-10-12 02:42 | 60.006 | 3727.6833 | 350 | -223.0157 | 16 | 443 | 10 | 0 | -103 | 7792.38
2009-10-12 02:42 | 60.012 | 3727.2314 | 350 | -223.0157 | 16 | 443.5 | 10 | 0 | -103 | 7792.71
2009-10-12 02:42 | 60.014 | 3725.0122 | 350 | -223.0157 | 16 | 444 | 10 | 0 | -103 | 7793.04
2009-10-12 02:42 | 60.019 | 3726.4463 | 350 | -223.0157 | 16 | 444.5 | 10 | 0 | -103 | 7793.37
2009-10-12 02:42 | 60.021 | 3726.0156 | 350 | -223.0157 | 16 | 445 | 10 | 0 | -103 | 7793.7
2009-10-12 02:42 | 60.025 | 3719.123 | 350 | -223.0157 | 16 | 445.5 | 10 | 0 | -103 | 7794.03
2009-10-12 02:42 | 60.026 | 3716.3745 | 350 | -223.0157 | 16 | 446 | 10 | 0 | -103 | 7794.36
2009-10-12 02:42 | 60.027 | 3717.3325 | 350 | -223.0157 | 16 | 446.5 | 10 | 0 | -103 | 7794.69
2009-10-12 02:42 | 60.029 | 3717.5598 | 350 | -223.0157 | 16 | 447 | 10 | 0 | -103 | 7795.02
2009-10-12 02:42 | 60.029 | 3717.1421 | 350 | -223.0157 | 16 | 447.5 | 10 | 0 | -103 | 7795.35
2009-10-12 02:42 | 60.037 | 3715.166 | 350 | -223.0157 | 16 | 448 | 10 | 0 | -103 | 7795.68
2009-10-12 02:42 | 60.036 | 3713.6318 | 350 | -223.0157 | 16 | 448.5 | 10 | 0 | -103 | 7796.01
2009-10-12 02:42 | 60.037 | 3710.2834 | 350 | -223.0157 | 16 | 449 | 10 | 0 | -103 | 7796.34
2009-10-12 02:42 | 60.037 | 3710.1577 | 350 | -223.0157 | 16 | 449.5 | 10 | 0 | -103 | 7796.67
2009-10-12 02:42 | 60.036 | 3699.3557 | 350 | -223.0157 | 16 | 450 | 10 | 0 | -103 | 7797
2009-10-12 02:42 | 60.041 | 3698.5911 | 350 | -223.0157 | 16 | 450.5 | 10 | 0 | -103 | 7797.33
2009-10-12 02:42 | 60.043 | 3704.5913 | 350 | -223.0157 | 16 | 451 | 10 | 0 | -103 | 7797.66
2009-10-12 02:42 | 60.044 | 3703.2754 | 350 | -223.0157 | 16 | 451.5 | 10 | 0 | -103 | 7797.99
2009-10-12 02:42 | 60.043 | 3702.4824 | 350 | -223.0157 | 16 | 452 | 10 | 0 | -103 | 7798.32
2009-10-12 02:42 | 60.046 | 3701.3164 | 350 | -223.0157 | 16 | 452.5 | 10 | 0 | -103 | 7798.65
2009-10-12 02:42 | 60.048 | 3700.8259 | 350 | -223.0157 | 16 | 453 | 10 | 0 | -103 | 7798.98
2009-10-12 02:42 | 60.046 | 3699.5286 | 350 | -223.0157 | 16 | 453.5 | 10 | 0 | -103 | 7799.31
2009-10-12 02:42 | 60.046 | 3699.7261 | 350 | -223.0157 | 16 | 454 | 10 | 0 | -103 | 7799.64
2009-10-12 02:42 | 60.043 | 3690.0996 | 350 | -223.0157 | 16 | 454.5 | 10 | 0 | -103 | 7799.97
2009-10-12 02:42 | 60.043 | 3690.4773 | 350 | -223.0157 | 16 | 455 | 10 | 0 | -103 | 7800.3
2009-10-12 02:42 | 60.044 | 3696.8645 | 350 | -223.0157 | 16 | 455.5 | 10 | 0 | -103 | 7800.63
2009-10-12 02:42 | 60.043 | 3696.8772 | 350 | -223.0157 | 16 | 456 | 10 | 0 | -103 | 7800.96
2009-10-12 02:42 | 60.043 | 3696.1819 | 350 | -223.0157 | 16 | 456.5 | 10 | 0 | -103 | 7801.29
2009-10-12 02:42 | 60.045 | 3696.5413 | 350 | -223.0157 | 16 | 457 | 10 | 0 | -103 | 7801.62
2009-10-12 02:42 | 60.04 | 3696.9678 | 350 | -223.0157 | 16 | 457.5 | 10 | 0 | -103 | 7801.95
2009-10-12 02:43 | 60.041 | 3698.686 | 350 | -223.0157 | 16 | 458 | 10 | 0 | -103 | 7802.28
2009-10-12 02:43 | 60.039 | 3699.6306 | 350 | -223.0157 | 16 | 458.5 | 10 | 0 | -103 | 7802.61
2009-10-12 02:43 | 60.039 | 3698.7869 | 350 | -223.0157 | 16 | 459 | 10 | 0 | -103 | 7802.94
2009-10-12 02:43 | 60.036 | 3699.7122 | 350 | -223.0157 | 16 | 459.5 | 10 | 0 | -103 | 7803.27
2009-10-12 02:43 | 60.038 | 3700.1057 | 350 | -223.0157 | 16 | 460 | 10 | 0 | -103 | 7803.6
2009-10-12 02:43 | 60.033 | 3699.968 | 350 | -223.0157 | 16 | 460.5 | 10 | 0 | -103 | 7803.93
2009-10-12 02:43 | 60.034 | 3701.1218 | 350 | -223.0157 | 16 | 461 | 10 | 0 | -103 | 7804.26
2009-10-12 02:43 | 60.037 | 3701.8652 | 350 | -223.0157 | 16 | 461.5 | 10 | 0 | -103 | 7804.59
2009-10-12 02:43 | 60.037 | 3701.6138 | 350 | -223.0157 | 16 | 462 | 10 | 0 | -103 | 7804.92
2009-10-12 02:43 | 60.035 | 3701.9978 | 350 | -223.0157 | 16 | 462.5 | 10 | 0 | -103 | 7805.25
2009-10-12 02:43 | 60.03 | 3702.9126 | 350 | -223.0157 | 16 | 463 | 10 | 0 | -103 | 7805.58
2009-10-12 02:43 | 60.033 | 3703.9092 | 350 | -223.0157 | 16 | 463.5 | 10 | 0 | -103 | 7805.91
2009-10-12 02:43 | 60.036 | 3705.5225 | 350 | -223.0157 | 16 | 464 | 10 | 0 | -103 | 7806.24
2009-10-12 02:43 | 60.033 | 3704.9668 | 350 | -223.0157 | 16 | 464.5 | 10 | 0 | -103 | 7806.57
2009-10-12 02:43 | 60.034 | 3704.0874 | 350 | -223.0157 | 16 | 465 | 10 | 0 | -103 | 7806.9
2009-10-12 02:43 | 60.032 | 3702.7708 | 350 | -223.0157 | 16 | 465.5 | 10 | 0 | -103 | 7807.23
2009-10-12 02:43 | 60.032 | 3703.7063 | 350 | -223.0157 | 16 | 466 | 10 | 0 | -103 | 7807.56
2009-10-12 02:43 | 60.034 | 3704.9053 | 350 | -223.0157 | 16 | 466.5 | 10 | 0 | -103 | 7807.89
2009-10-12 02:43 | 60.033 | 3705.4353 | 350 | -223.0157 | 16 | 467 | 10 | 0 | -103 | 7808.22
2009-10-12 02:43 | 60.037 | 3704.3601 | 350 | -223.0157 | 16 | 467.5 | 10 | 0 | -103 | 7808.55
2009-10-12 02:43 | 60.035 | 3702.5879 | 350 | -223.0157 | 16 | 468 | 10 | 0 | -103 | 7808.88
2009-10-12 02:43 | 60.035 | 3702.2043 | 350 | -223.0157 | 16 | 468.5 | 10 | 0 | -103 | 7809.21
2009-10-12 02:43 | 60.036 | 3701.9419 | 350 | -223.0157 | 16 | 469 | 10 | 0 | -103 | 7809.54
2009-10-12 02:43 | 60.039 | 3702.2505 | 350 | -223.0157 | 16 | 469.5 | 10 | 0 | -103 | 7809.87
2009-10-12 02:43 | 60.037 | 3703.3179 | 350 | -223.0157 | 16 | 470 | 10 | 0 | -103 | 7810.2
2009-10-12 02:43 | 60.039 | 3702.457 | 350 | -223.0157 | 16 | 470.5 | 10 | 0 | -103 | 7810.53
2009-10-12 02:43 | 60.036 | 3702.5249 | 350 | -223.0157 | 16 | 471 | 10 | 0 | -103 | 7810.86
2009-10-12 02:43 | 60.034 | 3703.2686 | 350 | -223.0157 | 16 | 471.5 | 10 | 0 | -103 | 7811.19
2009-10-12 02:43 | 60.038 | 3703.8435 | 350 | -223.0157 | 16 | 472 | 10 | 0 | -103 | 7811.52
2009-10-12 02:44 | 60.037 | 3702.8652 | 350 | -223.0157 | 16 | 472.5 | 10 | 0 | -103 | 7811.85
2009-10-12 02:44 | 60.037 | 3702.5176 | 350 | -223.0157 | 16 | 473 | 10 | 0 | -103 | 7812.18
2009-10-12 02:44 | 60.037 | 3702.2795 | 350 | -223.0157 | 16 | 473.5 | 10 | 0 | -103 | 7812.51
2009-10-12 02:44 | 60.038 | 3692.427 | 350 | -223.0157 | 16 | 474 | 10 | 0 | -103 | 7812.84
2009-10-12 02:44 | 60.04 | 3692.178 | 350 | -223.0157 | 16 | 474.5 | 10 | 0 | -103 | 7813.17
2009-10-12 02:44 | 60.043 | 3700.2759 | 350 | -223.0157 | 16 | 475 | 10 | 0 | -103 | 7813.5
2009-10-12 02:44 | 60.045 | 3698.7554 | 350 | -223.0157 | 16 | 475.5 | 10 | 0 | -103 | 7813.83
2009-10-12 02:44 | 60.045 | 3697.7285 | 350 | -223.0157 | 16 | 476 | 10 | 0 | -103 | 7814.16
2009-10-12 02:44 | 60.042 | 3696.916 | 350 | -223.0157 | 16 | 476.5 | 10 | 0 | -103 | 7814.49
2009-10-12 02:44 | 60.043 | 3697.3684 | 350 | -223.0157 | 16 | 477 | 10 | 0 | -103 | 7814.82
2009-10-12 02:44 | 60.04 | 3697.3459 | 350 | -223.0157 | 16 | 477.5 | 10 | 0 | -103 | 7815.15
2009-10-12 02:44 | 60.044 | 3698.4292 | 350 | -223.0157 | 16 | 478 | 10 | 0 | -103 | 7815.48
2009-10-12 02:44 | 60.046 | 3694.7629 | 350 | -223.0157 | 16 | 478.5 | 10 | 0 | -103 | 7815.81
2009-10-12 02:44 | 60.042 | 3693.5837 | 350 | -223.0157 | 16 | 479 | 10 | 0 | -103 | 7816.14
2009-10-12 02:44 | 60.034 | 3693.2407 | 350 | -223.0157 | 16 | 479.5 | 10 | 0 | -103 | 7816.47
2009-10-12 02:44 | 60.039 | 3696.7983 | 350 | -223.0157 | 16 | 480 | 10 | 0 | -103 | 7816.8
2009-10-12 02:44 | 60.039 | 3699.3643 | 350 | -223.0157 | 16 | 480.5 | 10 | 0 | -103 | 7817.13
2009-10-12 02:44 | 60.036 | 3701.791 | 350 | -223.0157 | 16 | 481 | 10 | 0 | -103 | 7817.46
2009-10-12 02:44 | 60.037 | 3700.7083 | 350 | -223.0157 | 16 | 481.5 | 10 | 0 | -103 | 7817.79
2009-10-12 02:44 | 60.034 | 3700.7534 | 350 | -223.0157 | 16 | 482 | 10 | 0 | -103 | 7818.12
2009-10-12 02:44 | 60.033 | 3702.1479 | 350 | -223.0157 | 16 | 482.5 | 10 | 0 | -103 | 7818.45
2009-10-12 02:44 | 60.032 | 3705.2126 | 350 | -223.0157 | 16 | 483 | 10 | 0 | -103 | 7818.78
2009-10-12 02:44 | 60.031 | 3707.521 | 350 | -223.0157 | 16 | 483.5 | 10 | 0 | -103 | 7819.11
2009-10-12 02:44 | 60.033 | 3707.2866 | 350 | -223.0157 | 16 | 484 | 10 | 0 | -103 | 7819.44
2009-10-12 02:44 | 60.027 | 3706.988 | 350 | -223.0157 | 16 | 484.5 | 10 | 0 | -103 | 7819.77
2009-10-12 02:44 | 60.031 | 3707.3403 | 350 | -223.0157 | 16 | 485 | 10 | 0 | -103 | 7820.1
2009-10-12 02:44 | 60.032 | 3707.9165 | 350 | -223.0157 | 16 | 485.5 | 10 | 0 | -103 | 7820.43
2009-10-12 02:44 | 60.031 | 3707.3838 | 350 | -223.0157 | 16 | 486 | 10 | 0 | -103 | 7820.76
2009-10-12 02:44 | 60.031 | 3706.8574 | 350 | -223.0157 | 16 | 486.5 | 10 | 0 | -103 | 7821.09
2009-10-12 02:44 | 60.033 | 3707.6152 | 350 | -223.0157 | 16 | 487 | 10 | 0 | -103 | 7821.42
2009-10-12 02:44 | 60.039 | 3706.8232 | 350 | -223.0157 | 16 | 487.5 | 10 | 0 | -103 | 7821.75
2009-10-12 02:45 | 60.039 | 3703.7461 | 350 | -223.0157 | 16 | 488 | 10 | 0 | -103 | 7822.08
2009-10-12 02:45 | 60.038 | 3701.582 | 350 | -223.0157 | 16 | 488.5 | 10 | 0 | -103 | 7822.41
2009-10-12 02:45 | 60.037 | 3700.8474 | 350 | -223.0157 | 16 | 489 | 10 | 0 | -103 | 7822.74
2009-10-12 02:45 | 60.035 | 3701.2075 | 350 | -223.0157 | 16 | 489.5 | 10 | 0 | -103 | 7823.07
2009-10-12 02:45 | 60.037 | 3702.2122 | 350 | -223.0157 | 16 | 490 | 10 | 0 | -103 | 7823.4
2009-10-12 02:45 | 60.04 | 3701.6863 | 350 | -223.0157 | 16 | 490.5 | 10 | 0 | -103 | 7823.73
2009-10-12 02:45 | 60.042 | 3700.3975 | 350 | -223.0157 | 16 | 491 | 10 | 0 | -103 | 7824.06
2009-10-12 02:45 | 60.035 | 3699.6897 | 350 | -223.0157 | 16 | 491.5 | 10 | 0 | -103 | 7824.39
2009-10-12 02:45 | 60.036 | 3700.3665 | 350 | -223.0157 | 16 | 492 | 10 | 0 | -103 | 7824.72
2009-10-12 02:45 | 60.04 | 3700.8271 | 350 | -223.0157 | 16 | 492.5 | 10 | 0 | -103 | 7825.05
2009-10-12 02:45 | 60.045 | 3700.6616 | 350 | -223.0157 | 16 | 493 | 10 | 0 | -103 | 7825.38
2009-10-12 02:45 | 60.045 | 3696.9351 | 350 | -223.0157 | 16 | 493.5 | 10 | 0 | -103 | 7825.71
2009-10-12 02:45 | 60.048 | 3695.6882 | 350 | -223.0157 | 16 | 494 | 10 | 0 | -103 | 7826.04
2009-10-12 02:45 | 60.042 | 3695.8186 | 350 | -223.0157 | 16 | 494.5 | 10 | 0 | -103 | 7826.37
2009-10-12 02:45 | 60.044 | 3693.8242 | 350 | -223.0157 | 16 | 495 | 10 | 0 | -103 | 7826.7
2009-10-12 02:45 | 60.044 | 3694.7991 | 350 | -223.0157 | 16 | 495.5 | 10 | 0 | -103 | 7827.03
2009-10-12 02:45 | 60.044 | 3696.897 | 350 | -223.0157 | 16 | 496 | 10 | 0 | -103 | 7827.36
2009-10-12 02:45 | 60.041 | 3696.0227 | 350 | -223.0157 | 16 | 496.5 | 10 | 0 | -103 | 7827.69
2009-10-12 02:45 | 60.04 | 3697.5024 | 350 | -223.0157 | 16 | 497 | 10 | 0 | -103 | 7828.02
2009-10-12 02:45 | 60.04 | 3698.4243 | 350 | -223.0157 | 16 | 497.5 | 10 | 0 | -103 | 7828.35
2009-10-12 02:45 | 60.045 | 3699.4268 | 350 | -223.0157 | 16 | 498 | 10 | 0 | -103 | 7828.68
2009-10-12 02:45 | 60.044 | 3700.1768 | 350 | -223.0157 | 16 | 498.5 | 10 | 0 | -103 | 7829.01
2009-10-12 02:45 | 60.042 | 3699.8064 | 350 | -223.0157 | 16 | 499 | 10 | 0 | -103 | 7829.34
2009-10-12 02:45 | 60.039 | 3697.5774 | 350 | -223.0157 | 16 | 499.5 | 10 | 0 | -103 | 7829.67
2009-10-12 02:45 | 60.042 | 3697.6807 | 350 | -223.0157 | 16 | 500 | 10 | 0 | -103 | 7830
2009-10-12 02:45 | 60.042 | 3698.5073 | 350 | -223.0157 | 16 | 500.5 | 10 | 0 | -103 | 7830.33
2009-10-12 02:45 | 60.041 | 3698.3589 | 350 | -223.0157 | 16 | 501 | 10 | 0 | -103 | 7830.66
2009-10-12 02:45 | 60.038 | 3698.4658 | 350 | -223.0157 | 16 | 501.5 | 10 | 0 | -103 | 7830.99
2009-10-12 02:45 | 60.036 | 3699.0771 | 350 | -223.0157 | 16 | 502 | 10 | 0 | -103 | 7831.32
2009-10-12 02:46 | 60.037 | 3700.2622 | 350 | -223.0157 | 16 | 502.5 | 10 | 0 | -103 | 7831.65
2009-10-12 02:46 | 60.039 | 3701.5918 | 350 | -223.0157 | 16 | 503 | 10 | 0 | -103 | 7831.98
2009-10-12 02:46 | 60.038 | 3700.9023 | 350 | -223.0157 | 16 | 503.5 | 10 | 0 | -103 | 7832.31
2009-10-12 02:46 | 60.04 | 3700.1428 | 350 | -223.0157 | 16 | 504 | 10 | 0 | -103 | 7832.64
2009-10-12 02:46 | 60.039 | 3700.27 | 350 | -223.0157 | 16 | 504.5 | 10 | 0 | -103 | 7832.97
2009-10-12 02:46 | 60.037 | 3701.1394 | 350 | -223.0157 | 16 | 505 | 10 | 0 | -103 | 7833.3
2009-10-12 02:46 | 60.038 | 3701.5857 | 350 | -223.0157 | 16 | 505.5 | 10 | 0 | -103 | 7833.63
2009-10-12 02:46 | 60.039 | 3700.2644 | 350 | -223.0157 | 16 | 506 | 10 | 0 | -103 | 7833.96
2009-10-12 02:46 | 60.04 | 3699.4585 | 350 | -223.0157 | 16 | 506.5 | 10 | 0 | -103 | 7834.29
2009-10-12 02:46 | 60.037 | 3699.7212 | 350 | -223.0157 | 16 | 507 | 10 | 0 | -103 | 7834.62
2009-10-12 02:46 | 60.037 | 3700.4575 | 350 | -223.0157 | 16 | 507.5 | 10 | 0 | -103 | 7834.95
2009-10-12 02:46 | 60.037 | 3699.5051 | 350 | -223.0157 | 16 | 508 | 10 | 0 | -103 | 7835.28
2009-10-12 02:46 | 60.039 | 3698.7944 | 350 | -223.0157 | 16 | 508.5 | 10 | 0 | -103 | 7835.61
2009-10-12 02:46 | 60.038 | 3699.2161 | 350 | -223.0157 | 16 | 509 | 10 | 0 | -103 | 7835.94
2009-10-12 02:46 | 60.036 | 3699.4004 | 350 | -223.0157 | 16 | 509.5 | 10 | 0 | -103 | 7836.27
2009-10-12 02:46 | 60.035 | 3700.6614 | 350 | -223.0157 | 16 | 510 | 10 | 0 | -103 | 7836.6
2009-10-12 02:46 | 60.033 | 3702.1731 | 350 | -223.0157 | 16 | 510.5 | 10 | 0 | -103 | 7836.93
2009-10-12 02:46 | 60.031 | 3702.9675 | 350 | -223.0157 | 16 | 511 | 10 | 0 | -103 | 7837.26
2009-10-12 02:46 | 60.03 | 3705.1951 | 350 | -223.0157 | 16 | 511.5 | 10 | 0 | -103 | 7837.59
2009-10-12 02:46 | 60.032 | 3704.9517 | 350 | -223.0157 | 16 | 512 | 10 | 0 | -103 | 7837.92
2009-10-12 02:46 | 60.032 | 3705.7751 | 350 | -223.0157 | 16 | 512.5 | 10 | 0 | -103 | 7838.25
2009-10-12 02:46 | 60.037 | 3705.6213 | 350 | -223.0157 | 16 | 513 | 10 | 0 | -103 | 7838.58
2009-10-12 02:46 | 60.042 | 3703.7441 | 350 | -223.0157 | 16 | 513.5 | 10 | 0 | -103 | 7838.91
2009-10-12 02:46 | 60.041 | 3701.9812 | 350 | -223.0157 | 16 | 514 | 10 | 0 | -103 | 7839.24
2009-10-12 02:46 | 60.036 | 3700.7563 | 350 | -223.0157 | 16 | 514.5 | 10 | 0 | -103 | 7839.57
2009-10-12 02:46 | 60.031 | 3700.7471 | 350 | -223.0157 | 16 | 515 | 10 | 0 | -103 | 7839.9
2009-10-12 02:46 | 60.032 | 3702.2126 | 350 | -223.0157 | 16 | 515.5 | 10 | 0 | -103 | 7840.23
2009-10-12 02:46 | 60.031 | 3705.0593 | 350 | -223.0157 | 16 | 516 | 10 | 0 | -103 | 7840.56
2009-10-12 02:46 | 60.034 | 3705.5137 | 350 | -223.0157 | 16 | 516.5 | 10 | 0 | -103 | 7840.89
2009-10-12 02:46 | 60.034 | 3704.4487 | 350 | -223.0157 | 16 | 517 | 10 | 0 | -103 | 7841.22
2009-10-12 02:46 | 60.032 | 3703.8308 | 350 | -223.0157 | 16 | 517.5 | 10 | 0 | -103 | 7841.55
2009-10-12 02:47 | 60.038 | 3703.6196 | 350 | -223.0157 | 16 | 518 | 10 | 0 | -103 | 7841.88
2009-10-12 02:47 | 60.043 | 3702.7954 | 350 | -223.0157 | 16 | 518.5 | 10 | 0 | -103 | 7842.21
2009-10-12 02:47 | 60.044 | 3701.4316 | 350 | -223.0157 | 16 | 519 | 10 | 0 | -103 | 7842.54
2009-10-12 02:47 | 60.042 | 3697.3804 | 350 | -223.0157 | 16 | 519.5 | 10 | 0 | -103 | 7842.87
2009-10-12 02:47 | 60.045 | 3696.2495 | 350 | -223.0157 | 16 | 520 | 10 | 0 | -103 | 7843.2
2009-10-12 02:47 | 60.04 | 3696.302 | 350 | -223.0157 | 16 | 520.5 | 10 | 0 | -103 | 7843.53
2009-10-12 02:47 | 60.04 | 3693.5181 | 350 | -223.0157 | 16 | 521 | 10 | 0 | -103 | 7843.86
2009-10-12 02:47 | 60.043 | 3693.5771 | 350 | -223.0157 | 16 | 521.5 | 10 | 0 | -103 | 7844.19
2009-10-12 02:47 | 60.043 | 3695.197 | 350 | -223.0157 | 16 | 522 | 10 | 0 | -103 | 7844.52
2009-10-12 02:47 | 60.041 | 3695.1855 | 350 | -223.0157 | 16 | 522.5 | 10 | 0 | -103 | 7844.85
2009-10-12 02:47 | 60.04 | 3693.7861 | 350 | -223.0157 | 16 | 523 | 10 | 0 | -103 | 7845.18
2009-10-12 02:47 | 60.038 | 3694.7534 | 350 | -223.0157 | 16 | 523.5 | 10 | 0 | -103 | 7845.51
2009-10-12 02:47 | 60.043 | 3694.9263 | 350 | -223.0157 | 16 | 524 | 10 | 0 | -103 | 7845.84
2009-10-12 02:47 | 60.044 | 3694.9377 | 350 | -223.0157 | 16 | 524.5 | 10 | 0 | -103 | 7846.17
2009-10-12 02:47 | 60.042 | 3694.1594 | 350 | -223.0157 | 16 | 525 | 10 | 0 | -103 | 7846.5
2009-10-12 02:47 | 60.036 | 3691.3301 | 350 | -223.0157 | 16 | 525.5 | 10 | 0 | -103 | 7846.83
2009-10-12 02:47 | 60.043 | 3692.6863 | 350 | -223.0157 | 16 | 526 | 10 | 0 | -103 | 7847.16
2009-10-12 02:47 | 60.041 | 3693.2383 | 350 | -223.0157 | 16 | 526.5 | 10 | 0 | -103 | 7847.49
2009-10-12 02:47 | 60.042 | 3693.3901 | 350 | -223.0157 | 16 | 527 | 10 | 0 | -103 | 7847.82
2009-10-12 02:47 | 60.043 | 3692.3569 | 350 | -223.0157 | 16 | 527.5 | 10 | 0 | -103 | 7848.15
2009-10-12 02:47 | 60.043 | 3690.9514 | 350 | -223.0157 | 16 | 528 | 10 | 0 | -103 | 7848.48
2009-10-12 02:47 | 60.036 | 3690.8362 | 350 | -223.0157 | 16 | 528.5 | 10 | 0 | -103 | 7848.81
2009-10-12 02:47 | 60.039 | 3692.0422 | 350 | -223.0157 | 16 | 529 | 10 | 0 | -103 | 7849.14
2009-10-12 02:47 | 60.039 | 3693.1143 | 350 | -223.0157 | 16 | 529.5 | 10 | 0 | -103 | 7849.47
2009-10-12 02:47 | 60.037 | 3694.1172 | 350 | -223.0157 | 16 | 530 | 10 | 0 | -103 | 7849.8
2009-10-12 02:47 | 60.034 | 3695.2583 | 350 | -223.0157 | 16 | 530.5 | 10 | 0 | -103 | 7850.13
2009-10-12 02:47 | 60.035 | 3695.5808 | 350 | -223.0157 | 16 | 531 | 10 | 0 | -103 | 7850.46
2009-10-12 02:47 | 60.035 | 3695.9492 | 350 | -223.0157 | 16 | 531.5 | 10 | 0 | -103 | 7850.79
2009-10-12 02:47 | 60.035 | 3695.4912 | 350 | -223.0157 | 16 | 532 | 10 | 0 | -103 | 7851.12
2009-10-12 02:48 | 60.036 | 3696.3049 | 350 | -223.0157 | 16 | 532.5 | 10 | 0 | -103 | 7851.45
2009-10-12 02:48 | 60.03 | 3696.4863 | 350 | -223.0157 | 16 | 533 | 10 | 0 | -103 | 7851.78
2009-10-12 02:48 | 60.03 | 3697.3357 | 350 | -223.0157 | 16 | 533.5 | 10 | 0 | -103 | 7852.11
2009-10-12 02:48 | 60.03 | 3699.1709 | 350 | -223.0157 | 16 | 534 | 10 | 0 | -103 | 7852.44
2009-10-12 02:48 | 60.031 | 3699.3569 | 350 | -223.0157 | 16 | 534.5 | 10 | 0 | -103 | 7852.77
2009-10-12 02:48 | 60.031 | 3699.2512 | 350 | -223.0157 | 16 | 535 | 10 | 0 | -103 | 7853.1
2009-10-12 02:48 | 60.032 | 3699.1172 | 350 | -223.0157 | 16 | 535.5 | 10 | 0 | -103 | 7853.43
2009-10-12 02:48 | 60.031 | 3699.1052 | 350 | -223.0157 | 16 | 536 | 10 | 0 | -103 | 7853.76
2009-10-12 02:48 | 60.032 | 3699.1265 | 350 | -223.0157 | 16 | 536.5 | 10 | 0 | -103 | 7854.09
2009-10-12 02:48 | 60.032 | 3698.9543 | 350 | -223.0157 | 16 | 537 | 10 | 0 | -103 | 7854.42
2009-10-12 02:48 | 60.032 | 3698.136 | 350 | -223.0157 | 16 | 537.5 | 10 | 0 | -103 | 7854.75
2009-10-12 02:48 | 60.033 | 3698.2773 | 350 | -223.0157 | 16 | 538 | 10 | 0 | -103 | 7855.08
2009-10-12 02:48 | 60.037 | 3697.4119 | 350 | -223.0157 | 16 | 538.5 | 10 | 0 | -103 | 7855.41
2009-10-12 02:48 | 60.04 | 3695.9404 | 350 | -223.0157 | 16 | 539 | 10 | 0 | -103 | 7855.74
2009-10-12 02:48 | 60.039 | 3693.7358 | 350 | -223.0157 | 16 | 539.5 | 10 | 0 | -103 | 7856.07
2009-10-12 02:48 | 60.042 | 3693.2236 | 350 | -223.0157 | 16 | 540 | 10 | 0 | -103 | 7856.4
2009-10-12 02:48 | 60.036 | 3691.7585 | 350 | -223.0157 | 16 | 540.5 | 10 | 0 | -103 | 7856.73
2009-10-12 02:48 | 60.039 | 3691.9189 | 350 | -223.0157 | 16 | 541 | 10 | 0 | -103 | 7857.06
2009-10-12 02:48 | 60.041 | 3692.7983 | 350 | -223.0157 | 16 | 541.5 | 10 | 0 | -103 | 7857.39
2009-10-12 02:48 | 60.04 | 3691.5815 | 350 | -223.0157 | 16 | 542 | 10 | 0 | -103 | 7857.72
2009-10-12 02:48 | 60.035 | 3692.3735 | 350 | -223.0157 | 16 | 542.5 | 10 | 0 | -103 | 7858.05
2009-10-12 02:48 | 60.036 | 3693.3018 | 350 | -223.0157 | 16 | 543 | 10 | 0 | -103 | 7858.38
2009-10-12 02:48 | 60.038 | 3694.7102 | 350 | -223.0157 | 16 | 543.5 | 10 | 0 | -103 | 7858.71
2009-10-12 02:48 | 60.037 | 3694.3313 | 350 | -223.0157 | 16 | 544 | 10 | 0 | -103 | 7859.04
2009-10-12 02:48 | 60.041 | 3693.8147 | 350 | -223.0157 | 16 | 544.5 | 10 | 0 | -103 | 7859.37
2009-10-12 02:48 | 60.04 | 3693.6172 | 350 | -223.0157 | 16 | 545 | 10 | 0 | -103 | 7859.7
2009-10-12 02:48 | 60.036 | 3694.324 | 350 | -223.0157 | 16 | 545.5 | 10 | 0 | -103 | 7860.03
2009-10-12 02:48 | 60.033 | 3694.27 | 350 | -223.0157 | 16 | 546 | 10 | 0 | -103 | 7860.36
2009-10-12 02:48 | 60.034 | 3694.6604 | 350 | -223.0157 | 16 | 546.5 | 10 | 0 | -103 | 7860.69
2009-10-12 02:48 | 60.038 | 3693.7476 | 350 | -223.0157 | 16 | 547 | 10 | 0 | -103 | 7861.02
2009-10-12 02:49 | 60.04 | 3692.5322 | 350 | -223.0157 | 16 | 547.5 | 10 | 0 | -103 | 7861.35
2009-10-12 02:49 | 60.041 | 3691.4453 | 350 | -223.0157 | 16 | 548 | 10 | 0 | -103 | 7861.68
2009-10-12 02:49 | 60.037 | 3691.0117 | 350 | -223.0157 | 16 | 548.5 | 10 | 0 | -103 | 7862.01
2009-10-12 02:49 | 60.037 | 3691.7988 | 350 | -223.0157 | 16 | 549 | 10 | 0 | -103 | 7862.34
2009-10-12 02:49 | 60.036 | 3693.0767 | 350 | -223.0157 | 16 | 549.5 | 10 | 0 | -103 | 7862.67
2009-10-12 02:49 | 60.037 | 3693.7271 | 350 | -223.0157 | 16 | 550 | 10 | 0 | -103 | 7863
2009-10-12 02:49 | 60.038 | 3693.1172 | 350 | -223.0157 | 16 | 550.5 | 10 | 0 | -103 | 7863.33
2009-10-12 02:49 | 60.039 | 3692.6406 | 350 | -223.0157 | 16 | 551 | 10 | 0 | -103 | 7863.66
2009-10-12 02:49 | 60.038 | 3688.1594 | 350 | -223.0157 | 16 | 551.5 | 10 | 0 | -103 | 7863.99
2009-10-12 02:49 | 60.034 | 3689.0195 | 350 | -223.0157 | 16 | 552 | 10 | 0 | -103 | 7864.32
2009-10-12 02:49 | 60.033 | 3688.2085 | 350 | -223.0157 | 16 | 552.5 | 10 | 0 | -103 | 7864.65
2009-10-12 02:49 | 60.031 | 3690.0918 | 350 | -223.0157 | 16 | 553 | 10 | 0 | -103 | 7864.98
2009-10-12 02:49 | 60.034 | 3693.1724 | 350 | -223.0157 | 16 | 553.5 | 10 | 0 | -103 | 7865.31
2009-10-12 02:49 | 60.029 | 3693.3208 | 350 | -223.0157 | 16 | 554 | 10 | 0 | -103 | 7865.64
2009-10-12 02:49 | 60.029 | 3694.5933 | 350 | -223.0157 | 16 | 554.5 | 10 | 0 | -103 | 7865.97
2009-10-12 02:49 | 60.031 | 3695.2249 | 350 | -223.0157 | 16 | 555 | 10 | 0 | -103 | 7866.3
2009-10-12 02:49 | 60.03 | 3694.6089 | 350 | -223.0157 | 16 | 555.5 | 10 | 0 | -103 | 7866.63
2009-10-12 02:49 | 60.03 | 3693.4116 | 350 | -223.0157 | 16 | 556 | 10 | 0 | -103 | 7866.96
2009-10-12 02:49 | 60.026 | 3693.5085 | 350 | -223.0157 | 16 | 556.5 | 10 | 0 | -103 | 7867.29
2009-10-12 02:49 | 60.022 | 3696.0259 | 350 | -223.0157 | 16 | 557 | 10 | 0 | -103 | 7867.62
2009-10-12 02:49 | 60.021 | 3698.0122 | 350 | -223.0157 | 16 | 557.5 | 10 | 0 | -103 | 7867.95
2009-10-12 02:49 | 60.024 | 3699.0615 | 350 | -223.0157 | 16 | 558 | 10 | 0 | -103 | 7868.28
2009-10-12 02:49 | 60.023 | 3699.4143 | 350 | -223.0157 | 16 | 558.5 | 10 | 0 | -103 | 7868.61
2009-10-12 02:49 | 60.02 | 3698.9351 | 350 | -223.0157 | 16 | 559 | 10 | 0 | -103 | 7868.94
2009-10-12 02:49 | 60.021 | 3700.0837 | 350 | -223.0157 | 16 | 559.5 | 10 | 0 | -103 | 7869.27
2009-10-12 02:49 | 60.023 | 3700.5442 | 350 | -223.0157 | 16 | 560 | 10 | 0 | -103 | 7869.6
2009-10-12 02:49 | 60.025 | 3700.4858 | 350 | -223.0157 | 16 | 560.5 | 10 | 0 | -103 | 7869.93
2009-10-12 02:49 | 60.026 | 3698.5957 | 350 | -223.0157 | 16 | 561 | 10 | 0 | -103 | 7870.26
2009-10-12 02:49 | 60.026 | 3697.9607 | 350 | -223.0157 | 16 | 561.5 | 10 | 0 | -103 | 7870.59
2009-10-12 02:49 | 60.025 | 3699.9138 | 350 | -223.0157 | 16 | 562 | 10 | 0 | -103 | 7870.92
2009-10-12 02:50 | 60.024 | 3700.8025 | 350 | -223.0157 | 16 | 562.5 | 10 | 0 | -103 | 7871.25
2009-10-12 02:50 | 60.024 | 3701.3013 | 350 | -223.0157 | 16 | 563 | 10 | 0 | -103 | 7871.58
2009-10-12 02:50 | 60.025 | 3701.4502 | 350 | -223.0157 | 16 | 563.5 | 10 | 0 | -103 | 7871.91
2009-10-12 02:50 | 60.023 | 3701.3486 | 350 | -223.0157 | 16 | 564 | 10 | 0 | -103 | 7872.24
2009-10-12 02:50 | 60.023 | 3701.0938 | 350 | -223.0157 | 16 | 564.5 | 10 | 0 | -103 | 7872.57
2009-10-12 02:50 | 60.022 | 3701.7017 | 350 | -223.0157 | 16 | 565 | 10 | 0 | -103 | 7872.9
2009-10-12 02:50 | 60.026 | 3702.0703 | 350 | -223.0157 | 16 | 565.5 | 10 | 0 | -103 | 7873.23
2009-10-12 02:50 | 60.029 | 3701.9648 | 350 | -223.0157 | 16 | 566 | 10 | 0 | -103 | 7873.56
2009-10-12 02:50 | 60.026 | 3700.2688 | 350 | -223.0157 | 16 | 566.5 | 10 | 0 | -103 | 7873.89
2009-10-12 02:50 | 60.024 | 3700.2412 | 350 | -223.0157 | 16 | 567 | 10 | 0 | -103 | 7874.22
2009-10-12 02:50 | 60.021 | 3701.0898 | 350 | -223.0157 | 16 | 567.5 | 10 | 0 | -103 | 7874.55
2009-10-12 02:50 | 60.025 | 3701.2681 | 350 | -223.0157 | 16 | 568 | 10 | 0 | -103 | 7874.88
2009-10-12 02:50 | 60.025 | 3701.2046 | 350 | -223.0157 | 16 | 568.5 | 10 | 0 | -103 | 7875.21
2009-10-12 02:50 | 60.025 | 3700.5874 | 350 | -223.0157 | 16 | 569 | 10 | 0 | -103 | 7875.54
2009-10-12 02:50 | 60.023 | 3700.5317 | 350 | -223.0157 | 16 | 569.5 | 10 | 0 | -103 | 7875.87
2009-10-12 02:50 | 60.026 | 3700.1768 | 350 | -223.0157 | 16 | 570 | 10 | 0 | -103 | 7876.2
2009-10-12 02:50 | 60.024 | 3700.2954 | 350 | -223.0157 | 16 | 570.5 | 10 | 0 | -103 | 7876.53
2009-10-12 02:50 | 60.022 | 3700.2773 | 350 | -223.0157 | 16 | 571 | 10 | 0 | -103 | 7876.86
2009-10-12 02:50 | 60.023 | 3700.8408 | 350 | -223.0157 | 16 | 571.5 | 10 | 0 | -103 | 7877.19
2009-10-12 02:50 | 60.026 | 3700.8628 | 350 | -223.0157 | 16 | 572 | 10 | 0 | -103 | 7877.52
2009-10-12 02:50 | 60.025 | 3700.2603 | 350 | -223.0157 | 16 | 572.5 | 10 | 0 | -103 | 7877.85
2009-10-12 02:50 | 60.02 | 3700.0525 | 350 | -223.0157 | 16 | 573 | 10 | 0 | -103 | 7878.18
2009-10-12 02:50 | 60.02 | 3699.9255 | 350 | -223.0157 | 16 | 573.5 | 10 | 0 | -103 | 7878.51
2009-10-12 02:50 | 60.019 | 3700.9648 | 350 | -223.0157 | 16 | 574 | 10 | 0 | -103 | 7878.84
2009-10-12 02:50 | 60.015 | 3702.5811 | 350 | -223.0157 | 16 | 574.5 | 10 | 0 | -103 | 7879.17
2009-10-12 02:50 | 60.016 | 3703.5161 | 350 | -223.0157 | 16 | 575 | 10 | 0 | -103 | 7879.5
2009-10-12 02:50 | 60.017 | 3703.8237 | 350 | -223.0157 | 16 | 575.5 | 10 | 0 | -103 | 7879.83
2009-10-12 02:50 | 60.015 | 3703.6724 | 350 | -223.0157 | 16 | 576 | 10 | 0 | -103 | 7880.16
2009-10-12 02:50 | 60.015 | 3703.6895 | 350 | -223.0157 | 16 | 576.5 | 10 | 0 | -103 | 7880.49
2009-10-12 02:50 | 60.017 | 3703.0034 | 350 | -223.0157 | 16 | 577 | 10 | 0 | -103 | 7880.82
2009-10-12 02:50 | 60.017 | 3702.9214 | 350 | -223.0157 | 16 | 577.5 | 10 | 0 | -103 | 7881.15
2009-10-12 02:51 | 60.012 | 3702.9995 | 350 | -223.0157 | 16 | 578 | 10 | 0 | -103 | 7881.48
2009-10-12 02:51 | 60.01 | 3703.1667 | 350 | -223.0157 | 16 | 578.5 | 10 | 0 | -103 | 7881.81
2009-10-12 02:51 | 60.008 | 3703.9182 | 350 | -223.0157 | 16 | 579 | 10 | 0 | -103 | 7882.14
2009-10-12 02:51 | 60.002 | 3703.6157 | 350 | -223.0157 | 16 | 579.5 | 10 | 0 | -103 | 7882.47
2009-10-12 02:51 | 59.999 | 3703.7754 | 350 | -223.0157 | 16 | 580 | 10 | 0 | -103 | 7882.8
2009-10-12 02:51 | 59.999 | 3703.751 | 350 | -223.0157 | 16 | 580.5 | 10 | 0 | -103 | 7883.13
2009-10-12 02:51 | 60.002 | 3701.5337 | 350 | -223.0157 | 16 | 581 | 10 | 0 | -103 | 7883.46
2009-10-12 02:51 | 60.003 | 3700.6167 | 350 | -223.0157 | 16 | 581.5 | 10 | 0 | -103 | 7883.79
2009-10-12 02:51 | 60.004 | 3700.8804 | 350 | -223.0157 | 16 | 582 | 10 | 0 | -103 | 7884.12
2009-10-12 02:51 | 60.001 | 3700.6252 | 350 | -223.0157 | 16 | 582.5 | 10 | 0 | -103 | 7884.45
2009-10-12 02:51 | 59.996 | 3701.3889 | 350 | -223.0157 | 16 | 583 | 10 | 0 | -103 | 7884.78
2009-10-12 02:51 | 59.993 | 3701.7366 | 350 | -223.0157 | 16 | 583.5 | 10 | 0 | -103 | 7885.11
2009-10-12 02:51 | 59.992 | 3700.6714 | 350 | -223.0157 | 16 | 584 | 10 | 0 | -103 | 7885.44
2009-10-12 02:51 | 59.989 | 3700.8264 | 350 | -223.0157 | 16 | 584.5 | 10 | 0 | -103 | 7885.77
2009-10-12 02:51 | 59.987 | 3700.9771 | 350 | -223.0157 | 16 | 585 | 10 | 0 | -103 | 7886.1
2009-10-12 02:51 | 59.985 | 3700.7 | 350 | -223.0157 | 16 | 585.5 | 10 | 0 | -103 | 7886.43
2009-10-12 02:51 | 59.985 | 3699.8538 | 350 | -223.0157 | 16 | 586 | 10 | 0 | -103 | 7886.76
2009-10-12 02:51 | 59.986 | 3700.2373 | 350 | -223.0157 | 16 | 586.5 | 10 | 0 | -103 | 7887.09
2009-10-12 02:51 | 59.984 | 3700.3423 | 350 | -223.0157 | 16 | 587 | 10 | 0 | -103 | 7887.42
2009-10-12 02:51 | 59.981 | 3700.7698 | 350 | -223.0157 | 16 | 587.5 | 10 | 0 | -103 | 7887.75
2009-10-12 02:51 | 59.98 | 3700.7893 | 350 | -223.0157 | 16 | 588 | 10 | 0 | -103 | 7888.08
2009-10-12 02:51 | 59.977 | 3701.6252 | 350 | -223.0157 | 16 | 588.5 | 10 | 0 | -103 | 7888.41
2009-10-12 02:51 | 59.975 | 3703.1658 | 350 | -223.0157 | 16 | 589 | 10 | 0 | -103 | 7888.74
2009-10-12 02:51 | 59.976 | 3704.187 | 350 | -223.0157 | 16 | 589.5 | 10 | 0 | -103 | 7889.07
2009-10-12 02:51 | 59.972 | 3704.7847 | 350 | -223.0157 | 16 | 590 | 10 | 0 | -103 | 7889.4
2009-10-12 02:51 | 59.974 | 3705.8105 | 350 | -223.0157 | 16 | 590.5 | 10 | 0 | -103 | 7889.73
2009-10-12 02:51 | 59.977 | 3706.958 | 350 | -223.0157 | 16 | 591 | 10 | 0 | -103 | 7890.06
2009-10-12 02:51 | 59.975 | 3706.688 | 350 | -223.0157 | 16 | 591.5 | 10 | 0 | -103 | 7890.39
2009-10-12 02:51 | 59.973 | 3706.543 | 350 | -223.0157 | 16 | 592 | 10 | 0 | -103 | 7890.72
2009-10-12 02:52 | 59.971 | 3706.2571 | 350 | -223.0157 | 16 | 592.5 | 10 | 0 | -103 | 7891.05
2009-10-12 02:52 | 59.971 | 3707.0266 | 350 | -223.0157 | 16 | 593 | 10 | 0 | -103 | 7891.38
2009-10-12 02:52 | 59.976 | 3710.1182 | 350 | -223.0157 | 16 | 593.5 | 10 | 0 | -103 | 7891.71
2009-10-12 02:52 | 59.979 | 3710.5312 | 350 | -223.0157 | 16 | 594 | 10 | 0 | -103 | 7892.04
2009-10-12 02:52 | 59.98 | 3708.7007 | 350 | -223.0157 | 16 | 594.5 | 10 | 0 | -103 | 7892.37
2009-10-12 02:52 | 59.979 | 3708.0181 | 350 | -223.0157 | 16 | 595 | 10 | 0 | -103 | 7892.7
2009-10-12 02:52 | 59.982 | 3706.9424 | 350 | -223.0157 | 16 | 595.5 | 10 | 0 | -103 | 7893.03
2009-10-12 02:52 | 59.982 | 3706.3425 | 350 | -223.0157 | 16 | 596 | 10 | 0 | -103 | 7893.36
2009-10-12 02:52 | 59.983 | 3706.1255 | 350 | -223.0157 | 16 | 596.5 | 10 | 0 | -103 | 7893.69
2009-10-12 02:52 | 59.981 | 3706.3105 | 350 | -223.0157 | 16 | 597 | 10 | 0 | -103 | 7894.02
2009-10-12 02:52 | 59.979 | 3706.1187 | 350 | -223.0157 | 16 | 597.5 | 10 | 0 | -103 | 7894.35
2009-10-12 02:52 | 59.978 | 3706.1904 | 350 | -223.0157 | 16 | 598 | 10 | 0 | -103 | 7894.68
2009-10-12 02:52 | 59.976 | 3707.7209 | 350 | -223.0157 | 16 | 598.5 | 10 | 0 | -103 | 7895.01
2009-10-12 02:52 | 59.978 | 3709.4089 | 350 | -223.0157 | 16 | 599 | 10 | 0 | -103 | 7895.34
2009-10-12 02:52 | 59.977 | 3708.9714 | 350 | -223.0157 | 16 | 599.5 | 10 | 0 | -103 | 7895.67
2009-10-12 02:52 | 59.976 | 3708.5305 | 350 | -223.0157 | 16 | 600 | 10 | 0 | -103 | 7896
2009-10-12 02:52 | 59.978 | 3708.0708 | 350 | -223.0157 | 16 | 600.5 | 10 | 0 | -103 | 7896.33
2009-10-12 02:52 | 59.975 | 3707.24 | 350 | -223.0157 | 16 | 601 | 10 | 0 | -103 | 7896.66
2009-10-12 02:52 | 59.971 | 3709.2126 | 350 | -223.0157 | 16 | 601.5 | 10 | 0 | -103 | 7896.99
2009-10-12 02:52 | 59.97 | 3709.9612 | 350 | -223.0157 | 16 | 602 | 10 | 0 | -103 | 7897.32
2009-10-12 02:52 | 59.97 | 3711.75 | 350 | -223.0157 | 16 | 602.5 | 10 | 0 | -103 | 7897.65
2009-10-12 02:52 | 59.971 | 3711.9805 | 350 | -223.0157 | 16 | 603 | 10 | 0 | -103 | 7897.98
2009-10-12 02:52 | 59.99 | 3710.6953 | 350 | -223.0157 | 16 | 603.5 | 10 | 0 | -103 | 7898.31
2009-10-12 02:52 | 59.998 | 3707.8667 | 350 | -223.0157 | 16 | 604 | 10 | 0 | -103 | 7898.64
2009-10-12 02:52 | 59.999 | 3704.9119 | 350 | -223.0157 | 16 | 604.5 | 10 | 0 | -103 | 7898.97
2009-10-12 02:52 | 59.999 | 3705.6392 | 350 | -223.0157 | 16 | 605 | 10 | 0 | -103 | 7899.3
2009-10-12 02:52 | 59.998 | 3703.7869 | 350 | -223.0157 | 16 | 605.5 | 10 | 0 | -103 | 7899.63
2009-10-12 02:52 | 59.999 | 3703.1909 | 350 | -223.0157 | 16 | 606 | 10 | 0 | -103 | 7899.96
2009-10-12 02:52 | 60.003 | 3702.0706 | 350 | -223.0157 | 16 | 606.5 | 10 | 0 | -103 | 7900.29
2009-10-12 02:52 | 60.005 | 3699.51 | 350 | -223.0157 | 16 | 607 | 10 | 0 | -103 | 7900.62
2009-10-12 02:52 | 60.005 | 3698.658 | 350 | -223.0157 | 16 | 607.5 | 10 | 0 | -103 | 7900.95
2009-10-12 02:53 | 60.01 | 3698.1367 | 350 | -223.0157 | 16 | 608 | 10 | 0 | -103 | 7901.28
2009-10-12 02:53 | 60.013 | 3697.8821 | 350 | -223.0157 | 16 | 608.5 | 10 | 0 | -103 | 7901.61
2009-10-12 02:53 | 60.02 | 3698.6682 | 350 | -223.0157 | 16 | 609 | 10 | 0 | -103 | 7901.94
2009-10-12 02:53 | 60.022 | 3698.6045 | 350 | -223.0157 | 16 | 609.5 | 10 | 0 | -103 | 7902.27
2009-10-12 02:53 | 60.024 | 3697.8684 | 350 | -223.0157 | 16 | 610 | 10 | 0 | -103 | 7902.6
2009-10-12 02:53 | 60.025 | 3694.6719 | 350 | -223.0157 | 16 | 610.5 | 10 | 0 | -103 | 7902.93
2009-10-12 02:53 | 60.025 | 3693.9121 | 350 | -223.0157 | 16 | 611 | 10 | 0 | -103 | 7903.26
2009-10-12 02:53 | 60.024 | 3693.4177 | 350 | -223.0157 | 16 | 611.5 | 10 | 0 | -103 | 7903.59
2009-10-12 02:53 | 60.023 | 3688.3013 | 350 | -223.0157 | 16 | 612 | 10 | 0 | -103 | 7903.92
2009-10-12 02:53 | 60.029 | 3688.021 | 350 | -223.0157 | 16 | 612.5 | 10 | 0 | -103 | 7904.25
2009-10-12 02:53 | 60.029 | 3689.1431 | 350 | -223.0157 | 16 | 613 | 10 | 0 | -103 | 7904.58
2009-10-12 02:53 | 60.029 | 3688.2368 | 350 | -223.0157 | 16 | 613.5 | 10 | 0 | -103 | 7904.91
2009-10-12 02:53 | 60.028 | 3687.8779 | 350 | -223.0157 | 16 | 614 | 10 | 0 | -103 | 7905.24
2009-10-12 02:53 | 60.028 | 3687.0264 | 350 | -223.0157 | 16 | 614.5 | 10 | 0 | -103 | 7905.57
2009-10-12 02:53 | 60.031 | 3686.6831 | 350 | -223.0157 | 16 | 615 | 10 | 0 | -103 | 7905.9
2009-10-12 02:53 | 60.032 | 3685.2756 | 350 | -223.0157 | 16 | 615.5 | 10 | 0 | -103 | 7906.23
2009-10-12 02:53 | 60.033 | 3685.5762 | 350 | -223.0157 | 16 | 616 | 10 | 0 | -103 | 7906.56
2009-10-12 02:53 | 60.031 | 3685.9849 | 350 | -223.0157 | 16 | 616.5 | 10 | 0 | -103 | 7906.89
2009-10-12 02:53 | 60.03 | 3686.418 | 350 | -223.0157 | 16 | 617 | 10 | 0 | -103 | 7907.22
2009-10-12 02:53 | 60.022 | 3687.1589 | 350 | -223.0157 | 16 | 617.5 | 10 | 0 | -103 | 7907.55
2009-10-12 02:53 | 60.021 | 3687.873 | 350 | -223.0157 | 16 | 618 | 10 | 0 | -103 | 7907.88
2009-10-12 02:53 | 60.019 | 3688.9971 | 350 | -223.0157 | 16 | 618.5 | 10 | 0 | -103 | 7908.21
2009-10-12 02:53 | 60.017 | 3690.4258 | 350 | -223.0157 | 16 | 619 | 10 | 0 | -103 | 7908.54
2009-10-12 02:53 | 60.017 | 3690.7756 | 350 | -223.0157 | 16 | 619.5 | 10 | 0 | -103 | 7908.87
2009-10-12 02:53 | 60.017 | 3692.7153 | 350 | -223.0157 | 16 | 620 | 10 | 0 | -103 | 7909.2
2009-10-12 02:53 | 60.016 | 3692.5776 | 350 | -223.0157 | 16 | 620.5 | 10 | 0 | -103 | 7909.53
2009-10-12 02:53 | 60.015 | 3692.4617 | 350 | -223.0157 | 16 | 621 | 10 | 0 | -103 | 7909.86
2009-10-12 02:53 | 60.015 | 3693.1731 | 350 | -223.0157 | 16 | 621.5 | 10 | 0 | -103 | 7910.19
2009-10-12 02:53 | 60.012 | 3693.2488 | 350 | -223.0157 | 16 | 622 | 10 | 0 | -103 | 7910.52
2009-10-12 02:54 | 60.009 | 3693.7434 | 350 | -223.0157 | 16 | 622.5 | 10 | 0 | -103 | 7910.85
2009-10-12 02:54 | 60.008 | 3695.1243 | 350 | -223.0157 | 16 | 623 | 10 | 0 | -103 | 7911.18
2009-10-12 02:54 | 60.008 | 3694.6807 | 350 | -223.0157 | 16 | 623.5 | 10 | 0 | -103 | 7911.51
2009-10-12 02:54 | 60.005 | 3694.7407 | 350 | -223.0157 | 16 | 624 | 10 | 0 | -103 | 7911.84
2009-10-12 02:54 | 60.005 | 3694.1987 | 350 | -223.0157 | 16 | 624.5 | 10 | 0 | -103 | 7912.17
2009-10-12 02:54 | 60.003 | 3693.7495 | 350 | -223.0157 | 16 | 625 | 10 | 0 | -103 | 7912.5
2009-10-12 02:54 | 59.999 | 3693.624 | 350 | -223.0157 | 16 | 625.5 | 10 | 0 | -103 | 7912.83
2009-10-12 02:54 | 59.997 | 3692.8062 | 350 | -223.0157 | 16 | 626 | 10 | 0 | -103 | 7913.16
2009-10-12 02:54 | 59.999 | 3691.1499 | 350 | -223.0157 | 16 | 626.5 | 10 | 0 | -103 | 7913.49
2009-10-12 02:54 | 60 | 3691.4067 | 350 | -223.0157 | 16 | 627 | 10 | 0 | -103 | 7913.82
2009-10-12 02:54 | 59.998 | 3691.0769 | 350 | -223.0157 | 16 | 627.5 | 10 | 0 | -103 | 7914.15
2009-10-12 02:54 | 59.995 | 3690.5876 | 350 | -223.0157 | 16 | 628 | 10 | 0 | -103 | 7914.48
2009-10-12 02:54 | 59.994 | 3689.7974 | 350 | -223.0157 | 16 | 628.5 | 10 | 0 | -103 | 7914.81
2009-10-12 02:54 | 59.992 | 3688.4827 | 350 | -223.0157 | 16 | 629 | 10 | 0 | -103 | 7915.14
2009-10-12 02:54 | 59.993 | 3689.4453 | 350 | -223.0157 | 16 | 629.5 | 10 | 0 | -103 | 7915.47
2009-10-12 02:54 | 59.988 | 3689.5535 | 350 | -223.0157 | 16 | 630 | 10 | 0 | -103 | 7915.8
2009-10-12 02:54 | 59.985 | 3689.5249 | 350 | -223.0157 | 16 | 630.5 | 10 | 0 | -103 | 7916.13
2009-10-12 02:54 | 59.986 | 3689.7356 | 350 | -223.0157 | 16 | 631 | 10 | 0 | -103 | 7916.46
2009-10-12 02:54 | 59.988 | 3688.8528 | 350 | -223.0157 | 16 | 631.5 | 10 | 0 | -103 | 7916.79
2009-10-12 02:54 | 59.988 | 3688.2402 | 350 | -223.0157 | 16 | 632 | 10 | 0 | -103 | 7917.12
2009-10-12 02:54 | 59.985 | 3687.4937 | 350 | -223.0157 | 16 | 632.5 | 10 | 0 | -103 | 7917.45
2009-10-12 02:54 | 59.983 | 3687.4753 | 350 | -223.0157 | 16 | 633 | 10 | 0 | -103 | 7917.78
2009-10-12 02:54 | 59.983 | 3686.7073 | 350 | -223.0157 | 16 | 633.5 | 10 | 0 | -103 | 7918.11
2009-10-12 02:54 | 59.985 | 3685.6597 | 350 | -223.0157 | 16 | 634 | 10 | 0 | -103 | 7918.44
2009-10-12 02:54 | 59.986 | 3684.5098 | 350 | -223.0157 | 16 | 634.5 | 10 | 0 | -103 | 7918.77
2009-10-12 02:54 | 59.987 | 3684.3335 | 350 | -223.0157 | 16 | 635 | 10 | 0 | -103 | 7919.1
2009-10-12 02:54 | 59.99 | 3683.9109 | 350 | -223.0157 | 16 | 635.5 | 10 | 0 | -103 | 7919.43
2009-10-12 02:54 | 59.986 | 3683.7349 | 350 | -223.0157 | 16 | 636 | 10 | 0 | -103 | 7919.76
2009-10-12 02:54 | 59.985 | 3684.2083 | 350 | -223.0157 | 16 | 636.5 | 10 | 0 | -103 | 7920.09
2009-10-12 02:54 | 59.984 | 3683.811 | 350 | -223.0157 | 16 | 637 | 10 | 0 | -103 | 7920.42
2009-10-12 02:54 | 59.983 | 3683.4731 | 350 | -223.0157 | 16 | 637.5 | 10 | 0 | -103 | 7920.75
2009-10-12 02:55 | 59.982 | 3684.2578 | 350 | -223.0157 | 16 | 638 | 10 | 0 | -103 | 7921.08
2009-10-12 02:55 | 59.982 | 3684.8843 | 350 | -223.0157 | 16 | 638.5 | 10 | 0 | -103 | 7921.41
2009-10-12 02:55 | 59.98 | 3685.0918 | 350 | -223.0157 | 16 | 639 | 10 | 0 | -103 | 7921.74
2009-10-12 02:55 | 59.978 | 3685.6543 | 350 | -223.0157 | 16 | 639.5 | 10 | 0 | -103 | 7922.07
2009-10-12 02:55 | 59.977 | 3685.0869 | 350 | -223.0157 | 16 | 640 | 10 | 0 | -103 | 7922.4
2009-10-12 02:55 | 59.975 | 3685.4912 | 350 | -223.0157 | 16 | 640.5 | 10 | 0 | -103 | 7922.73
2009-10-12 02:55 | 59.973 | 3685.196 | 350 | -223.0157 | 16 | 641 | 10 | 0 | -103 | 7923.06
2009-10-12 02:55 | 59.975 | 3687.4124 | 350 | -223.0157 | 16 | 641.5 | 10 | 0 | -103 | 7923.39
2009-10-12 02:55 | 59.976 | 3688.417 | 350 | -223.0157 | 16 | 642 | 10 | 0 | -103 | 7923.72
2009-10-12 02:55 | 59.976 | 3688.5986 | 350 | -223.0157 | 16 | 642.5 | 10 | 0 | -103 | 7924.05
2009-10-12 02:55 | 59.979 | 3687.8477 | 350 | -223.0157 | 16 | 643 | 10 | 0 | -103 | 7924.38
2009-10-12 02:55 | 59.982 | 3686.6782 | 350 | -223.0157 | 16 | 643.5 | 10 | 0 | -103 | 7924.71
2009-10-12 02:55 | 59.979 | 3685.7822 | 350 | -223.0157 | 16 | 644 | 10 | 0 | -103 | 7925.04
2009-10-12 02:55 | 59.979 | 3684.8901 | 350 | -223.0157 | 16 | 644.5 | 10 | 0 | -103 | 7925.37
2009-10-12 02:55 | 59.977 | 3685.1426 | 350 | -223.0157 | 16 | 645 | 10 | 0 | -103 | 7925.7
2009-10-12 02:55 | 59.977 | 3684.5493 | 350 | -223.0157 | 16 | 645.5 | 10 | 0 | -103 | 7926.03
2009-10-12 02:55 | 59.978 | 3684.0933 | 350 | -223.0157 | 16 | 646 | 10 | 0 | -103 | 7926.36
2009-10-12 02:55 | 59.978 | 3684.5547 | 350 | -223.0157 | 16 | 646.5 | 10 | 0 | -103 | 7926.69
2009-10-12 02:55 | 59.978 | 3682.8142 | 350 | -223.0157 | 16 | 647 | 10 | 0 | -103 | 7927.02
2009-10-12 02:55 | 59.979 | 3682.3176 | 350 | -223.0157 | 16 | 647.5 | 10 | 0 | -103 | 7927.35
2009-10-12 02:55 | 59.983 | 3682.3657 | 350 | -223.0157 | 16 | 648 | 10 | 0 | -103 | 7927.68
2009-10-12 02:55 | 59.981 | 3682.6475 | 350 | -223.0157 | 16 | 648.5 | 10 | 0 | -103 | 7928.01
2009-10-12 02:55 | 59.98 | 3682.8555 | 350 | -223.0157 | 16 | 649 | 10 | 0 | -103 | 7928.34
2009-10-12 02:55 | 59.978 | 3683.5566 | 350 | -223.0157 | 16 | 649.5 | 10 | 0 | -103 | 7928.67
2009-10-12 02:55 | 59.979 | 3684.0518 | 350 | -223.0157 | 16 | 650 | 10 | 0 | -103 | 7929
2009-10-12 02:55 | 59.978 | 3684.3184 | 350 | -223.0157 | 16 | 650.5 | 10 | 0 | -103 | 7929.33
2009-10-12 02:55 | 59.979 | 3686.0488 | 350 | -223.0157 | 16 | 651 | 10 | 0 | -103 | 7929.66
2009-10-12 02:55 | 59.983 | 3686.6294 | 350 | -223.0157 | 16 | 651.5 | 10 | 0 | -103 | 7929.99
2009-10-12 02:55 | 59.987 | 3685.2864 | 350 | -223.0157 | 16 | 652 | 10 | 0 | -103 | 7930.32
2009-10-12 02:55 | 59.99 | 3683.4146 | 350 | -223.0157 | 16 | 652.5 | 10 | 0 | -103 | 7930.65
2009-10-12 02:56 | 59.992 | 3682.416 | 350 | -223.0157 | 16 | 653 | 10 | 0 | -103 | 7930.98
2009-10-12 02:56 | 59.993 | 3681.4026 | 350 | -223.0157 | 16 | 653.5 | 10 | 0 | -103 | 7931.31
2009-10-12 02:56 | 59.99 | 3679.0125 | 350 | -223.0157 | 16 | 654 | 10 | 0 | -103 | 7931.64
2009-10-12 02:56 | 59.988 | 3679.4358 | 350 | -223.0157 | 16 | 654.5 | 10 | 0 | -103 | 7931.97
2009-10-12 02:56 | 59.988 | 3671.7612 | 350 | -223.0157 | 16 | 655 | 10 | 0 | -103 | 7932.3
2009-10-12 02:56 | 59.99 | 3670.7168 | 350 | -223.0157 | 16 | 655.5 | 10 | 0 | -103 | 7932.63
2009-10-12 02:56 | 59.993 | 3670.1594 | 350 | -223.0157 | 16 | 656 | 10 | 0 | -103 | 7932.96
2009-10-12 02:56 | 59.994 | 3679.0005 | 350 | -223.0157 | 16 | 656.5 | 10 | 0 | -103 | 7933.29
2009-10-12 02:56 | 59.993 | 3680.1763 | 350 | -223.0157 | 16 | 657 | 10 | 0 | -103 | 7933.62
2009-10-12 02:56 | 59.994 | 3681.7988 | 350 | -223.0157 | 16 | 657.5 | 10 | 0 | -103 | 7933.95
2009-10-12 02:56 | 59.994 | 3682.7004 | 350 | -223.0157 | 16 | 658 | 10 | 0 | -103 | 7934.28
2009-10-12 02:56 | 59.993 | 3684.1157 | 350 | -223.0157 | 16 | 658.5 | 10 | 0 | -103 | 7934.61
2009-10-12 02:56 | 59.989 | 3685.0303 | 350 | -223.0157 | 16 | 659 | 10 | 0 | -103 | 7934.94
2009-10-12 02:56 | 59.984 | 3684.8784 | 350 | -223.0157 | 16 | 659.5 | 10 | 0 | -103 | 7935.27
2009-10-12 02:56 | 59.986 | 3684.165 | 350 | -223.0157 | 16 | 660 | 10 | 0 | -103 | 7935.6
2009-10-12 02:56 | 59.985 | 3684.478 | 350 | -223.0157 | 16 | 660.5 | 10 | 0 | -103 | 7935.93
2009-10-12 02:56 | 59.988 | 3685.5837 | 350 | -223.0157 | 16 | 661 | 10 | 0 | -103 | 7936.26
2009-10-12 02:56 | 59.987 | 3685.1484 | 350 | -223.0157 | 16 | 661.5 | 10 | 0 | -103 | 7936.59
2009-10-12 02:56 | 59.986 | 3684.5867 | 350 | -223.0157 | 16 | 662 | 10 | 0 | -103 | 7936.92
2009-10-12 02:56 | 59.987 | 3684.9761 | 350 | -223.0157 | 16 | 662.5 | 10 | 0 | -103 | 7937.25
2009-10-12 02:56 | 59.985 | 3683.6743 | 350 | -223.0157 | 16 | 663 | 10 | 0 | -103 | 7937.58
2009-10-12 02:56 | 59.982 | 3684.8721 | 350 | -223.0157 | 16 | 663.5 | 10 | 0 | -103 | 7937.91
2009-10-12 02:56 | 59.981 | 3684.2446 | 350 | -223.0157 | 16 | 664 | 10 | 0 | -103 | 7938.24
2009-10-12 02:56 | 59.982 | 3684.7114 | 350 | -223.0157 | 16 | 664.5 | 10 | 0 | -103 | 7938.57
2009-10-12 02:56 | 59.987 | 3685.5891 | 350 | -223.0157 | 16 | 665 | 10 | 0 | -103 | 7938.9
2009-10-12 02:56 | 59.992 | 3683.7358 | 350 | -223.0157 | 16 | 665.5 | 10 | 0 | -103 | 7939.23
2009-10-12 02:56 | 59.997 | 3682.5789 | 350 | -223.0157 | 16 | 666 | 10 | 0 | -103 | 7939.56
2009-10-12 02:56 | 60 | 3682.2341 | 350 | -223.0157 | 16 | 666.5 | 10 | 0 | -103 | 7939.89
2009-10-12 02:56 | 60.003 | 3682.1377 | 350 | -223.0157 | 16 | 667 | 10 | 0 | -103 | 7940.22
2009-10-12 02:56 | 60.003 | 3682.2239 | 350 | -223.0157 | 16 | 667.5 | 10 | 0 | -103 | 7940.55
2009-10-12 02:57 | 60.003 | 3681.689 | 350 | -223.0157 | 16 | 668 | 10 | 0 | -103 | 7940.88
2009-10-12 02:57 | 60.002 | 3681.4585 | 350 | -223.0157 | 16 | 668.5 | 10 | 0 | -103 | 7941.21
2009-10-12 02:57 | 60.003 | 3681.6504 | 350 | -223.0157 | 16 | 669 | 10 | 0 | -103 | 7941.54
2009-10-12 02:57 | 60.002 | 3681.0129 | 350 | -223.0157 | 16 | 669.5 | 10 | 0 | -103 | 7941.87
2009-10-12 02:57 | 60.003 | 3680.167 | 350 | -223.0157 | 16 | 670 | 10 | 0 | -103 | 7942.2
2009-10-12 02:57 | 60.004 | 3679.9429 | 350 | -223.0157 | 16 | 670.5 | 10 | 0 | -103 | 7942.53
2009-10-12 02:57 | 60.005 | 3679.4292 | 350 | -223.0157 | 16 | 671 | 10 | 0 | -103 | 7942.86
2009-10-12 02:57 | 60.006 | 3679.6692 | 350 | -223.0157 | 16 | 671.5 | 10 | 0 | -103 | 7943.19
2009-10-12 02:57 | 60.009 | 3678.9812 | 350 | -223.0157 | 16 | 672 | 10 | 0 | -103 | 7943.52
2009-10-12 02:57 | 60.012 | 3678.2673 | 350 | -223.0157 | 16 | 672.5 | 10 | 0 | -103 | 7943.85
2009-10-12 02:57 | 60.017 | 3676.7961 | 350 | -223.0157 | 16 | 673 | 10 | 0 | -103 | 7944.18
2009-10-12 02:57 | 60.021 | 3676.8096 | 350 | -223.0157 | 16 | 673.5 | 10 | 0 | -103 | 7944.51
2009-10-12 02:57 | 60.022 | 3674.7976 | 350 | -223.0157 | 16 | 674 | 10 | 0 | -103 | 7944.84
2009-10-12 02:57 | 60.021 | 3673.906 | 350 | -223.0157 | 16 | 674.5 | 10 | 0 | -103 | 7945.17
2009-10-12 02:57 | 60.02 | 3671.145 | 350 | -223.0157 | 16 | 675 | 10 | 0 | -103 | 7945.5
2009-10-12 02:57 | 60.018 | 3670.5098 | 350 | -223.0157 | 16 | 675.5 | 10 | 0 | -103 | 7945.83
2009-10-12 02:57 | 60.021 | 3673.6479 | 350 | -223.0157 | 16 | 676 | 10 | 0 | -103 | 7946.16
2009-10-12 02:57 | 60.02 | 3673.6838 | 350 | -223.0157 | 16 | 676.5 | 10 | 0 | -103 | 7946.49
2009-10-12 02:57 | 60.02 | 3675.8647 | 350 | -223.0157 | 16 | 677 | 10 | 0 | -103 | 7946.82
2009-10-12 02:57 | 60.018 | 3676.6758 | 350 | -223.0157 | 16 | 677.5 | 10 | 0 | -103 | 7947.15
2009-10-12 02:57 | 60.018 | 3676.4038 | 350 | -223.0157 | 16 | 678 | 10 | 0 | -103 | 7947.48
2009-10-12 02:57 | 60.019 | 3676.437 | 350 | -223.0157 | 16 | 678.5 | 10 | 0 | -103 | 7947.81
2009-10-12 02:57 | 60.019 | 3677.1848 | 350 | -223.0157 | 16 | 679 | 10 | 0 | -103 | 7948.14
2009-10-12 02:57 | 60.018 | 3677.6589 | 350 | -223.0157 | 16 | 679.5 | 10 | 0 | -103 | 7948.47
2009-10-12 02:57 | 60.017 | 3678.8284 | 350 | -223.0157 | 16 | 680 | 10 | 0 | -103 | 7948.8
2009-10-12 02:57 | 60.016 | 3679.2888 | 350 | -223.0157 | 16 | 680.5 | 10 | 0 | -103 | 7949.13
2009-10-12 02:57 | 60.016 | 3678.9146 | 350 | -223.0157 | 16 | 681 | 10 | 0 | -103 | 7949.46
2009-10-12 02:57 | 60.016 | 3679.2756 | 350 | -223.0157 | 16 | 681.5 | 10 | 0 | -103 | 7949.79
2009-10-12 02:57 | 60.015 | 3678.5986 | 350 | -223.0157 | 16 | 682 | 10 | 0 | -103 | 7950.12
2009-10-12 02:58 | 60.014 | 3678.3669 | 350 | -223.0157 | 16 | 682.5 | 10 | 0 | -103 | 7950.45
2009-10-12 02:58 | 60.014 | 3678.2505 | 350 | -223.0157 | 16 | 683 | 10 | 0 | -103 | 7950.78
2009-10-12 02:58 | 60.013 | 3678.5894 | 350 | -223.0157 | 16 | 683.5 | 10 | 0 | -103 | 7951.11
2009-10-12 02:58 | 60.013 | 3677.251 | 350 | -223.0157 | 16 | 684 | 10 | 0 | -103 | 7951.44
2009-10-12 02:58 | 60.015 | 3675.6978 | 350 | -223.0157 | 16 | 684.5 | 10 | 0 | -103 | 7951.77
2009-10-12 02:58 | 60.017 | 3674.6694 | 350 | -223.0157 | 16 | 685 | 10 | 0 | -103 | 7952.1
2009-10-12 02:58 | 60.016 | 3674.8701 | 350 | -223.0157 | 16 | 685.5 | 10 | 0 | -103 | 7952.43
2009-10-12 02:58 | 60.019 | 3674.4019 | 350 | -223.0157 | 16 | 686 | 10 | 0 | -103 | 7952.76
2009-10-12 02:58 | 60.021 | 3674.5461 | 350 | -223.0157 | 16 | 686.5 | 10 | 0 | -103 | 7953.09
2009-10-12 02:58 | 60.021 | 3672.9688 | 350 | -223.0157 | 16 | 687 | 10 | 0 | -103 | 7953.42
2009-10-12 02:58 | 60.02 | 3671.9136 | 350 | -223.0157 | 16 | 687.5 | 10 | 0 | -103 | 7953.75
2009-10-12 02:58 | 60.022 | 3671.9819 | 350 | -223.0157 | 16 | 688 | 10 | 0 | -103 | 7954.08
2009-10-12 02:58 | 60.024 | 3670.9456 | 350 | -223.0157 | 16 | 688.5 | 10 | 0 | -103 | 7954.41
2009-10-12 02:58 | 60.026 | 3670.821 | 350 | -223.0157 | 16 | 689 | 10 | 0 | -103 | 7954.74
2009-10-12 02:58 | 60.025 | 3671.0596 | 350 | -223.0157 | 16 | 689.5 | 10 | 0 | -103 | 7955.07
2009-10-12 02:58 | 60.026 | 3671.5386 | 350 | -223.0157 | 16 | 690 | 10 | 0 | -103 | 7955.4
2009-10-12 02:58 | 60.022 | 3673.7937 | 350 | -223.0157 | 16 | 690.5 | 10 | 0 | -103 | 7955.73
2009-10-12 02:58 | 60.021 | 3674.0095 | 350 | -223.0157 | 16 | 691 | 10 | 0 | -103 | 7956.06
2009-10-12 02:58 | 60.022 | 3675.1016 | 350 | -223.0157 | 16 | 691.5 | 10 | 0 | -103 | 7956.39
2009-10-12 02:58 | 60.024 | 3675.2842 | 350 | -223.0157 | 16 | 692 | 10 | 0 | -103 | 7956.72
2009-10-12 02:58 | 60.027 | 3676.0513 | 350 | -223.0157 | 16 | 692.5 | 10 | 0 | -103 | 7957.05
2009-10-12 02:58 | 60.029 | 3675.7036 | 350 | -223.0157 | 16 | 693 | 10 | 0 | -103 | 7957.38
2009-10-12 02:58 | 60.028 | 3672.5835 | 350 | -223.0157 | 16 | 693.5 | 10 | 0 | -103 | 7957.71
2009-10-12 02:58 | 60.028 | 3671.3428 | 350 | -223.0157 | 16 | 694 | 10 | 0 | -103 | 7958.04
2009-10-12 02:58 | 60.032 | 3670.2317 | 350 | -223.0157 | 16 | 694.5 | 10 | 0 | -103 | 7958.37
2009-10-12 02:58 | 60.035 | 3668.6538 | 350 | -223.0157 | 16 | 695 | 10 | 0 | -103 | 7958.7
2009-10-12 02:58 | 60.03 | 3668.7671 | 350 | -223.0157 | 16 | 695.5 | 10 | 0 | -103 | 7959.03
2009-10-12 02:58 | 60.028 | 3666.3123 | 350 | -223.0157 | 16 | 696 | 10 | 0 | -103 | 7959.36
2009-10-12 02:58 | 60.021 | 3667.3218 | 350 | -223.0157 | 16 | 696.5 | 10 | 0 | -103 | 7959.69
2009-10-12 02:58 | 60.021 | 3657.1641 | 350 | -223.0157 | 16 | 697 | 10 | 0 | -103 | 7960.02
2009-10-12 02:58 | 60.024 | 3657.7141 | 350 | -223.0157 | 16 | 697.5 | 10 | 0 | -103 | 7960.35
2009-10-12 02:59 | 60.025 | 3668.6375 | 350 | -223.0157 | 16 | 698 | 10 | 0 | -103 | 7960.68
2009-10-12 02:59 | 60.024 | 3669.3088 | 350 | -223.0157 | 16 | 698.5 | 10 | 0 | -103 | 7961.01
2009-10-12 02:59 | 60.022 | 3670.1123 | 350 | -223.0157 | 16 | 699 | 10 | 0 | -103 | 7961.34
2009-10-12 02:59 | 60.023 | 3670.7354 | 350 | -223.0157 | 16 | 699.5 | 10 | 0 | -103 | 7961.67
2009-10-12 02:59 | 60.021 | 3671.332 | 350 | -223.0157 | 16 | 700 | 10 | 0 | -103 | 7962
2009-10-12 02:59 | 60.02 | 3672.0955 | 350 | -223.0157 | 16 | 700.5 | 10 | 0 | -103 | 7962.33
2009-10-12 02:59 | 60.02 | 3672.6831 | 350 | -223.0157 | 16 | 701 | 10 | 0 | -103 | 7962.66
2009-10-12 02:59 | 60.02 | 3673.8325 | 350 | -223.0157 | 16 | 701.5 | 10 | 0 | -103 | 7962.99
2009-10-12 02:59 | 60.02 | 3674.6448 | 350 | -223.0157 | 16 | 702 | 10 | 0 | -103 | 7963.32
2009-10-12 02:59 | 60.017 | 3675.6406 | 350 | -223.0157 | 16 | 702.5 | 10 | 0 | -103 | 7963.65
2009-10-12 02:59 | 60.014 | 3675.9707 | 350 | -223.0157 | 16 | 703 | 10 | 0 | -103 | 7963.98
2009-10-12 02:59 | 60.012 | 3677.0093 | 350 | -223.0157 | 16 | 703.5 | 10 | 0 | -103 | 7964.31
2009-10-12 02:59 | 60.01 | 3678.3137 | 350 | -223.0157 | 16 | 704 | 10 | 0 | -103 | 7964.64
2009-10-12 02:59 | 60.011 | 3679.3928 | 350 | -223.0157 | 16 | 704.5 | 10 | 0 | -103 | 7964.97
2009-10-12 02:59 | 60.01 | 3680.0203 | 350 | -223.0157 | 16 | 705 | 10 | 0 | -103 | 7965.3
2009-10-12 02:59 | 60.01 | 3679.7915 | 350 | -223.0157 | 16 | 705.5 | 10 | 0 | -103 | 7965.63
2009-10-12 02:59 | 60.01 | 3679.5967 | 350 | -223.0157 | 16 | 706 | 10 | 0 | -103 | 7965.96
2009-10-12 02:59 | 60.012 | 3680.3149 | 350 | -223.0157 | 16 | 706.5 | 10 | 0 | -103 | 7966.29
2009-10-12 02:59 | 60.012 | 3680.1104 | 350 | -223.0157 | 16 | 707 | 10 | 0 | -103 | 7966.62
2009-10-12 02:59 | 60.013 | 3679.0615 | 350 | -223.0157 | 16 | 707.5 | 10 | 0 | -103 | 7966.95
2009-10-12 02:59 | 60.014 | 3679.1272 | 350 | -223.0157 | 16 | 708 | 10 | 0 | -103 | 7967.28
2009-10-12 02:59 | 60.013 | 3679.5869 | 350 | -223.0157 | 16 | 708.5 | 10 | 0 | -103 | 7967.61
2009-10-12 02:59 | 60.012 | 3679.6367 | 350 | -223.0157 | 16 | 709 | 10 | 0 | -103 | 7967.94
2009-10-12 02:59 | 60.011 | 3679.02 | 350 | -223.0157 | 16 | 709.5 | 10 | 0 | -103 | 7968.27
2009-10-12 02:59 | 60.01 | 3678.4177 | 350 | -223.0157 | 16 | 710 | 10 | 0 | -103 | 7968.6
2009-10-12 02:59 | 60.008 | 3679.3831 | 350 | -223.0157 | 16 | 710.5 | 10 | 0 | -103 | 7968.93
2009-10-12 02:59 | 60.01 | 3679.6809 | 350 | -223.0157 | 16 | 711 | 10 | 0 | -103 | 7969.26
2009-10-12 02:59 | 60.011 | 3679.9324 | 350 | -223.0157 | 16 | 711.5 | 10 | 0 | -103 | 7969.59
2009-10-12 02:59 | 60.013 | 3679.1382 | 350 | -223.0157 | 16 | 712 | 10 | 0 | -103 | 7969.92
2009-10-12 03:00 | 60.016 | 3678.4688 | 350 | -223.0157 | 16 | 712.5 | 10 | 0 | -103 | 7970.25
2009-10-12 03:00 | 60.018 | 3678.4985 | 350 | -223.0157 | 16 | 713 | 10 | 0 | -103 | 7970.58
2009-10-12 03:00 | 60.019 | 3678.4556 | 350 | -223.0157 | 16 | 713.5 | 10 | 0 | -103 | 7970.91
2009-10-12 03:00 | 60.019 | 3677.6152 | 350 | -223.0157 | 16 | 714 | 10 | 0 | -103 | 7971.24
2009-10-12 03:00 | 60.019 | 3677.4463 | 350 | -223.0157 | 16 | 714.5 | 10 | 0 | -103 | 7971.57
2009-10-12 03:00 | 60.02 | 3677.4314 | 350 | -223.0157 | 16 | 715 | 10 | 0 | -103 | 7971.9
2009-10-12 03:00 | 60.02 | 3677.4509 | 350 | -223.0157 | 16 | 715.5 | 10 | 0 | -103 | 7972.23
2009-10-12 03:00 | 60.018 | 3677.3154 | 350 | -223.0157 | 16 | 716 | 10 | 0 | -103 | 7972.56
2009-10-12 03:00 | 60.018 | 3678.1511 | 350 | -223.0157 | 16 | 716.5 | 10 | 0 | -103 | 7972.89
2009-10-12 03:00 | 60.016 | 3678.3621 | 350 | -223.0157 | 16 | 717 | 10 | 0 | -103 | 7973.22
2009-10-12 03:00 | 60.016 | 3678.8735 | 350 | -223.0157 | 16 | 717.5 | 10 | 0 | -103 | 7973.55
2009-10-12 03:00 | 60.019 | 3680.7708 | 350 | -223.0157 | 16 | 718 | 10 | 0 | -103 | 7973.88
2009-10-12 03:00 | 60.023 | 3681.0581 | 350 | -223.0157 | 16 | 718.5 | 10 | 0 | -103 | 7974.21
2009-10-12 03:00 | 60.022 | 3680.353 | 350 | -223.0157 | 16 | 719 | 10 | 0 | -103 | 7974.54
2009-10-12 03:00 | 60.018 | 3679.1665 | 350 | -223.0157 | 16 | 719.5 | 10 | 0 | -103 | 7974.87
2009-10-12 03:00 | 60.015 | 3679.5532 | 350 | -223.0157 | 16 | 720 | 10 | 0 | -103 | 7975.2
2009-10-12 03:00 | 60.016 | 3680.6724 | 350 | -223.0157 | 16 | 720.5 | 10 | 0 | -103 | 7975.53
2009-10-12 03:00 | 60.017 | 3682.7297 | 350 | -223.0157 | 16 | 721 | 10 | 0 | -103 | 7975.86
2009-10-12 03:00 | 60.015 | 3682.7136 | 350 | -223.0157 | 16 | 721.5 | 10 | 0 | -103 | 7976.19
2009-10-12 03:00 | 60.01 | 3681.9146 | 350 | -223.0157 | 16 | 722 | 10 | 0 | -103 | 7976.52
2009-10-12 03:00 | 60.004 | 3682.0103 | 350 | -223.0157 | 16 | 722.5 | 10 | 0 | -103 | 7976.85
2009-10-12 03:00 | 59.999 | 3682.4834 | 350 | -223.0157 | 16 | 723 | 10 | 0 | -103 | 7977.18
2009-10-12 03:00 | 59.995 | 3683.8135 | 350 | -223.0157 | 16 | 723.5 | 10 | 0 | -103 | 7977.51
2009-10-12 03:00 | 59.99 | 3685.3064 | 350 | -223.0157 | 16 | 724 | 10 | 0 | -103 | 7977.84
2009-10-12 03:00 | 59.982 | 3684.8457 | 350 | -223.0157 | 16 | 724.5 | 10 | 0 | -103 | 7978.17
2009-10-12 03:00 | 59.974 | 3684.6426 | 350 | -223.0157 | 16 | 725 | 10 | 0 | -103 | 7978.5
2009-10-12 03:00 | 59.97 | 3687.5271 | 350 | -223.0157 | 16 | 725.5 | 10 | 0 | -103 | 7978.83
2009-10-12 03:00 | 59.97 | 3689.4038 | 350 | -223.0157 | 16 | 726 | 10 | 0 | -103 | 7979.16
2009-10-12 03:00 | 59.968 | 3692.2874 | 350 | -223.0157 | 16 | 726.5 | 10 | 0 | -103 | 7979.49
2009-10-12 03:00 | 59.968 | 3692.9663 | 350 | -223.0157 | 16 | 727 | 10 | 0 | -103 | 7979.82
2009-10-12 03:00 | 59.968 | 3693.7932 | 350 | -223.0157 | 16 | 727.5 | 10 | 0 | -103 | 7980.15
2009-10-12 03:01 | 59.972 | 3694.3972 | 350 | -223.0157 | 16 | 728 | 10 | 0 | -103 | 7980.48
2009-10-12 03:01 | 59.967 | 3694.9736 | 350 | -223.0157 | 16 | 728.5 | 10 | 0 | -103 | 7980.81
2009-10-12 03:01 | 59.966 | 3697.407 | 350 | -223.0157 | 16 | 729 | 10 | 0 | -103 | 7981.14
2009-10-12 03:01 | 59.964 | 3698.502 | 350 | -223.0157 | 16 | 729.5 | 10 | 0 | -103 | 7981.47
2009-10-12 03:01 | 59.965 | 3698.6169 | 350 | -223.0157 | 16 | 730 | 10 | 0 | -103 | 7981.8
2009-10-12 03:01 | 59.966 | 3698.9924 | 350 | -223.0157 | 16 | 730.5 | 10 | 0 | -103 | 7982.13
2009-10-12 03:01 | 59.963 | 3699.8501 | 350 | -223.0157 | 16 | 731 | 10 | 0 | -103 | 7982.46
2009-10-12 03:01 | 59.963 | 3702.6448 | 350 | -223.0157 | 16 | 731.5 | 10 | 0 | -103 | 7982.79
2009-10-12 03:01 | 59.965 | 3701.9885 | 350 | -223.0157 | 16 | 732 | 10 | 0 | -103 | 7983.12
2009-10-12 03:01 | 59.968 | 3702.218 | 350 | -223.0157 | 16 | 732.5 | 10 | 0 | -103 | 7983.45
2009-10-12 03:01 | 59.97 | 3704.0234 | 350 | -223.0157 | 16 | 733 | 10 | 0 | -103 | 7983.78
2009-10-12 03:01 | 59.97 | 3703.3655 | 350 | -223.0157 | 16 | 733.5 | 10 | 0 | -103 | 7984.11
2009-10-12 03:01 | 59.97 | 3702.9883 | 350 | -223.0157 | 16 | 734 | 10 | 0 | -103 | 7984.44
2009-10-12 03:01 | 59.973 | 3703.8137 | 350 | -223.0157 | 16 | 734.5 | 10 | 0 | -103 | 7984.77
2009-10-12 03:01 | 59.972 | 3704.8994 | 350 | -223.0157 | 16 | 735 | 10 | 0 | -103 | 7985.1
2009-10-12 03:01 | 59.976 | 3705.625 | 350 | -223.0157 | 16 | 735.5 | 10 | 0 | -103 | 7985.43
2009-10-12 03:01 | 59.975 | 3704.2935 | 350 | -223.0157 | 16 | 736 | 10 | 0 | -103 | 7985.76
2009-10-12 03:01 | 59.975 | 3702.0942 | 350 | -223.0157 | 16 | 736.5 | 10 | 0 | -103 | 7986.09
2009-10-12 03:01 | 59.977 | 3701.9438 | 350 | -223.0157 | 16 | 737 | 10 | 0 | -103 | 7986.42
2009-10-12 03:01 | 59.976 | 3703.1421 | 350 | -223.0157 | 16 | 737.5 | 10 | 0 | -103 | 7986.75
2009-10-12 03:01 | 59.976 | 3704.6689 | 350 | -223.0157 | 16 | 738 | 10 | 0 | -103 | 7987.08
2009-10-12 03:01 | 59.974 | 3705.3757 | 350 | -223.0157 | 16 | 738.5 | 10 | 0 | -103 | 7987.41
2009-10-12 03:01 | 59.975 | 3705.6624 | 350 | -223.0157 | 16 | 739 | 10 | 0 | -103 | 7987.74
2009-10-12 03:01 | 59.974 | 3705.8547 | 350 | -223.0157 | 16 | 739.5 | 10 | 0 | -103 | 7988.07
2009-10-12 03:01 | 59.974 | 3706.7764 | 350 | -223.0157 | 16 | 740 | 10 | 0 | -103 | 7988.4
2009-10-12 03:01 | 59.976 | 3707.5139 | 350 | -223.0157 | 16 | 740.5 | 10 | 0 | -103 | 7988.73
2009-10-12 03:01 | 59.977 | 3706.9282 | 350 | -223.0157 | 16 | 741 | 10 | 0 | -103 | 7989.06
2009-10-12 03:01 | 59.979 | 3706.446 | 350 | -223.0157 | 16 | 741.5 | 10 | 0 | -103 | 7989.39
2009-10-12 03:01 | 59.981 | 3706.335 | 350 | -223.0157 | 16 | 742 | 10 | 0 | -103 | 7989.72
2009-10-12 03:02 | 59.983 | 3706.771 | 350 | -223.0157 | 16 | 742.5 | 10 | 0 | -103 | 7990.05
2009-10-12 03:02 | 59.985 | 3705.9431 | 350 | -223.0157 | 16 | 743 | 10 | 0 | -103 | 7990.38
2009-10-12 03:02 | 59.983 | 3704.1272 | 350 | -223.0157 | 16 | 743.5 | 10 | 0 | -103 | 7990.71
2009-10-12 03:02 | 59.98 | 3704.7773 | 350 | -223.0157 | 16 | 744 | 10 | 0 | -103 | 7991.04
2009-10-12 03:02 | 59.979 | 3705.9744 | 350 | -223.0157 | 16 | 744.5 | 10 | 0 | -103 | 7991.37
2009-10-12 03:02 | 59.983 | 3705.9675 | 350 | -223.0157 | 16 | 745 | 10 | 0 | -103 | 7991.7
2009-10-12 03:02 | 59.987 | 3705.3564 | 350 | -223.0157 | 16 | 745.5 | 10 | 0 | -103 | 7992.03
2009-10-12 03:02 | 59.986 | 3704.6831 | 350 | -223.0157 | 16 | 746 | 10 | 0 | -103 | 7992.36
2009-10-12 03:02 | 59.984 | 3703.9133 | 350 | -223.0157 | 16 | 746.5 | 10 | 0 | -103 | 7992.69
2009-10-12 03:02 | 59.98 | 3704.3606 | 350 | -223.0157 | 16 | 747 | 10 | 0 | -103 | 7993.02
2009-10-12 03:02 | 59.982 | 3704.9883 | 350 | -223.0157 | 16 | 747.5 | 10 | 0 | -103 | 7993.35
2009-10-12 03:02 | 59.984 | 3705.0498 | 350 | -223.0157 | 16 | 748 | 10 | 0 | -103 | 7993.68
2009-10-12 03:02 | 59.985 | 3704.8928 | 350 | -223.0157 | 16 | 748.5 | 10 | 0 | -103 | 7994.01
2009-10-12 03:02 | 59.987 | 3703.7407 | 350 | -223.0157 | 16 | 749 | 10 | 0 | -103 | 7994.34
2009-10-12 03:02 | 59.989 | 3701.8311 | 350 | -223.0157 | 16 | 749.5 | 10 | 0 | -103 | 7994.67
2009-10-12 03:02 | 59.992 | 3701.7952 | 350 | -223.0157 | 16 | 750 | 10 | 0 | -103 | 7995
2009-10-12 03:02 | 59.996 | 3700.0698 | 350 | -223.0157 | 16 | 750.5 | 10 | 0 | -103 | 7995.33
2009-10-12 03:02 | 59.999 | 3701.3081 | 350 | -223.0157 | 16 | 751 | 10 | 0 | -103 | 7995.66
2009-10-12 03:02 | 59.997 | 3700.4294 | 350 | -223.0157 | 16 | 751.5 | 10 | 0 | -103 | 7995.99
2009-10-12 03:02 | 59.997 | 3700.9128 | 350 | -223.0157 | 16 | 752 | 10 | 0 | -103 | 7996.32
2009-10-12 03:02 | 59.997 | 3700.541 | 350 | -223.0157 | 16 | 752.5 | 10 | 0 | -103 | 7996.65
2009-10-12 03:02 | 59.997 | 3699.9265 | 350 | -223.0157 | 16 | 753 | 10 | 0 | -103 | 7996.98
2009-10-12 03:02 | 59.996 | 3700.8582 | 350 | -223.0157 | 16 | 753.5 | 10 | 0 | -103 | 7997.31
2009-10-12 03:02 | 59.997 | 3700.5486 | 350 | -223.0157 | 16 | 754 | 10 | 0 | -103 | 7997.64
2009-10-12 03:02 | 59.996 | 3700.6135 | 350 | -223.0157 | 16 | 754.5 | 10 | 0 | -103 | 7997.97
2009-10-12 03:02 | 59.998 | 3700.2239 | 350 | -223.0157 | 16 | 755 | 10 | 0 | -103 | 7998.3
2009-10-12 03:02 | 60.003 | 3699.5 | 350 | -223.0157 | 16 | 755.5 | 10 | 0 | -103 | 7998.63
2009-10-12 03:02 | 60.009 | 3698.0317 | 350 | -223.0157 | 16 | 756 | 10 | 0 | -103 | 7998.96
2009-10-12 03:02 | 60.01 | 3697.96 | 350 | -223.0157 | 16 | 756.5 | 10 | 0 | -103 | 7999.29
2009-10-12 03:02 | 60.008 | 3699.4087 | 350 | -223.0157 | 16 | 757 | 10 | 0 | -103 | 7999.62
2009-10-12 03:02 | 60.005 | 3699.2407 | 350 | -223.0157 | 16 | 757.5 | 10 | 0 | -103 | 7999.95
2009-10-12 03:03 | 60.004 | 3700.7383 | 350 | -223.0157 | 16 | 758 | 10 | 0 | -103 | 8000.28
2009-10-12 03:03 | 60.006 | 3701.1099 | 350 | -223.0157 | 16 | 758.5 | 10 | 0 | -103 | 8000.61
2009-10-12 03:03 | 60.003 | 3701.2378 | 350 | -223.0157 | 16 | 759 | 10 | 0 | -103 | 8000.94
2009-10-12 03:03 | 60.001 | 3699.9976 | 350 | -223.0157 | 16 | 759.5 | 10 | 0 | -103 | 8001.27
2009-10-12 03:03 | 60.002 | 3700.2202 | 350 | -223.0157 | 16 | 760 | 10 | 0 | -103 | 8001.6
2009-10-12 03:03 | 60.004 | 3701.8228 | 350 | -223.0157 | 16 | 760.5 | 10 | 0 | -103 | 8001.93
2009-10-12 03:03 | 60.007 | 3702.5542 | 350 | -223.0157 | 16 | 761 | 10 | 0 | -103 | 8002.26
2009-10-12 03:03 | 60.007 | 3702.2759 | 350 | -223.0157 | 16 | 761.5 | 10 | 0 | -103 | 8002.59
2009-10-12 03:03 | 60.008 | 3701.0264 | 350 | -223.0157 | 16 | 762 | 10 | 0 | -103 | 8002.92
2009-10-12 03:03 | 60.008 | 3701.9229 | 350 | -223.0157 | 16 | 762.5 | 10 | 0 | -103 | 8003.25
2009-10-12 03:03 | 60.006 | 3702.9431 | 350 | -223.0157 | 16 | 763 | 10 | 0 | -103 | 8003.58
2009-10-12 03:03 | 60.006 | 3704.0928 | 350 | -223.0157 | 16 | 763.5 | 10 | 0 | -103 | 8003.91
2009-10-12 03:03 | 60.006 | 3703.9604 | 350 | -223.0157 | 16 | 764 | 10 | 0 | -103 | 8004.24
2009-10-12 03:03 | 60.005 | 3703.8193 | 350 | -223.0157 | 16 | 764.5 | 10 | 0 | -103 | 8004.57
2009-10-12 03:03 | 60 | 3704.4551 | 350 | -223.0157 | 16 | 765 | 10 | 0 | -103 | 8004.9
2009-10-12 03:03 | 59.999 | 3704.3457 | 350 | -223.0157 | 16 | 765.5 | 10 | 0 | -103 | 8005.23
2009-10-12 03:03 | 60 | 3705.3291 | 350 | -223.0157 | 16 | 766 | 10 | 0 | -103 | 8005.56
2009-10-12 03:03 | 60 | 3704.9302 | 350 | -223.0157 | 16 | 766.5 | 10 | 0 | -103 | 8005.89
2009-10-12 03:03 | 60.004 | 3704.4048 | 350 | -223.0157 | 16 | 767 | 10 | 0 | -103 | 8006.22
2009-10-12 03:03 | 60.008 | 3703.6753 | 350 | -223.0157 | 16 | 767.5 | 10 | 0 | -103 | 8006.55
2009-10-12 03:03 | 60.013 | 3702.748 | 350 | -223.0157 | 16 | 768 | 10 | 0 | -103 | 8006.88
2009-10-12 03:03 | 60.015 | 3702.6692 | 350 | -223.0157 | 16 | 768.5 | 10 | 0 | -103 | 8007.21
2009-10-12 03:03 | 60.015 | 3703.0166 | 350 | -223.0157 | 16 | 769 | 10 | 0 | -103 | 8007.54
2009-10-12 03:03 | 60.012 | 3703.4155 | 350 | -223.0157 | 16 | 769.5 | 10 | 0 | -103 | 8007.87
2009-10-12 03:03 | 60.009 | 3703.2974 | 350 | -223.0157 | 16 | 770 | 10 | 0 | -103 | 8008.2
2009-10-12 03:03 | 60.005 | 3705.1887 | 350 | -223.0157 | 16 | 770.5 | 10 | 0 | -103 | 8008.53
2009-10-12 03:03 | 60.008 | 3705.2791 | 350 | -223.0157 | 16 | 771 | 10 | 0 | -103 | 8008.86
2009-10-12 03:03 | 60.011 | 3704.646 | 350 | -223.0157 | 16 | 771.5 | 10 | 0 | -103 | 8009.19
2009-10-12 03:03 | 60.011 | 3704.0513 | 350 | -223.0157 | 16 | 772 | 10 | 0 | -103 | 8009.52
2009-10-12 03:04 | 60.013 | 3703.438 | 350 | -223.0157 | 16 | 772.5 | 10 | 0 | -103 | 8009.85
2009-10-12 03:04 | 60.016 | 3704.2551 | 350 | -223.0157 | 16 | 773 | 10 | 0 | -103 | 8010.18
2009-10-12 03:04 | 60.018 | 3703.7075 | 350 | -223.0157 | 16 | 773.5 | 10 | 0 | -103 | 8010.51
2009-10-12 03:04 | 60.018 | 3703.8303 | 350 | -223.0157 | 16 | 774 | 10 | 0 | -103 | 8010.84
2009-10-12 03:04 | 60.019 | 3704.5239 | 350 | -223.0157 | 16 | 774.5 | 10 | 0 | -103 | 8011.17
2009-10-12 03:04 | 60.018 | 3704.1392 | 350 | -223.0157 | 16 | 775 | 10 | 0 | -103 | 8011.5
2009-10-12 03:04 | 60.013 | 3704.27 | 350 | -223.0157 | 16 | 775.5 | 10 | 0 | -103 | 8011.83
2009-10-12 03:04 | 60.011 | 3705.4294 | 350 | -223.0157 | 16 | 776 | 10 | 0 | -103 | 8012.16
2009-10-12 03:04 | 60.009 | 3705.9419 | 350 | -223.0157 | 16 | 776.5 | 10 | 0 | -103 | 8012.49
2009-10-12 03:04 | 60.009 | 3705.5398 | 350 | -223.0157 | 16 | 777 | 10 | 0 | -103 | 8012.82
2009-10-12 03:04 | 60.008 | 3705.634 | 350 | -223.0157 | 16 | 777.5 | 10 | 0 | -103 | 8013.15
2009-10-12 03:04 | 60.009 | 3705.7485 | 350 | -223.0157 | 16 | 778 | 10 | 0 | -103 | 8013.48
2009-10-12 03:04 | 60.011 | 3707.2673 | 350 | -223.0157 | 16 | 778.5 | 10 | 0 | -103 | 8013.81
2009-10-12 03:04 | 60.015 | 3706.9453 | 350 | -223.0157 | 16 | 779 | 10 | 0 | -103 | 8014.14
2009-10-12 03:04 | 60.02 | 3706.6299 | 350 | -223.0157 | 16 | 779.5 | 10 | 0 | -103 | 8014.47
2009-10-12 03:04 | 60.021 | 3705.6545 | 350 | -223.0157 | 16 | 780 | 10 | 0 | -103 | 8014.8
2009-10-12 03:04 | 60.018 | 3703.8948 | 350 | -223.0157 | 16 | 780.5 | 10 | 0 | -103 | 8015.13
2009-10-12 03:04 | 60.017 | 3704.2239 | 350 | -223.0157 | 16 | 781 | 10 | 0 | -103 | 8015.46
2009-10-12 03:04 | 60.019 | 3703.887 | 350 | -223.0157 | 16 | 781.5 | 10 | 0 | -103 | 8015.79
2009-10-12 03:04 | 60.019 | 3704.6484 | 350 | -223.0157 | 16 | 782 | 10 | 0 | -103 | 8016.12
2009-10-12 03:04 | 60.021 | 3704.7954 | 350 | -223.0157 | 16 | 782.5 | 10 | 0 | -103 | 8016.45
2009-10-12 03:04 | 60.022 | 3704.1665 | 350 | -223.0157 | 16 | 783 | 10 | 0 | -103 | 8016.78
2009-10-12 03:04 | 60.025 | 3702.7642 | 350 | -223.0157 | 16 | 783.5 | 10 | 0 | -103 | 8017.11
2009-10-12 03:04 | 60.027 | 3702.0083 | 350 | -223.0157 | 16 | 784 | 10 | 0 | -103 | 8017.44
2009-10-12 03:04 | 60.03 | 3700.3601 | 350 | -223.0157 | 16 | 784.5 | 10 | 0 | -103 | 8017.77
2009-10-12 03:04 | 60.027 | 3701.063 | 350 | -223.0157 | 16 | 785 | 10 | 0 | -103 | 8018.1
2009-10-12 03:04 | 60.023 | 3700.3401 | 350 | -223.0157 | 16 | 785.5 | 10 | 0 | -103 | 8018.43
2009-10-12 03:04 | 60.021 | 3699.3694 | 350 | -223.0157 | 16 | 786 | 10 | 0 | -103 | 8018.76
2009-10-12 03:04 | 60.023 | 3701.5676 | 350 | -223.0157 | 16 | 786.5 | 10 | 0 | -103 | 8019.09
2009-10-12 03:04 | 60.023 | 3702.9587 | 350 | -223.0157 | 16 | 787 | 10 | 0 | -103 | 8019.42
2009-10-12 03:05 | 60.02 | 3704.2495 | 350 | -223.0157 | 16 | 787.5 | 10 | 0 | -103 | 8019.75
2009-10-12 03:05 | 60.024 | 3703.6211 | 350 | -223.0157 | 16 | 788 | 10 | 0 | -103 | 8020.08
2009-10-12 03:05 | 60.024 | 3703.374 | 350 | -223.0157 | 16 | 788.5 | 10 | 0 | -103 | 8020.41
2009-10-12 03:05 | 60.022 | 3703.0359 | 350 | -223.0157 | 16 | 789 | 10 | 0 | -103 | 8020.74
2009-10-12 03:05 | 60.022 | 3703.9307 | 350 | -223.0157 | 16 | 789.5 | 10 | 0 | -103 | 8021.07
2009-10-12 03:05 | 60.024 | 3704.9473 | 350 | -223.0157 | 16 | 790 | 10 | 0 | -103 | 8021.4
2009-10-12 03:05 | 60.025 | 3704.208 | 350 | -223.0157 | 16 | 790.5 | 10 | 0 | -103 | 8021.73
2009-10-12 03:05 | 60.023 | 3703.5413 | 350 | -223.0157 | 16 | 791 | 10 | 0 | -103 | 8022.06
2009-10-12 03:05 | 60.024 | 3703.1602 | 350 | -223.0157 | 16 | 791.5 | 10 | 0 | -103 | 8022.39
2009-10-12 03:05 | 60.02 | 3703.3975 | 350 | -223.0157 | 16 | 792 | 10 | 0 | -103 | 8022.72
2009-10-12 03:05 | 60.018 | 3704.3765 | 350 | -223.0157 | 16 | 792.5 | 10 | 0 | -103 | 8023.05
2009-10-12 03:05 | 60.013 | 3705.4412 | 350 | -223.0157 | 16 | 793 | 10 | 0 | -103 | 8023.38
2009-10-12 03:05 | 60.008 | 3706.9949 | 350 | -223.0157 | 16 | 793.5 | 10 | 0 | -103 | 8023.71
2009-10-12 03:05 | 60.012 | 3710.072 | 350 | -223.0157 | 16 | 794 | 10 | 0 | -103 | 8024.04
2009-10-12 03:05 | 60.017 | 3707.9707 | 350 | -223.0157 | 16 | 794.5 | 10 | 0 | -103 | 8024.37
2009-10-12 03:05 | 60.019 | 3707.7671 | 350 | -223.0157 | 16 | 795 | 10 | 0 | -103 | 8024.7
2009-10-12 03:05 | 60.019 | 3707.6094 | 350 | -223.0157 | 16 | 795.5 | 10 | 0 | -103 | 8025.03
2009-10-12 03:05 | 60.015 | 3708.8311 | 350 | -223.0157 | 16 | 796 | 10 | 0 | -103 | 8025.36
2009-10-12 03:05 | 60.016 | 3709.4646 | 350 | -223.0157 | 16 | 796.5 | 10 | 0 | -103 | 8025.69
2009-10-12 03:05 | 60.015 | 3709.8135 | 350 | -223.0157 | 16 | 797 | 10 | 0 | -103 | 8026.02
2009-10-12 03:05 | 60.016 | 3709.8169 | 350 | -223.0157 | 16 | 797.5 | 10 | 0 | -103 | 8026.35
2009-10-12 03:05 | 60.014 | 3709.9905 | 350 | -223.0157 | 16 | 798 | 10 | 0 | -103 | 8026.68
2009-10-12 03:05 | 60.016 | 3709.0938 | 350 | -223.0157 | 16 | 798.5 | 10 | 0 | -103 | 8027.01
2009-10-12 03:05 | 60.018 | 3709.6416 | 350 | -223.0157 | 16 | 799 | 10 | 0 | -103 | 8027.34
2009-10-12 03:05 | 60.019 | 3709.8115 | 350 | -223.0157 | 16 | 799.5 | 10 | 0 | -103 | 8027.67
2009-10-12 03:05 | 60.016 | 3709.9331 | 350 | -223.0157 | 16 | 800 | 10 | 0 | -103 | 8028
2009-10-12 03:05 | 60.014 | 3710.6768 | 350 | -223.0157 | 16 | 800.5 | 10 | 0 | -103 | 8028.33
2009-10-12 03:05 | 60.014 | 3710.5911 | 350 | -223.0157 | 16 | 801 | 10 | 0 | -103 | 8028.66
2009-10-12 03:05 | 60.018 | 3709.3545 | 350 | -223.0157 | 16 | 801.5 | 10 | 0 | -103 | 8028.99
2009-10-12 03:05 | 60.022 | 3707.696 | 350 | -223.0157 | 16 | 802 | 10 | 0 | -103 | 8029.32
2009-10-12 03:06 | 60.023 | 3707.3804 | 350 | -223.0157 | 16 | 802.5 | 10 | 0 | -103 | 8029.65
2009-10-12 03:06 | 60.024 | 3707.1201 | 350 | -223.0157 | 16 | 803 | 10 | 0 | -103 | 8029.98
2009-10-12 03:06 | 60.026 | 3706.99 | 350 | -223.0157 | 16 | 803.5 | 10 | 0 | -103 | 8030.31
2009-10-12 03:06 | 60.026 | 3705.8481 | 350 | -223.0157 | 16 | 804 | 10 | 0 | -103 | 8030.64
2009-10-12 03:06 | 60.024 | 3704.1851 | 350 | -223.0157 | 16 | 804.5 | 10 | 0 | -103 | 8030.97
2009-10-12 03:06 | 60.022 | 3704.4058 | 350 | -223.0157 | 16 | 805 | 10 | 0 | -103 | 8031.3
2009-10-12 03:06 | 60.02 | 3704.9626 | 350 | -223.0157 | 16 | 805.5 | 10 | 0 | -103 | 8031.63
2009-10-12 03:06 | 60.019 | 3706.5674 | 350 | -223.0157 | 16 | 806 | 10 | 0 | -103 | 8031.96
2009-10-12 03:06 | 60.022 | 3705.5159 | 350 | -223.0157 | 16 | 806.5 | 10 | 0 | -103 | 8032.29
2009-10-12 03:06 | 60.025 | 3704.8687 | 350 | -223.0157 | 16 | 807 | 10 | 0 | -103 | 8032.62
2009-10-12 03:06 | 60.028 | 3704.4285 | 350 | -223.0157 | 16 | 807.5 | 10 | 0 | -103 | 8032.95
2009-10-12 03:06 | 60.03 | 3704.7734 | 350 | -223.0157 | 16 | 808 | 10 | 0 | -103 | 8033.28
2009-10-12 03:06 | 60.031 | 3703.5317 | 350 | -223.0157 | 16 | 808.5 | 10 | 0 | -103 | 8033.61
2009-10-12 03:06 | 60.029 | 3702.6855 | 350 | -223.0157 | 16 | 809 | 10 | 0 | -103 | 8033.94
2009-10-12 03:06 | 60.026 | 3702.093 | 350 | -223.0157 | 16 | 809.5 | 10 | 0 | -103 | 8034.27
2009-10-12 03:06 | 60.026 | 3703.1692 | 350 | -223.0157 | 16 | 810 | 10 | 0 | -103 | 8034.6
2009-10-12 03:06 | 60.029 | 3703.6755 | 350 | -223.0157 | 16 | 810.5 | 10 | 0 | -103 | 8034.93
2009-10-12 03:06 | 60.03 | 3701.5195 | 350 | -223.0157 | 16 | 811 | 10 | 0 | -103 | 8035.26
2009-10-12 03:06 | 60.033 | 3700.1062 | 350 | -223.0157 | 16 | 811.5 | 10 | 0 | -103 | 8035.59
2009-10-12 03:06 | 60.03 | 3698.2217 | 350 | -223.0157 | 16 | 812 | 10 | 0 | -103 | 8035.92
2009-10-12 03:06 | 60.022 | 3698.0088 | 350 | -223.0157 | 16 | 812.5 | 10 | 0 | -103 | 8036.25
2009-10-12 03:06 | 60.016 | 3700.2798 | 350 | -223.0157 | 16 | 813 | 10 | 0 | -103 | 8036.58
2009-10-12 03:06 | 60.019 | 3703.1924 | 350 | -223.0157 | 16 | 813.5 | 10 | 0 | -103 | 8036.91
2009-10-12 03:06 | 60.03 | 3703.8147 | 350 | -223.0157 | 16 | 814 | 10 | 0 | -103 | 8037.24
2009-10-12 03:06 | 60.028 | 3701.8633 | 350 | -223.0157 | 16 | 814.5 | 10 | 0 | -103 | 8037.57
2009-10-12 03:06 | 60.021 | 3699.9561 | 350 | -223.0157 | 16 | 815 | 10 | 0 | -103 | 8037.9
2009-10-12 03:06 | 60.015 | 3700.8157 | 350 | -223.0157 | 16 | 815.5 | 10 | 0 | -103 | 8038.23
2009-10-12 03:06 | 60.015 | 3703.8022 | 350 | -223.0157 | 16 | 816 | 10 | 0 | -103 | 8038.56
2009-10-12 03:06 | 60.012 | 3706.9434 | 350 | -223.0157 | 16 | 816.5 | 10 | 0 | -103 | 8038.89
2009-10-12 03:06 | 60.011 | 3708.5273 | 350 | -223.0157 | 16 | 817 | 10 | 0 | -103 | 8039.22
2009-10-12 03:06 | 60.014 | 3707.4895 | 350 | -223.0157 | 16 | 817.5 | 10 | 0 | -103 | 8039.55
2009-10-12 03:07 | 60.013 | 3707.6475 | 350 | -223.0157 | 16 | 818 | 10 | 0 | -103 | 8039.88
2009-10-12 03:07 | 60.014 | 3706.9912 | 350 | -223.0157 | 16 | 818.5 | 10 | 0 | -103 | 8040.21
2009-10-12 03:07 | 60.016 | 3707.4949 | 350 | -223.0157 | 16 | 819 | 10 | 0 | -103 | 8040.54
2009-10-12 03:07 | 60.016 | 3705.5845 | 350 | -223.0157 | 16 | 819.5 | 10 | 0 | -103 | 8040.87
2009-10-12 03:07 | 60.015 | 3705.3979 | 350 | -223.0157 | 16 | 820 | 10 | 0 | -103 | 8041.2
2009-10-12 03:07 | 60.013 | 3707.1201 | 350 | -223.0157 | 16 | 820.5 | 10 | 0 | -103 | 8041.53
2009-10-12 03:07 | 60.007 | 3709.144 | 350 | -223.0157 | 16 | 821 | 10 | 0 | -103 | 8041.86
2009-10-12 03:07 | 59.997 | 3708.9895 | 350 | -223.0157 | 16 | 821.5 | 10 | 0 | -103 | 8042.19
2009-10-12 03:07 | 59.994 | 3708.291 | 350 | -223.0157 | 16 | 822 | 10 | 0 | -103 | 8042.52
2009-10-12 03:07 | 59.993 | 3706.1926 | 350 | -223.0157 | 16 | 822.5 | 10 | 0 | -103 | 8042.85
2009-10-12 03:07 | 59.99 | 3707.3037 | 350 | -223.0157 | 16 | 823 | 10 | 0 | -103 | 8043.18
2009-10-12 03:07 | 59.993 | 3707.9033 | 350 | -223.0157 | 16 | 823.5 | 10 | 0 | -103 | 8043.51
2009-10-12 03:07 | 59.994 | 3706.7603 | 350 | -223.0157 | 16 | 824 | 10 | 0 | -103 | 8043.84
2009-10-12 03:07 | 59.993 | 3706.9211 | 350 | -223.0157 | 16 | 824.5 | 10 | 0 | -103 | 8044.17
2009-10-12 03:07 | 59.994 | 3706.6831 | 350 | -223.0157 | 16 | 825 | 10 | 0 | -103 | 8044.5
2009-10-12 03:07 | 59.993 | 3706.8879 | 350 | -223.0157 | 16 | 825.5 | 10 | 0 | -103 | 8044.83
2009-10-12 03:07 | 59.996 | 3704.9336 | 350 | -223.0157 | 16 | 826 | 10 | 0 | -103 | 8045.16
2009-10-12 03:07 | 59.988 | 3705.6777 | 350 | -223.0157 | 16 | 826.5 | 10 | 0 | -103 | 8045.49
2009-10-12 03:07 | 59.985 | 3706.481 | 350 | -223.0157 | 16 | 827 | 10 | 0 | -103 | 8045.82
2009-10-12 03:07 | 59.983 | 3707.0713 | 350 | -223.0157 | 16 | 827.5 | 10 | 0 | -103 | 8046.15
2009-10-12 03:07 | 59.982 | 3706.6963 | 350 | -223.0157 | 16 | 828 | 10 | 0 | -103 | 8046.48
2009-10-12 03:07 | 59.98 | 3707.4785 | 350 | -223.0157 | 16 | 828.5 | 10 | 0 | -103 | 8046.81
2009-10-12 03:07 | 59.977 | 3708.2458 | 350 | -223.0157 | 16 | 829 | 10 | 0 | -103 | 8047.14
2009-10-12 03:07 | 59.981 | 3709.4358 | 350 | -223.0157 | 16 | 829.5 | 10 | 0 | -103 | 8047.47
2009-10-12 03:07 | 59.982 | 3710.4194 | 350 | -223.0157 | 16 | 830 | 10 | 0 | -103 | 8047.8
2009-10-12 03:07 | 59.978 | 3710.1338 | 350 | -223.0157 | 16 | 830.5 | 10 | 0 | -103 | 8048.13
2009-10-12 03:07 | 59.98 | 3708.7078 | 350 | -223.0157 | 16 | 831 | 10 | 0 | -103 | 8048.46
2009-10-12 03:07 | 59.98 | 3710.0239 | 350 | -223.0157 | 16 | 831.5 | 10 | 0 | -103 | 8048.79
2009-10-12 03:07 | 59.977 | 3709.1919 | 350 | -223.0157 | 16 | 832 | 10 | 0 | -103 | 8049.12
2009-10-12 03:08 | 59.98 | 3708.3354 | 350 | -223.0157 | 16 | 832.5 | 10 | 0 | -103 | 8049.45
2009-10-12 03:08 | 59.983 | 3709.3994 | 350 | -223.0157 | 16 | 833 | 10 | 0 | -103 | 8049.78
2009-10-12 03:08 | 59.984 | 3707.9114 | 350 | -223.0157 | 16 | 833.5 | 10 | 0 | -103 | 8050.11
2009-10-12 03:08 | 59.981 | 3709.0039 | 350 | -223.0157 | 16 | 834 | 10 | 0 | -103 | 8050.44
2009-10-12 03:08 | 59.981 | 3707.6382 | 350 | -223.0157 | 16 | 834.5 | 10 | 0 | -103 | 8050.77
2009-10-12 03:08 | 59.98 | 3709.689 | 350 | -223.0157 | 16 | 835 | 10 | 0 | -103 | 8051.1
2009-10-12 03:08 | 59.981 | 3708.9453 | 350 | -223.0157 | 16 | 835.5 | 10 | 0 | -103 | 8051.43
2009-10-12 03:08 | 59.981 | 3706.541 | 350 | -223.0157 | 16 | 836 | 10 | 0 | -103 | 8051.76
2009-10-12 03:08 | 59.981 | 3711.2563 | 350 | -223.0157 | 16 | 836.5 | 10 | 0 | -103 | 8052.09
2009-10-12 03:08 | 59.98 | 3711.3621 | 350 | -223.0157 | 16 | 837 | 10 | 0 | -103 | 8052.42
2009-10-12 03:08 | 59.978 | 3712.3032 | 350 | -223.0157 | 16 | 837.5 | 10 | 0 | -103 | 8052.75
2009-10-12 03:08 | 59.978 | 3712.0122 | 350 | -223.0157 | 16 | 838 | 10 | 0 | -103 | 8053.08
2009-10-12 03:08 | 59.979 | 3711.7034 | 350 | -223.0157 | 16 | 838.5 | 10 | 0 | -103 | 8053.41
2009-10-12 03:08 | 59.978 | 3712.0928 | 350 | -223.0157 | 16 | 839 | 10 | 0 | -103 | 8053.74
2009-10-12 03:08 | 59.976 | 3713.9917 | 350 | -223.0157 | 16 |  |  |  |  | 8054.07
2009-10-12 03:08 | 59.976 | 3714.6121 | 350 | -223.0157 | 16 |  |  |  |  | 8054.4
2009-10-12 03:08 | 59.975 | 3715.0835 | 350 | -223.0157 | 16 |  |  |  |  | 8054.73
2009-10-12 03:08 | 59.976 | 3715.3228 | 350 | -223.0157 | 16 |  |  |  |  | 8055.06
2009-10-12 03:08 | 59.975 | 3714.7939 | 350 | -223.0157 | 16 |  |  |  |  | 8055.39
2009-10-12 03:08 | 59.979 | 3714.7173 | 350 | -223.0157 | 16 |  |  |  |  | 8055.72
2009-10-12 03:08 | 59.978 | 3715.1614 | 350 | -223.0157 | 16 |  |  |  |  | 8056.05
2009-10-12 03:08 | 59.975 | 3715.0012 | 350 | -223.0157 | 16 |  |  |  |  | 8056.38
2009-10-12 03:08 | 59.976 | 3713.9963 | 350 | -223.0157 | 16 |  |  |  |  | 8056.71
2009-10-12 03:08 | 59.981 | 3714.0627 | 350 | -223.0157 | 16 |  |  |  |  | 8057.04
2009-10-12 03:08 | 59.977 | 3714.3347 | 350 | -223.0157 | 16 |  |  |  |  | 8057.37
2009-10-12 03:08 | 59.975 | 3715.6311 | 350 | -223.0157 | 16 |  |  |  |  | 8057.7
2009-10-12 03:08 | 59.976 | 3715.6885 | 350 | -223.0157 | 16 |  |  |  |  | 8058.03
2009-10-12 03:08 | 59.979 | 3715.5674 | 350 | -223.0157 | 16 |  |  |  |  | 8058.36
2009-10-12 03:08 | 59.98 | 3715.7246 | 350 | -223.0157 | 16 |  |  |  |  | 8058.69
2009-10-12 03:08 | 59.979 | 3714.8481 | 350 | -223.0157 | 16 |  |  |  |  | 8059.02
2009-10-12 03:08 | 59.978 | 3713.1416 | 350 | -223.0157 | 16 |  |  |  |  | 8059.35
2009-10-12 03:09 | 59.979 | 3713.3584 | 350 | -223.0157 | 16 |  |  |  |  | 8059.68
2009-10-12 03:09 | 59.982 | 3712.2747 | 350 | -223.0157 | 16 |  |  |  |  | 8060.01
2009-10-12 03:09 | 59.983 | 3712.6194 | 350 | -223.0157 | 16 |  |  |  |  | 8060.34
2009-10-12 03:09 | 59.987 | 3712.1526 | 350 | -223.0157 | 16 |  |  |  |  | 8060.67
2009-10-12 03:09 | 59.988 | 3710.0503 | 350 | -223.0157 | 16 |  |  |  |  | 8061
2009-10-12 03:09 | 59.984 | 3709.0815 | 350 | -223.0157 | 16 |  |  |  |  | 8061.33
2009-10-12 03:09 | 59.98 | 3710.4719 | 350 | -223.0157 | 16 |  |  |  |  | 8061.66
2009-10-12 03:09 | 59.979 | 3710.6235 | 350 | -223.0157 | 16 |  |  |  |  | 8061.99
2009-10-12 03:09 | 59.98 | 3710.9463 | 350 | -223.0157 | 16 |  |  |  |  | 8062.32
2009-10-12 03:09 | 59.979 | 3710.1997 | 350 | -223.0157 | 16 |  |  |  |  | 8062.65
2009-10-12 03:09 | 59.978 | 3710.4746 | 350 | -223.0157 | 16 |  |  |  |  | 8062.98
2009-10-12 03:09 | 59.975 | 3709.4622 | 350 | -223.0157 | 16 |  |  |  |  | 8063.31
2009-10-12 03:09 | 59.979 | 3710.803 | 350 | -223.0157 | 16 |  |  |  |  | 8063.64
2009-10-12 03:09 | 59.982 | 3709.2859 | 350 | -223.0157 | 16 |  |  |  |  | 8063.97
2009-10-12 03:09 | 59.983 | 3710.573 | 350 | -223.0157 | 16 |  |  |  |  | 8064.3
2009-10-12 03:09 | 59.983 | 3709.5251 | 350 | -223.0157 | 16 |  |  |  |  | 8064.63
2009-10-12 03:09 | 59.985 | 3708.3711 | 350 | -223.0157 | 16 |  |  |  |  | 8064.96
2009-10-12 03:09 | 59.99 | 3708.5273 | 350 | -223.0157 | 16 |  |  |  |  | 8065.29
2009-10-12 03:09 | 59.987 | 3706.512 | 350 | -223.0157 | 16 |  |  |  |  | 8065.62
2009-10-12 03:09 | 59.984 | 3707.4905 | 350 | -223.0157 | 16 |  |  |  |  | 8065.95
2009-10-12 03:09 | 59.976 | 3708.9624 | 350 | -223.0157 | 16 |  |  |  |  | 8066.28
2009-10-12 03:09 | 59.979 | 3709.894 | 350 | -223.0157 | 16 |  |  |  |  | 8066.61
2009-10-12 03:09 | 59.985 | 3712.3035 | 350 | -223.0157 | 16 |  |  |  |  | 8066.94
2009-10-12 03:09 | 59.983 | 3711.3501 | 350 | -223.0157 | 16 |  |  |  |  | 8067.27
2009-10-12 03:09 | 59.979 | 3711.6272 | 350 | -223.0157 | 16 |  |  |  |  | 8067.6
2009-10-12 03:09 | 59.981 | 3712.0762 | 350 | -223.0157 | 16 |  |  |  |  | 8067.93
2009-10-12 03:09 | 59.978 | 3712.3926 | 350 | -223.0157 | 16 |  |  |  |  | 8068.26
2009-10-12 03:09 | 59.975 | 3712.9985 | 350 | -223.0157 | 16 |  |  |  |  | 8068.59
2009-10-12 03:09 | 59.978 | 3713.5103 | 350 | -223.0157 | 16 |  |  |  |  | 8068.92
2009-10-12 03:10 | 59.989 | 3716.6257 | 350 | -223.0157 | 16 |  |  |  |  | 8069.25
2009-10-12 03:10 | 59.999 | 3715.4429 | 350 | -223.0157 | 16 |  |  |  |  | 8069.58
2009-10-12 03:10 | 59.994 | 3712.0918 | 350 | -223.0157 | 16 |  |  |  |  | 8069.91
2009-10-12 03:10 | 59.989 | 3713.906 | 350 | -223.0157 | 16 |  |  |  |  | 8070.24
2009-10-12 03:10 | 59.986 | 3714.8936 | 350 | -223.0157 | 16 |  |  |  |  | 8070.57
2009-10-12 03:10 | 59.984 | 3714.9531 | 350 | -223.0157 | 16 |  |  |  |  | 8070.9
2009-10-12 03:10 | 59.983 | 3716.1216 | 350 | -223.0157 | 16 |  |  |  |  | 8071.23
2009-10-12 03:10 | 59.982 | 3716.3083 | 350 | -223.0157 | 16 |  |  |  |  | 8071.56
2009-10-12 03:10 | 59.98 | 3715.4385 | 350 | -223.0157 | 16 |  |  |  |  | 8071.89
2009-10-12 03:10 | 59.99 | 3714.7637 | 350 | -223.0157 | 16 |  |  |  |  | 8072.22
2009-10-12 03:10 | 59.995 | 3714.7141 | 350 | -223.0157 | 16 |  |  |  |  | 8072.55
2009-10-12 03:10 | 59.995 | 3715.0676 | 350 | -223.0157 | 16 |  |  |  |  | 8072.88
2009-10-12 03:10 | 59.99 | 3715.9268 | 350 | -223.0157 | 16 |  |  |  |  | 8073.21
2009-10-12 03:10 | 59.989 | 3715.7913 | 350 | -223.0157 | 16 |  |  |  |  | 8073.54
2009-10-12 03:10 | 59.991 | 3716.2847 | 350 | -223.0157 | 16 |  |  |  |  | 8073.87
2009-10-12 03:10 | 59.996 | 3715.3245 | 350 | -223.0157 | 16 |  |  |  |  | 8074.2
2009-10-12 03:10 | 60 | 3714.4604 | 350 | -223.0157 | 16 |  |  |  |  | 8074.53
2009-10-12 03:10 | 60.002 | 3711.7085 | 350 | -223.0157 | 16 |  |  |  |  | 8074.86
2009-10-12 03:10 | 60.004 | 3712.6975 | 350 | -223.0157 | 16 |  |  |  |  | 8075.19
2009-10-12 03:10 | 60.004 | 3712.8506 | 350 | -223.0157 | 16 |  |  |  |  | 8075.52
2009-10-12 03:10 | 60.002 | 3713.3616 | 350 | -223.0157 | 16 |  |  |  |  | 8075.85
2009-10-12 03:10 | 59.999 | 3716.6414 | 350 | -223.0157 | 16 |  |  |  |  | 8076.18
2009-10-12 03:10 | 59.998 | 3718.2925 | 350 | -223.0157 | 16 |  |  |  |  | 8076.51
2009-10-12 03:10 | 59.995 | 3719.0791 | 350 | -223.0157 | 16 |  |  |  |  | 8076.84
2009-10-12 03:10 | 59.996 | 3718.2334 | 350 | -223.0157 | 16 |  |  |  |  | 8077.17
2009-10-12 03:10 | 60.001 | 3717.8152 | 350 | -223.0157 | 16 |  |  |  |  | 8077.5
2009-10-12 03:10 | 60.002 | 3717.8887 | 350 | -223.0157 | 16 |  |  |  |  | 8077.83
2009-10-12 03:10 | 60.001 | 3718.5603 | 350 | -223.0157 | 16 |  |  |  |  | 8078.16
2009-10-12 03:10 | 60.003 | 3718.1953 | 350 | -223.0157 | 16 |  |  |  |  | 8078.49
2009-10-12 03:10 | 60.005 | 3719.0212 | 350 | -223.0157 | 16 |  |  |  |  | 8078.82
2009-10-12 03:10 | 60.004 | 3718.8213 | 350 | -223.0157 | 16 |  |  |  |  | 8079.15
2009-10-12 03:11 | 60.004 | 3719.8975 | 350 | -223.0157 | 16 |  |  |  |  | 8079.48
2009-10-12 03:11 | 60.004 | 3719.2993 | 350 | -223.0157 | 16 |  |  |  |  | 8079.81
2009-10-12 03:11 | 60.006 | 3719.6428 | 350 | -223.0157 | 16 |  |  |  |  | 8080.14
2009-10-12 03:11 | 60.003 | 3719.5273 | 350 | -223.0157 | 16 |  |  |  |  | 8080.47
2009-10-12 03:11 | 60.005 | 3719.731 | 350 | -223.0157 | 16 |  |  |  |  | 8080.8
2009-10-12 03:11 | 60.006 | 3720.2786 | 350 | -223.0157 | 16 |  |  |  |  | 8081.13
2009-10-12 03:11 | 60.009 | 3718.5796 | 350 | -223.0157 | 16 |  |  |  |  | 8081.46
2009-10-12 03:11 | 60.009 | 3718.9761 | 350 | -223.0157 | 16 |  |  |  |  | 8081.79
2009-10-12 03:11 | 60.01 | 3718.9822 | 350 | -223.0157 | 16 |  |  |  |  | 8082.12
2009-10-12 03:11 | 60.009 | 3720.0337 | 350 | -223.0157 | 16 |  |  |  |  | 8082.45
2009-10-12 03:11 | 60.013 | 3720.6089 | 350 | -223.0157 | 16 |  |  |  |  | 8082.78
2009-10-12 03:11 | 60.015 | 3720.8105 | 350 | -223.0157 | 16 |  |  |  |  | 8083.11
2009-10-12 03:11 | 60.014 | 3721.2388 | 350 | -223.0157 | 16 |  |  |  |  | 8083.44
2009-10-12 03:11 | 60.009 | 3720.3804 | 350 | -223.0157 | 16 |  |  |  |  | 8083.77
2009-10-12 03:11 | 60.009 | 3719.4473 | 350 | -223.0157 | 16 |  |  |  |  | 8084.1
2009-10-12 03:11 | 60.008 | 3720.8071 | 350 | -223.0157 | 16 |  |  |  |  | 8084.43
2009-10-12 03:11 | 60.011 | 3721.2722 | 350 | -223.0157 | 16 |  |  |  |  | 8084.76
2009-10-12 03:11 | 60.01 | 3720.5916 | 350 | -223.0157 | 16 |  |  |  |  | 8085.09
2009-10-12 03:11 | 60.009 | 3721.2446 | 350 | -223.0157 | 16 |  |  |  |  | 8085.42
2009-10-12 03:11 | 60.013 | 3721.5938 | 350 | -223.0157 | 16 |  |  |  |  | 8085.75
2009-10-12 03:11 | 60.013 | 3722.1763 | 350 | -223.0157 | 16 |  |  |  |  | 8086.08
2009-10-12 03:11 | 60.014 | 3721.999 | 350 | -223.0157 | 16 |  |  |  |  | 8086.41
2009-10-12 03:11 | 60.014 | 3721.646 | 350 | -223.0157 | 16 |  |  |  |  | 8086.74
2009-10-12 03:11 | 60.012 | 3721.6777 | 350 | -223.0157 | 16 |  |  |  |  | 8087.07
2009-10-12 03:11 | 60.01 | 3720.8596 | 350 | -223.0157 | 16 |  |  |  |  | 8087.4
2009-10-12 03:11 | 60.011 | 3721.6453 | 350 | -223.0157 | 16 |  |  |  |  | 8087.73
2009-10-12 03:11 | 60.007 | 3723.8157 | 350 | -223.0157 | 16 |  |  |  |  | 8088.06
2009-10-12 03:11 | 60.003 | 3725.0703 | 350 | -223.0157 | 16 |  |  |  |  | 8088.39
2009-10-12 03:11 | 60.001 | 3724.656 | 350 | -223.0157 | 16 |  |  |  |  | 8088.72
2009-10-12 03:11 | 60 | 3724.8694 | 350 | -223.0157 | 16 |  |  |  |  | 8089.05
2009-10-12 03:12 | 59.998 | 3724.6606 | 350 | -223.0157 | 16 |  |  |  |  | 8089.38
2009-10-12 03:12 | 59.998 | 3723.696 | 350 | -223.0157 | 16 |  |  |  |  | 8089.71
2009-10-12 03:12 | 59.999 | 3723.5801 | 350 | -223.0157 | 16 |  |  |  |  | 8090.04
2009-10-12 03:12 | 60.002 | 3723.4053 | 350 | -223.0157 | 16 |  |  |  |  | 8090.37
2009-10-12 03:12 | 60.003 | 3721.8789 | 350 | -223.0157 | 16 |  |  |  |  | 8090.7
2009-10-12 03:12 | 60.003 | 3722.4014 | 350 | -223.0157 | 16 |  |  |  |  | 8091.03
2009-10-12 03:12 | 59.999 | 3722.9065 | 350 | -223.0157 | 16 |  |  |  |  | 8091.36
2009-10-12 03:12 | 59.998 | 3724.1421 | 350 | -223.0157 | 16 |  |  |  |  | 8091.69
2009-10-12 03:12 | 60.001 | 3723.6504 | 350 | -223.0157 | 16 |  |  |  |  | 8092.02
2009-10-12 03:12 | 59.995 | 3723.2012 | 350 | -223.0157 | 16 |  |  |  |  | 8092.35
2009-10-12 03:12 | 59.989 | 3723.6389 | 350 | -223.0157 | 16 |  |  |  |  | 8092.68
2009-10-12 03:12 | 59.987 | 3723.8813 | 350 | -223.0157 | 16 |  |  |  |  | 8093.01
2009-10-12 03:12 | 59.988 | 3724.6543 | 350 | -223.0157 | 16 |  |  |  |  | 8093.34
2009-10-12 03:12 | 59.988 | 3725.3608 | 350 | -223.0157 | 16 |  |  |  |  | 8093.67
2009-10-12 03:12 | 59.99 | 3724.9438 | 350 | -223.0157 | 16 |  |  |  |  | 8094

## Entry Data
Balancing Authority Name: | My BA
Balancing Authority Frequency Response Obligation (FRO from FRS Form 1) | -80
Note: See "Instruction" tab for more detailed instructions.
Step 1. | Copy and Paste Event Data into the appropriate cells of the "Data" worksheet.
Maintain date and time format of mm/dd/yy hh:mm:ss.
Step 2. | Determine Time of T(0) and edit formula in cell "C8" to reference the correct row of the "Data" worksheet. | 40098.1024
T(0) is the first change in frequency of about 0.010 Hz (10 mHz) which should be the first scan of frequency data of the event.
Step 3. | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1062
Step 4. | Enter MW output of generator or load that caused event (+ for gen loss, - for load loss) | 633 | MW
(Value from NERC Event List. If multiple units, enter total MW loss.)
If MW loss value is not known, enter a default 1000 MW.
Step 5. | Hit the big blue button to copy your data for pasting into FRS Form 1 "BA Event Data" worksheet.
Step 6. | Paste data into "FRS Form 1" in the appropriate row on the "BA Event Data" worksheet.
Step 7. | Save this workbook using the following file name format:MyBA_yymmdd_hhmm_FRS_Form2.xlsm
| 2009-10-12 02:27 | Date yymmdd
| 40098.1024 | Time hh:ss of T(0)
Where "MyBA" = your BA mnemonic
Copy Form 2 data for Pasting into Form 1
Note on C8: Cell "C8": Observe the first change in frequency that identifies the beginning of the event. Look in column "B" of the "Data" worksheet. Select and edit the formula in this cell ("=Data!Axxx") to reference that row number in the "Data" sheet of this first change in frequency where xxx is that row number.
Note on C11: Cell "C11": Similar to identifying the end of a DCS event but only looking at frequency, observe frequency following the beginning of the event. When actual frequency recovers to 60.00 Hz or to the pre-event frequency, edit the formula in this cell to reference that row number in the "Data" worksheet that this occurs. ("=Data!Axxx")

## IPFR (hidden)
IPFR = Interconnection Primary Frequency Response

## Evaluation
scan rate | 2 | seconds |  |  | Date: | 2009-10-12 02:27 |  |  | Balancing Authority | My BA | [10 empty] | A Point | 40098.1024 |  |  |  |  | A Point | 40098.1024 | [13 empty] | Non-Conforming Load sign convention | + | (Data is positive for Load then enter "+" else "-" | [11 empty] | Date: | 2009-10-12 02:27 | [12 empty] | Date: | 2009-10-12 02:27 | [12 empty] | Date: | 2009-10-12 02:27 | [12 empty] | Date: | 2009-10-12 02:27 | [12 empty] | Date: | 2009-10-12 02:27
[5 empty] | Time of T(0) | 40098.1024 |  |  | Grid Nominal Frequency | 60 | Hz | [9 empty] | FPointA | 60.039 | 40098.1024 |  |  |  | FPointA | 60.039 | 40098.1024 | [26 empty] | Time of T(0) | 40098.1024 | [12 empty] | Time of T(0) | 40098.1024 | [12 empty] | Time of T(0) | 40098.1024 | [12 empty] | Time of T(0) | 40098.1024 | [12 empty] | Time of T(0) | 40098.1024
[5 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1062 |  |  | Capacity @ Droop for Minimum Performance | 2400 | MW | [9 empty] | A Value | 60.0421 |  |  |  |  | A Value | 60.0421 | [27 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1062 | [12 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1062 | [12 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1062 | [12 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1062 | [12 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1062
[5 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0421 | Hz |  | Droop Setting | 5% | 3 | Hz | [8 empty] | C Value | 59.836 | #N/A |  |  |  | C Value | 59.836 | #N/A | [26 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0421 | Hz | [11 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0421 | Hz | [11 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0421 | Hz | [11 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0421 | Hz | [11 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0421 | Hz
[5 empty] | Value B Post-Perturbation Average Frequency [T(+20 to T(+52)] | 59.8891 | Hz |  | Deadband Setting | 0 | Hz | [9 empty] | Delta FCA | -0.20613 |  |  |  |  | Delta FC | [28 empty] | Value B Post-Perturbation Average Frequency [T(+12 to T(+24)] | 59.8826 | Hz | [11 empty] | Value B Post-Perturbation Average Frequency [T(+18 to T(+30)] | 59.8844 | Hz | [11 empty] | Value B Post-Perturbation Average Frequency [T(+20 to T(+40)] | 59.8893 | Hz | [11 empty] | Value B Post-Perturbation Average Frequency [T(+18 to T(+52)] | 59.8883 | Hz | [11 empty] | Value B Post-Perturbation Average Frequency [T(+20 to T(+52)] | 59.8891 | Hz
[5 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15301 | Hz |  | Hz Span | 3 | Hz | [9 empty] | FR C | -307.0927 | MW/0.1 Hz | [32 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15955 | Hz | [11 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.1577 | Hz | [11 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15285 | Hz | [11 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15379 | Hz | [11 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15301 | Hz
[5 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3645.7271 | MW |  | Frequency Response Obligation (FRO) | -80 | MW/0.1 Hz | [9 empty] | Slope A-C dF/dT | #N/A | Hz/second |  |  |  |  | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | [18 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3645.7271 | MW | [11 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3645.7271 | MW | [11 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3645.7271 | MW | [11 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3645.7271 | MW | [11 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 3645.7271 | MW
[5 empty] | Value B Post-Perturbation Average Interchange MW [T(+20 to T(+52)] | 3788.3545 | MW | [13 empty] | C Value Maximum Resource Loss | 633 | [5 empty] | 12 to 24 sec | 12 to 24 sec | 18 to 30 sec | 18 to 30 sec | 20 to 40 sec | 20 to 40 sec | 18 to 52 sec | 18 to 52 sec | 20 to 52 sec | 20 to 52 sec | [18 empty] | Value B Post-Perturbation Average Interchange MW [T(+12 to T(+24)] | 3770.653 | MW | [11 empty] | Value B Post-Perturbation Average Interchange MW [T(+18 to T(+30)] | 3779.0294 | MW | [11 empty] | Value B Post-Perturbation Average Interchange MW [T(+20 to T(+40)] | 3783.8625 | MW | [11 empty] | Value B Post-Perturbation Average Interchange MW [T(+18 to T(+52)] | 3787.2724 | MW | [11 empty] | Value B Post-Perturbation Average Interchange MW [T(+20 to T(+52)] | 3788.3545 | MW
[5 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 142.6275 | MW | [13 empty] | Secondary C Value | No | n/a | Time |  |  | B Frequency Value | 59.8826 |  | 59.8844 |  | 59.8891 |  | 59.8883 |  | 59.8891 | [19 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 124.9259 | MW | [11 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 133.3023 | MW | [11 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 138.1355 | MW | [11 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 141.5454 | MW | [11 empty] | Pre to Post Perturbation Interchange Delta MW Actual | 142.6275 | MW
[5 empty] | Initial Performance Ramp Magnitude Adjustment | -15.4021 | MW | [19 empty] | Delta FB | -0.15955 | -397.1996 | -0.1577 | -401.67 | -0.15301 | -414.4045 | -0.15379 | -411.9963 | -0.15301 | -413.9515 | [18 empty] | Net Total Adjustments | 39.8657 | MW | [11 empty] | Net Total Adjustments | 43.076 | MW | [11 empty] | Net Total Adjustments | 45.8223 | MW | [11 empty] | Net Total Adjustments | 50.567 | MW | [11 empty] | Net Total Adjustments | 51.1955 | MW
[5 empty] | EPFR Pre-Perturbation Average | -33.7002 | MW | [19 empty] | Slope B dF/dT | -0.0079777 |  | -0.0078848 |  | -0.0076504 |  | -0.0076896 |  | -0.0076504 | [19 empty] | EPFR for FRO Pre-Perturbation Average | -33.7002 | MW | [11 empty] | EPFR for FRO Pre-Perturbation Average | -33.7002 | MW | [11 empty] | EPFR for FRO Pre-Perturbation Average | -33.7002 | MW | [11 empty] | EPFR for FRO Pre-Perturbation Average | -33.7002 | MW | [11 empty] | EPFR for FRO Pre-Perturbation Average | -33.7002 | MW
[5 empty] | EPFR Post-Perturbation Average | 88.7058 | MW | [19 empty] | RatioB-C | 77.4056 |  | 76.5046 |  | 74.2298 |  | 74.6103 |  | 74.2298 | [19 empty] | EPFR for FRO Post-Perturbation Average | 93.9427 | MW | [11 empty] | EPFR for FRO Post-Perturbation Average | 92.4569 | MW | [11 empty] | EPFR for FRO Post-Perturbation Average | 88.5814 | MW | [11 empty] | EPFR for FRO Post-Perturbation Average | 89.3333 | MW | [11 empty] | EPFR for FRO Post-Perturbation Average | 88.7058 | MW
[5 empty] | EPFR Delta | 122.406 | MW |  | TC (frequency response filter constant) | 0.35 | Time Constant for delayed delivery of PFR during Sustained Measure | [15 empty] | Sustainability Index | -0.017171 |  | -0.019029 |  | -0.023717 |  | -0.022933 |  | -0.023717 | [19 empty] | EPFR for FRO Delta | 127.6429 | MW | [11 empty] | EPFR for FRO Delta | 126.1571 | MW | [11 empty] | EPFR for FRO Delta | 122.2816 | MW | [11 empty] | EPFR for FRO Delta | 123.0334 | MW | [11 empty] | EPFR for FRO Delta | 122.406 | MW
[21 empty] | Tzero | 40098.1024 | [33 empty] | EPFR for FRO Adjusted | 167.5086 | MW | [11 empty] | EPFR for FRO Adjusted | 169.2331 | MW | [11 empty] | EPFR for FRO Adjusted | 168.1039 | MW | [11 empty] | EPFR for FRO Adjusted | 173.6005 | MW | [11 empty] | EPFR for FRO Adjusted | 173.6015 | MW
[21 empty] | FT+4 | 59.836 | [33 empty] | Pre JOU Dynamic Schedules MW | 350 |  |  |  | Pre-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre JOU Dynamic Schedules MW | 350 |  |  |  | Pre-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre JOU Dynamic Schedules MW | 350 | MW |  |  | Pre-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre JOU Dynamic Schedules MW | 350 | MW |  |  | Pre-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre JOU Dynamic Schedules MW | 350 | MW |  |  | Pre-Perturbation Bias Setting | -103 | MW/0.1 Hz
[9 empty] | Low Hz | Delta Hz Event | [10 empty] | FT+10 | 59.892 | [33 empty] | Pre Non-Conforming Load MW | 165.3359 |  |  |  | Post-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre Non-Conforming Load MW | 165.3359 |  |  |  | Post-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre Non-Conforming Load MW | 165.3359 | MW |  |  | Post-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre Non-Conforming Load MW | 165.3359 | MW |  |  | Post-Perturbation Bias Setting | -103 | MW/0.1 Hz | [6 empty] | Pre Non-Conforming Load MW | 165.3359 | MW |  |  | Post-Perturbation Bias Setting | -103 | MW/0.1 Hz
[9 empty] | 3764.4573 | Actual Interchange MW Average during frequency recovery period | [10 empty] | FT+20 | 59.883 | [33 empty] | Pre Pumped Hydro MW | 0 |  |  |  | EPFR for Bias Setting Pre-Perturbation Average | -43.389 | MW | [6 empty] | Pre Pumped Hydro MW | 0 |  |  |  | EPFR for Bias Setting Pre-Perturbation Average | -43.389 | MW | [6 empty] | Pre Pumped Hydro MW | 0 | MW |  |  | EPFR for Bias Setting Pre-Perturbation Average | -43.389 | MW | [6 empty] | Pre Pumped Hydro MW | 0 | MW |  |  | EPFR for Bias Setting Pre-Perturbation Average | -43.389 | MW | [6 empty] | Pre Pumped Hydro MW | 0 | MW |  |  | EPFR for Bias Setting Pre-Perturbation Average | -43.389 | MW
[9 empty] | 3774.7801 | Target Interchange MW Average during frequency recovery period | [10 empty] | FT+60 | 59.89 | [33 empty] | Pre Ramping Units MW | 229.25 |  |  |  | EPFR for Bias Setting Post-Perturbation Average | 120.9512 | MW | [6 empty] | Pre Ramping Units MW | 229.25 |  |  |  | EPFR for Bias Setting Post-Perturbation Average | 119.0383 | MW | [6 empty] | Pre Ramping Units MW | 229.25 | MW |  |  | EPFR for Bias Setting Post-Perturbation Average | 114.0486 | MW | [6 empty] | Pre Ramping Units MW | 229.25 | MW |  |  | EPFR for Bias Setting Post-Perturbation Average | 115.0166 | MW | [6 empty] | Pre Ramping Units MW | 229.25 | MW |  |  | EPFR for Bias Setting Post-Perturbation Average | 114.2087 | MW
|  |  | EPFR = Expected Primary Frequency Response |  | EPFR(Final) | 107.0039 | MW |  | 3719.6464 | Interchange Average Ramp MW during frequency recovery period | [8 empty] | Interconnection Evaluation | [36 empty] | Pre Transferred Frequency Response MW | -4.2125 |  |  |  | EPFR for Bias Setting Delta | 164.3402 | MW | [6 empty] | Pre Transferred Frequency Response MW | -4.2125 |  |  |  | EPFR for Bias Setting Delta | 162.4273 | MW | [6 empty] | Pre Transferred Frequency Response MW | -4.2125 | MW |  |  | EPFR for Bias Setting Delta | 157.4376 | MW | [6 empty] | Pre Transferred Frequency Response MW | -4.2125 | MW |  |  | EPFR for Bias Setting Delta | 158.4056 | MW | [6 empty] | Pre Transferred Frequency Response MW | -4.2125 | MW |  |  | EPFR for Bias Setting Delta | 157.5977 | MW
[5 empty] | MW Response in right direction for frequency delta | Yes |  |  | 3640.6821 | Actual MW @ T(-4) | [45 empty] | Pre Contingent BA Lost Generation MW | 15 |  |  |  | Primary Frequency Response Delivery of Bias | 76.02% | [7 empty] | Pre Contingent BA Lost Generation MW | 15 |  |  |  | Primary Frequency Response Delivery of Bias | 82.07% | [7 empty] | Pre Contingent BA Lost Generation MW | 15 | MW |  |  | Primary Frequency Response Delivery of Bias | 87.74% | [7 empty] | Pre Contingent BA Lost Generation MW | 15 | MW |  |  | Primary Frequency Response Delivery of Bias | 89.36% | [7 empty] | Pre Contingent BA Lost Generation MW | 15 | MW |  |  | Primary Frequency Response Delivery of Bias | 90.5%
[9 empty] | 92.162 | Starting and Ending Difference in Interchange MW during frequency recovery period (indicates ramp direction during recovery period) | [45 empty] | Sum of Pre Perturbation Adjustments | 755.3734 | [12 empty] | Sum of Pre Perturbation Adjustments | 755.3734 | [12 empty] | Sum of Pre Perturbation Adjustments | 755.3734 | MW | [11 empty] | Sum of Pre Perturbation Adjustments | 755.3734 | MW | [11 empty] | Sum of Pre Perturbation Adjustments | 755.3734 | MW
[9 empty] | 0:05 | Event Duration (h:mm:ss)
[9 empty] | No | Target MW Average minus MW @ T(-4) less than zero | [10 empty] | B Value Average Resource Loss | 633 | [33 empty] | Post JOU Dynamic Schedules MW | 335 |  |  |  | Pre-Perturbation BA Load | 7651.305 | MW | [6 empty] | Post JOU Dynamic Schedules MW | 335 |  |  |  | Pre-Perturbation BA Load | 7651.305 | MW | [6 empty] | Post JOU Dynamic Schedules MW | 335 | MW |  |  | Pre-Perturbation BA Load | 7651.305 | MW | [6 empty] | Post JOU Dynamic Schedules MW | 335 | MW |  |  | Pre-Perturbation BA Load | 7651.305 | MW | [6 empty] | Post JOU Dynamic Schedules MW | 335 | MW |  |  | Pre-Perturbation BA Load | 7651.305 | MW
[9 empty] | 134.098 | Interchange Target Relative Average Change - MW (Low Frequency Event) | [10 empty] | B Value Average LaaR Loss | 0 | [33 empty] | Post Non-Conforming Load MW | 212.1391 |  |  |  | Post-Perturbation BA Load | 7632 | MW | [6 empty] | Post Non-Conforming Load MW | 213.4637 |  |  |  | Post-Perturbation BA Load | 7632 | MW | [6 empty] | Post Non-Conforming Load MW | 213.0775 | MW |  |  | Post-Perturbation BA Load | 7632 | MW | [6 empty] | Post Non-Conforming Load MW | 213.9682 | MW |  |  | Post-Perturbation BA Load | 7632 | MW | [6 empty] | Post Non-Conforming Load MW | 214.1277 | MW |  |  | Post-Perturbation BA Load | 7632 | MW
[9 empty] | 123.7752 | Interchange Actual Relative Average Change - MW (Low Frequency Event) | [10 empty] | B Value Average Net Loss | 633 | [33 empty] | Post Pumped Hydro MW | 0.85714 |  |  |  | Pre to Post Perturbation BA Load Change | -19.305 | MW | [6 empty] | Post Pumped Hydro MW | 1.4286 |  |  |  | Pre to Post Perturbation BA Load Change | -19.305 | MW | [6 empty] | Post Pumped Hydro MW | 3.5455 | MW |  |  | Pre to Post Perturbation BA Load Change | -19.305 | MW | [6 empty] | Post Pumped Hydro MW | 6.0556 | MW |  |  | Pre to Post Perturbation BA Load Change | -19.305 | MW | [6 empty] | Post Pumped Hydro MW | 6.3529 | MW |  |  | Pre to Post Perturbation BA Load Change | -19.305 | MW
[9 empty] | No | Interchange Actual Average minus MW @ T(-4) less than zero | [45 empty] | Post Ramping Units MW | 235.5 |  |  |  | Load Dampening Frequency Response | -12.0994 | MW/0.1 Hz | [6 empty] | Post Ramping Units MW | 237 |  |  |  | Load Dampening Frequency Response | -12.2419 | MW/0.1 Hz | [6 empty] | Post Ramping Units MW | 238.5 | MW |  |  | Load Dampening Frequency Response | -12.6299 | MW/0.1 Hz | [6 empty] | Post Ramping Units MW | 239.75 | MW |  |  | Load Dampening Frequency Response | -12.5527 | MW/0.1 Hz | [6 empty] | Post Ramping Units MW | 240 | MW |  |  | Load Dampening Frequency Response | -12.617 | MW/0.1 Hz
[9 empty] | Yes | Interchange Average MW minus MW @ T(-4) greater than zero | [13 empty] | Interconnection Bias Total | [31 empty] | Post Transferred Frequency Response MW | 11.7428 |  |  |  | Load Dampening % of Total BA Frequency Response | 15.45% | [7 empty] | Post Transferred Frequency Response MW | 11.5571 |  |  |  | Load Dampening % of Total BA Frequency Response | 14.48% | [7 empty] | Post Transferred Frequency Response MW | 11.0727 | MW |  |  | Load Dampening % of Total BA Frequency Response | 13.98% | [7 empty] | Post Transferred Frequency Response MW | 11.1667 | MW |  |  | Load Dampening % of Total BA Frequency Response | 13.64% | [7 empty] | Post Transferred Frequency Response MW | 11.0882 | MW |  |  | Load Dampening % of Total BA Frequency Response | 13.54%
[9 empty] | Yes | Interchange Target MW Average minus MW @ T(-4) greater than zero | [13 empty] | EI | ERCOT | WECC | [29 empty] | Post Contingent BA Lost Generation MW | 0 | [12 empty] | Post Contingent BA Lost Generation MW | 0 | [12 empty] | Post Contingent BA Lost Generation MW | 0 | MW | [11 empty] | Post Contingent BA Lost Generation MW | 0 | MW | [11 empty] | Post Contingent BA Lost Generation MW | 0 | MW
[9 empty] | 41.9359 | Interchange Target Relative Average Change - MW (High Frequency Event) | [10 empty] | Interconnection Bias Setting | -660 |  | -6349 | -660 | -2024 | [29 empty] | Sum of Post Perturbation Adjustments | 795.2391 | [12 empty] | Sum of Post Perturbation Adjustments | 798.4493 | [12 empty] | Sum of Post Perturbation Adjustments | 801.1957 | MW | [11 empty] | Sum of Post Perturbation Adjustments | 805.9404 | MW | [11 empty] | Sum of Post Perturbation Adjustments | 806.5689 | MW
[9 empty] | 31.6131 | Interchange Actual Relative Average Change - MW (High Frequency Event) | [10 empty] | IPFR as a % of Bias Setting | 0% | [33 empty] | Net Total Adjustments MW | 39.8657 | [12 empty] | Net Total Adjustments MW | 43.076 | [12 empty] | Net Total Adjustments MW | 45.8223 | MW | [11 empty] | Net Total Adjustments MW | 50.567 | MW | [11 empty] | Net Total Adjustments MW | 51.1955 | MW
[9 empty] | Up | Ramp Direction during frequency recovery period | [10 empty] | Interconnection Total Energy | 37446 | 60.07%
[21 empty] | Interconnection Peak Energy | 62339 |  |  |  |  | Frequency and Interconnection Frequency Response @ different Average periods of B | [11 empty] | Frequency, Actual Interchange, Adjustment Data, Bias and Load used in the evaluation | [12 empty] | 12 to 24 second Average Period Evaluation | [13 empty] | 18 to 30 second Average Period Evaluation | [13 empty] | 20 to 40 second Average Period Evaluation | [13 empty] | 18 to 52 second Average Period Evaluation | [13 empty] | 20 to 52 second Average Period Evaluation
[5 empty] | Initial Response P.U. Performance | 1.3329 | P.U. |  | 0.92302 | P.U. Sustianed Response P.U. Performance | [45 empty] | Initial P.U. Performance for FRO | 0.97871 | P.U. | [11 empty] | Initial P.U. Performance for FRO | 1.0566 | P.U. | [11 empty] | Initial P.U. Performance for FRO | 1.1297 | P.U. | [11 empty] | Initial P.U. Performance for FRO | 1.1505 | P.U. | [11 empty] | Initial P.U. Performance for FRO | 1.1652 | P.U.
[56 empty] | Initial P.U. Performance Adjusted for FRO | 0.66639 | P.U. | [11 empty] | Initial P.U. Performance Adjusted for FRO | 0.71519 | P.U. | [11 empty] | Initial P.U. Performance Adjusted for FRO | 0.75492 | P.U. | [11 empty] | Initial P.U. Performance Adjusted for FRO | 0.73946 | P.U. | [11 empty] | Initial P.U. Performance Adjusted for FRO | 0.74696 | P.U.
[9 empty] | Initial | [6 empty] | Generator | Generator | Generator | Generator | Generator | Generator | Generator | LaaR | Total | Interconnection | FR B | [15 empty] | JOU | Non- |  |  | Transferred | Contingent | [7 empty] | JOU | Non- |  |  | Transferred | Contingent |  |  |  | Expected |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  |  | Expected |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  |  | Expected |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  |  | Expected |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  |  | Expected
[7 empty] | FRO |  | Measure |  |  | Average | Average |  | Average | Trip | Trip | Trip | Trip | Trip | Trip | Trip | Trip | Generation | Primary | 20 to 52 sec |  | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA | Expected |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA |  | Net |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA |  | Net |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA |  | Net |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA |  | Net |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA |  | Net
[7 empty] | (EPFR) | (TC) | Final |  |  | Output | Target |  | Ramp | MW | MW | MW | MW | MW | MW | MW | MW | Trip | Frequency | Average |  | 12 to 24 sec | 12 to 24 sec | 18 to 30 sec | 18 to 30 sec | 20 to 40 sec | 20 to 40 sec | 18 to 52 sec | 18 to 52 sec | 20 to 52 sec | 20 to 52 sec |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load | Primary |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load |  | Actual |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load |  | Actual |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load |  | Actual |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load |  | Actual |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load |  | Actual
|  |  |  | Value B |  |  | Expected | Delayed | Expected |  | Recovery | During | During | Recovery | During | [8 empty] | MW | Response | MW |  | Average | Average | Average | Average | Average | Average | Average | Average | Average | Average |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | Freq Response |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange
|  |  |  | 20 to 52 sec |  |  | Primary | Delivery | Primary | Average | Period | Recovery | Recovery | Period | Recovery | [12 empty] | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW
|  | Frequency | Interchange | Average | Average |  | Frequency | Frequency | Frequency | Ramp | Target | Period | Period | Ramp | Period
| T | Hz | MW | Frequency | MW |  | Response | Response | Response | MW/scan | MW | MW | MW | MW | MW | 633 | [8 empty] | MW/0.1 Hz
0
T-72 sec | 40098.1016 | 60.027 | 3671.189 |  |  |  | -21.6003 | -7.5601 | [15 empty] | 0 |  |  | T-72 sec | [10 empty] | T-72 sec | 40098.1016 | 60.027 | 3671.189 | 350 | 157.6281 | 0 | 213.5 | 10 | 15 | -103 | 7640.91 | -21.6003 | T-72 sec | 40098.1016 | [12 empty] | T-72 sec | 40098.1016 | [12 empty] | T-72 sec | 40098.1016 | [12 empty] | T-72 sec | 40098.1016 | [12 empty] | T-72 sec | 40098.1016
T-70 sec | 40098.1016 | 60.026 | 3668.6106 |  |  |  | -20.8008 | -12.1944 | [15 empty] | 0 |  |  | T-70 sec | [10 empty] | T-70 sec | 40098.1016 | 60.026 | 3668.6106 | 350 | 155.5317 | 0 | 214 | 10 | 15 | -103 | 7641.24 | -20.8008 | T-70 sec | 40098.1016 | [12 empty] | T-70 sec | 40098.1016 | [12 empty] | T-70 sec | 40098.1016 | [12 empty] | T-70 sec | 40098.1016 | [12 empty] | T-70 sec | 40098.1016
T-68 sec | 40098.1016 | 60.026 | 3665.2322 |  |  |  | -20.8008 | -15.2066 | [15 empty] | 0 |  |  | T-68 sec | [10 empty] | T-68 sec | 40098.1016 | 60.026 | 3665.2322 | 350 | 155.5317 | 0 | 214.5 | 10 | 15 | -103 | 7641.57 | -20.8008 | T-68 sec | 40098.1016 | [12 empty] | T-68 sec | 40098.1016 | [12 empty] | T-68 sec | 40098.1016 | [12 empty] | T-68 sec | 40098.1016 | [12 empty] | T-68 sec | 40098.1016
T-66 sec | 40098.1016 | 60.022 | 3664.4951 |  |  |  | -17.5995 | -16.0441 | [15 empty] | 0 |  |  | T-66 sec | [10 empty] | T-66 sec | 40098.1016 | 60.022 | 3664.4951 | 350 | 155.5317 | 0 | 215 | 10 | 15 | -103 | 7641.9 | -17.5995 | T-66 sec | 40098.1016 | [12 empty] | T-66 sec | 40098.1016 | [12 empty] | T-66 sec | 40098.1016 | [12 empty] | T-66 sec | 40098.1016 | [12 empty] | T-66 sec | 40098.1016
T-64 sec | 40098.1016 | 60.019 | 3666.0618 |  |  |  | -15.2008 | -15.749 | [15 empty] | 0 |  |  | T-64 sec | [10 empty] | T-64 sec | 40098.1016 | 60.019 | 3666.0618 | 350 | 155.5317 | 0 | 215.5 | 10 | 15 | -103 | 7642.23 | -15.2008 | T-64 sec | 40098.1016 | [12 empty] | T-64 sec | 40098.1016 | [12 empty] | T-64 sec | 40098.1016 | [12 empty] | T-64 sec | 40098.1016 | [12 empty] | T-64 sec | 40098.1016
T-62 sec | 40098.1017 | 60.017 | 3666.8208 |  |  |  | -13.5986 | -14.9963 | [15 empty] | 0 |  |  | T-62 sec | [10 empty] | T-62 sec | 40098.1017 | 60.017 | 3666.8208 | 350 | 155.5317 | 0 | 216 | 10 | 15 | -103 | 7642.56 | -13.5986 | T-62 sec | 40098.1017 | [12 empty] | T-62 sec | 40098.1017 | [12 empty] | T-62 sec | 40098.1017 | [12 empty] | T-62 sec | 40098.1017 | [12 empty] | T-62 sec | 40098.1017
T-60 sec | 40098.1017 | 60.019 | 3666.7874 |  |  |  | -15.2008 | -15.0679 |  | -0.27611 | 3666.7874 | [12 empty] | 0 |  |  | T-60 sec | [10 empty] | T-60 sec | 40098.1017 | 60.019 | 3666.7874 | 350 | 160.4472 | 0 | 216.5 | 10 | 15 | -103 | 7642.89 | -15.2008 | T-60 sec | 40098.1017 | [12 empty] | T-60 sec | 40098.1017 | [12 empty] | T-60 sec | 40098.1017 | [12 empty] | T-60 sec | 40098.1017 | [12 empty] | T-60 sec | 40098.1017
T-58 sec | 40098.1017 | 60.02 | 3670.4536 |  |  |  | -16.0004 | -15.3943 |  | -0.27611 | 3666.1849 | [12 empty] | 0 |  |  | T-58 sec | [10 empty] | T-58 sec | 40098.1017 | 60.02 | 3670.4536 | 350 | 160.4472 | 0 | 217 | 10 | 15 | -103 | 7643.22 | -16.0004 | T-58 sec | 40098.1017 | [12 empty] | T-58 sec | 40098.1017 | [12 empty] | T-58 sec | 40098.1017 | [12 empty] | T-58 sec | 40098.1017 | [12 empty] | T-58 sec | 40098.1017
T-56 sec | 40098.1017 | 60.019 | 3670.2668 |  |  |  | -15.2008 | -15.3266 |  | -0.27611 | 3665.9765 | [12 empty] | 0 |  |  | T-56 sec | [10 empty] | T-56 sec | 40098.1017 | 60.019 | 3670.2668 | 350 | 160.4472 | 0 | 217.5 | 10 | 15 | -103 | 7643.55 | -15.2008 | T-56 sec | 40098.1017 | [12 empty] | T-56 sec | 40098.1017 | [12 empty] | T-56 sec | 40098.1017 | [12 empty] | T-56 sec | 40098.1017 | [12 empty] | T-56 sec | 40098.1017
T-54 sec | 40098.1018 | 60.021 | 3671.668 |  |  |  | -16.7999 | -15.8422 |  | -0.27611 | 3665.1847 | [12 empty] | 0 |  |  | T-54 sec | [10 empty] | T-54 sec | 40098.1018 | 60.021 | 3671.668 | 350 | 160.4472 | 0 | 218 | 10 | 15 | -103 | 7643.88 | -16.7999 | T-54 sec | 40098.1018 | [12 empty] | T-54 sec | 40098.1018 | [12 empty] | T-54 sec | 40098.1018 | [12 empty] | T-54 sec | 40098.1018 | [12 empty] | T-54 sec | 40098.1018
T-52 sec | 40098.1018 | 60.021 | 3672.4932 |  |  |  | -16.7999 | -16.1774 |  | -0.27611 | 3664.5734 | [12 empty] | 0 |  |  | T-52 sec | [10 empty] | T-52 sec | 40098.1018 | 60.021 | 3672.4932 | 350 | 160.4472 | 0 | 218.5 | 10 | 15 | -103 | 7644.21 | -16.7999 | T-52 sec | 40098.1018 | [12 empty] | T-52 sec | 40098.1018 | [12 empty] | T-52 sec | 40098.1018 | [12 empty] | T-52 sec | 40098.1018 | [12 empty] | T-52 sec | 40098.1018
T-50 sec | 40098.1018 | 60.021 | 3672.6851 |  |  |  | -16.7999 | -16.3953 |  | -0.27611 | 3664.0794 | [12 empty] | 0 |  |  | T-50 sec | [10 empty] | T-50 sec | 40098.1018 | 60.021 | 3672.6851 | 350 | 163.9586 | 0 | 219 | 10 | 15 | -103 | 7644.54 | -16.7999 | T-50 sec | 40098.1018 | [12 empty] | T-50 sec | 40098.1018 | [12 empty] | T-50 sec | 40098.1018 | [12 empty] | T-50 sec | 40098.1018 | [12 empty] | T-50 sec | 40098.1018
T-48 sec | 40098.1018 | 60.019 | 3672.8574 |  |  |  | -15.2008 | -15.9772 |  | -0.27611 | 3664.2214 | [12 empty] | 0 |  |  | T-48 sec | [10 empty] | T-48 sec | 40098.1018 | 60.019 | 3672.8574 | 350 | 163.9586 | 0 | 219.5 | 10 | 15 | -103 | 7644.87 | -15.2008 | T-48 sec | 40098.1018 | [12 empty] | T-48 sec | 40098.1018 | [12 empty] | T-48 sec | 40098.1018 | [12 empty] | T-48 sec | 40098.1018 | [12 empty] | T-48 sec | 40098.1018
T-46 sec | 40098.1019 | 60.018 | 3672.1641 |  |  |  | -14.4012 | -15.4256 |  | -0.27611 | 3664.4968 | [12 empty] | 0 |  |  | T-46 sec | [10 empty] | T-46 sec | 40098.1019 | 60.018 | 3672.1641 | 350 | 163.9586 | 0 | 220 | 10 | 15 | -103 | 7645.2 | -14.4012 | T-46 sec | 40098.1019 | [12 empty] | T-46 sec | 40098.1019 | [12 empty] | T-46 sec | 40098.1019 | [12 empty] | T-46 sec | 40098.1019 | [12 empty] | T-46 sec | 40098.1019
T-44 sec | 40098.1019 | 60.022 | 3671.4131 |  |  |  | -17.5995 | -16.1865 |  | -0.27611 | 3663.4599 | [12 empty] | 0 |  |  | T-44 sec | [10 empty] | T-44 sec | 40098.1019 | 60.022 | 3671.4131 | 350 | 163.9586 | 0 | 220.5 | 10 | 15 | -103 | 7645.53 | -17.5995 | T-44 sec | 40098.1019 | [12 empty] | T-44 sec | 40098.1019 | [12 empty] | T-44 sec | 40098.1019 | [12 empty] | T-44 sec | 40098.1019 | [12 empty] | T-44 sec | 40098.1019
T-42 sec | 40098.1019 | 60.031 | 3669.9829 |  |  |  | -24.7986 | -19.2007 |  | -0.27611 | 3660.1695 | [12 empty] | 0 |  |  | T-42 sec | [10 empty] | T-42 sec | 40098.1019 | 60.031 | 3669.9829 | 350 | 163.9586 | 0 | 221 | 10 | 15 | -103 | 7645.86 | -24.7986 | T-42 sec | 40098.1019 | [12 empty] | T-42 sec | 40098.1019 | [12 empty] | T-42 sec | 40098.1019 | [12 empty] | T-42 sec | 40098.1019 | [12 empty] | T-42 sec | 40098.1019
T-40 sec | 40098.1019 | 60.037 | 3666.4673 |  |  |  | -29.599 | -22.8401 |  | -0.27611 | 3656.254 | [12 empty] | 0 |  |  | T-40 sec | [10 empty] | T-40 sec | 40098.1019 | 60.037 | 3666.4673 | 350 | 166.0724 | 0 | 221.5 | 10 | 15 | -103 | 7646.19 | -29.599 | T-40 sec | 40098.1019 | [12 empty] | T-40 sec | 40098.1019 | [12 empty] | T-40 sec | 40098.1019 | [12 empty] | T-40 sec | 40098.1019 | [12 empty] | T-40 sec | 40098.1019
T-38 sec | 40098.1019 | 60.037 | 3663.7581 |  |  |  | -29.599 | -25.2057 |  | -0.27611 | 3653.6123 | [12 empty] | 0 |  |  | T-38 sec | [10 empty] | T-38 sec | 40098.1019 | 60.037 | 3663.7581 | 350 | 166.0724 | 0 | 222 | 10 | 15 | -103 | 7646.52 | -29.599 | T-38 sec | 40098.1019 | [12 empty] | T-38 sec | 40098.1019 | [12 empty] | T-38 sec | 40098.1019 | [12 empty] | T-38 sec | 40098.1019 | [12 empty] | T-38 sec | 40098.1019
T-36 sec | 40098.102 | 60.036 | 3661.5991 |  |  |  | -28.7994 | -26.4635 |  | -0.27611 | 3652.0784 | [12 empty] | 0 |  |  | T-36 sec | [10 empty] | T-36 sec | 40098.102 | 60.036 | 3661.5991 | 350 | 166.0724 | 0 | 222.5 | 10 | 15 | -103 | 7646.85 | -28.7994 | T-36 sec | 40098.102 | [12 empty] | T-36 sec | 40098.102 | [12 empty] | T-36 sec | 40098.102 | [12 empty] | T-36 sec | 40098.102 | [12 empty] | T-36 sec | 40098.102
T-34 sec | 40098.102 | 60.037 | 3660.6724 |  |  |  | -29.599 | -27.5609 |  | -0.27611 | 3650.7049 | [12 empty] | 0 |  |  | T-34 sec | [10 empty] | T-34 sec | 40098.102 | 60.037 | 3660.6724 | 350 | 166.0724 | 0 | 223 | 10 | 15 | -103 | 7647.18 | -29.599 | T-34 sec | 40098.102 | [12 empty] | T-34 sec | 40098.102 | [12 empty] | T-34 sec | 40098.102 | [12 empty] | T-34 sec | 40098.102 | [12 empty] | T-34 sec | 40098.102
T-32 sec | 40098.102 | 60.046 | 3651.4917 |  |  |  | -36.8011 | -30.795 |  | -0.27611 | 3647.1947 | [12 empty] | 0 |  |  | T-32 sec | [10 empty] | T-32 sec | 40098.102 | 60.046 | 3651.4917 | 350 | 166.0724 | 0 | 223.5 | 10 | 15 | -103 | 7647.51 | -36.8011 | T-32 sec | 40098.102 | [12 empty] | T-32 sec | 40098.102 | [12 empty] | T-32 sec | 40098.102 | [12 empty] | T-32 sec | 40098.102 | [12 empty] | T-32 sec | 40098.102
T-30 sec | 40098.102 | 60.048 | 3649.1904 |  |  |  | -38.4003 | -33.4569 |  | -0.27611 | 3644.2567 | [12 empty] | 0 |  |  | T-30 sec | [10 empty] | T-30 sec | 40098.102 | 60.048 | 3649.1904 | 350 | 163.7666 | 0 | 224 | 10 | 15 | -103 | 7647.84 | -38.4003 | T-30 sec | 40098.102 | [12 empty] | T-30 sec | 40098.102 | [12 empty] | T-30 sec | 40098.102 | [12 empty] | T-30 sec | 40098.102 | [12 empty] | T-30 sec | 40098.102
T-28 sec | 40098.1021 | 60.048 | 3650.0251 |  |  |  | -38.4003 | -35.187 |  | -0.27611 | 3642.2504 | [12 empty] | 0 |  |  | T-28 sec | [10 empty] | T-28 sec | 40098.1021 | 60.048 | 3650.0251 | 350 | 163.7666 | 0 | 224.5 | 10 | 15 | -103 | 7648.17 | -38.4003 | T-28 sec | 40098.1021 | [12 empty] | T-28 sec | 40098.1021 | [12 empty] | T-28 sec | 40098.1021 | [12 empty] | T-28 sec | 40098.1021 | [12 empty] | T-28 sec | 40098.1021
T-26 sec | 40098.1021 | 60.043 | 3648.2463 |  |  |  | -34.3994 | -34.9114 |  | -0.27611 | 3642.25 | [12 empty] | 0 |  |  | T-26 sec | [10 empty] | T-26 sec | 40098.1021 | 60.043 | 3648.2463 | 350 | 163.7666 | 0 | 225 | 10 | 15 | -103 | 7648.5 | -34.3994 | T-26 sec | 40098.1021 | [12 empty] | T-26 sec | 40098.1021 | [12 empty] | T-26 sec | 40098.1021 | [12 empty] | T-26 sec | 40098.1021 | [12 empty] | T-26 sec | 40098.1021
T-24 sec | 40098.1021 | 60.041 | 3649.512 |  |  |  | -32.8003 | -34.1725 |  | -0.27611 | 3642.7127 | [12 empty] | 0 |  |  | T-24 sec | [10 empty] | T-24 sec | 40098.1021 | 60.041 | 3649.512 | 350 | 163.7666 | 0 | 225.5 | 10 | 15 | -103 | 7648.83 | -32.8003 | T-24 sec | 40098.1021 | [12 empty] | T-24 sec | 40098.1021 | [12 empty] | T-24 sec | 40098.1021 | [12 empty] | T-24 sec | 40098.1021 | [12 empty] | T-24 sec | 40098.1021
T-22 sec | 40098.1021 | 60.041 | 3654.2944 |  |  |  | -32.8003 | -33.6922 |  | -0.27611 | 3642.9169 | [12 empty] | 0 |  |  | T-22 sec | [10 empty] | T-22 sec | 40098.1021 | 60.041 | 3654.2944 | 350 | 163.7666 | 0 | 226 | 10 | 15 | -103 | 7649.16 | -32.8003 | T-22 sec | 40098.1021 | [12 empty] | T-22 sec | 40098.1021 | [12 empty] | T-22 sec | 40098.1021 | [12 empty] | T-22 sec | 40098.1021 | [12 empty] | T-22 sec | 40098.1021
T-20 sec | 40098.1022 | 60.041 | 3655.0068 |  |  |  | -32.8003 | -33.38 |  | -0.27611 | 3642.953 | [12 empty] | 0 |  |  | T-20 sec | [10 empty] | T-20 sec | 40098.1022 | 60.041 | 3655.0068 | 350 | 165.1017 | 0 | 226.5 | 10 | 15 | -103 | 7649.49 | -32.8003 | T-20 sec | 40098.1022 | [12 empty] | T-20 sec | 40098.1022 | [12 empty] | T-20 sec | 40098.1022 | [12 empty] | T-20 sec | 40098.1022 | [12 empty] | T-20 sec | 40098.1022
T-18 sec | 40098.1022 | 60.039 | 3651.8743 |  |  |  | -31.2012 | -32.6174 |  | -0.27611 | 3643.4394 | [12 empty] | 0 |  |  | T-18 sec | [10 empty] | T-18 sec | 40098.1022 | 60.039 | 3651.8743 | 350 | 165.1017 | 0 | 227 | 10 | 15 | -103 | 7649.82 | -31.2012 | T-18 sec | 40098.1022 | [12 empty] | T-18 sec | 40098.1022 | [12 empty] | T-18 sec | 40098.1022 | [12 empty] | T-18 sec | 40098.1022 | [12 empty] | T-18 sec | 40098.1022
T-16 sec | 40098.1022 | 60.041 | 3651.0593 | 60.0421 | 3645.7271 |  | -32.8003 | -32.6814 |  | -0.27611 | 3643.0993 | [12 empty] | 0 |  |  | T-16 sec | 60.0421 | [9 empty] | T-16 sec | 40098.1022 | 60.041 | 3651.0593 | 350 | 165.1017 | 0 | 227.5 | 10 | 15 | -103 | 7650.15 | -32.8003 | T-16 sec | 40098.1022 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-16 sec | 40098.1022 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-16 sec | 40098.1022 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-16 sec | 40098.1022 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-16 sec | 40098.1022 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002
T-14 sec | 40098.1022 | 60.043 | 3649.187 | 60.0421 | 3645.7271 |  | -34.3994 | -33.2827 |  | -0.27611 | 3642.2219 | [12 empty] | 0 |  |  | T-14 sec | 60.0421 | [9 empty] | T-14 sec | 40098.1022 | 60.043 | 3649.187 | 350 | 165.1017 | 0 | 228 | 10 | 15 | -103 | 7650.48 | -34.3994 | T-14 sec | 40098.1022 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-14 sec | 40098.1022 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-14 sec | 40098.1022 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-14 sec | 40098.1022 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-14 sec | 40098.1022 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002
T-12 sec | 40098.1022 | 60.045 | 3648.2363 | 60.0421 | 3645.7271 |  | -35.9985 | -34.2333 |  | -0.27611 | 3640.9953 | [12 empty] | 0 |  |  | T-12 sec | 60.0421 | [9 empty] | T-12 sec | 40098.1022 | 60.045 | 3648.2363 | 350 | 165.1017 | 0 | 228.5 | 10 | 15 | -103 | 7650.81 | -35.9985 | T-12 sec | 40098.1022 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-12 sec | 40098.1022 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-12 sec | 40098.1022 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-12 sec | 40098.1022 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-12 sec | 40098.1022 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002
T-10 sec | 40098.1023 | 60.046 | 3645.387 | 60.0421 | 3645.7271 |  | -36.8011 | -35.132 |  | -0.27611 | 3639.8204 | [12 empty] | 0 |  |  | T-10 sec | 60.0421 | [9 empty] | T-10 sec | 40098.1023 | 60.046 | 3645.387 | 350 | 165.4764 | 0 | 229 | 10 | 15 | -103 | 7651.14 | -36.8011 | T-10 sec | 40098.1023 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-10 sec | 40098.1023 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-10 sec | 40098.1023 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-10 sec | 40098.1023 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-10 sec | 40098.1023 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002
T-08 sec | 40098.1023 | 60.041 | 3644.6277 | 60.0421 | 3645.7271 |  | -32.8003 | -34.3159 |  | -0.27611 | 3640.3604 | [12 empty] | 0 |  |  | T-08 sec | 60.0421 | [9 empty] | T-08 sec | 40098.1023 | 60.041 | 3644.6277 | 350 | 165.4764 | 0 | 229.5 | 10 | 15 | -103 | 7651.47 | -32.8003 | T-08 sec | 40098.1023 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-08 sec | 40098.1023 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-08 sec | 40098.1023 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-08 sec | 40098.1023 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-08 sec | 40098.1023 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002
T-06 sec | 40098.1023 | 60.041 | 3645.4458 | 60.0421 | 3645.7271 |  | -32.8003 | -33.7854 |  | -0.27611 | 3640.6148 | [12 empty] | 0 |  |  | T-06 sec | 60.0421 | [9 empty] | T-06 sec | 40098.1023 | 60.041 | 3645.4458 | 350 | 165.4764 | 0 | 230 | 10 | 15 | -103 | 7651.8 | -32.8003 | T-06 sec | 40098.1023 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-06 sec | 40098.1023 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-06 sec | 40098.1023 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-06 sec | 40098.1023 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-06 sec | 40098.1023 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002
T-04 sec | 40098.1023 | 60.041 | 3640.6821 | 60.0421 | 3645.7271 |  | -32.8003 | -33.4406 |  | -0.27611 | 3640.6835 | [12 empty] | 0 |  |  | T-04 sec | 60.0421 | [9 empty] | T-04 sec | 40098.1023 | 60.041 | 3640.6821 | 350 | 165.4764 | 0 | 230.5 | 10 | 15 | -103 | 7652.13 | -32.8003 | T-04 sec | 40098.1023 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-04 sec | 40098.1023 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-04 sec | 40098.1023 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-04 sec | 40098.1023 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-04 sec | 40098.1023 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002
T-02 sec | 40098.1024 | 60.039 | 3641.1912 | 60.0421 | 3645.7271 |  | -31.2012 | -32.6568 |  | -0.27611 | 3641.1912 | [12 empty] | 0 |  |  | T-02 sec | 60.0421 | [9 empty] | T-02 sec | 40098.1024 | 60.039 | 3641.1912 | 350 | 165.4764 | 0 | 231 | 10 | 15 | -103 | 7652.46 | -31.2012 | T-02 sec | 40098.1024 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-02 sec | 40098.1024 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-02 sec | 40098.1024 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-02 sec | 40098.1024 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002 |  | T-02 sec | 40098.1024 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | 10 | 15 | -103 | 7651.305 | -33.7002
T+0 sec | 40098.1024 | 59.978 | 3659.4648 |  |  |  | 17.5995 | -15.0671 |  | 0 | 3658.7809 |  |  |  |  | 633 | [7 empty] | 633 | -987.1409 |  | T+0 sec | [10 empty] | T+0 sec | 40098.1024 | 59.978 | 3659.4648 | 350 | 206.4591 | 0 | 231.5 | 10 | 15 | -103 | 7652.79 | 17.5995 | T+0 sec | 40098.1024 | [12 empty] | T+0 sec | 40098.1024 | [12 empty] | T+0 sec | 40098.1024 | [12 empty] | T+0 sec | 40098.1024 | [12 empty] | T+0 sec | 40098.1024
T+02 sec | 40098.1024 | 59.852 | 3696.3623 |  |  |  | 118.399 | 31.646 |  | 0.56196 | 3706.056 | 3677.9136 | 3682.4184 | 3673.8467 | 3673.8467 | 633 | [7 empty] | 633 | -332.9405 |  | T+02 sec | [10 empty] | T+02 sec | 40098.1024 | 59.852 | 3696.3623 | 350 | 206.4591 | 0 | 232 | 10 | 0 | -103 | 7616 | 118.399 | T+02 sec | 40098.1024 | [12 empty] | T+02 sec | 40098.1024 | [12 empty] | T+02 sec | 40098.1024 | [12 empty] | T+02 sec | 40098.1024 | [12 empty] | T+02 sec | 40098.1024
T+04 sec | 40098.1024 | 59.836 | 3734.9043 |  |  |  | 131.2012 | 66.4903 |  | 0.56196 | 3741.4622 | 3696.9105 | 3702.0997 | 3674.4086 | 3674.1276 | 633 | [7 empty] | 633 | -307.0927 |  | T+04 sec | [10 empty] | T+04 sec | 40098.1024 | 59.836 | 3734.9043 | 335 | 206.4591 | 0 | 232.5 | 10 | 0 | -103 | 7626 | 131.2012 | T+04 sec | 40098.1024 | [12 empty] | T+04 sec | 40098.1024 | [12 empty] | T+04 sec | 40098.1024 | [12 empty] | T+04 sec | 40098.1024 | [12 empty] | T+04 sec | 40098.1024
T+06 sec | 40098.1025 | 59.869 | 3734.6726 |  |  |  | 104.8004 | 79.8989 |  | 0.56196 | 3755.4327 | 3706.351 | 3715.433 | 3674.9706 | 3674.4086 | 633 | [6 empty] | 0 | 633 | -365.6302 |  | T+06 sec | [10 empty] | T+06 sec | 40098.1025 | 59.869 | 3734.6726 | 335 | 206.4591 | 0 | 233 | 10 | 0 | -103 | 7632 | 104.8004 | T+06 sec | 40098.1025 | [12 empty] | T+06 sec | 40098.1025 | [12 empty] | T+06 sec | 40098.1025 | [12 empty] | T+06 sec | 40098.1025 | [12 empty] | T+06 sec | 40098.1025
T+08 sec | 40098.1025 | 59.869 | 3734.6726 |  |  |  | 104.8004 | 88.6144 |  | 0.56196 | 3764.7102 | 3712.0153 | 3725.2884 | 3675.5325 | 3674.6896 | 633 | [6 empty] | 0 | 633 | -365.6302 |  | T+08 sec | [10 empty] | T+08 sec | 40098.1025 | 59.869 | 3734.6726 | 335 | 206.4591 | 0 | 233 | 10 | 0 | -103 | 7632 | 104.8004 | T+08 sec | 40098.1025 | [12 empty] | T+08 sec | 40098.1025 | [12 empty] | T+08 sec | 40098.1025 | [12 empty] | T+08 sec | 40098.1025 | [12 empty] | T+08 sec | 40098.1025
T+10 sec | 40098.1025 | 59.892 | 3737.1567 |  |  |  | 86.4014 | 87.8398 |  | 0.56196 | 3764.4976 | 3716.2056 | 3731.8233 | 3676.0945 | 3674.9706 | 633 | [6 empty] | 0 | 633 | -421.6432 |  | T+10 sec | [10 empty] | T+10 sec | 40098.1025 | 59.892 | 3737.1567 | 335 | 206.4591 | 0 | 233.5 | 10 | 0 | -103 | 7632 | 86.4014 | T+10 sec | 40098.1025 | [12 empty] | T+10 sec | 40098.1025 | [12 empty] | T+10 sec | 40098.1025 | [12 empty] | T+10 sec | 40098.1025 | [12 empty] | T+10 sec | 40098.1025
T+12 sec | 40098.1025 | 59.891 | 3761.2495 |  |  |  | 87.2009 | 87.6162 |  | 0.56196 | 3764.836 | 3722.6404 | 3736.5394 | 3676.6565 | 3675.2516 | 633 | [6 empty] | 0 | 633 | -418.8547 |  | T+12 sec | 59.8826 | -397.1996 | [8 empty] | T+12 sec | 40098.1025 | 59.891 | 3761.2495 | 335 | 211.256 | 0 | 234 | 10 | 0 | -103 | 7632 | 87.2009 | T+12 sec | 40098.1025 | 59.8826 | 3770.653 | 335 | 212.1391 | 0.85714 | 235.5 | 10 | 0 | -103 | 7632 | 93.9427 | 3813.2356 | T+12 sec | 40098.1025 | [12 empty] | T+12 sec | 40098.1025 | [12 empty] | T+12 sec | 40098.1025 | [12 empty] | T+12 sec | 40098.1025
T+14 sec | 40098.1025 | 59.88 | 3766.113 |  |  |  | 95.9991 | 90.5502 |  | 0.56196 | 3768.332 | 3728.0745 | 3740.5135 | 3677.2184 | 3675.5325 | 633 | [6 empty] | 0 | 633 | -390.4415 |  | T+14 sec | 59.8826 | -397.1996 | [8 empty] | T+14 sec | 40098.1025 | 59.88 | 3766.113 | 335 | 211.256 | 1 | 234.5 | 10 | 0 | -103 | 7632 | 95.9991 | T+14 sec | 40098.1025 | 59.8826 | 3770.653 | 335 | 212.1391 | 0.85714 | 235.5 | 10 | 0 | -103 | 7632 | 93.9427 | 3813.2356 | T+14 sec | 40098.1025 | [12 empty] | T+14 sec | 40098.1025 | [12 empty] | T+14 sec | 40098.1025 | [12 empty] | T+14 sec | 40098.1025
T+16 sec | 40098.1026 | 59.876 | 3766.1938 |  |  |  | 99.2004 | 93.5778 |  | 0.56196 | 3771.9215 | 3732.31 | 3744.0032 | 3677.7804 | 3675.8135 | 633 | [6 empty] | 0 | 633 | -381.0366 |  | T+16 sec | 59.8826 | -397.1996 | [8 empty] | T+16 sec | 40098.1026 | 59.876 | 3766.1938 | 335 | 211.256 | 1 | 235 | 10 | 0 | -103 | 7632 | 99.2004 | T+16 sec | 40098.1026 | 59.8826 | 3770.653 | 335 | 212.1391 | 0.85714 | 235.5 | 10 | 0 | -103 | 7632 | 93.9427 | 3813.2356 | T+16 sec | 40098.1026 | [12 empty] | T+16 sec | 40098.1026 | [12 empty] | T+16 sec | 40098.1026 | [12 empty] | T+16 sec | 40098.1026
T+18 sec | 40098.1026 | 59.875 | 3768.877 |  |  |  | 100 | 95.8256 |  | 0.56196 | 3774.7312 | 3735.9667 | 3747.076 | 3678.3423 | 3676.0945 | 633 | [6 empty] | 0 | 633 | -378.7579 |  | T+18 sec | 59.8826 | -397.1996 | 59.8844 | -401.67 |  |  | 59.8883 | -411.9963 |  |  | T+18 sec | 40098.1026 | 59.875 | 3768.877 | 335 | 211.256 | 1 | 235.5 | 10 | 0 | -103 | 7632 | 100 | T+18 sec | 40098.1026 | 59.8826 | 3770.653 | 335 | 212.1391 | 0.85714 | 235.5 | 10 | 0 | -103 | 7632 | 93.9427 | 3813.2356 | T+18 sec | 40098.1026 | 59.8844 | 3779.0294 | 335 | 213.4637 | 1.4286 | 237 | 10 | 0 | -103 | 7632 | 92.4569 | 3814.9601 | T+18 sec | 40098.1026 | [12 empty] | T+18 sec | 40098.1026 | 59.8883 | 3787.2724 | 335 | 213.9682 | 6.0556 | 239.75 | 10 | 0 | -103 | 7632 | 89.3333 | 3819.3275 | T+18 sec | 40098.1026
T+20 sec | 40098.1026 | 59.883 | 3769.925 | 59.8891 | 3788.3545 |  | 93.6005 | 95.0468 | 3752.731 | 0.56196 | 3774.5144 | 3739.0538 | 3749.5704 | 3678.9043 | 3676.3755 | 633 | [6 empty] | 0 | 633 | -397.7985 | -413.9515 | T+20 sec | 59.8826 | -397.1996 | 59.8844 | -401.67 | 59.8891 | -414.4045 | 59.8883 | -411.9963 | 59.8891 | -413.9515 | T+20 sec | 40098.1026 | 59.883 | 3769.925 | 335 | 211.256 | 1 | 236 | 10 | 0 | -103 | 7632 | 93.6005 | T+20 sec | 40098.1026 | 59.8826 | 3770.653 | 335 | 212.1391 | 0.85714 | 235.5 | 10 | 0 | -103 | 7632 | 93.9427 | 3813.2356 | T+20 sec | 40098.1026 | 59.8844 | 3779.0294 | 335 | 213.4637 | 1.4286 | 237 | 10 | 0 | -103 | 7632 | 92.4569 | 3814.9601 | T+20 sec | 40098.1026 | 59.8893 | 3783.8625 | 335 | 213.0775 | 3.5455 | 238.5 | 10 | 0 | -103 | 7632 | 88.5814 | 3813.831 | T+20 sec | 40098.1026 | 59.8883 | 3787.2724 | 335 | 213.9682 | 6.0556 | 239.75 | 10 | 0 | -103 | 7632 | 89.3333 | 3819.3275 | T+20 sec | 40098.1026 | 59.8891 | 3788.3545 | 335 | 214.1277 | 6.3529 | 240 | 10 | 0 | -103 | 7632 | 88.7058 | 3819.3286
T+22 sec | 40098.1026 | 59.887 | 3780.6206 | 59.8891 | 3788.3545 |  | 90.3992 | 93.4201 | 3752.731 | 0.56196 | 3773.4497 | 3742.5177 | 3751.5604 | 3679.4663 | 3676.6565 | 633 | [6 empty] | 0 | 633 | -408.0602 | -413.9515 | T+22 sec | 59.8826 | -397.1996 | 59.8844 | -401.67 | 59.8891 | -414.4045 | 59.8883 | -411.9963 | 59.8891 | -413.9515 | T+22 sec | 40098.1026 | 59.887 | 3780.6206 | 335 | 214.3467 | 1 | 236.5 | 10 | 0 | -103 | 7632 | 90.3992 | T+22 sec | 40098.1026 | 59.8826 | 3770.653 | 335 | 212.1391 | 0.85714 | 235.5 | 10 | 0 | -103 | 7632 | 93.9427 | 3813.2356 | T+22 sec | 40098.1026 | 59.8844 | 3779.0294 | 335 | 213.4637 | 1.4286 | 237 | 10 | 0 | -103 | 7632 | 92.4569 | 3814.9601 | T+22 sec | 40098.1026 | 59.8893 | 3783.8625 | 335 | 213.0775 | 3.5455 | 238.5 | 10 | 0 | -103 | 7632 | 88.5814 | 3813.831 | T+22 sec | 40098.1026 | 59.8883 | 3787.2724 | 335 | 213.9682 | 6.0556 | 239.75 | 10 | 0 | -103 | 7632 | 89.3333 | 3819.3275 | T+22 sec | 40098.1026 | 59.8891 | 3788.3545 | 335 | 214.1277 | 6.3529 | 240 | 10 | 0 | -103 | 7632 | 88.7058 | 3819.3286
T+24 sec | 40098.1027 | 59.886 | 3781.5918 | 59.8891 | 3788.3545 |  | 91.1987 | 92.6426 | 3752.731 | 0.56196 | 3773.2341 | 3745.5234 | 3753.2276 | 3680.0282 | 3676.9374 | 633 | [6 empty] | 0 | 633 | -405.4479 | -413.9515 | T+24 sec | 59.8826 | -397.1996 | 59.8844 | -401.67 | 59.8891 | -414.4045 | 59.8883 | -411.9963 | 59.8891 | -413.9515 | T+24 sec | 40098.1027 | 59.886 | 3781.5918 | 335 | 214.3467 | 1 | 237 | 10 | 0 | -103 | 7632 | 91.1987 | T+24 sec | 40098.1027 | 59.8826 | 3770.653 | 335 | 212.1391 | 0.85714 | 235.5 | 10 | 0 | -103 | 7632 | 93.9427 | 3813.2356 | T+24 sec | 40098.1027 | 59.8844 | 3779.0294 | 335 | 213.4637 | 1.4286 | 237 | 10 | 0 | -103 | 7632 | 92.4569 | 3814.9601 | T+24 sec | 40098.1027 | 59.8893 | 3783.8625 | 335 | 213.0775 | 3.5455 | 238.5 | 10 | 0 | -103 | 7632 | 88.5814 | 3813.831 | T+24 sec | 40098.1027 | 59.8883 | 3787.2724 | 335 | 213.9682 | 6.0556 | 239.75 | 10 | 0 | -103 | 7632 | 89.3333 | 3819.3275 | T+24 sec | 40098.1027 | 59.8891 | 3788.3545 | 335 | 214.1277 | 6.3529 | 240 | 10 | 0 | -103 | 7632 | 88.7058 | 3819.3286
T+26 sec | 40098.1027 | 59.885 | 3782.4995 | 59.8891 | 3788.3545 |  | 92.0013 | 92.4182 | 3752.731 | 0.56196 | 3773.5717 | 3748.1646 | 3754.6807 | 3680.5902 | 3677.2184 | 633 | [6 empty] | 0 | 633 | -402.8591 | -413.9515 | T+26 sec |  |  | 59.8844 | -401.67 | 59.8891 | -414.4045 | 59.8883 | -411.9963 | 59.8891 | -413.9515 | T+26 sec | 40098.1027 | 59.885 | 3782.4995 | 335 | 214.3467 | 1 | 237.5 | 10 | 0 | -103 | 7632 | 92.0013 | T+26 sec | 40098.1027 | [12 empty] | T+26 sec | 40098.1027 | 59.8844 | 3779.0294 | 335 | 213.4637 | 1.4286 | 237 | 10 | 0 | -103 | 7632 | 92.4569 | 3814.9601 | T+26 sec | 40098.1027 | 59.8893 | 3783.8625 | 335 | 213.0775 | 3.5455 | 238.5 | 10 | 0 | -103 | 7632 | 88.5814 | 3813.831 | T+26 sec | 40098.1027 | 59.8883 | 3787.2724 | 335 | 213.9682 | 6.0556 | 239.75 | 10 | 0 | -103 | 7632 | 89.3333 | 3819.3275 | T+26 sec | 40098.1027 | 59.8891 | 3788.3545 | 335 | 214.1277 | 6.3529 | 240 | 10 | 0 | -103 | 7632 | 88.7058 | 3819.3286
T+28 sec | 40098.1027 | 59.887 | 3784.9619 | 59.8891 | 3788.3545 |  | 90.3992 | 91.7115 | 3752.731 | 0.56196 | 3773.427 | 3750.6177 | 3755.9305 | 3681.1521 | 3677.4994 | 633 | [6 empty] | 0 | 633 | -408.0602 | -413.9515 | T+28 sec |  |  | 59.8844 | -401.67 | 59.8891 | -414.4045 | 59.8883 | -411.9963 | 59.8891 | -413.9515 | T+28 sec | 40098.1027 | 59.887 | 3784.9619 | 335 | 214.3467 | 2 | 238 | 10 | 0 | -103 | 7632 | 90.3992 | T+28 sec | 40098.1027 | [12 empty] | T+28 sec | 40098.1027 | 59.8844 | 3779.0294 | 335 | 213.4637 | 1.4286 | 237 | 10 | 0 | -103 | 7632 | 92.4569 | 3814.9601 | T+28 sec | 40098.1027 | 59.8893 | 3783.8625 | 335 | 213.0775 | 3.5455 | 238.5 | 10 | 0 | -103 | 7632 | 88.5814 | 3813.831 | T+28 sec | 40098.1027 | 59.8883 | 3787.2724 | 335 | 213.9682 | 6.0556 | 239.75 | 10 | 0 | -103 | 7632 | 89.3333 | 3819.3275 | T+28 sec | 40098.1027 | 59.8891 | 3788.3545 | 335 | 214.1277 | 6.3529 | 240 | 10 | 0 | -103 | 7632 | 88.7058 | 3819.3286
T+30 sec | 40098.1027 | 59.888 | 3784.7297 | 59.8891 | 3788.3545 |  | 89.5996 | 90.9724 | 3752.731 | 0.56196 | 3773.2497 | 3752.7497 | 3757.0129 | 3681.7141 | 3677.7804 | 633 | [6 empty] | 0 | 633 | -410.7063 | -413.9515 | T+30 sec |  |  | 59.8844 | -401.67 | 59.8891 | -414.4045 | 59.8883 | -411.9963 | 59.8891 | -413.9515 | T+30 sec | 40098.1027 | 59.888 | 3784.7297 | 335 | 214.3467 | 3 | 238.5 | 10 | 0 | -103 | 7632 | 89.5996 | T+30 sec | 40098.1027 | [12 empty] | T+30 sec | 40098.1027 | 59.8844 | 3779.0294 | 335 | 213.4637 | 1.4286 | 237 | 10 | 0 | -103 | 7632 | 92.4569 | 3814.9601 | T+30 sec | 40098.1027 | 59.8893 | 3783.8625 | 335 | 213.0775 | 3.5455 | 238.5 | 10 | 0 | -103 | 7632 | 88.5814 | 3813.831 | T+30 sec | 40098.1027 | 59.8883 | 3787.2724 | 335 | 213.9682 | 6.0556 | 239.75 | 10 | 0 | -103 | 7632 | 89.3333 | 3819.3275 | T+30 sec | 40098.1027 | 59.8891 | 3788.3545 | 335 | 214.1277 | 6.3529 | 240 | 10 | 0 | -103 | 7632 | 88.7058 | 3819.3286
T+32 sec | 40098.1028 | 59.89 | 3784.4189 | 59.8891 | 3788.3545 |  | 88.0005 | 89.9322 | 3752.731 | 0.56196 | 3772.7716 | 3754.6126 | 3757.9399 | 3682.2761 | 3678.0614 | 633 | [6 empty] | 0 | 633 | -416.1029 | -413.9515 | T+32 sec |  |  |  |  | 59.8891 | -414.4045 | 59.8883 | -411.9963 | 59.8891 | -413.9515 | T+32 sec | 40098.1028 | 59.89 | 3784.4189 | 335 | 212.1727 | 4 | 239 | 10 | 0 | -103 | 7632 | 88.0005 | T+32 sec | 40098.1028 | [12 empty] | T+32 sec | 40098.1028 | [12 empty] | T+32 sec | 40098.1028 | 59.8893 | 3783.8625 | 335 | 213.0775 | 3.5455 | 238.5 | 10 | 0 | -103 | 7632 | 88.5814 | 3813.831 | T+32 sec | 40098.1028 | 59.8883 | 3787.2724 | 335 | 213.9682 | 6.0556 | 239.75 | 10 | 0 | -103 | 7632 | 89.3333 | 3819.3275 | T+32 sec | 40098.1028 | 59.8891 | 3788.3545 | 335 | 214.1277 | 6.3529 | 240 | 10 | 0 | -103 | 7632 | 88.7058 | 3819.3286
T+34 sec | 40098.1028 | 59.895 | 3788.0723 | 59.8891 | 3788.3545 |  | 83.9996 | 87.8558 | 3752.731 | 0.56196 | 3771.2571 | 3756.4715 | 3758.6798 | 3682.838 | 3678.3423 | 633 | [6 empty] | 0 | 633 | -430.2471 | -413.9515 | T+34 sec |  |  |  |  | 59.8891 | -414.4045 | 59.8883 | -411.9963 | 59.8891 | -413.9515 | T+34 sec | 40098.1028 | 59.895 | 3788.0723 | 335 | 212.1727 | 5 | 239.5 | 10 | 0 | -103 | 7632 | 83.9996 | T+34 sec | 40098.1028 | [12 empty] | T+34 sec | 40098.1028 | [12 empty] | T+34 sec | 40098.1028 | 59.8893 | 3783.8625 | 335 | 213.0775 | 3.5455 | 238.5 | 10 | 0 | -103 | 7632 | 88.5814 | 3813.831 | T+34 sec | 40098.1028 | 59.8883 | 3787.2724 | 335 | 213.9682 | 6.0556 | 239.75 | 10 | 0 | -103 | 7632 | 89.3333 | 3819.3275 | T+34 sec | 40098.1028 | 59.8891 | 3788.3545 | 335 | 214.1277 | 6.3529 | 240 | 10 | 0 | -103 | 7632 | 88.7058 | 3819.3286
T+36 sec | 40098.1028 | 59.894 | 3788.3276 | 59.8891 | 3788.3545 |  | 84.7992 | 86.786 | 3752.731 | 0.56196 | 3770.7493 | 3758.1481 | 3759.315 | 3683.4 | 3678.6233 | 633 | [6 empty] | 0 | 633 | -427.344 | -413.9515 | T+36 sec |  |  |  |  | 59.8891 | -414.4045 | 59.8883 | -411.9963 | 59.8891 | -413.9515 | T+36 sec | 40098.1028 | 59.894 | 3788.3276 | 335 | 212.1727 | 6 | 240 | 10 | 0 | -103 | 7632 | 84.7992 | T+36 sec | 40098.1028 | [12 empty] | T+36 sec | 40098.1028 | [12 empty] | T+36 sec | 40098.1028 | 59.8893 | 3783.8625 | 335 | 213.0775 | 3.5455 | 238.5 | 10 | 0 | -103 | 7632 | 88.5814 | 3813.831 | T+36 sec | 40098.1028 | 59.8883 | 3787.2724 | 335 | 213.9682 | 6.0556 | 239.75 | 10 | 0 | -103 | 7632 | 89.3333 | 3819.3275 | T+36 sec | 40098.1028 | 59.8891 | 3788.3545 | 335 | 214.1277 | 6.3529 | 240 | 10 | 0 | -103 | 7632 | 88.7058 | 3819.3286
T+38 sec | 40098.1028 | 59.893 | 3788.8684 | 59.8891 | 3788.3545 |  | 85.5988 | 86.3705 | 3752.731 | 0.56196 | 3770.8957 | 3759.6841 | 3759.894 | 3683.9619 | 3678.9043 | 633 | [6 empty] | 0 | 633 | -424.4799 | -413.9515 | T+38 sec |  |  |  |  | 59.8891 | -414.4045 | 59.8883 | -411.9963 | 59.8891 | -413.9515 | T+38 sec | 40098.1028 | 59.893 | 3788.8684 | 335 | 212.1727 | 7 | 240.5 | 10 | 0 | -103 | 7632 | 85.5988 | T+38 sec | 40098.1028 | [12 empty] | T+38 sec | 40098.1028 | [12 empty] | T+38 sec | 40098.1028 | 59.8893 | 3783.8625 | 335 | 213.0775 | 3.5455 | 238.5 | 10 | 0 | -103 | 7632 | 88.5814 | 3813.831 | T+38 sec | 40098.1028 | 59.8883 | 3787.2724 | 335 | 213.9682 | 6.0556 | 239.75 | 10 | 0 | -103 | 7632 | 89.3333 | 3819.3275 | T+38 sec | 40098.1028 | 59.8891 | 3788.3545 | 335 | 214.1277 | 6.3529 | 240 | 10 | 0 | -103 | 7632 | 88.7058 | 3819.3286
T+40 sec | 40098.1028 | 59.894 | 3788.4719 | 59.8891 | 3788.3545 |  | 84.7992 | 85.8205 | 3752.731 | 0.56196 | 3770.9077 | 3761.055 | 3760.4185 | 3684.5239 | 3679.1853 | 633 | [6 empty] | 0 | 633 | -427.344 | -413.9515 | T+40 sec |  |  |  |  | 59.8891 | -414.4045 | 59.8883 | -411.9963 | 59.8891 | -413.9515 | T+40 sec | 40098.1028 | 59.894 | 3788.4719 | 335 | 212.1727 | 8 | 241 | 10 | 0 | -103 | 7632 | 84.7992 | T+40 sec | 40098.1028 | [12 empty] | T+40 sec | 40098.1028 | [12 empty] | T+40 sec | 40098.1028 | 59.8893 | 3783.8625 | 335 | 213.0775 | 3.5455 | 238.5 | 10 | 0 | -103 | 7632 | 88.5814 | 3813.831 | T+40 sec | 40098.1028 | 59.8883 | 3787.2724 | 335 | 213.9682 | 6.0556 | 239.75 | 10 | 0 | -103 | 7632 | 89.3333 | 3819.3275 | T+40 sec | 40098.1028 | 59.8891 | 3788.3545 | 335 | 214.1277 | 6.3529 | 240 | 10 | 0 | -103 | 7632 | 88.7058 | 3819.3286
T+42 sec | 40098.1029 | 59.894 | 3792.2756 | 59.8891 | 3788.3545 |  | 84.7992 | 85.4631 | 3752.731 | 0.56196 | 3771.1122 | 3762.4741 | 3760.9046 | 3685.0859 | 3679.4663 | 633 | [6 empty] | 0 | 633 | -427.344 | -413.9515 | T+42 sec | [6 empty] | 59.8883 | -411.9963 | 59.8891 | -413.9515 | T+42 sec | 40098.1029 | 59.894 | 3792.2756 | 335 | 215.5982 | 9 | 241.5 | 10 | 0 | -103 | 7632 | 84.7992 | T+42 sec | 40098.1029 | [12 empty] | T+42 sec | 40098.1029 | [12 empty] | T+42 sec | 40098.1029 | [12 empty] | T+42 sec | 40098.1029 | 59.8883 | 3787.2724 | 335 | 213.9682 | 6.0556 | 239.75 | 10 | 0 | -103 | 7632 | 89.3333 | 3819.3275 | T+42 sec | 40098.1029 | 59.8891 | 3788.3545 | 335 | 214.1277 | 6.3529 | 240 | 10 | 0 | -103 | 7632 | 88.7058 | 3819.3286
T+44 sec | 40098.1029 | 59.891 | 3793.0745 | 59.8891 | 3788.3545 |  | 87.2009 | 86.0713 | 3752.731 | 0.56196 | 3772.2824 | 3763.8045 | 3761.3993 | 3685.6478 | 3679.7472 | 633 | [6 empty] | 0 | 633 | -418.8547 | -413.9515 | T+44 sec | [6 empty] | 59.8883 | -411.9963 | 59.8891 | -413.9515 | T+44 sec | 40098.1029 | 59.891 | 3793.0745 | 335 | 215.5982 | 10 | 242 | 10 | 0 | -103 | 7632 | 87.2009 | T+44 sec | 40098.1029 | [12 empty] | T+44 sec | 40098.1029 | [12 empty] | T+44 sec | 40098.1029 | [12 empty] | T+44 sec | 40098.1029 | 59.8883 | 3787.2724 | 335 | 213.9682 | 6.0556 | 239.75 | 10 | 0 | -103 | 7632 | 89.3333 | 3819.3275 | T+44 sec | 40098.1029 | 59.8891 | 3788.3545 | 335 | 214.1277 | 6.3529 | 240 | 10 | 0 | -103 | 7632 | 88.7058 | 3819.3286
T+46 sec | 40098.1029 | 59.89 | 3794.3743 | 59.8891 | 3788.3545 |  | 88.0005 | 86.7465 | 3752.731 | 0.56196 | 3773.5196 | 3765.0783 | 3761.9043 | 3686.2098 | 3680.0282 | 633 | [6 empty] | 0 | 633 | -416.1029 | -413.9515 | T+46 sec | [6 empty] | 59.8883 | -411.9963 | 59.8891 | -413.9515 | T+46 sec | 40098.1029 | 59.89 | 3794.3743 | 335 | 215.5982 | 11 | 242.5 | 10 | 0 | -103 | 7632 | 88.0005 | T+46 sec | 40098.1029 | [12 empty] | T+46 sec | 40098.1029 | [12 empty] | T+46 sec | 40098.1029 | [12 empty] | T+46 sec | 40098.1029 | 59.8883 | 3787.2724 | 335 | 213.9682 | 6.0556 | 239.75 | 10 | 0 | -103 | 7632 | 89.3333 | 3819.3275 | T+46 sec | 40098.1029 | 59.8891 | 3788.3545 | 335 | 214.1277 | 6.3529 | 240 | 10 | 0 | -103 | 7632 | 88.7058 | 3819.3286
T+48 sec | 40098.1029 | 59.885 | 3799.4277 | 59.8891 | 3788.3545 |  | 92.0013 | 88.5857 | 3752.731 | 0.56196 | 3775.9207 | 3766.4523 | 3762.4649 | 3686.7717 | 3680.3092 | 633 | [6 empty] | 0 | 633 | -402.8591 | -413.9515 | T+48 sec | [6 empty] | 59.8883 | -411.9963 | 59.8891 | -413.9515 | T+48 sec | 40098.1029 | 59.885 | 3799.4277 | 335 | 215.5982 | 12 | 243 | 10 | 0 | -103 | 7632 | 92.0013 | T+48 sec | 40098.1029 | [12 empty] | T+48 sec | 40098.1029 | [12 empty] | T+48 sec | 40098.1029 | [12 empty] | T+48 sec | 40098.1029 | 59.8883 | 3787.2724 | 335 | 213.9682 | 6.0556 | 239.75 | 10 | 0 | -103 | 7632 | 89.3333 | 3819.3275 | T+48 sec | 40098.1029 | 59.8891 | 3788.3545 | 335 | 214.1277 | 6.3529 | 240 | 10 | 0 | -103 | 7632 | 88.7058 | 3819.3286
T+50 sec | 40098.103 | 59.885 | 3800.4275 | 59.8891 | 3788.3545 |  | 92.0013 | 89.7812 | 3752.731 | 0.56196 | 3777.6782 | 3767.759 | 3763.0501 | 3687.3337 | 3680.5902 | 633 | [6 empty] | 0 | 633 | -402.8591 | -413.9515 | T+50 sec | [6 empty] | 59.8883 | -411.9963 | 59.8891 | -413.9515 | T+50 sec | 40098.103 | 59.885 | 3800.4275 | 335 | 215.5982 | 13 | 243.5 | 10 | 0 | -103 | 7632 | 92.0013 | T+50 sec | 40098.103 | [12 empty] | T+50 sec | 40098.103 | [12 empty] | T+50 sec | 40098.103 | [12 empty] | T+50 sec | 40098.103 | 59.8883 | 3787.2724 | 335 | 213.9682 | 6.0556 | 239.75 | 10 | 0 | -103 | 7632 | 89.3333 | 3819.3275 | T+50 sec | 40098.103 | 59.8891 | 3788.3545 | 335 | 214.1277 | 6.3529 | 240 | 10 | 0 | -103 | 7632 | 88.7058 | 3819.3286
T+52 sec | 40098.103 | 59.888 | 3799.9592 | 59.8891 | 3788.3545 |  | 89.5996 | 89.7176 | 3752.731 | 0.56196 | 3778.1766 | 3768.9516 | 3763.6103 | 3687.8957 | 3680.8712 | 633 | [6 empty] | 0 | 633 | -410.7063 | -413.9515 | T+52 sec | [6 empty] | 59.8883 | -411.9963 | 59.8891 | -413.9515 | T+52 sec | 40098.103 | 59.888 | 3799.9592 | 335 | 218.3273 | 14 | 244 | 10 | 0 | -103 | 7632 | 89.5996 | T+52 sec | 40098.103 | [12 empty] | T+52 sec | 40098.103 | [12 empty] | T+52 sec | 40098.103 | [12 empty] | T+52 sec | 40098.103 | 59.8883 | 3787.2724 | 335 | 213.9682 | 6.0556 | 239.75 | 10 | 0 | -103 | 7632 | 89.3333 | 3819.3275 | T+52 sec | 40098.103 | 59.8891 | 3788.3545 | 335 | 214.1277 | 6.3529 | 240 | 10 | 0 | -103 | 7632 | 88.7058 | 3819.3286
T+54 sec | 40098.103 | 59.887 | 3803.625 |  |  |  | 90.3992 | 89.9562 |  | 0.56196 | 3778.9771 | 3770.1899 | 3764.1591 | 3688.4576 | 3681.1521 | 633 | [6 empty] | 0 | 633 | -408.0602 |  | T+54 sec | [10 empty] | T+54 sec | 40098.103 | 59.887 | 3803.625 | 335 | 218.3273 | 15 | 244.5 | 10 | 0 | -103 | 7632 | 90.3992 | T+54 sec | 40098.103 | [12 empty] | T+54 sec | 40098.103 | [12 empty] | T+54 sec | 40098.103 | [12 empty] | T+54 sec | 40098.103 | [12 empty] | T+54 sec | 40098.103
T+56 sec | 40098.103 | 59.888 | 3802.925 |  |  |  | 89.5996 | 89.8314 |  | 0.56196 | 3779.4142 | 3771.3187 | 3764.6851 | 3689.0196 | 3681.4331 | 633 | [6 empty] | 0 | 633 | -410.7063 |  | T+56 sec | [10 empty] | T+56 sec | 40098.103 | 59.888 | 3802.925 | 335 | 218.3273 | 16 | 245 | 10 | 0 | -103 | 7632 | 89.5996 | T+56 sec | 40098.103 | [12 empty] | T+56 sec | 40098.103 | [12 empty] | T+56 sec | 40098.103 | [12 empty] | T+56 sec | 40098.103 | [12 empty] | T+56 sec | 40098.103
T+58 sec | 40098.1031 | 59.888 | 3802.9509 |  |  |  | 89.5996 | 89.7503 |  | 0.56196 | 3779.8951 | 3772.3731 | 3765.1921 | 3689.5815 | 3681.7141 | 633 | [6 empty] | 0 | 633 | -410.7063 |  | T+58 sec | [10 empty] | T+58 sec | 40098.1031 | 59.888 | 3802.9509 | 335 | 218.3273 | 16 | 245.5 | 10 | 0 | -103 | 7632 | 89.5996 | T+58 sec | 40098.1031 | [12 empty] | T+58 sec | 40098.1031 | [12 empty] | T+58 sec | 40098.1031 | [12 empty] | T+58 sec | 40098.1031 | [12 empty] | T+58 sec | 40098.1031
T+60 sec | 40098.1031 | 59.89 | 3804.3879 |  |  |  | 88.0005 | 89.1378 |  | 0.56196 | 3779.8446 | 3773.4059 | 3765.6648 | 3690.1435 | 3681.9951 | 633 | [6 empty] | 0 | 633 | -416.1029 |  | T+60 sec | [10 empty] | T+60 sec | 40098.1031 | 59.89 | 3804.3879 | 335 | 218.3273 | 16 | 246 | 10 | 0 | -103 | 7632 | 88.0005 | T+60 sec | 40098.1031 | [12 empty] | T+60 sec | 40098.1031 | [12 empty] | T+60 sec | 40098.1031 | [12 empty] | T+60 sec | 40098.1031 | [12 empty] | T+60 sec | 40098.1031
T+62 sec | 40098.1031 | 59.889 | 3805.4961 |  |  |  | 88.8 | 89.0196 |  | 0.56196 | 3780.2884 | 3774.4087 | 3766.1218 | 3690.7055 | 3682.2761 | 633 | [6 empty] | 0 | 633 | -413.387 |  | T+62 sec | [10 empty] | T+62 sec | 40098.1031 | 59.889 | 3805.4961 | 335 | 217.3794 | 16 | 246.5 | 10 | 0 | -103 | 7632 | 88.8 | T+62 sec | 40098.1031 | [12 empty] | T+62 sec | 40098.1031 | [12 empty] | T+62 sec | 40098.1031 | [12 empty] | T+62 sec | 40098.1031 | [12 empty] | T+62 sec | 40098.1031
T+64 sec | 40098.1031 | 59.882 | 3805.6167 |  |  |  | 94.4 | 90.9028 |  | 0.56196 | 3782.7335 | 3775.3544 | 3766.6252 | 3691.2674 | 3682.557 | 633 | [6 empty] | 0 | 633 | -395.3155 |  | T+64 sec | [10 empty] | T+64 sec | 40098.1031 | 59.882 | 3805.6167 | 335 | 217.3794 | 16 | 247 | 10 | 0 | -103 | 7632 | 94.4 | T+64 sec | 40098.1031 | [12 empty] | T+64 sec | 40098.1031 | [12 empty] | T+64 sec | 40098.1031 | [12 empty] | T+64 sec | 40098.1031 | [12 empty] | T+64 sec | 40098.1031
T+66 sec | 40098.1031 | 59.873 | 3809.2373 |  |  |  | 101.5991 | 94.6465 |  | 0.56196 | 3787.0392 | 3776.351 | 3767.2256 | 3691.8294 | 3682.838 | 633 | [6 empty] | 0 | 633 | -374.2813 |  | T+66 sec | [10 empty] | T+66 sec | 40098.1031 | 59.873 | 3809.2373 | 335 | 217.3794 | 16 | 247.5 | 10 | 0 | -103 | 7631 | 101.5991 | T+66 sec | 40098.1031 | [12 empty] | T+66 sec | 40098.1031 | [12 empty] | T+66 sec | 40098.1031 | [12 empty] | T+66 sec | 40098.1031 | [12 empty] | T+66 sec | 40098.1031
T+68 sec | 40098.1032 | 59.857 | 3811.5029 |  |  |  | 114.4012 | 101.5607 |  | 0.56196 | 3794.5153 | 3777.3553 | 3768.0053 | 3692.3913 | 3683.119 | 633 | [6 empty] | 0 | 633 | -341.9278 |  | T+68 sec | [10 empty] | T+68 sec | 40098.1032 | 59.857 | 3811.5029 | 335 | 217.3794 | 16 | 248 | 10 | 0 | -103 | 7625 | 114.4012 | T+68 sec | 40098.1032 | [12 empty] | T+68 sec | 40098.1032 | [12 empty] | T+68 sec | 40098.1032 | [12 empty] | T+68 sec | 40098.1032 | [12 empty] | T+68 sec | 40098.1032
T+70 sec | 40098.1032 | 59.849 | 3814.8623 |  |  |  | 120.8008 | 108.2947 |  | 0.56196 | 3801.8113 | 3778.3972 | 3768.9443 | 3692.9533 | 3683.4 | 633 | [6 empty] | 0 | 633 | -327.765 |  | T+70 sec | [10 empty] | T+70 sec | 40098.1032 | 59.849 | 3814.8623 | 335 | 217.3794 | 16 | 248.5 | 10 | 0 | -103 | 7623 | 120.8008 | T+70 sec | 40098.1032 | [12 empty] | T+70 sec | 40098.1032 | [12 empty] | T+70 sec | 40098.1032 | [12 empty] | T+70 sec | 40098.1032 | [12 empty] | T+70 sec | 40098.1032
T+72 sec | 40098.1032 | 59.852 | 3815.8889 |  |  |  | 118.399 | 111.8312 |  | 0.56196 | 3805.9098 | 3779.4104 | 3769.9434 | 3693.5153 | 3683.681 | 633 | [6 empty] | 0 | 633 | -332.9405 |  | T+72 sec | [10 empty] | T+72 sec | 40098.1032 | 59.852 | 3815.8889 | 335 | 214.8304 | 16 | 249 | 10 | 0 | -103 | 7621 | 118.399 | T+72 sec | 40098.1032 | [12 empty] | T+72 sec | 40098.1032 | [12 empty] | T+72 sec | 40098.1032 | [12 empty] | T+72 sec | 40098.1032 | [12 empty] | T+72 sec | 40098.1032
T+74 sec | 40098.1032 | 59.858 | 3825.6426 |  |  |  | 113.5986 | 112.4498 |  | 0.56196 | 3807.0903 | 3780.6271 | 3770.921 | 3694.0772 | 3683.9619 | 633 | [6 empty] | 0 | 633 | -343.791 |  | T+74 sec | [10 empty] | T+74 sec | 40098.1032 | 59.858 | 3825.6426 | 335 | 214.8304 | 16 | 249.5 | 10 | 0 | -103 | 7623 | 113.5986 | T+74 sec | 40098.1032 | [12 empty] | T+74 sec | 40098.1032 | [12 empty] | T+74 sec | 40098.1032 | [12 empty] | T+74 sec | 40098.1032 | [12 empty] | T+74 sec | 40098.1032
T+76 sec | 40098.1033 | 59.863 | 3826.0532 |  |  |  | 109.6008 | 111.4527 |  | 0.56196 | 3806.6551 | 3781.7919 | 3771.8372 | 3694.6392 | 3684.2429 | 633 | [6 empty] | 0 | 633 | -353.382 |  | T+76 sec | [10 empty] | T+76 sec | 40098.1033 | 59.863 | 3826.0532 | 335 | 214.8304 | 16 | 250 | 10 | 0 | -103 | 7625 | 109.6008 | T+76 sec | 40098.1033 | [12 empty] | T+76 sec | 40098.1033 | [12 empty] | T+76 sec | 40098.1033 | [12 empty] | T+76 sec | 40098.1033 | [12 empty] | T+76 sec | 40098.1033
T+78 sec | 40098.1033 | 59.866 | 3826.0024 |  |  |  | 107.1991 | 109.9639 |  | 0.56196 | 3805.7284 | 3782.8971 | 3772.6845 | 3695.2011 | 3684.5239 | 633 | [6 empty] | 0 | 633 | -359.4057 |  | T+78 sec | [10 empty] | T+78 sec | 40098.1033 | 59.866 | 3826.0024 | 335 | 214.8304 | 16 | 250.5 | 10 | 0 | -103 | 7627 | 107.1991 | T+78 sec | 40098.1033 | [12 empty] | T+78 sec | 40098.1033 | [12 empty] | T+78 sec | 40098.1033 | [12 empty] | T+78 sec | 40098.1033 | [12 empty] | T+78 sec | 40098.1033
T+80 sec | 40098.1033 | 59.865 | 3827.5239 |  |  |  | 107.9987 | 109.2761 |  | 0.56196 | 3805.6025 | 3783.9856 | 3773.4874 | 3695.7631 | 3684.8049 | 633 | [6 empty] | 0 | 633 | -357.3777 |  | T+80 sec | [10 empty] | T+80 sec | 40098.1033 | 59.865 | 3827.5239 | 335 | 214.8304 | 16 | 251 | 10 | 0 | -103 | 7628 | 107.9987 | T+80 sec | 40098.1033 | [12 empty] | T+80 sec | 40098.1033 | [12 empty] | T+80 sec | 40098.1033 | [12 empty] | T+80 sec | 40098.1033 | [12 empty] | T+80 sec | 40098.1033
| 40098.1033 | 59.867 | 3826.7532 |  |  |  | 106.3995 | 108.2693 |  | 0.56196 | 3805.1576 | 3785.0039 | 3774.2414 | 3696.3251 | 3685.0859 | 633 | [6 empty] | 0 | 633 | -361.4568 | [13 empty] | 40098.1033 | 59.867 | 3826.7532 | 335 | 227.6559 | 16 | 251.5 | 10 | 0 | -103 | 7628 | 106.3995
| 40098.1034 | 59.866 | 3826.7834 |  |  |  | 107.1991 | 107.8947 |  | 0.56196 | 3805.345 | 3785.9755 | 3774.9648 | 3696.887 | 3685.3668 | 633 | [6 empty] | 0 | 633 | -359.4057 | [13 empty] | 40098.1034 | 59.866 | 3826.7834 | 335 | 227.6559 | 16 | 252 | 10 | 0 | -103 | 7629 | 107.1991
| 40098.1034 | 59.871 | 3826.4536 |  |  |  | 103.2013 | 106.252 |  | 0.56196 | 3804.2643 | 3786.8954 | 3775.6307 | 3697.449 | 3685.6478 | 633 | [6 empty] | 0 | 633 | -369.9011 | [13 empty] | 40098.1034 | 59.871 | 3826.4536 | 335 | 227.6559 | 16 | 252.5 | 10 | 0 | -103 | 7630 | 103.2013
| 40098.1034 | 59.874 | 3825.7134 |  |  |  | 100.7996 | 104.3437 |  | 0.56196 | 3802.9179 | 3787.7581 | 3776.2371 | 3698.0109 | 3685.9288 | 633 | [6 empty] | 0 | 633 | -376.5063 | [13 empty] | 40098.1034 | 59.874 | 3825.7134 | 335 | 227.6559 | 16 | 253 | 10 | 0 | -103 | 7631 | 100.7996
| 40098.1034 | 59.879 | 3823.8257 |  |  |  | 96.7987 | 101.7029 |  | 0.56196 | 3800.8391 | 3788.5421 | 3776.7719 | 3698.5729 | 3686.2098 | 633 | [6 empty] | 0 | 633 | -388.0493 | [13 empty] | 40098.1034 | 59.879 | 3823.8257 | 335 | 227.6559 | 16 | 253.5 | 10 | 0 | -103 | 7635 | 96.7987
| 40098.1034 | 59.88 | 3822.5054 |  |  |  | 95.9991 | 99.7066 |  | 0.56196 | 3799.4048 | 3789.2648 | 3777.2534 | 3699.1349 | 3686.4908 | 633 | [6 empty] | 0 | 633 | -390.4415 | [13 empty] | 40098.1034 | 59.88 | 3822.5054 | 335 | 225.0181 | 16 | 254 | 10 | 0 | -103 | 7638 | 95.9991
| 40098.1035 | 59.883 | 3819.0811 |  |  |  | 93.6005 | 97.5695 |  | 0.56196 | 3797.8296 | 3789.8859 | 3777.6821 | 3699.6968 | 3686.7717 | 633 | [6 empty] | 0 | 633 | -397.7985 | [13 empty] | 40098.1035 | 59.883 | 3819.0811 | 335 | 225.0181 | 16 | 254.5 | 10 | 0 | -103 | 7639 | 93.6005
| 40098.1035 | 59.886 | 3818.0552 |  |  |  | 91.1987 | 95.3397 |  | 0.56196 | 3796.1618 | 3790.4608 | 3778.0592 | 3700.2588 | 3687.0527 | 633 | [6 empty] | 0 | 633 | -405.4479 | [13 empty] | 40098.1035 | 59.886 | 3818.0552 | 335 | 225.0181 | 16 | 255 | 10 | 0 | -103 | 7642 | 91.1987
| 40098.1035 | 59.89 | 3816.8147 |  |  |  | 88.0005 | 92.771 |  | 0.56196 | 3794.155 | 3790.9879 | 3778.3812 | 3700.8207 | 3687.3337 | 633 | [6 empty] | 0 | 633 | -416.1029 | [13 empty] | 40098.1035 | 59.89 | 3816.8147 | 335 | 225.0181 | 16 | 255.5 | 10 | 0 | -103 | 7644 | 88.0005
| 40098.1035 | 59.892 | 3815.0098 |  |  |  | 86.4014 | 90.5416 |  | 0.56196 | 3792.4876 | 3791.4589 | 3778.6578 | 3701.3827 | 3687.6147 | 633 | [6 empty] | 0 | 633 | -421.6432 | [13 empty] | 40098.1035 | 59.892 | 3815.0098 | 335 | 225.0181 | 16 | 256 | 10 | 0 | -103 | 7645 | 86.4014
| 40098.1036 | 59.889 | 3813.7827 |  |  |  | 88.8 | 89.9321 |  | 0.56196 | 3792.44 | 3791.8882 | 3778.9228 | 3701.9447 | 3687.8957 | 633 | [6 empty] | 0 | 633 | -413.387 | [13 empty] | 40098.1036 | 59.889 | 3813.7827 | 335 | 228.3652 | 16 | 256.5 | 10 | 0 | -103 | 7647 | 88.8
| 40098.1036 | 59.893 | 3811.8384 |  |  |  | 85.5988 | 88.4154 |  | 0.56196 | 3791.4853 | 3792.2646 | 3779.1598 | 3702.5066 | 3688.1766 | 633 | [6 empty] | 0 | 633 | -424.4799 | [13 empty] | 40098.1036 | 59.893 | 3811.8384 | 335 | 228.3652 | 16 | 257 | 10 | 0 | -103 | 7648 | 85.5988
| 40098.1036 | 59.899 | 3809.6519 |  |  |  | 80.8014 | 85.7505 |  | 0.56196 | 3789.3824 | 3792.5866 | 3779.3491 | 3703.0686 | 3688.4576 | 633 | [6 empty] | 0 | 633 | -442.2647 | [13 empty] | 40098.1036 | 59.899 | 3809.6519 | 335 | 228.3652 | 16 | 257.5 | 10 | 0 | -103 | 7649 | 80.8014
| 40098.1036 | 59.903 | 3806.9722 |  |  |  | 77.6001 | 82.8979 |  | 0.56196 | 3787.0917 | 3792.8482 | 3779.4899 | 3703.6305 | 3688.7386 | 633 | [6 empty] | 0 | 633 | -454.9854 | [13 empty] | 40098.1036 | 59.903 | 3806.9722 | 335 | 228.3652 | 16 | 258 | 10 | 0 | -103 | 7650 | 77.6001
| 40098.1037 | 59.902 | 3805.5933 |  |  |  | 78.3997 | 81.3235 |  | 0.56196 | 3786.0793 | 3793.0758 | 3779.6076 | 3704.1925 | 3689.0196 | 633 | [6 empty] | 0 | 633 | -451.7402 | [13 empty] | 40098.1037 | 59.902 | 3805.5933 | 335 | 228.3652 | 16 | 258.5 | 10 | 0 | -103 | 7651 | 78.3997
| 40098.1037 | 59.902 | 3804.1885 |  |  |  | 78.3997 | 80.3001 |  | 0.56196 | 3785.6179 | 3793.2707 | 3779.713 | 3704.7545 | 3689.3006 | 633 | [6 empty] | 0 | 633 | -451.7402 | [13 empty] | 40098.1037 | 59.902 | 3804.1885 | 335 | 234.0753 | 16 | 259 | 10 | 0 | -103 | 7652 | 78.3997
| 40098.1037 | 59.904 | 3796.0776 |  |  |  | 76.8005 | 79.0753 |  | 0.56196 | 3784.955 | 3793.3191 | 3779.8034 | 3705.3164 | 3689.5815 | 633 | [6 empty] | 0 | 633 | -458.2776 | [13 empty] | 40098.1037 | 59.904 | 3796.0776 | 335 | 234.0753 | 16 | 259.5 | 10 | 0 | -103 | 7653 | 76.8005
| 40098.1037 | 59.907 | 3793.9751 |  |  |  | 74.3988 | 77.4385 |  | 0.56196 | 3783.8802 | 3793.3302 | 3779.8725 | 3705.8784 | 3689.8625 | 633 | [6 empty] | 0 | 633 | -468.4595 | [13 empty] | 40098.1037 | 59.907 | 3793.9751 | 335 | 234.0753 | 16 | 260 | 10 | 0 | -103 | 7654 | 74.3988
| 40098.1037 | 59.911 | 3792.1694 |  |  |  | 71.2006 | 75.2552 |  | 0.56196 | 3782.2589 | 3793.3109 | 3779.9123 | 3706.4403 | 3690.1435 | 633 | [6 empty] | 0 | 633 | -482.7421 | [13 empty] | 40098.1037 | 59.911 | 3792.1694 | 335 | 234.0753 | 16 | 260.5 | 10 | 0 | -103 | 7655 | 71.2006
| 40098.1038 | 59.916 | 3791.502 |  |  |  | 67.1997 | 72.4358 |  | 0.56196 | 3780.0014 | 3793.2812 | 3779.9137 | 3707.0023 | 3690.4245 | 633 | [6 empty] | 0 | 633 | -501.8836 | [13 empty] | 40098.1038 | 59.916 | 3791.502 | 335 | 234.0753 | 16 | 261 | 10 | 0 | -103 | 7655 | 67.1997
| 40098.1038 | 59.916 | 3789.5337 |  |  |  | 67.1997 | 70.6032 |  | 0.56196 | 3778.7307 | 3793.2208 | 3779.8946 | 3707.5643 | 3690.7055 | 633 | [6 empty] | 0 | 633 | -501.8836 | [13 empty] | 40098.1038 | 59.916 | 3789.5337 | 335 | 228.7982 | 16 | 261.5 | 10 | 0 | -103 | 7656 | 67.1997
| 40098.1038 | 59.917 | 3788.1321 |  |  |  | 66.4001 | 69.1321 |  | 0.56196 | 3777.8216 | 3793.14 | 3779.8617 | 3708.1262 | 3690.9864 | 633 | [6 empty] | 0 | 633 | -505.8925 | [13 empty] | 40098.1038 | 59.917 | 3788.1321 | 335 | 228.7982 | 16 | 262 | 10 | 0 | -103 | 7656 | 66.4001
| 40098.1038 | 59.918 | 3784.5635 |  |  |  | 65.6006 | 67.8961 |  | 0.56196 | 3777.1476 | 3793.006 | 3779.8193 | 3708.6882 | 3691.2674 | 633 | [6 empty] | 0 | 633 | -509.9659 | [13 empty] | 40098.1038 | 59.918 | 3784.5635 | 335 | 228.7982 | 16 | 262.5 | 10 | 0 | -103 | 7657 | 65.6006
| 40098.1039 | 59.92 | 3783.0283 |  |  |  | 64.0015 | 66.533 |  | 0.56196 | 3776.3464 | 3792.8525 | 3779.7659 | 3709.2501 | 3691.5484 | 633 | [6 empty] | 0 | 633 | -518.3127 | [13 empty] | 40098.1039 | 59.92 | 3783.0283 | 335 | 228.7982 | 16 | 263 | 10 | 0 | -103 | 7657 | 64.0015
| 40098.1039 | 59.921 | 3781.7012 |  |  |  | 63.1989 | 65.366 |  | 0.56196 | 3775.7414 | 3792.6835 | 3779.7049 | 3709.8121 | 3691.8294 | 633 | [6 empty] | 0 | 633 | -522.6058 | [13 empty] | 40098.1039 | 59.921 | 3781.7012 | 335 | 228.7982 | 16 | 263.5 | 10 | 0 | -103 | 7658 | 63.1989
| 40098.1039 | 59.92 | 3776.3584 |  |  |  | 64.0015 | 64.8884 |  | 0.56196 | 3775.8258 | 3792.4399 | 3779.647 | 3710.3741 | 3692.1104 | 633 | [6 empty] | 0 | 633 | -518.3127 | [13 empty] | 40098.1039 | 59.92 | 3776.3584 | 335 | 229.467 | 16 | 264 | 10 | 0 | -103 | 7658 | 64.0015
| 40098.1039 | 59.917 | 3775.6355 |  |  |  | 66.4001 | 65.4175 |  | 0.56196 | 3776.9168 | 3792.1928 | 3779.6069 | 3710.936 | 3692.3913 | 633 | [6 empty] | 0 | 633 | -505.8925 | [13 empty] | 40098.1039 | 59.917 | 3775.6355 | 335 | 229.467 | 16 | 264.5 | 10 | 0 | -103 | 7659 | 66.4001
| 40098.104 | 59.92 | 3774.6042 |  |  |  | 64.0015 | 64.9219 |  | 0.56196 | 3776.9832 | 3791.9379 | 3779.5689 | 3711.498 | 3692.6723 | 633 | [6 empty] | 0 | 633 | -518.3127 | [13 empty] | 40098.104 | 59.92 | 3774.6042 | 335 | 229.467 | 16 | 265 | 10 | 0 | -103 | 7659 | 64.0015
| 40098.104 | 59.921 | 3773.3337 |  |  |  | 63.1989 | 64.3188 |  | 0.56196 | 3776.9421 | 3791.6721 | 3779.5313 | 3712.0599 | 3692.9533 | 633 | [6 empty] | 0 | 633 | -522.6058 | [13 empty] | 40098.104 | 59.921 | 3773.3337 | 335 | 229.467 | 16 | 265.5 | 10 | 0 | -103 | 7659 | 63.1989
| 40098.104 | 59.923 | 3773.9578 |  |  |  | 61.5997 | 63.3672 |  | 0.56196 | 3776.5523 | 3791.4226 | 3779.4894 | 3712.6219 | 3693.2343 | 633 | [6 empty] | 0 | 633 | -531.3751 | [13 empty] | 40098.104 | 59.923 | 3773.9578 | 335 | 229.467 | 16 | 266 | 10 | 0 | -103 | 7660 | 61.5997
| 40098.104 | 59.926 | 3772.7224 |  |  |  | 59.201 | 61.909 |  | 0.56196 | 3775.6562 | 3791.1629 | 3779.4361 | 3713.1839 | 3693.5153 | 633 | [6 empty] | 0 | 633 | -545.095 | [13 empty] | 40098.104 | 59.926 | 3772.7224 | 335 | 228.9802 | 16 | 266.5 | 10 | 0 | -103 | 7660 | 59.201
| 40098.1041 | 59.925 | 3771.6704 |  |  |  | 60.0006 | 61.2411 |  | 0.56196 | 3775.5502 | 3790.8958 | 3779.3829 | 3713.7458 | 3693.7962 | 633 | [6 empty] | 0 | 633 | -540.4437 | [13 empty] | 40098.1041 | 59.925 | 3771.6704 | 335 | 228.9802 | 16 | 267 | 10 | 0 | -103 | 7661 | 60.0006
| 40098.1041 | 59.928 | 3769.6296 |  |  |  | 57.5989 | 59.9663 |  | 0.56196 | 3774.8374 | 3790.6085 | 3779.3215 | 3714.3078 | 3694.0772 | 633 | [6 empty] | 0 | 633 | -554.6607 | [13 empty] | 40098.1041 | 59.928 | 3769.6296 | 335 | 228.9802 | 16 | 267.5 | 10 | 0 | -103 | 7661 | 57.5989
| 40098.1041 | 59.927 | 3768.707 |  |  |  | 58.4015 | 59.4186 |  | 0.56196 | 3774.8517 | 3790.3164 | 3779.2619 | 3714.8697 | 3694.3582 | 633 | [6 empty] | 0 | 633 | -549.8272 | [13 empty] | 40098.1041 | 59.927 | 3768.707 | 335 | 228.9802 | 16 | 268 | 10 | 0 | -103 | 7662 | 58.4015
| 40098.1041 | 59.932 | 3767.6428 |  |  |  | 54.4006 | 57.6623 |  | 0.56196 | 3773.6573 | 3790.0181 | 3779.1881 | 3715.4317 | 3694.6392 | 633 | [6 empty] | 0 | 633 | -574.796 | [13 empty] | 40098.1041 | 59.932 | 3767.6428 | 335 | 228.9802 | 16 | 268.5 | 10 | 0 | -103 | 7662 | 54.4006
| 40098.1041 | 59.927 | 3767.021 |  |  |  | 58.4015 | 57.921 |  | 0.56196 | 3774.478 | 3789.7194 | 3779.127 | 3715.9937 | 3694.9202 | 633 | [6 empty] | 0 | 633 | -549.8272 | [13 empty] | 40098.1041 | 59.927 | 3767.021 | 335 | 219.9756 | 16 | 269 | 10 | 0 | -103 | 7663 | 58.4015
| 40098.1042 | 59.928 | 3767.408 |  |  |  | 57.5989 | 57.8083 |  | 0.56196 | 3774.9272 | 3789.4334 | 3779.0731 | 3716.5556 | 3695.2011 | 633 | [6 empty] | 0 | 633 | -554.6607 | [13 empty] | 40098.1042 | 59.928 | 3767.408 | 335 | 219.9756 | 16 | 269.5 | 10 | 0 | -103 | 7663 | 57.5989
| 40098.1042 | 59.931 | 3766.7881 |  |  |  | 55.2002 | 56.8954 |  | 0.56196 | 3774.5763 | 3789.1467 | 3779.0162 | 3717.1176 | 3695.4821 | 633 | [6 empty] | 0 | 633 | -569.6264 | [13 empty] | 40098.1042 | 59.931 | 3766.7881 | 335 | 219.9756 | 16 | 270 | 10 | 0 | -103 | 7664 | 55.2002
| 40098.1042 | 59.929 | 3766.259 |  |  |  | 56.7993 | 56.8618 |  | 0.56196 | 3775.1046 | 3788.8606 | 3778.9673 | 3717.6795 | 3695.7631 | 633 | [6 empty] | 0 | 633 | -559.5611 | [13 empty] | 40098.1042 | 59.929 | 3766.259 | 335 | 219.9756 | 16 | 270.5 | 10 | 0 | -103 | 7664 | 56.7993
| 40098.1042 | 59.931 | 3765.6716 |  |  |  | 55.2002 | 56.2802 |  | 0.56196 | 3775.085 | 3788.5744 | 3778.9194 | 3718.2415 | 3696.0441 | 633 | [6 empty] | 0 | 633 | -569.6264 | [13 empty] | 40098.1042 | 59.931 | 3765.6716 | 335 | 219.9756 | 16 | 271 | 10 | 0 | -103 | 7665 | 55.2002
| 40098.1043 | 59.933 | 3766.1226 |  |  |  | 53.6011 | 55.3425 |  | 0.56196 | 3774.7093 | 3788.3006 | 3778.868 | 3718.8035 | 3696.3251 | 633 | [6 empty] | 0 | 633 | -580.0604 | [13 empty] | 40098.1043 | 59.933 | 3766.1226 | 335 | 229.0892 | 16 | 271.5 | 10 | 0 | -103 | 7666 | 53.6011
| 40098.1043 | 59.937 | 3764.2427 |  |  |  | 50.3998 | 53.6126 |  | 0.56196 | 3773.5413 | 3788.0107 | 3778.8039 | 3719.3654 | 3696.606 | 633 | [6 empty] | 0 | 633 | -602.1406 | [13 empty] | 40098.1043 | 59.937 | 3764.2427 | 335 | 229.0892 | 16 | 272 | 10 | 0 | -103 | 7666 | 50.3998
| 40098.1043 | 59.937 | 3765.105 |  |  |  | 50.3998 | 52.4881 |  | 0.56196 | 3772.9788 | 3787.738 | 3778.7345 | 3719.9274 | 3696.887 | 633 | [6 empty] | 0 | 633 | -602.1406 | [13 empty] | 40098.1043 | 59.937 | 3765.105 | 335 | 229.0892 | 16 | 272.5 | 10 | 0 | -103 | 7667 | 50.3998
| 40098.1043 | 59.945 | 3762.9353 |  |  |  | 44.0002 | 49.5173 |  | 0.56196 | 3770.57 | 3787.4462 | 3778.6385 | 3720.4893 | 3697.168 | 633 | [6 empty] | 0 | 633 | -651.7339 | [13 empty] | 40098.1043 | 59.945 | 3762.9353 | 335 | 229.0892 | 16 | 273 | 10 | 0 | -103 | 7668 | 44.0002
| 40098.1044 | 59.949 | 3758.3872 |  |  |  | 40.799 | 46.4659 |  | 0.56196 | 3768.0805 | 3787.1083 | 3778.5157 | 3721.0513 | 3697.449 | 633 | [6 empty] | 0 | 633 | -679.7395 | [13 empty] | 40098.1044 | 59.949 | 3758.3872 | 335 | 229.0892 | 16 | 273.5 | 10 | 0 | -103 | 7668 | 40.799
| 40098.1044 | 59.947 | 3753.9224 |  |  |  | 42.4011 | 45.0432 |  | 0.56196 | 3767.2198 | 3786.7269 | 3778.3859 | 3721.6133 | 3697.73 | 633 | [6 empty] | 0 | 633 | -665.4288 | [13 empty] | 40098.1044 | 59.947 | 3753.9224 | 335 | 229.6633 | 16 | 274 | 10 | 0 | -103 | 7669 | 42.4011
| 40098.1044 | 59.942 | 3749.8672 |  |  |  | 46.3989 | 45.5177 |  | 0.56196 | 3768.2562 | 3786.308 | 3778.2707 | 3722.1752 | 3698.0109 | 633 | [6 empty] | 0 | 633 | -632.2168 | [13 empty] | 40098.1044 | 59.942 | 3749.8672 | 335 | 229.6633 | 16 | 274.5 | 10 | 0 | -103 | 7669 | 46.3989
| 40098.1044 | 59.941 | 3746.8887 |  |  |  | 47.1985 | 46.106 |  | 0.56196 | 3769.4065 | 3785.8651 | 3778.1711 | 3722.7372 | 3698.2919 | 633 | [6 empty] | 0 | 633 | -625.9683 | [13 empty] | 40098.1044 | 59.941 | 3746.8887 | 335 | 229.6633 | 16 | 275 | 10 | 0 | -103 | 7670 | 47.1985
| 40098.1044 | 59.942 | 3747.8755 |  |  |  | 46.3989 | 46.2085 |  | 0.56196 | 3770.071 | 3785.443 | 3778.0811 | 3723.2991 | 3698.5729 | 633 | [6 empty] | 0 | 633 | -632.2168 | [13 empty] | 40098.1044 | 59.942 | 3747.8755 | 335 | 229.6633 | 16 | 275.5 | 10 | 0 | -103 | 7670 | 46.3989
| 40098.1045 | 59.945 | 3749.5933 |  |  |  | 44.0002 | 45.4356 |  | 0.56196 | 3769.86 | 3785.049 | 3777.9908 | 3723.8611 | 3698.8539 | 633 | [6 empty] | 0 | 633 | -651.7339 | [13 empty] | 40098.1045 | 59.945 | 3749.5933 | 335 | 229.6633 | 16 | 276 | 10 | 0 | -103 | 7671 | 44.0002
| 40098.1045 | 59.948 | 3748.6611 |  |  |  | 41.5985 | 44.0926 |  | 0.56196 | 3769.079 | 3784.6535 | 3777.8939 | 3724.4231 | 3699.1349 | 633 | [6 empty] | 0 | 633 | -672.5217 | [13 empty] | 40098.1045 | 59.948 | 3748.6611 | 335 | 229.2339 | 16 | 276.5 | 10 | 0 | -103 | 7671 | 41.5985
| 40098.1045 | 59.947 | 3746.7061 |  |  |  | 42.4011 | 43.5006 |  | 0.56196 | 3769.0489 | 3784.2455 | 3777.7988 | 3724.985 | 3699.4158 | 633 | [6 empty] | 0 | 633 | -665.4288 | [13 empty] | 40098.1045 | 59.947 | 3746.7061 | 335 | 229.2339 | 16 | 277 | 10 | 0 | -103 | 7672 | 42.4011
| 40098.1045 | 59.949 | 3749.0769 |  |  |  | 40.799 | 42.555 |  | 0.56196 | 3768.6653 | 3783.8714 | 3777.7017 | 3725.547 | 3699.6968 | 633 | [6 empty] | 0 | 633 | -679.7395 | [13 empty] | 40098.1045 | 59.949 | 3749.0769 | 335 | 229.2339 | 16 | 277.5 | 10 | 0 | -103 | 7673 | 40.799
| 40098.1046 | 59.951 | 3742.7415 |  |  |  | 39.1998 | 41.3807 |  | 0.56196 | 3768.0529 | 3783.4384 | 3777.6001 | 3726.1089 | 3699.9778 | 633 | [6 empty] | 0 | 633 | -694.6501 | [13 empty] | 40098.1046 | 59.951 | 3742.7415 | 335 | 229.2339 | 16 | 278 | 10 | 0 | -103 | 7673 | 39.1998
| 40098.1046 | 59.952 | 3740.259 |  |  |  | 38.4003 | 40.3376 |  | 0.56196 | 3767.5718 | 3782.9886 | 3777.4956 | 3726.6709 | 3700.2588 | 633 | [6 empty] | 0 | 633 | -702.3535 | [13 empty] | 40098.1046 | 59.952 | 3740.259 | 350 | 229.2339 | 16 | 278.5 | 10 | 0 | -103 | 7673 | 38.4003
| 40098.1046 | 59.953 | 3736.1392 |  |  |  | 37.6007 | 39.3797 |  | 0.56196 | 3767.1758 | 3782.5056 | 3777.3892 | 3727.2329 | 3700.5398 | 633 | [6 empty] | 0 | 633 | -710.2296 | [13 empty] | 40098.1046 | 59.953 | 3736.1392 | 350 | 231.4099 | 16 | 279 | 10 | 0 | -103 | 7673 | 37.6007
| 40098.1046 | 59.951 | 3731.3821 |  |  |  | 39.1998 | 39.3167 |  | 0.56196 | 3767.6748 | 3781.984 | 3777.2901 | 3727.7948 | 3700.8207 | 633 | [6 empty] | 0 | 633 | -694.6501 | [13 empty] | 40098.1046 | 59.951 | 3731.3821 | 350 | 231.4099 | 16 | 279.5 | 10 | 0 | -103 | 7673 | 39.1998
| 40098.1047 | 59.952 | 3727.8384 |  |  |  | 38.4003 | 38.996 |  | 0.56196 | 3767.916 | 3781.437 | 3777.1954 | 3728.3568 | 3701.1017 | 633 | [6 empty] | 0 | 633 | -702.3535 | [13 empty] | 40098.1047 | 59.952 | 3727.8384 | 350 | 231.4099 | 16 | 280 | 10 | 0 | -103 | 7673 | 38.4003
| 40098.1047 | 59.952 | 3725.9517 |  |  |  | 38.4003 | 38.7875 |  | 0.56196 | 3768.2695 | 3780.8822 | 3777.1062 | 3728.9188 | 3701.3827 | 633 | [6 empty] | 0 | 633 | -702.3535 | [13 empty] | 40098.1047 | 59.952 | 3725.9517 | 350 | 231.4099 | 16 | 280.5 | 10 | 0 | -103 | 7673 | 38.4003
| 40098.1047 | 59.952 | 3722.6489 |  |  |  | 38.4003 | 38.6519 |  | 0.56196 | 3768.6959 | 3780.3056 | 3777.0229 | 3729.4807 | 3701.6637 | 633 | [6 empty] | 0 | 633 | -702.3535 | [13 empty] | 40098.1047 | 59.952 | 3722.6489 | 350 | 231.4099 | 16 | 281 | 10 | 0 | -103 | 7673 | 38.4003
| 40098.1047 | 59.955 | 3720.5781 |  |  |  | 35.9985 | 37.7233 |  | 0.56196 | 3768.3292 | 3779.7201 | 3776.9377 | 3730.0427 | 3701.9447 | 633 | [6 empty] | 0 | 633 | -726.5557 | [13 empty] | 40098.1047 | 59.955 | 3720.5781 | 350 | 218.6223 | 16 | 281.5 | 10 | 0 | -103 | 7673 | 35.9985
| 40098.1047 | 59.952 | 3717.9961 |  |  |  | 38.4003 | 37.9602 |  | 0.56196 | 3769.1281 | 3779.1208 | 3776.8618 | 3730.6046 | 3702.2256 | 633 | [6 empty] | 0 | 633 | -702.3535 | [13 empty] | 40098.1047 | 59.952 | 3717.9961 | 350 | 218.6223 | 16 | 282 | 10 | 0 | -103 | 7673 | 38.4003
| 40098.1048 | 59.954 | 3718.1418 |  |  |  | 36.8011 | 37.5545 |  | 0.56196 | 3769.2844 | 3778.5345 | 3776.789 | 3731.1666 | 3702.5066 | 633 | [6 empty] | 0 | 633 | -718.2843 | [13 empty] | 40098.1048 | 59.954 | 3718.1418 | 350 | 218.6223 | 16 | 282.5 | 10 | 0 | -103 | 7673 | 36.8011
| 40098.1048 | 59.952 | 3715.7527 |  |  |  | 38.4003 | 37.8505 |  | 0.56196 | 3770.1424 | 3777.9365 | 3776.7257 | 3731.7286 | 3702.7876 | 633 | [6 empty] | 0 | 633 | -702.3535 | [13 empty] | 40098.1048 | 59.952 | 3715.7527 | 350 | 218.6223 | 16 | 283 | 10 | 0 | -103 | 7673 | 38.4003
| 40098.1048 | 59.953 | 3713.6938 |  |  |  | 37.6007 | 37.7631 |  | 0.56196 | 3770.6169 | 3777.3305 | 3776.6681 | 3732.2905 | 3703.0686 | 633 | [6 empty] | 0 | 633 | -710.2296 | [13 empty] | 40098.1048 | 59.953 | 3713.6938 | 350 | 218.6223 | 16 | 283.5 | 10 | 0 | -103 | 7673 | 37.6007
| 40098.1048 | 59.953 | 3713.4836 |  |  |  | 37.6007 | 37.7063 |  | 0.56196 | 3771.122 | 3776.7338 | 3776.6162 | 3732.8525 | 3703.3496 | 633 | [6 empty] | 0 | 633 | -710.2296 | [13 empty] | 40098.1048 | 59.953 | 3713.4836 | 350 | 213.5359 | 16 | 284 | 10 | 0 | -103 | 7673 | 37.6007
| 40098.1049 | 59.952 | 3710.8481 |  |  |  | 38.4003 | 37.9492 |  | 0.56196 | 3771.9269 | 3776.1237 | 3776.5728 | 3733.4144 | 3703.6305 | 633 | [6 empty] | 0 | 633 | -702.3535 | [13 empty] | 40098.1049 | 59.952 | 3710.8481 | 350 | 213.5359 | 16 | 284.5 | 10 | 0 | -103 | 7673 | 38.4003
| 40098.1049 | 59.954 | 3710.8101 |  |  |  | 36.8011 | 37.5474 |  | 0.56196 | 3772.087 | 3775.5245 | 3776.5316 | 3733.9764 | 3703.9115 | 633 | [6 empty] | 0 | 633 | -718.2843 | [13 empty] | 40098.1049 | 59.954 | 3710.8101 | 350 | 213.5359 | 16 | 285 | 10 | 0 | -103 | 7673 | 36.8011
| 40098.1049 | 59.954 | 3712.0918 |  |  |  | 36.8011 | 37.2862 |  | 0.56196 | 3772.3878 | 3774.9479 | 3776.494 | 3734.5384 | 3704.1925 | 633 | [6 empty] | 0 | 633 | -718.2843 | [13 empty] | 40098.1049 | 59.954 | 3712.0918 | 350 | 213.5359 | 16 | 285.5 | 10 | 0 | -103 | 7674 | 36.8011
| 40098.1049 | 59.959 | 3714.6226 |  |  |  | 32.8003 | 35.7161 |  | 0.56196 | 3771.3797 | 3774.4044 | 3776.4479 | 3735.1003 | 3704.4735 | 633 | [6 empty] | 0 | 633 | -761.4983 | [13 empty] | 40098.1049 | 59.959 | 3714.6226 | 350 | 213.5359 | 16 | 286 | 10 | 0 | -103 | 7675 | 32.8003
| 40098.105 | 59.957 | 3715.1296 |  |  |  | 34.3994 | 35.2553 |  | 0.56196 | 3771.4808 | 3773.8751 | 3776.4036 | 3735.6623 | 3704.7545 | 633 | [6 empty] | 0 | 633 | -743.6168 | [13 empty] | 40098.105 | 59.957 | 3715.1296 | 350 | 225.6519 | 16 | 286.5 | 10 | 0 | -103 | 7676 | 34.3994
| 40098.105 | 59.956 | 3716.1682 |  |  |  | 35.199 | 35.2356 |  | 0.56196 | 3772.0231 | 3773.3645 | 3776.3648 | 3736.2242 | 3705.0354 | 633 | [6 empty] | 0 | 633 | -734.9872 | [13 empty] | 40098.105 | 59.956 | 3716.1682 | 350 | 225.6519 | 16 | 287 | 10 | 0 | -103 | 7677 | 35.199
| 40098.105 | 59.954 | 3716.4614 |  |  |  | 36.8011 | 35.7835 |  | 0.56196 | 3773.133 | 3772.8653 | 3776.3364 | 3736.7862 | 3705.3164 | 633 | [6 empty] | 0 | 633 | -718.2843 | [13 empty] | 40098.105 | 59.954 | 3716.4614 | 350 | 225.6519 | 16 | 287.5 | 10 | 0 | -103 | 7678 | 36.8011
| 40098.105 | 59.956 | 3716.98 |  |  |  | 35.199 | 35.5789 |  | 0.56196 | 3773.4904 | 3772.3794 | 3776.3117 | 3737.3482 | 3705.5974 | 633 | [6 empty] | 0 | 633 | -734.9872 | [13 empty] | 40098.105 | 59.956 | 3716.98 | 350 | 225.6519 | 16 | 288 | 10 | 0 | -103 | 7679 | 35.199
| 40098.105 | 59.955 | 3717.759 |  |  |  | 35.9985 | 35.7258 |  | 0.56196 | 3774.1992 | 3771.9085 | 3776.2935 | 3737.9101 | 3705.8784 | 633 | [6 empty] | 0 | 633 | -726.5557 | [13 empty] | 40098.105 | 59.955 | 3717.759 | 350 | 225.6519 | 16 | 288.5 | 10 | 0 | -103 | 7680 | 35.9985
| 40098.1051 | 59.958 | 3722.3613 |  |  |  | 33.5999 | 34.9817 |  | 0.56196 | 3774.0171 | 3771.485 | 3776.274 | 3738.4721 | 3706.1594 | 633 | [6 empty] | 0 | 633 | -752.4513 | [13 empty] | 40098.1051 | 59.958 | 3722.3613 | 350 | 212.5736 | 16 | 289 | 10 | 0 | -103 | 7681 | 33.5999
| 40098.1051 | 59.961 | 3721.9731 |  |  |  | 31.2012 | 33.6585 |  | 0.56196 | 3773.2558 | 3771.0654 | 3776.2484 | 3739.034 | 3706.4403 | 633 | [6 empty] | 0 | 633 | -780.2611 | [13 empty] | 40098.1051 | 59.961 | 3721.9731 | 350 | 212.5736 | 16 | 289.5 | 10 | 0 | -103 | 7682 | 31.2012
| 40098.1051 | 59.962 | 3722.658 |  |  |  | 30.3986 | 32.5175 |  | 0.56196 | 3772.6768 | 3770.6586 | 3776.2184 | 3739.596 | 3706.7213 | 633 | [6 empty] | 0 | 633 | -790.0311 | [13 empty] | 40098.1051 | 59.962 | 3722.658 | 350 | 212.5736 | 16 | 290 | 10 | 0 | -103 | 7684 | 30.3986
| 40098.1051 | 59.962 | 3722.2666 |  |  |  | 30.3986 | 31.7759 |  | 0.56196 | 3772.4971 | 3770.2554 | 3776.1874 | 3740.158 | 3707.0023 | 633 | [6 empty] | 0 | 633 | -790.0311 | [13 empty] | 40098.1051 | 59.962 | 3722.2666 | 350 | 212.5736 | 16 | 290.5 | 10 | 0 | -103 | 7685 | 30.3986
| 40098.1052 | 59.968 | 3722.2776 |  |  |  | 25.6012 | 29.6148 |  | 0.56196 | 3770.898 | 3769.8589 | 3776.1437 | 3740.7199 | 3707.2833 | 633 | [6 empty] | 0 | 633 | -853.9431 | [13 empty] | 40098.1052 | 59.968 | 3722.2776 | 350 | 212.5736 | 16 | 291 | 10 | 0 | -103 | 7687 | 25.6012
| 40098.1052 | 59.966 | 3721.7866 |  |  |  | 27.2003 | 28.7697 |  | 0.56196 | 3770.6149 | 3769.4648 | 3776.0984 | 3741.2819 | 3707.5643 | 633 | [6 empty] | 0 | 633 | -831.5203 | [13 empty] | 40098.1052 | 59.966 | 3721.7866 | 350 | 219.8973 | 16 | 291.5 | 10 | 0 | -103 | 7689 | 27.2003
| 40098.1052 | 59.966 | 3723.0908 |  |  |  | 27.2003 | 28.2204 |  | 0.56196 | 3770.6275 | 3769.0878 | 3776.0539 | 3741.8438 | 3707.8452 | 633 | [6 empty] | 0 | 633 | -831.5203 | [13 empty] | 40098.1052 | 59.966 | 3723.0908 | 350 | 219.8973 | 16 | 292 | 10 | 0 | -103 | 7690 | 27.2003
| 40098.1052 | 59.968 | 3723.9839 |  |  |  | 25.6012 | 27.3037 |  | 0.56196 | 3770.2728 | 3768.7241 | 3776.0073 | 3742.4058 | 3708.1262 | 633 | [6 empty] | 0 | 633 | -853.9431 | [13 empty] | 40098.1052 | 59.968 | 3723.9839 | 350 | 219.8973 | 16 | 292.5 | 10 | 0 | -103 | 7692 | 25.6012
| 40098.1053 | 59.97 | 3723.4346 |  |  |  | 23.999 | 26.1471 |  | 0.56196 | 3769.6781 | 3768.3617 | 3775.9567 | 3742.9678 | 3708.4072 | 633 | [6 empty] | 0 | 633 | -877.6551 | [13 empty] | 40098.1053 | 59.97 | 3723.4346 | 350 | 219.8973 | 16 | 293 | 10 | 0 | -103 | 7692 | 23.999
| 40098.1053 | 59.974 | 3723.8931 |  |  |  | 20.8008 | 24.2759 |  | 0.56196 | 3768.3689 | 3768.0088 | 3775.8964 | 3743.5297 | 3708.6882 | 633 | [6 empty] | 0 | 633 | -929.1579 | [13 empty] | 40098.1053 | 59.974 | 3723.8931 | 350 | 219.8973 | 16 | 293.5 | 10 | 0 | -103 | 7693 | 20.8008
| 40098.1053 | 59.97 | 3725.4028 |  |  |  | 23.999 | 24.179 |  | 0.56196 | 3768.8339 | 3767.6733 | 3775.8408 | 3744.0917 | 3708.9692 | 633 | [6 empty] | 0 | 633 | -877.6551 | [13 empty] | 40098.1053 | 59.97 | 3725.4028 | 350 | 231.1754 | 16 | 294 | 10 | 0 | -103 | 7693 | 23.999
| 40098.1053 | 59.969 | 3727.1211 |  |  |  | 24.7986 | 24.3958 |  | 0.56196 | 3769.6128 | 3767.3565 | 3775.7922 | 3744.6536 | 3709.2501 | 633 | [6 empty] | 0 | 633 | -865.6593 | [13 empty] | 40098.1053 | 59.969 | 3727.1211 | 350 | 231.1754 | 16 | 294.5 | 10 | 0 | -103 | 7694 | 24.7986
| 40098.1053 | 59.969 | 3728.053 |  |  |  | 24.7986 | 24.5368 |  | 0.56196 | 3770.3157 | 3767.0518 | 3775.7497 | 3745.2156 | 3709.5311 | 633 | [6 empty] | 0 | 633 | -865.6593 | [13 empty] | 40098.1053 | 59.969 | 3728.053 | 350 | 231.1754 | 16 | 295 | 10 | 0 | -103 | 7694 | 24.7986
| 40098.1054 | 59.97 | 3731.1299 |  |  |  | 23.999 | 24.3486 |  | 0.56196 | 3770.6894 | 3766.7755 | 3775.7108 | 3745.7776 | 3709.8121 | 633 | [6 empty] | 0 | 633 | -877.6551 | [13 empty] | 40098.1054 | 59.97 | 3731.1299 | 350 | 231.1754 | 16 | 295.5 | 10 | 0 | -103 | 7695 | 23.999
| 40098.1054 | 59.971 | 3732.53 |  |  |  | 23.1995 | 23.9464 |  | 0.56196 | 3770.8492 | 3766.5141 | 3775.6737 | 3746.3395 | 3710.0931 | 633 | [6 empty] | 0 | 633 | -889.988 | [13 empty] | 40098.1054 | 59.971 | 3732.53 | 350 | 231.1754 | 16 | 296 | 10 | 0 | -103 | 7695 | 23.1995
| 40098.1054 | 59.973 | 3733.3271 |  |  |  | 21.6003 | 23.1253 |  | 0.56196 | 3770.59 | 3766.2627 | 3775.6352 | 3746.9015 | 3710.3741 | 633 | [6 empty] | 0 | 633 | -915.7237 | [13 empty] | 40098.1054 | 59.973 | 3733.3271 | 350 | 226.6341 | 16 | 296.5 | 10 | 0 | -103 | 7695 | 21.6003
| 40098.1054 | 59.973 | 3736.5352 |  |  |  | 21.6003 | 22.5915 |  | 0.56196 | 3770.6183 | 3766.0392 | 3775.5974 | 3747.4634 | 3710.655 | 633 | [6 empty] | 0 | 633 | -915.7237 | [13 empty] | 40098.1054 | 59.973 | 3736.5352 | 350 | 226.6341 | 16 | 297 | 10 | 0 | -103 | 7696 | 21.6003
| 40098.1055 | 59.976 | 3736.9075 |  |  |  | 19.1986 | 21.404 |  | 0.56196 | 3769.9927 | 3765.8218 | 3775.5556 | 3748.0254 | 3710.936 | 633 | [6 empty] | 0 | 633 | -957.2998 | [13 empty] | 40098.1055 | 59.976 | 3736.9075 | 350 | 226.6341 | 16 | 297.5 | 10 | 0 | -103 | 7696 | 19.1986
| 40098.1055 | 59.978 | 3736.8218 |  |  |  | 17.5995 | 20.0724 |  | 0.56196 | 3769.2231 | 3765.607 | 3775.5087 | 3748.5874 | 3711.217 | 633 | [6 empty] | 0 | 633 | -987.1409 | [13 empty] | 40098.1055 | 59.978 | 3736.8218 | 350 | 226.6341 | 16 | 298 | 10 | 0 | -103 | 7697 | 17.5995
| 40098.1055 | 59.978 | 3738.6992 |  |  |  | 17.5995 | 19.2069 |  | 0.56196 | 3768.9195 | 3765.4091 | 3775.4603 | 3749.1493 | 3711.498 | 633 | [6 empty] | 0 | 633 | -987.1409 | [13 empty] | 40098.1055 | 59.978 | 3738.6992 | 350 | 226.6341 | 16 | 298.5 | 10 | 0 | -103 | 7697 | 17.5995
| 40098.1055 | 59.976 | 3739.9438 |  |  |  | 19.1986 | 19.204 |  | 0.56196 | 3769.4786 | 3765.2232 | 3775.4166 | 3749.7113 | 3711.779 | 633 | [6 empty] | 0 | 633 | -957.2998 | [13 empty] | 40098.1055 | 59.976 | 3739.9438 | 350 | 227.2551 | 16 | 299 | 10 | 0 | -103 | 7697 | 19.1986
| 40098.1056 | 59.978 | 3740.877 |  |  |  | 17.5995 | 18.6424 |  | 0.56196 | 3769.4789 | 3765.0468 | 3775.3736 | 3750.2732 | 3712.0599 | 633 | [6 empty] | 0 | 633 | -987.1409 | [13 empty] | 40098.1056 | 59.978 | 3740.877 | 350 | 227.2551 | 16 | 299.5 | 10 | 0 | -103 | 7698 | 17.5995
| 40098.1056 | 59.976 | 3741.7937 |  |  |  | 19.1986 | 18.8371 |  | 0.56196 | 3770.2356 | 3764.8795 | 3775.3366 | 3750.8352 | 3712.3409 | 633 | [6 empty] | 0 | 633 | -957.2998 | [13 empty] | 40098.1056 | 59.976 | 3741.7937 | 350 | 227.2551 | 16 | 300 | 10 | 0 | -103 | 7698 | 19.1986
| 40098.1056 | 59.978 | 3745.2336 |  |  |  | 17.5995 | 18.4039 |  | 0.56196 | 3770.3644 | 3764.7392 | 3775.3011 | 3751.3972 | 3712.6219 | 633 | [6 empty] | 0 | 633 | -987.1409 | [13 empty] | 40098.1056 | 59.978 | 3745.2336 | 350 | 227.2551 | 16 | 300.5 | 10 | 0 | -103 | 7698.33 | 17.5995
| 40098.1056 | 59.977 | 3746.6079 |  |  |  | 18.399 | 18.4022 |  | 0.56196 | 3770.9246 | 3764.6106 | 3775.2701 | 3751.9591 | 3712.9029 | 633 | [6 empty] | 0 | 633 | -971.9914 | [13 empty] | 40098.1056 | 59.977 | 3746.6079 | 350 | 227.2551 | 16 | 301 | 10 | 0 | -103 | 7698.66 | 18.399
| 40098.1056 | 59.98 | 3748.2998 |  |  |  | 16.0004 | 17.5616 |  | 0.56196 | 3770.6459 | 3764.4957 | 3775.2375 | 3752.5211 | 3713.1839 | 633 | [6 empty] | 0 | 633 | -1018.9023 | [13 empty] | 40098.1056 | 59.98 | 3748.2998 | 350 | 229.2902 | 16 | 301.5 | 10 | 0 | -103 | 7698.99 | 16.0004
| 40098.1057 | 59.982 | 3750.7163 |  |  |  | 14.4012 | 16.4555 |  | 0.56196 | 3770.1018 | 3764.3994 | 3775.2016 | 3753.083 | 3713.4648 | 633 | [6 empty] | 0 | 633 | -1052.7755 | [13 empty] | 40098.1057 | 59.982 | 3750.7163 | 350 | 229.2902 | 16 | 302 | 10 | 0 | -103 | 7699.32 | 14.4012
| 40098.1057 | 59.981 | 3751.5576 |  |  |  | 15.2008 | 16.0163 |  | 0.56196 | 3770.2246 | 3764.3102 | 3775.167 | 3753.645 | 3713.7458 | 633 | [6 empty] | 0 | 633 | -1035.5619 | [13 empty] | 40098.1057 | 59.981 | 3751.5576 | 350 | 229.2902 | 16 | 302.5 | 10 | 0 | -103 | 7699.65 | 15.2008
| 40098.1057 | 59.98 | 3752.7476 |  |  |  | 16.0004 | 16.0107 |  | 0.56196 | 3770.781 | 3764.2305 | 3775.1368 | 3754.207 | 3714.0268 | 633 | [6 empty] | 0 | 633 | -1018.9023 | [13 empty] | 40098.1057 | 59.98 | 3752.7476 | 350 | 229.2902 | 16 | 303 | 10 | 0 | -103 | 7699.98 | 16.0004
| 40098.1057 | 59.979 | 3755.5986 |  |  |  | 16.7999 | 16.287 |  | 0.56196 | 3771.6192 | 3764.1713 | 3775.1127 | 3754.7689 | 3714.3078 | 633 | [6 empty] | 0 | 633 | -1002.7702 | [13 empty] | 40098.1057 | 59.979 | 3755.5986 | 350 | 229.2902 | 16 | 303.5 | 10 | 0 | -103 | 7700.31 | 16.7999
| 40098.1058 | 59.98 | 3756.4072 |  |  |  | 16.0004 | 16.1866 |  | 0.56196 | 3772.0808 | 3764.1185 | 3775.092 | 3755.3309 | 3714.5888 | 633 | [6 empty] | 0 | 633 | -1018.9023 | [13 empty] | 40098.1058 | 59.98 | 3756.4072 | 350 | 221.4614 | 16 | 304 | 10 | 0 | -103 | 7700.64 | 16.0004
| 40098.1058 | 59.979 | 3756.9753 |  |  |  | 16.7999 | 16.4013 |  | 0.56196 | 3772.8574 | 3764.0702 | 3775.0769 | 3755.8928 | 3714.8697 | 633 | [6 empty] | 0 | 633 | -1002.7702 | [13 empty] | 40098.1058 | 59.979 | 3756.9753 | 350 | 221.4614 | 16 | 304.5 | 10 | 0 | -103 | 7700.97 | 16.7999
| 40098.1058 | 59.983 | 3760.4053 |  |  |  | 13.5986 | 15.4204 |  | 0.56196 | 3772.4384 | 3764.0457 | 3775.0592 | 3756.4548 | 3715.1507 | 633 | [6 empty] | 0 | 633 | -1070.64 | [13 empty] | 40098.1058 | 59.983 | 3760.4053 | 350 | 221.4614 | 16 | 305 | 10 | 0 | -103 | 7701.3 | 13.5986
| 40098.1058 | 59.983 | 3760.9822 |  |  |  | 13.5986 | 14.7828 |  | 0.56196 | 3772.3628 | 3764.0252 | 3775.0413 | 3757.0168 | 3715.4317 | 633 | [6 empty] | 0 | 633 | -1070.64 | [13 empty] | 40098.1058 | 59.983 | 3760.9822 | 350 | 221.4614 | 16 | 305.5 | 10 | 0 | -103 | 7701.63 | 13.5986
| 40098.1059 | 59.984 | 3761.407 |  |  |  | 12.7991 | 14.0885 |  | 0.56196 | 3772.2305 | 3764.0079 | 3775.0226 | 3757.5787 | 3715.7127 | 633 | [6 empty] | 0 | 633 | -1089.0498 | [13 empty] | 40098.1059 | 59.984 | 3761.407 | 350 | 221.4614 | 16 | 306 | 10 | 0 | -103 | 7701.96 | 12.7991
| 40098.1059 | 59.988 | 3762.7373 |  |  |  | 9.6008 | 12.5178 |  | 0.56196 | 3771.2218 | 3763.9995 | 3774.9976 | 3758.1407 | 3715.9937 | 633 | [6 empty] | 0 | 633 | -1169.4877 | [13 empty] | 40098.1059 | 59.988 | 3762.7373 | 350 | 241.2744 | 16 | 306.5 | 10 | 0 | -103 | 7702.29 | 9.6008
| 40098.1059 | 59.989 | 3763.2122 |  |  |  | 8.8013 | 11.217 |  | 0.56196 | 3770.4829 | 3763.9944 | 3774.9681 | 3758.7026 | 3716.2746 | 633 | [6 empty] | 0 | 633 | -1191.4888 | [13 empty] | 40098.1059 | 59.989 | 3763.2122 | 350 | 241.2744 | 16 | 307 | 10 | 0 | -103 | 7702.62 | 8.8013
| 40098.1059 | 59.987 | 3764.9575 |  |  |  | 10.4004 | 10.9312 |  | 0.56196 | 3770.7591 | 3764.0006 | 3774.9408 | 3759.2646 | 3716.5556 | 633 | [6 empty] | 0 | 633 | -1148.2845 | [13 empty] | 40098.1059 | 59.987 | 3764.9575 | 350 | 241.2744 | 16 | 307.5 | 10 | 0 | -103 | 7702.95 | 10.4004
| 40098.1059 | 59.987 | 3766.0852 |  |  |  | 10.4004 | 10.7454 |  | 0.56196 | 3771.1353 | 3764.0141 | 3774.9163 | 3759.8266 | 3716.8366 | 633 | [6 empty] | 0 | 633 | -1148.2845 | [13 empty] | 40098.1059 | 59.987 | 3766.0852 | 350 | 241.2744 | 16 | 308 | 10 | 0 | -103 | 7703.28 | 10.4004
| 40098.106 | 59.991 | 3766.4331 |  |  |  | 7.1991 | 9.5042 |  | 0.56196 | 3770.456 | 3764.0296 | 3774.8877 | 3760.3885 | 3717.1176 | 633 | [6 empty] | 0 | 633 | -1238.1637 | [13 empty] | 40098.106 | 59.991 | 3766.4331 | 350 | 241.2744 | 16 | 308.5 | 10 | 0 | -103 | 7703.61 | 7.1991
| 40098.106 | 59.993 | 3767.251 |  |  |  | 5.6 | 8.1377 |  | 0.56196 | 3769.6515 | 3764.0501 | 3774.8543 | 3760.9505 | 3717.3986 | 633 | [6 empty] | 0 | 633 | -1288.5445 | [13 empty] | 40098.106 | 59.993 | 3767.251 | 350 | 243.0719 | 16 | 309 | 10 | 0 | -103 | 7703.94 | 5.6
| 40098.106 | 59.992 | 3767.7925 |  |  |  | 6.3995 | 7.5294 |  | 0.56196 | 3769.6051 | 3764.0738 | 3774.8211 | 3761.5124 | 3717.6795 | 633 | [6 empty] | 0 | 633 | -1262.8518 | [13 empty] | 40098.106 | 59.992 | 3767.7925 | 350 | 243.0719 | 16 | 309.5 | 10 | 0 | -103 | 7704.27 | 6.3995
| 40098.106 | 59.991 | 3768.6335 |  |  |  | 7.1991 | 7.4138 |  | 0.56196 | 3770.0515 | 3764.1025 | 3774.7911 | 3762.0744 | 3717.9605 | 633 | [6 empty] | 0 | 633 | -1238.1637 | [13 empty] | 40098.106 | 59.991 | 3768.6335 | 350 | 243.0719 | 16 | 310 | 10 | 0 | -103 | 7704.6 | 7.1991
| 40098.1061 | 59.989 | 3771.1465 |  |  |  | 8.8013 | 7.8994 |  | 0.56196 | 3771.099 | 3764.1465 | 3774.768 | 3762.6364 | 3718.2415 | 633 | [6 empty] | 0 | 633 | -1191.4888 | [13 empty] | 40098.1061 | 59.989 | 3771.1465 | 350 | 243.0719 | 16 | 310.5 | 10 | 0 | -103 | 7704.93 | 8.8013
| 40098.1061 | 59.986 | 3772.4446 |  |  |  | 11.2 | 9.0546 |  | 0.56196 | 3772.8162 | 3764.198 | 3774.7559 | 3763.1983 | 3718.5225 | 633 | [6 empty] | 0 | 633 | -1127.8363 | [13 empty] | 40098.1061 | 59.986 | 3772.4446 | 350 | 243.0719 | 16 | 311 | 10 | 0 | -103 | 7705.26 | 11.2
| 40098.1061 | 59.983 | 3773.6948 |  |  |  | 13.5986 | 10.645 |  | 0.56196 | 3774.9686 | 3764.2567 | 3774.7572 | 3763.7603 | 3718.8035 | 633 | [6 empty] | 0 | 633 | -1070.64 | [13 empty] | 40098.1061 | 59.983 | 3773.6948 | 350 | 241.6702 | 16 | 311.5 | 10 | 0 | -103 | 7705.59 | 13.5986
| 40098.1061 | 59.983 | 3774.6685 |  |  |  | 13.5986 | 11.6788 |  | 0.56196 | 3776.5643 | 3764.3205 | 3774.7683 | 3764.3222 | 3719.0844 | 633 | [6 empty] | 0 | 633 | -1070.64 | [13 empty] | 40098.1061 | 59.983 | 3774.6685 | 350 | 241.6702 | 16 | 312 | 10 | 0 | -103 | 7705.92 | 13.5986
| 40098.1062 | 59.988 | 3775.8408 |  |  |  | 9.6008 | 10.9515 |  | 0.56196 | 3776.399 | 3764.3908 | 3774.7782 | 3764.8842 | 3719.3654 | 633 | [6 empty] | 0 | 633 | -1169.4877 | [13 empty] | 40098.1062 | 59.988 | 3775.8408 | 350 | 241.6702 | 16 | 312.5 | 10 | 0 | -103 | 7706.25 | 9.6008
| 40098.1062 | 59.993 | 3775.3633 |  |  |  | 5.6 | 9.0785 |  | 0.56196 | 3775.0879 | 3764.4573 | 3774.7801 | 3765.4462 | 3719.6464 | 633 | [6 empty] | 0 | 633 | -1288.5445 | [13 empty] | 40098.1062 | 59.993 | 3775.3633 | 350 | 241.6702 | 16 | 313 | 10 | 0 | -103 | 7706.58 | 5.6
| 40098.1062 | 59.996 | 3774.8662 |  |  |  | 3.2013 | 7.0215 |  | 0 | 3773.0309 | 3764.52 | 3774.7696 | 3765.4462 | 3719.924 | 633 | [6 empty] | 0 | 633 | -1372.3029 | [13 empty] | 40098.1062 | 59.996 | 3774.8662 | 350 | 241.6702 | 16 | 313.5 | 10 | 0 | -103 | 7706.91 | 3.2013
| 40098.1062 | 59.998 | 3775.4917 |  |  |  | 1.5991 | 5.1236 |  | 0 | 3771.1331 | 3764.5857 | 3774.7478 | 3765.4462 | 3720.1982 | 633 | [6 empty] | 0 | 633 | -1434.5893 | [13 empty] | 40098.1062 | 59.998 | 3775.4917 | 350 | 228.1493 | 16 | 314 | 10 | 0 | -103 | 7707.24 | 1.5991
| 40098.1062 | 59.999 | 3776.4202 |  |  |  | 0.79956 | 3.6102 |  | 0 | 3769.6197 | 3764.6561 | 3774.7173 | 3765.4462 | 3720.4692 | 633 | [6 empty] | 0 | 633 | -1467.8371 | [13 empty] | 40098.1062 | 59.999 | 3776.4202 | 350 | 228.1493 | 16 | 314.5 | 10 | 0 | -103 | 7707.57 | 0.79956
| 40098.1063 | 60.001 | 3778.5537 |  |  |  | -0.79956 | 2.0668 |  | 0 | 3768.0762 | 3764.7384 | 3774.678 | 3765.4462 | 3720.7369 | 633 | [6 empty] | 0 | 633 | -1539.1807 | [13 empty] | 40098.1063 | 60.001 | 3778.5537 | 350 | 228.1493 | 16 | 315 | 10 | 0 | -103 | 7707.9 | -0.79956
| 40098.1063 | 59.999 | 3779.6919 |  |  |  | 0.79956 | 1.6233 |  | 0 | 3767.6327 | 3764.8263 | 3774.6365 | 3765.4462 | 3721.0014 | 633 | [6 empty] | 0 | 633 | -1467.8371 | [13 empty] | 40098.1063 | 59.999 | 3779.6919 | 350 | 228.1493 | 16 | 315.5 | 10 | 0 | -103 | 7708.23 | 0.79956
| 40098.1063 | 59.999 | 3781.2559 |  |  |  | 0.79956 | 1.335 |  | 0 | 3767.3444 | 3764.9224 | 3774.5939 | 3765.4462 | 3721.2629 | 633 | [6 empty] | 0 | 633 | -1467.8371 | [13 empty] | 40098.1063 | 59.999 | 3781.2559 | 350 | 228.1493 | 16 | 316 | 10 | 0 | -103 | 7708.56 | 0.79956
| 40098.1063 | 59.999 | 3780.595 |  |  |  | 0.79956 | 1.1476 |  | 0 | 3767.157 | 3765.0135 | 3774.5507 | 3765.4462 | 3721.5213 | 633 | [6 empty] | 0 | 633 | -1467.8371 | [13 empty] | 40098.1063 | 59.999 | 3780.595 | 350 | 235.129 | 16 | 316.5 | 10 | 0 | -103 | 7708.89 | 0.79956
| 40098.1064 | 60.002 | 3783.092 |  |  |  | -1.5991 | 0.18623 |  | 0 | 3766.1957 | 3765.118 | 3774.5024 | 3765.4462 | 3721.7766 | 633 | [6 empty] | 0 | 633 | -1577.5181 | [13 empty] | 40098.1064 | 60.002 | 3783.092 | 350 | 235.129 | 16 | 317 | 10 | 0 | -103 | 7709.22 | -1.5991
| 40098.1064 | 60.005 | 3783.8955 |  |  |  | -4.0009 | -1.2792 |  | 0 | 3764.7302 | 3765.2259 | 3774.4462 | 3765.4462 | 3722.0291 | 633 | [6 empty] | 0 | 633 | -1705.0892 | [13 empty] | 40098.1064 | 60.005 | 3783.8955 | 350 | 235.129 | 16 | 317.5 | 10 | 0 | -103 | 7709.55 | -4.0009
| 40098.1064 | 60.007 | 3784.4209 |  |  |  | -5.6 | -2.7915 |  | 0 | 3763.2179 | 3765.3356 | 3774.382 | 3765.4462 | 3722.2786 | 633 | [6 empty] | 0 | 633 | -1802.1221 | [13 empty] | 40098.1064 | 60.007 | 3784.4209 | 350 | 235.129 | 16 | 318 | 10 | 0 | -103 | 7709.88 | -5.6
| 40098.1064 | 60.008 | 3785.7681 |  |  |  | -6.3995 | -4.0543 |  | 0 | 3761.9551 | 3765.4517 | 3774.3114 | 3765.4462 | 3722.5252 | 633 | [6 empty] | 0 | 633 | -1854.9013 | [13 empty] | 40098.1064 | 60.008 | 3785.7681 | 350 | 235.129 | 16 | 318.5 | 10 | 0 | -103 | 7710.21 | -6.3995
| 40098.1065 | 60.011 | 3785.4626 |  |  |  | -8.8013 | -5.7157 |  | 0 | 3760.2937 | 3765.5648 | 3774.2322 | 3765.4462 | 3722.7691 | 633 | [6 empty] | 0 | 633 | -2033.8239 | [13 empty] | 40098.1065 | 60.011 | 3785.4626 | 350 | 246.4331 | 16 | 319 | 10 | 0 | -103 | 7710.54 | -8.8013
| 40098.1065 | 60.014 | 3786.8503 |  |  |  | -11.2 | -7.6352 |  | 0 | 3758.3742 | 3765.6844 | 3774.1431 | 3765.4462 | 3723.0102 | 633 | [6 empty] | 0 | 633 | -2250.6438 | [13 empty] | 40098.1065 | 60.014 | 3786.8503 | 350 | 246.4331 | 16 | 319.5 | 10 | 0 | -103 | 7710.87 | -11.2
| 40098.1065 | 60.017 | 3786.3042 |  |  |  | -13.5986 | -9.7224 |  | 0 | 3756.287 | 3765.7996 | 3774.0434 | 3765.4462 | 3723.2486 | 633 | [6 empty] | 0 | 633 | -2519.2091 | [13 empty] | 40098.1065 | 60.017 | 3786.3042 | 350 | 246.4331 | 16 | 320 | 10 | 0 | -103 | 7711.2 | -13.5986
| 40098.1065 | 60.019 | 3787.2593 |  |  |  | -15.2008 | -11.6399 |  | 0 | 3754.3696 | 3765.9188 | 3773.9341 | 3765.4462 | 3723.4844 | 633 | [6 empty] | 0 | 633 | -2737.3899 | [13 empty] | 40098.1065 | 60.019 | 3787.2593 | 350 | 246.4331 | 16 | 320.5 | 10 | 0 | -103 | 7711.53 | -15.2008
| 40098.1066 | 60.021 | 3787.5159 |  |  |  | -16.7999 | -13.4459 |  | 0 | 3752.5636 | 3766.0381 | 3773.816 | 3765.4462 | 3723.7175 | 633 | [6 empty] | 0 | 633 | -2996.4048 | [13 empty] | 40098.1066 | 60.021 | 3787.5159 | 350 | 246.4331 | 16 | 321 | 10 | 0 | -103 | 7711.86 | -16.7999
| 40098.1066 | 60.017 | 3787.9551 |  |  |  | -13.5986 | -13.4993 |  | 0 | 3752.5101 | 3766.1585 | 3773.699 | 3765.4462 | 3723.948 | 633 | [6 empty] | 0 | 633 | -2519.2091 | [13 empty] | 40098.1066 | 60.017 | 3787.9551 | 350 | 236.5535 | 16 | 321.5 | 10 | 0 | -103 | 7712.19 | -13.5986
| 40098.1066 | 60.017 | 3788.0303 |  |  |  | -13.5986 | -13.5341 |  | 0 | 3752.4754 | 3766.278 | 3773.583 | 3765.4462 | 3724.1761 | 633 | [6 empty] | 0 | 633 | -2519.2091 | [13 empty] | 40098.1066 | 60.017 | 3788.0303 | 350 | 236.5535 | 16 | 322 | 10 | 0 | -103 | 7712.52 | -13.5986
| 40098.1066 | 60.019 | 3788.6067 |  |  |  | -15.2008 | -14.1174 |  | 0 | 3751.892 | 3766.3994 | 3773.4651 | 3765.4462 | 3724.4016 | 633 | [6 empty] | 0 | 633 | -2737.3899 | [13 empty] | 40098.1066 | 60.019 | 3788.6067 | 350 | 236.5535 | 16 | 322.5 | 10 | 0 | -103 | 7712.85 | -15.2008
| 40098.1066 | 60.023 | 3789.2158 |  |  |  | -18.399 | -15.616 |  | 0 | 3750.3934 | 3766.5227 | 3773.3404 | 3765.4462 | 3724.6246 | 633 | [6 empty] | 0 | 633 | -3309.559 | [13 empty] | 40098.1066 | 60.023 | 3789.2158 | 350 | 236.5535 | 16 | 323 | 10 | 0 | -103 | 7713.18 | -18.399
| 40098.1067 | 60.024 | 3787.5366 |  |  |  | -19.1986 | -16.8699 |  | 0 | 3749.1395 | 3766.6357 | 3773.2103 | 3765.4462 | 3724.8453 | 633 | [6 empty] | 0 | 633 | -3492.0353 | [13 empty] | 40098.1067 | 60.024 | 3787.5366 | 350 | 236.5535 | 16 | 323.5 | 10 | 0 | -103 | 7713.51 | -19.1986
| 40098.1067 | 60.025 | 3785.8418 |  |  |  | -20.0012 | -17.9659 |  | 0 | 3748.0436 | 3766.7384 | 3773.0757 | 3765.4462 | 3725.0636 | 633 | [6 empty] | 0 | 633 | -3696.6312 | [13 empty] | 40098.1067 | 60.025 | 3785.8418 | 350 | 230.2976 | 16 | 324 | 10 | 0 | -103 | 7713.84 | -20.0012
| 40098.1067 | 60.021 | 3786.0767 |  |  |  | -16.7999 | -17.5578 |  | 0 | 3748.4517 | 3766.8413 | 3772.9447 | 3765.4462 | 3725.2795 | 633 | [6 empty] | 0 | 633 | -2996.4048 | [13 empty] | 40098.1067 | 60.021 | 3786.0767 | 350 | 230.2976 | 16 | 324.5 | 10 | 0 | -103 | 7714.17 | -16.7999
| 40098.1067 | 60.019 | 3787.9304 |  |  |  | -15.2008 | -16.7328 |  | 0 | 3749.2766 | 3766.9528 | 3772.8195 | 3765.4462 | 3725.4932 | 633 | [6 empty] | 0 | 633 | -2737.3899 | [13 empty] | 40098.1067 | 60.019 | 3787.9304 | 350 | 230.2976 | 16 | 325 | 10 | 0 | -103 | 7714.5 | -15.2008
| 40098.1068 | 60.024 | 3788.7603 |  |  |  | -19.1986 | -17.5959 |  | 0 | 3748.4136 | 3767.0676 | 3772.691 | 3765.4462 | 3725.7046 | 633 | [6 empty] | 0 | 633 | -3492.0353 | [13 empty] | 40098.1068 | 60.024 | 3788.7603 | 350 | 230.2976 | 16 | 325.5 | 10 | 0 | -103 | 7714.83 | -19.1986
| 40098.1068 | 60.024 | 3786.8748 |  |  |  | -19.1986 | -18.1568 |  | 0 | 3747.8526 | 3767.1713 | 3772.561 | 3765.4462 | 3725.9137 | 633 | [6 empty] | 0 | 633 | -3492.0353 | [13 empty] | 40098.1068 | 60.024 | 3786.8748 | 350 | 230.2976 | 16 | 326 | 10 | 0 | -103 | 7715.16 | -19.1986
| 40098.1068 | 60.021 | 3786.5498 |  |  |  | -16.7999 | -17.6819 |  | 0 | 3748.3275 | 3767.2723 | 3772.4348 | 3765.4462 | 3726.1207 | 633 | [6 empty] | 0 | 633 | -2996.4048 | [13 empty] | 40098.1068 | 60.021 | 3786.5498 | 350 | 231.1755 | 16 | 326.5 | 10 | 0 | -103 | 7715.49 | -16.7999
| 40098.1068 | 60.02 | 3787.3577 |  |  |  | -16.0004 | -17.0934 |  | 0 | 3748.9161 | 3767.3763 | 3772.3129 | 3765.4462 | 3726.3255 | 633 | [6 empty] | 0 | 633 | -2861.047 | [13 empty] | 40098.1068 | 60.02 | 3787.3577 | 350 | 231.1755 | 16 | 327 | 10 | 0 | -103 | 7715.82 | -16.0004
| 40098.1069 | 60.025 | 3785.0181 |  |  |  | -20.0012 | -18.1111 |  | 0 | 3747.8983 | 3767.4673 | 3772.1871 | 3765.4462 | 3726.5282 | 633 | [6 empty] | 0 | 633 | -3696.6312 | [13 empty] | 40098.1069 | 60.025 | 3785.0181 | 350 | 231.1755 | 16 | 327.5 | 10 | 0 | -103 | 7716.15 | -20.0012
| 40098.1069 | 60.024 | 3785.614 |  |  |  | -19.1986 | -18.4917 |  | 0 | 3747.5177 | 3767.5603 | 3772.0605 | 3765.4462 | 3726.7288 | 633 | [6 empty] | 0 | 633 | -3492.0353 | [13 empty] | 40098.1069 | 60.024 | 3785.614 | 350 | 231.1755 | 16 | 328 | 10 | 0 | -103 | 7716.48 | -19.1986
| 40098.1069 | 60.02 | 3785.9492 |  |  |  | -16.0004 | -17.6198 |  | 0 | 3748.3897 | 3767.6541 | 3771.9398 | 3765.4462 | 3726.9274 | 633 | [6 empty] | 0 | 633 | -2861.047 | [13 empty] | 40098.1069 | 60.02 | 3785.9492 | 350 | 231.1755 | 16 | 328.5 | 10 | 0 | -103 | 7716.81 | -16.0004
| 40098.1069 | 60.02 | 3785.8037 |  |  |  | -16.0004 | -17.053 |  | 0 | 3748.9565 | 3767.7463 | 3771.8231 | 3765.4462 | 3727.1239 | 633 | [6 empty] | 0 | 633 | -2861.047 | [13 empty] | 40098.1069 | 60.02 | 3785.8037 | 350 | 225.6176 | 16 | 329 | 10 | 0 | -103 | 7717.14 | -16.0004
| 40098.1069 | 60.022 | 3786.8643 |  |  |  | -17.5995 | -17.2443 |  | 0 | 3748.7652 | 3767.8428 | 3771.7067 | 3765.4462 | 3727.3184 | 633 | [6 empty] | 0 | 633 | -3145.2063 | [13 empty] | 40098.1069 | 60.022 | 3786.8643 | 350 | 225.6176 | 16 | 329.5 | 10 | 0 | -103 | 7717.47 | -17.5995
| 40098.107 | 60.022 | 3786.8772 |  |  |  | -17.5995 | -17.3686 |  | 0 | 3748.6409 | 3767.9385 | 3771.5908 | 3765.4462 | 3727.511 | 633 | [6 empty] | 0 | 633 | -3145.2063 | [13 empty] | 40098.107 | 60.022 | 3786.8772 | 350 | 225.6176 | 16 | 330 | 10 | 0 | -103 | 7717.8 | -17.5995
| 40098.107 | 60.022 | 3785.2539 |  |  |  | -17.5995 | -17.4494 |  | 0 | 3748.56 | 3768.0251 | 3771.4756 | 3765.4462 | 3727.7016 | 633 | [6 empty] | 0 | 633 | -3145.2063 | [13 empty] | 40098.107 | 60.022 | 3785.2539 | 350 | 225.6176 | 16 | 330.5 | 10 | 0 | -103 | 7718.13 | -17.5995
| 40098.107 | 60.021 | 3785.7261 |  |  |  | -16.7999 | -17.2221 |  | 0 | 3748.7874 | 3768.1131 | 3771.3627 | 3765.4462 | 3727.8904 | 633 | [6 empty] | 0 | 633 | -2996.4048 | [13 empty] | 40098.107 | 60.021 | 3785.7261 | 350 | 225.6176 | 16 | 331 | 10 | 0 | -103 | 7718.46 | -16.7999
| 40098.107 | 60.021 | 3786.3469 |  |  |  | -16.7999 | -17.0743 |  | 0 | 3748.9351 | 3768.2034 | 3771.2517 | 3765.4462 | 3728.0772 | 633 | [6 empty] | 0 | 633 | -2996.4048 | [13 empty] | 40098.107 | 60.021 | 3786.3469 | 350 | 230.7344 | 16 | 331.5 | 10 | 0 | -103 | 7718.79 | -16.7999
| 40098.1071 | 60.023 | 3785.821 |  |  |  | -18.399 | -17.538 |  | 0 | 3748.4715 | 3768.2902 | 3771.1395 | 3765.4462 | 3728.2622 | 633 | [6 empty] | 0 | 633 | -3309.559 | [13 empty] | 40098.1071 | 60.023 | 3785.821 | 350 | 230.7344 | 16 | 332 | 10 | 0 | -103 | 7719.12 | -18.399
| 40098.1071 | 60.023 | 3785.7983 |  |  |  | -18.399 | -17.8394 |  | 0 | 3748.1701 | 3768.376 | 3771.0269 | 3765.4462 | 3728.4454 | 633 | [6 empty] | 0 | 633 | -3309.559 | [13 empty] | 40098.1071 | 60.023 | 3785.7983 | 350 | 230.7344 | 16 | 332.5 | 10 | 0 | -103 | 7719.45 | -18.399
| 40098.1071 | 60.022 | 3786.2842 |  |  |  | -17.5995 | -17.7554 |  | 0 | 3748.254 | 3768.4634 | 3770.9158 | 3765.4462 | 3728.6268 | 633 | [6 empty] | 0 | 633 | -3145.2063 | [13 empty] | 40098.1071 | 60.022 | 3786.2842 | 350 | 230.7344 | 16 | 333 | 10 | 0 | -103 | 7719.78 | -17.5995
| 40098.1071 | 60.019 | 3786.9392 |  |  |  | -15.2008 | -16.8613 |  | 0 | 3749.1482 | 3768.553 | 3770.8101 | 3765.4462 | 3728.8064 | 633 | [6 empty] | 0 | 633 | -2737.3899 | [13 empty] | 40098.1071 | 60.019 | 3786.9392 | 350 | 230.7344 | 16 | 333.5 | 10 | 0 | -103 | 7720.11 | -15.2008
| 40098.1072 | 60.016 | 3787.6274 |  |  |  | -12.7991 | -15.4395 |  | 0 | 3750.5699 | 3768.6452 | 3770.7123 | 3765.4462 | 3728.9842 | 633 | [6 empty] | 0 | 633 | -2422.8381 | [13 empty] | 40098.1072 | 60.016 | 3787.6274 | 350 | 234.8471 | 16 | 334 | 10 | 0 | -103 | 7720.44 | -12.7991
| 40098.1072 | 60.018 | 3789.4443 |  |  |  | -14.4012 | -15.0761 |  | 0 | 3750.9333 | 3768.7452 | 3770.6173 | 3765.4462 | 3729.1604 | 633 | [6 empty] | 0 | 633 | -2623.979 | [13 empty] | 40098.1072 | 60.018 | 3789.4443 | 350 | 234.8471 | 16 | 334.5 | 10 | 0 | -103 | 7720.77 | -14.4012
| 40098.1072 | 60.018 | 3789.6733 |  |  |  | -14.4012 | -14.8399 |  | 0 | 3751.1695 | 3768.8453 | 3770.5242 | 3765.4462 | 3729.3348 | 633 | [6 empty] | 0 | 633 | -2623.979 | [13 empty] | 40098.1072 | 60.018 | 3789.6733 | 350 | 234.8471 | 16 | 335 | 10 | 0 | -103 | 7721.1 | -14.4012
| 40098.1072 | 60.018 | 3789.4043 |  |  |  | -14.4012 | -14.6864 |  | 0 | 3751.3231 | 3768.9432 | 3770.4328 | 3765.4462 | 3729.5076 | 633 | [6 empty] | 0 | 633 | -2623.979 | [13 empty] | 40098.1072 | 60.018 | 3789.4043 | 350 | 234.8471 | 16 | 335.5 | 10 | 0 | -103 | 7721.43 | -14.4012
| 40098.1072 | 60.019 | 3788.4788 |  |  |  | -15.2008 | -14.8664 |  | 0 | 3751.143 | 3769.0358 | 3770.3413 | 3765.4462 | 3729.6787 | 633 | [6 empty] | 0 | 633 | -2737.3899 | [13 empty] | 40098.1072 | 60.019 | 3788.4788 | 350 | 234.8471 | 16 | 336 | 10 | 0 | -103 | 7721.76 | -15.2008
| 40098.1073 | 60.019 | 3789.1833 |  |  |  | -15.2008 | -14.9835 |  | 0 | 3751.026 | 3769.1308 | 3770.2502 | 3765.4462 | 3729.8482 | 633 | [6 empty] | 0 | 633 | -2737.3899 | [13 empty] | 40098.1073 | 60.019 | 3789.1833 | 350 | 228.9609 | 16 | 336.5 | 10 | 0 | -103 | 7722.09 | -15.2008
| 40098.1073 | 60.016 | 3789.3689 |  |  |  | -12.7991 | -14.2189 |  | 0 | 3751.7905 | 3769.2259 | 3770.1636 | 3765.4462 | 3730.0162 | 633 | [6 empty] | 0 | 633 | -2422.8381 | [13 empty] | 40098.1073 | 60.016 | 3789.3689 | 350 | 228.9609 | 16 | 337 | 10 | 0 | -103 | 7722.42 | -12.7991
| 40098.1073 | 60.015 | 3789.0049 |  |  |  | -11.9995 | -13.4421 |  | 0 | 3752.5673 | 3769.3183 | 3770.0813 | 3765.4462 | 3730.1825 | 633 | [6 empty] | 0 | 633 | -2333.5687 | [13 empty] | 40098.1073 | 60.015 | 3789.0049 | 350 | 228.9609 | 16 | 337.5 | 10 | 0 | -103 | 7722.75 | -11.9995
| 40098.1073 | 60.016 | 3788.6646 |  |  |  | -12.7991 | -13.2171 |  | 0 | 3752.7924 | 3769.4083 | 3770.0009 | 3765.4462 | 3730.3473 | 633 | [6 empty] | 0 | 633 | -2422.8381 | [13 empty] | 40098.1073 | 60.016 | 3788.6646 | 350 | 228.9609 | 16 | 338 | 10 | 0 | -103 | 7723.08 | -12.7991
| 40098.1074 | 60.014 | 3788.9329 |  |  |  | -11.2 | -12.5111 |  | 0 | 3753.4984 | 3769.4987 | 3769.9245 | 3765.4462 | 3730.5105 | 633 | [6 empty] | 0 | 633 | -2250.6438 | [13 empty] | 40098.1074 | 60.014 | 3788.9329 | 350 | 228.9609 | 16 | 338.5 | 10 | 0 | -103 | 7723.41 | -11.2
| 40098.1074 | 60.013 | 3790.667 |  |  |  | -10.4004 | -11.7723 |  | 0 | 3754.2371 | 3769.5962 | 3769.8522 | 3765.4462 | 3730.6723 | 633 | [6 empty] | 0 | 633 | -2173.4102 | [13 empty] | 40098.1074 | 60.013 | 3790.667 | 350 | 231.1779 | 16 | 339 | 10 | 0 | -103 | 7723.74 | -10.4004
| 40098.1074 | 60.012 | 3790.8052 |  |  |  | -9.6008 | -11.0123 |  | 0 | 3754.9971 | 3769.6935 | 3769.7841 | 3765.4462 | 3730.8325 | 633 | [6 empty] | 0 | 633 | -2101.3015 | [13 empty] | 40098.1074 | 60.012 | 3790.8052 | 350 | 231.1779 | 16 | 339.5 | 10 | 0 | -103 | 7724.07 | -9.6008
| 40098.1074 | 60.012 | 3790.4111 |  |  |  | -9.6008 | -10.5183 |  | 0 | 3755.4912 | 3769.7881 | 3769.7188 | 3765.4462 | 3730.9913 | 633 | [6 empty] | 0 | 633 | -2101.3015 | [13 empty] | 40098.1074 | 60.012 | 3790.4111 | 350 | 231.1779 | 16 | 340 | 10 | 0 | -103 | 7724.4 | -9.6008
| 40098.1075 | 60.01 | 3789.7686 |  |  |  | -7.9987 | -9.6364 |  | 0 | 3756.373 | 3769.8789 | 3769.6582 | 3765.4462 | 3731.1486 | 633 | [6 empty] | 0 | 633 | -1970.3113 | [13 empty] | 40098.1075 | 60.01 | 3789.7686 | 350 | 231.1779 | 16 | 340.5 | 10 | 0 | -103 | 7724.73 | -7.9987
| 40098.1075 | 60.007 | 3791.5398 |  |  |  | -5.6 | -8.2237 |  | 0 | 3757.7858 | 3769.9769 | 3769.6044 | 3765.4462 | 3731.3045 | 633 | [6 empty] | 0 | 633 | -1802.1221 | [13 empty] | 40098.1075 | 60.007 | 3791.5398 | 350 | 231.1779 | 16 | 341 | 10 | 0 | -103 | 7725.06 | -5.6
| 40098.1075 | 60.007 | 3792.9453 |  |  |  | -5.6 | -7.3054 |  | 0 | 3758.7041 | 3770.0804 | 3769.5553 | 3765.4462 | 3731.459 | 633 | [6 empty] | 0 | 633 | -1802.1221 | [13 empty] | 40098.1075 | 60.007 | 3792.9453 | 350 | 236.4893 | 16 | 341.5 | 10 | 0 | -103 | 7725.39 | -5.6
| 40098.1075 | 60.009 | 3791.0271 |  |  |  | -7.1991 | -7.2682 |  | 0 | 3758.7413 | 3770.1743 | 3769.5069 | 3765.4462 | 3731.6121 | 633 | [6 empty] | 0 | 633 | -1910.8653 | [13 empty] | 40098.1075 | 60.009 | 3791.0271 | 350 | 236.4893 | 16 | 342 | 10 | 0 | -103 | 7725.72 | -7.1991
| 40098.1075 | 60.009 | 3791.4431 |  |  |  | -7.1991 | -7.244 |  | 0 | 3758.7654 | 3770.2693 | 3769.4589 | 3765.4462 | 3731.7638 | 633 | [6 empty] | 0 | 633 | -1910.8653 | [13 empty] | 40098.1075 | 60.009 | 3791.4431 | 350 | 236.4893 | 16 | 342.5 | 10 | 0 | -103 | 7726.05 | -7.1991
| 40098.1076 | 60.01 | 3791.426 |  |  |  | -7.9987 | -7.5081 |  | 0 | 3758.5013 | 3770.3633 | 3769.4102 | 3765.4462 | 3731.9142 | 633 | [6 empty] | 0 | 633 | -1970.3113 | [13 empty] | 40098.1076 | 60.01 | 3791.426 | 350 | 236.4893 | 16 | 343 | 10 | 0 | -103 | 7726.38 | -7.9987
| 40098.1076 | 60.003 | 3790.603 |  |  |  | -2.3987 | -5.7198 |  | 0 | 3760.2896 | 3770.4529 | 3769.3698 | 3765.4462 | 3732.0632 | 633 | [6 empty] | 0 | 633 | -1617.8139 | [13 empty] | 40098.1076 | 60.003 | 3790.603 | 350 | 236.4893 | 16 | 343.5 | 10 | 0 | -103 | 7726.71 | -2.3987
| 40098.1076 | 59.999 | 3790.4573 |  |  |  | 0.79956 | -3.438 |  | 0 | 3762.5714 | 3770.541 | 3769.3399 | 3765.4462 | 3732.2109 | 633 | [6 empty] | 0 | 633 | -1467.8371 | [13 empty] | 40098.1076 | 59.999 | 3790.4573 | 350 | 245.0389 | 16 | 344 | 10 | 0 | -103 | 7727.04 | 0.79956
| 40098.1076 | 59.995 | 3790.2163 |  |  |  | 4.0009 | -0.83443 |  | 0 | 3765.175 | 3770.6273 | 3769.3216 | 3765.4462 | 3732.3574 | 633 | [6 empty] | 0 | 633 | -1343.1992 | [13 empty] | 40098.1076 | 59.995 | 3790.2163 | 350 | 245.0389 | 16 | 344.5 | 10 | 0 | -103 | 7727.37 | 4.0009
| 40098.1077 | 59.992 | 3789.585 |  |  |  | 6.3995 | 1.6975 |  | 0 | 3767.7069 | 3770.7101 | 3769.3146 | 3765.4462 | 3732.5025 | 633 | [6 empty] | 0 | 633 | -1262.8518 | [13 empty] | 40098.1077 | 59.992 | 3789.585 | 350 | 245.0389 | 16 | 345 | 10 | 0 | -103 | 7727.7 | 6.3995
| 40098.1077 | 59.991 | 3788.457 |  |  |  | 7.1991 | 3.623 |  | 0 | 3769.6325 | 3770.7872 | 3769.316 | 3765.4462 | 3732.6463 | 633 | [6 empty] | 0 | 633 | -1238.1637 | [13 empty] | 40098.1077 | 59.991 | 3788.457 | 350 | 245.0389 | 16 | 345.5 | 10 | 0 | -103 | 7728.03 | 7.1991
| 40098.1077 | 59.992 | 3788.105 |  |  |  | 6.3995 | 4.5948 |  | 0 | 3770.6043 | 3770.8622 | 3769.3215 | 3765.4462 | 3732.7889 | 633 | [6 empty] | 0 | 633 | -1262.8518 | [13 empty] | 40098.1077 | 59.992 | 3788.105 | 350 | 245.0389 | 16 | 346 | 10 | 0 | -103 | 7728.36 | 6.3995
| 40098.1077 | 59.992 | 3788.0571 |  |  |  | 6.3995 | 5.2265 |  | 0 | 3771.2359 | 3770.9363 | 3769.3298 | 3765.4462 | 3732.9303 | 633 | [6 empty] | 0 | 633 | -1262.8518 | [13 empty] | 40098.1077 | 59.992 | 3788.0571 | 350 | 223.6057 | 16 | 346.5 | 10 | 0 | -103 | 7728.69 | 6.3995
| 40098.1078 | 59.988 | 3788.1895 |  |  |  | 9.6008 | 6.7575 |  | 0 | 3772.7669 | 3771.0104 | 3769.3445 | 3765.4462 | 3733.0705 | 633 | [6 empty] | 0 | 633 | -1169.4877 | [13 empty] | 40098.1078 | 59.988 | 3788.1895 | 350 | 223.6057 | 16 | 347 | 10 | 0 | -103 | 7729.02 | 9.6008
| 40098.1078 | 59.986 | 3788.4973 |  |  |  | 11.2 | 8.3124 |  | 0 | 3774.3218 | 3771.0851 | 3769.3658 | 3765.4462 | 3733.2094 | 633 | [6 empty] | 0 | 633 | -1127.8363 | [13 empty] | 40098.1078 | 59.986 | 3788.4973 | 350 | 223.6057 | 16 | 347.5 | 10 | 0 | -103 | 7729.35 | 11.2
| 40098.1078 | 59.985 | 3788.54 |  |  |  | 11.9995 | 9.6029 |  | 0 | 3775.6123 | 3771.1594 | 3769.3924 | 3765.4462 | 3733.3472 | 633 | [6 empty] | 0 | 633 | -1108.1038 | [13 empty] | 40098.1078 | 59.985 | 3788.54 | 350 | 223.6057 | 16 | 348 | 10 | 0 | -103 | 7729.68 | 11.9995
| 40098.1078 | 59.984 | 3788.5708 |  |  |  | 12.7991 | 10.7215 |  | 0 | 3776.731 | 3771.2331 | 3769.4235 | 3765.4462 | 3733.4838 | 633 | [6 empty] | 0 | 633 | -1089.0498 | [13 empty] | 40098.1078 | 59.984 | 3788.5708 | 350 | 223.6057 | 16 | 348.5 | 10 | 0 | -103 | 7730.01 | 12.7991
| 40098.1078 | 59.985 | 3788.1011 |  |  |  | 11.9995 | 11.1688 |  | 0 | 3777.1783 | 3771.3043 | 3769.4562 | 3765.4462 | 3733.6192 | 633 | [6 empty] | 0 | 633 | -1108.1038 | [13 empty] | 40098.1078 | 59.985 | 3788.1011 | 350 | 231.1194 | 16 | 349 | 10 | 0 | -103 | 7730.34 | 11.9995
| 40098.1079 | 59.984 | 3787.1333 |  |  |  | 12.7991 | 11.7394 |  | 0 | 3777.7489 | 3771.3708 | 3769.4911 | 3765.4462 | 3733.7535 | 633 | [6 empty] | 0 | 633 | -1089.0498 | [13 empty] | 40098.1079 | 59.984 | 3787.1333 | 350 | 231.1194 | 16 | 349.5 | 10 | 0 | -103 | 7730.67 | 12.7991
| 40098.1079 | 59.982 | 3786.4529 |  |  |  | 14.4012 | 12.6711 |  | 0 | 3778.6805 | 3771.4339 | 3769.5295 | 3765.4462 | 3733.8867 | 633 | [6 empty] | 0 | 633 | -1052.7755 | [13 empty] | 40098.1079 | 59.982 | 3786.4529 | 350 | 231.1194 | 16 | 350 | 10 | 0 | -103 | 7731 | 14.4012
| 40098.1079 | 59.981 | 3787.7324 |  |  |  | 15.2008 | 13.5565 |  | 0 | 3779.5659 | 3771.5018 | 3769.5713 | 3765.4462 | 3734.0187 | 633 | [6 empty] | 0 | 633 | -1035.5619 | [13 empty] | 40098.1079 | 59.981 | 3787.7324 | 350 | 231.1194 | 16 | 350.5 | 10 | 0 | -103 | 7731.33 | 15.2008
| 40098.1079 | 59.982 | 3788.8135 |  |  |  | 14.4012 | 13.8521 |  | 0 | 3779.8616 | 3771.5737 | 3769.614 | 3765.4462 | 3734.1497 | 633 | [6 empty] | 0 | 633 | -1052.7755 | [13 empty] | 40098.1079 | 59.982 | 3788.8135 | 350 | 231.1194 | 16 | 351 | 10 | 0 | -103 | 7731.66 | 14.4012
| 40098.108 | 59.979 | 3789.2852 |  |  |  | 16.7999 | 14.8839 |  | 0 | 3780.8933 | 3771.6469 | 3769.6606 | 3765.4462 | 3734.2795 | 633 | [6 empty] | 0 | 633 | -1002.7702 | [13 empty] | 40098.108 | 59.979 | 3789.2852 | 350 | 237.2066 | 16 | 351.5 | 10 | 0 | -103 | 7731.99 | 16.7999
| 40098.108 | 59.977 | 3788.2563 |  |  |  | 18.399 | 16.1142 |  | 0 | 3782.1236 | 3771.7152 | 3769.7119 | 3765.4462 | 3734.4083 | 633 | [6 empty] | 0 | 633 | -971.9914 | [13 empty] | 40098.108 | 59.977 | 3788.2563 | 350 | 237.2066 | 16 | 352 | 10 | 0 | -103 | 7732.32 | 18.399
| 40098.108 | 59.976 | 3788.4097 |  |  |  | 19.1986 | 17.1937 |  | 0 | 3783.2032 | 3771.7836 | 3769.7672 | 3765.4462 | 3734.536 | 633 | [6 empty] | 0 | 633 | -957.2998 | [13 empty] | 40098.108 | 59.976 | 3788.4097 | 350 | 237.2066 | 16 | 352.5 | 10 | 0 | -103 | 7732.65 | 19.1986
| 40098.108 | 59.976 | 3790.4673 |  |  |  | 19.1986 | 17.8954 |  | 0 | 3783.9049 | 3771.8599 | 3769.8249 | 3765.4462 | 3734.6627 | 633 | [6 empty] | 0 | 633 | -957.2998 | [13 empty] | 40098.108 | 59.976 | 3790.4673 | 350 | 237.2066 | 16 | 353 | 10 | 0 | -103 | 7732.98 | 19.1986
| 40098.1081 | 59.979 | 3790.6646 |  |  |  | 16.7999 | 17.512 |  | 0 | 3783.5215 | 3771.9363 | 3769.8806 | 3765.4462 | 3734.7884 | 633 | [6 empty] | 0 | 633 | -1002.7702 | [13 empty] | 40098.1081 | 59.979 | 3790.6646 | 350 | 237.2066 | 16 | 353.5 | 10 | 0 | -103 | 7733.31 | 16.7999
| 40098.1081 | 59.982 | 3790.4204 |  |  |  | 14.4012 | 16.4232 |  | 0 | 3782.4327 | 3772.0112 | 3769.9314 | 3765.4462 | 3734.913 | 633 | [6 empty] | 0 | 633 | -1052.7755 | [13 empty] | 40098.1081 | 59.982 | 3790.4204 | 350 | 240.5164 | 16 | 354 | 10 | 0 | -103 | 7733.64 | 14.4012
| 40098.1081 | 59.978 | 3789.6738 |  |  |  | 17.5995 | 16.8349 |  | 0 | 3782.8444 | 3772.0824 | 3769.9835 | 3765.4462 | 3735.0366 | 633 | [6 empty] | 0 | 633 | -987.1409 | [13 empty] | 40098.1081 | 59.978 | 3789.6738 | 350 | 240.5164 | 16 | 354.5 | 10 | 0 | -103 | 7733.97 | 17.5995
| 40098.1081 | 59.976 | 3789.2671 |  |  |  | 19.1986 | 17.6622 |  | 0 | 3783.6717 | 3772.1514 | 3770.0384 | 3765.4462 | 3735.1592 | 633 | [6 empty] | 0 | 633 | -957.2998 | [13 empty] | 40098.1081 | 59.976 | 3789.2671 | 350 | 240.5164 | 16 | 355 | 10 | 0 | -103 | 7734.3 | 19.1986
| 40098.1081 | 59.974 | 3789.1479 |  |  |  | 20.8008 | 18.7607 |  | 0 | 3784.7702 | 3772.2194 | 3770.0974 | 3765.4462 | 3735.2809 | 633 | [6 empty] | 0 | 633 | -929.1579 | [13 empty] | 40098.1081 | 59.974 | 3789.1479 | 350 | 240.5164 | 16 | 355.5 | 10 | 0 | -103 | 7734.63 | 20.8008
| 40098.1082 | 59.976 | 3790.4304 |  |  |  | 19.1986 | 18.914 |  | 0 | 3784.9234 | 3772.2919 | 3770.1564 | 3765.4462 | 3735.4015 | 633 | [6 empty] | 0 | 633 | -957.2998 | [13 empty] | 40098.1082 | 59.976 | 3790.4304 | 350 | 240.5164 | 16 | 356 | 10 | 0 | -103 | 7734.96 | 19.1986
| 40098.1082 | 59.977 | 3789.9143 |  |  |  | 18.399 | 18.7338 |  | 0 | 3784.7432 | 3772.3619 | 3770.2143 | 3765.4462 | 3735.5212 | 633 | [6 empty] | 0 | 633 | -971.9914 | [13 empty] | 40098.1082 | 59.977 | 3789.9143 | 350 | 237.5661 | 16 | 356.5 | 10 | 0 | -103 | 7735.29 | 18.399
| 40098.1082 | 59.977 | 3786.2432 |  |  |  | 18.399 | 18.6166 |  | 0 | 3784.6261 | 3772.4167 | 3770.2713 | 3765.4462 | 3735.64 | 633 | [6 empty] | 0 | 633 | -971.9914 | [13 empty] | 40098.1082 | 59.977 | 3786.2432 | 350 | 237.5661 | 16 | 357 | 10 | 0 | -103 | 7735.62 | 18.399
| 40098.1082 | 59.975 | 3787.4421 |  |  |  | 20.0012 | 19.1012 |  | 0 | 3785.1107 | 3772.4759 | 3770.3297 | 3765.4462 | 3735.7578 | 633 | [6 empty] | 0 | 633 | -942.9922 | [13 empty] | 40098.1082 | 59.975 | 3787.4421 | 350 | 237.5661 | 16 | 357.5 | 10 | 0 | -103 | 7735.95 | 20.0012
| 40098.1083 | 59.973 | 3788.9629 |  |  |  | 21.6003 | 19.9759 |  | 0 | 3785.9854 | 3772.5405 | 3770.3911 | 3765.4462 | 3735.8747 | 633 | [6 empty] | 0 | 633 | -915.7237 | [13 empty] | 40098.1083 | 59.973 | 3788.9629 | 350 | 237.5661 | 16 | 358 | 10 | 0 | -103 | 7736.28 | 21.6003
| 40098.1083 | 59.969 | 3790.6016 |  |  |  | 24.7986 | 21.6638 |  | 0 | 3787.6733 | 3772.6111 | 3770.4586 | 3765.4462 | 3735.9906 | 633 | [6 empty] | 0 | 633 | -865.6593 | [13 empty] | 40098.1083 | 59.969 | 3790.6016 | 350 | 237.5661 | 16 | 358.5 | 10 | 0 | -103 | 7736.61 | 24.7986
| 40098.1083 | 59.97 | 3791.877 |  |  |  | 23.999 | 22.4812 |  | 0 | 3788.4906 | 3772.6861 | 3770.5288 | 3765.4462 | 3736.1057 | 633 | [6 empty] | 0 | 633 | -877.6551 | [13 empty] | 40098.1083 | 59.97 | 3791.877 | 350 | 231.5814 | 16 | 359 | 10 | 0 | -103 | 7736.94 | 23.999
| 40098.1083 | 59.971 | 3792.9106 |  |  |  | 23.1995 | 22.7326 |  | 0 | 3788.742 | 3772.7645 | 3770.5994 | 3765.4462 | 3736.2199 | 633 | [6 empty] | 0 | 633 | -889.988 | [13 empty] | 40098.1083 | 59.971 | 3792.9106 | 350 | 231.5814 | 16 | 359.5 | 10 | 0 | -103 | 7737.27 | 23.1995
| 40098.1084 | 59.973 | 3792.3113 |  |  |  | 21.6003 | 22.3363 |  | 0 | 3788.3457 | 3772.8399 | 3770.6679 | 3765.4462 | 3736.3331 | 633 | [6 empty] | 0 | 633 | -915.7237 | [13 empty] | 40098.1084 | 59.973 | 3792.3113 | 350 | 231.5814 | 16 | 360 | 10 | 0 | -103 | 7737.6 | 21.6003
| 40098.1084 | 59.978 | 3789.125 |  |  |  | 17.5995 | 20.6784 |  | 0 | 3786.6879 | 3772.9026 | 3770.7295 | 3765.4462 | 3736.4455 | 633 | [6 empty] | 0 | 633 | -987.1409 | [13 empty] | 40098.1084 | 59.978 | 3789.125 | 350 | 231.5814 | 16 | 360.5 | 10 | 0 | -103 | 7737.93 | 17.5995
| 40098.1084 | 59.981 | 3788.0796 |  |  |  | 15.2008 | 18.7612 |  | 0 | 3784.7707 | 3772.9607 | 3770.7833 | 3765.4462 | 3736.5571 | 633 | [6 empty] | 0 | 633 | -1035.5619 | [13 empty] | 40098.1084 | 59.981 | 3788.0796 | 350 | 231.5814 | 16 | 361 | 10 | 0 | -103 | 7738.26 | 15.2008
| 40098.1084 | 59.978 | 3787.844 |  |  |  | 17.5995 | 18.3546 |  | 0 | 3784.3641 | 3773.0175 | 3770.8351 | 3765.4462 | 3736.6678 | 633 | [6 empty] | 0 | 633 | -987.1409 | [13 empty] | 40098.1084 | 59.978 | 3787.844 | 350 | 235.8508 | 16 | 361.5 | 10 | 0 | -103 | 7738.59 | 17.5995
| 40098.1084 | 59.975 | 3787.135 |  |  |  | 20.0012 | 18.9309 |  | 0 | 3784.9404 | 3773.0712 | 3770.8888 | 3765.4462 | 3736.7776 | 633 | [6 empty] | 0 | 633 | -942.9922 | [13 empty] | 40098.1084 | 59.975 | 3787.135 | 350 | 235.8508 | 16 | 362 | 10 | 0 | -103 | 7738.92 | 20.0012
| 40098.1085 | 59.972 | 3787.1643 |  |  |  | 22.3999 | 20.1451 |  | 0 | 3786.1545 | 3773.1246 | 3770.9466 | 3765.4462 | 3736.8866 | 633 | [6 empty] | 0 | 633 | -902.6725 | [13 empty] | 40098.1085 | 59.972 | 3787.1643 | 350 | 235.8508 | 16 | 362.5 | 10 | 0 | -103 | 7739.25 | 22.3999
| 40098.1085 | 59.976 | 3786.9961 |  |  |  | 19.1986 | 19.8138 |  | 0 | 3785.8233 | 3773.1769 | 3771.0027 | 3765.4462 | 3736.9948 | 633 | [6 empty] | 0 | 633 | -957.2998 | [13 empty] | 40098.1085 | 59.976 | 3786.9961 | 350 | 235.8508 | 16 | 363 | 10 | 0 | -103 | 7739.58 | 19.1986
| 40098.1085 | 59.975 | 3787.4048 |  |  |  | 20.0012 | 19.8794 |  | 0 | 3785.8889 | 3773.2304 | 3771.0587 | 3765.4462 | 3737.1022 | 633 | [6 empty] | 0 | 633 | -942.9922 | [13 empty] | 40098.1085 | 59.975 | 3787.4048 | 350 | 235.8508 | 16 | 363.5 | 10 | 0 | -103 | 7739.91 | 20.0012
| 40098.1085 | 59.973 | 3786.4868 |  |  |  | 21.6003 | 20.4817 |  | 0 | 3786.4912 | 3773.2801 | 3771.1165 | 3765.4462 | 3737.2087 | 633 | [6 empty] | 0 | 633 | -915.7237 | [13 empty] | 40098.1085 | 59.973 | 3786.4868 | 350 | 233.56 | 16 | 364 | 10 | 0 | -103 | 7740.24 | 21.6003
| 40098.1086 | 59.969 | 3787.0791 |  |  |  | 24.7986 | 21.9926 |  | 0 | 3788.0021 | 3773.3315 | 3771.1795 | 3765.4462 | 3737.3145 | 633 | [6 empty] | 0 | 633 | -865.6593 | [13 empty] | 40098.1086 | 59.969 | 3787.0791 | 350 | 233.56 | 16 | 364.5 | 10 | 0 | -103 | 7740.57 | 24.7986
| 40098.1086 | 59.966 | 3789.2139 |  |  |  | 27.2003 | 23.8153 |  | 0 | 3789.8248 | 3773.3906 | 3771.2488 | 3765.4462 | 3737.4194 | 633 | [6 empty] | 0 | 633 | -831.5203 | [13 empty] | 40098.1086 | 59.966 | 3789.2139 | 350 | 233.56 | 16 | 365 | 10 | 0 | -103 | 7740.9 | 27.2003
| 40098.1086 | 59.965 | 3790.5117 |  |  |  | 27.9999 | 25.2799 |  | 0 | 3791.2894 | 3773.454 | 3771.323 | 3765.4462 | 3737.5236 | 633 | [6 empty] | 0 | 633 | -820.7448 | [13 empty] | 40098.1086 | 59.965 | 3790.5117 | 350 | 233.56 | 16 | 365.5 | 10 | 0 | -103 | 7741.23 | 27.9999
| 40098.1086 | 59.966 | 3791.2212 |  |  |  | 27.2003 | 25.9521 |  | 0 | 3791.9615 | 3773.5196 | 3771.3992 | 3765.4462 | 3737.6271 | 633 | [6 empty] | 0 | 633 | -831.5203 | [13 empty] | 40098.1086 | 59.966 | 3791.2212 | 350 | 233.56 | 16 | 366 | 10 | 0 | -103 | 7741.56 | 27.2003
| 40098.1087 | 59.969 | 3792.2183 |  |  |  | 24.7986 | 25.5483 |  | 0 | 3791.5578 | 3773.5883 | 3771.4733 | 3765.4462 | 3737.7297 | 633 | [6 empty] | 0 | 633 | -865.6593 | [13 empty] | 40098.1087 | 59.969 | 3792.2183 | 350 | 219.01 | 16 | 366.5 | 10 | 0 | -103 | 7741.89 | 24.7986
| 40098.1087 | 59.97 | 3790.9595 |  |  |  | 23.999 | 25.0061 |  | 0 | 3791.0155 | 3773.6519 | 3771.5449 | 3765.4462 | 3737.8316 | 633 | [6 empty] | 0 | 633 | -877.6551 | [13 empty] | 40098.1087 | 59.97 | 3790.9595 | 350 | 219.01 | 16 | 367 | 10 | 0 | -103 | 7742.22 | 23.999
| 40098.1087 | 59.968 | 3788.8242 |  |  |  | 25.6012 | 25.2144 |  | 0 | 3791.2238 | 3773.7073 | 3771.6167 | 3765.4462 | 3737.9328 | 633 | [6 empty] | 0 | 633 | -853.9431 | [13 empty] | 40098.1087 | 59.968 | 3788.8242 | 350 | 219.01 | 16 | 367.5 | 10 | 0 | -103 | 7742.55 | 25.6012
| 40098.1087 | 59.965 | 3789.0264 |  |  |  | 27.9999 | 26.1893 |  | 0 | 3792.1987 | 3773.763 | 3771.6916 | 3765.4462 | 3738.0332 | 633 | [6 empty] | 0 | 633 | -820.7448 | [13 empty] | 40098.1087 | 59.965 | 3789.0264 | 350 | 219.01 | 16 | 368 | 10 | 0 | -103 | 7742.88 | 27.9999
| 40098.1087 | 59.964 | 3789.1675 |  |  |  | 28.7994 | 27.1028 |  | 0 | 3793.1123 | 3773.8188 | 3771.7692 | 3765.4462 | 3738.1329 | 633 | [6 empty] | 0 | 633 | -810.2449 | [13 empty] | 40098.1087 | 59.964 | 3789.1675 | 350 | 219.01 | 16 | 368.5 | 10 | 0 | -103 | 7743.21 | 28.7994
| 40098.1088 | 59.97 | 3787.394 |  |  |  | 23.999 | 26.0165 |  | 0 | 3792.026 | 3773.8678 | 3771.8423 | 3765.4462 | 3738.2318 | 633 | [6 empty] | 0 | 633 | -877.6551 | [13 empty] | 40098.1088 | 59.97 | 3787.394 | 350 | 205.3389 | 16 | 369 | 10 | 0 | -103 | 7743.54 | 23.999
| 40098.1088 | 59.972 | 3785.6899 |  |  |  | 22.3999 | 24.7507 |  | 0 | 3790.7601 | 3773.9104 | 3771.9103 | 3765.4462 | 3738.3301 | 633 | [6 empty] | 0 | 633 | -902.6725 | [13 empty] | 40098.1088 | 59.972 | 3785.6899 | 350 | 205.3389 | 16 | 369.5 | 10 | 0 | -103 | 7743.87 | 22.3999
| 40098.1088 | 59.967 | 3784.8306 |  |  |  | 26.4008 | 25.3282 |  | 0 | 3791.3377 | 3773.9495 | 3771.98 | 3765.4462 | 3738.4276 | 633 | [6 empty] | 0 | 633 | -842.5825 | [13 empty] | 40098.1088 | 59.967 | 3784.8306 | 350 | 205.3389 | 16 | 370 | 10 | 0 | -103 | 7744.2 | 26.4008
| 40098.1088 | 59.967 | 3785.0095 |  |  |  | 26.4008 | 25.7036 |  | 0 | 3791.7131 | 3773.989 | 3772.0505 | 3765.4462 | 3738.5244 | 633 | [6 empty] | 0 | 633 | -842.5825 | [13 empty] | 40098.1088 | 59.967 | 3785.0095 | 350 | 205.3389 | 16 | 370.5 | 10 | 0 | -103 | 7744.53 | 26.4008
| 40098.1089 | 59.969 | 3784.3203 |  |  |  | 24.7986 | 25.3868 |  | 0 | 3791.3963 | 3774.0258 | 3772.1193 | 3765.4462 | 3738.6206 | 633 | [6 empty] | 0 | 633 | -865.6593 | [13 empty] | 40098.1089 | 59.969 | 3784.3203 | 350 | 205.3389 | 16 | 371 | 10 | 0 | -103 | 7744.86 | 24.7986
| 40098.1089 | 59.968 | 3782.8086 |  |  |  | 25.6012 | 25.4619 |  | 0 | 3791.4713 | 3774.0569 | 3772.1879 | 3765.4462 | 3738.7161 | 633 | [6 empty] | 0 | 633 | -853.9431 | [13 empty] | 40098.1089 | 59.968 | 3782.8086 | 350 | 236.2854 | 16 | 371.5 | 10 | 0 | -103 | 7745.19 | 25.6012
| 40098.1089 | 59.969 | 3782.1099 |  |  |  | 24.7986 | 25.2297 |  | 0 | 3791.2392 | 3774.0854 | 3772.2552 | 3765.4462 | 3738.8108 | 633 | [6 empty] | 0 | 633 | -865.6593 | [13 empty] | 40098.1089 | 59.969 | 3782.1099 | 350 | 236.2854 | 16 | 372 | 10 | 0 | -103 | 7745.52 | 24.7986
| 40098.1089 | 59.967 | 3779.3516 |  |  |  | 26.4008 | 25.6396 |  | 0 | 3791.649 | 3774.1039 | 3772.3235 | 3765.4462 | 3738.905 | 633 | [6 empty] | 0 | 633 | -842.5825 | [13 empty] | 40098.1089 | 59.967 | 3779.3516 | 350 | 236.2854 | 16 | 372.5 | 10 | 0 | -103 | 7745.85 | 26.4008
| 40098.109 | 59.967 | 3779.0562 |  |  |  | 26.4008 | 25.906 |  | 0 | 3791.9154 | 3774.1213 | 3772.3923 | 3765.4462 | 3738.9984 | 633 | [6 empty] | 0 | 633 | -842.5825 | [13 empty] | 40098.109 | 59.967 | 3779.0562 | 350 | 236.2854 | 16 | 373 | 10 | 0 | -103 | 7746.18 | 26.4008
| 40098.109 | 59.966 | 3778.6333 |  |  |  | 27.2003 | 26.359 |  | 0 | 3792.3685 | 3774.1371 | 3772.4621 | 3765.4462 | 3739.0912 | 633 | [6 empty] | 0 | 633 | -831.5203 | [13 empty] | 40098.109 | 59.966 | 3778.6333 | 350 | 236.2854 | 16 | 373.5 | 10 | 0 | -103 | 7746.51 | 27.2003
| 40098.109 | 59.965 | 3779.2117 |  |  |  | 27.9999 | 26.9333 |  | 0 | 3792.9428 | 3774.1547 | 3772.5335 | 3765.4462 | 3739.1834 | 633 | [6 empty] | 0 | 633 | -820.7448 | [13 empty] | 40098.109 | 59.965 | 3779.2117 | 350 | 223.0157 | 16 | 374 | 10 | 0 | -103 | 7746.84 | 27.9999
| 40098.109 | 59.971 | 3779.3347 |  |  |  | 23.1995 | 25.6265 |  | 0 | 3791.6359 | 3774.1727 | 3772.5998 | 3765.4462 | 3739.2749 | 633 | [6 empty] | 0 | 633 | -889.988 | [13 empty] | 40098.109 | 59.971 | 3779.3347 | 350 | 223.0157 | 16 | 374.5 | 10 | 0 | -103 | 7747.17 | 23.1995
| 40098.1091 | 59.967 | 3776.4292 |  |  |  | 26.4008 | 25.8975 |  | 0 | 3791.9069 | 3774.1805 | 3772.6666 | 3765.4462 | 3739.3657 | 633 | [6 empty] | 0 | 633 | -842.5825 | [13 empty] | 40098.1091 | 59.967 | 3776.4292 | 350 | 223.0157 | 16 | 375 | 10 | 0 | -103 | 7747.5 | 26.4008
| 40098.1091 | 59.965 | 3775.6467 |  |  |  | 27.9999 | 26.6333 |  | 0 | 3792.6428 | 3774.1856 | 3772.7355 | 3765.4462 | 3739.456 | 633 | [6 empty] | 0 | 633 | -820.7448 | [13 empty] | 40098.1091 | 59.965 | 3775.6467 | 350 | 223.0157 | 16 | 375.5 | 10 | 0 | -103 | 7747.83 | 27.9999
| 40098.1091 | 59.962 | 3776.5967 |  |  |  | 30.3986 | 27.9511 |  | 0 | 3793.9606 | 3774.1939 | 3772.8084 | 3765.4462 | 3739.5456 | 633 | [6 empty] | 0 | 633 | -790.0311 | [13 empty] | 40098.1091 | 59.962 | 3776.5967 | 350 | 223.0157 | 16 | 376 | 10 | 0 | -103 | 7748.16 | 30.3986
| 40098.1091 | 59.964 | 3776.5591 |  |  |  | 28.7994 | 28.248 |  | 0 | 3794.2575 | 3774.202 | 3772.8819 | 3765.4462 | 3739.6346 | 633 | [6 empty] | 0 | 633 | -810.2449 | [13 empty] | 40098.1091 | 59.964 | 3776.5591 | 350 | 223.0157 | 16 | 376.5 | 10 | 0 | -103 | 7748.49 | 28.7994
| 40098.1091 | 59.97 | 3776.0229 |  |  |  | 23.999 | 26.7609 |  | 0 | 3792.7703 | 3774.2082 | 3772.9498 | 3765.4462 | 3739.723 | 633 | [6 empty] | 0 | 633 | -877.6551 | [13 empty] | 40098.1091 | 59.97 | 3776.0229 | 350 | 223.0157 | 16 | 377 | 10 | 0 | -103 | 7748.82 | 23.999
| 40098.1092 | 59.967 | 3773.1699 |  |  |  | 26.4008 | 26.6348 |  | 0 | 3792.6443 | 3774.2047 | 3773.0168 | 3765.4462 | 3739.8108 | 633 | [6 empty] | 0 | 633 | -842.5825 | [13 empty] | 40098.1092 | 59.967 | 3773.1699 | 350 | 223.0157 | 16 | 377.5 | 10 | 0 | -103 | 7749.15 | 26.4008
| 40098.1092 | 59.969 | 3771.7305 |  |  |  | 24.7986 | 25.9922 |  | 0 | 3792.0016 | 3774.1963 | 3773.0811 | 3765.4462 | 3739.898 | 633 | [6 empty] | 0 | 633 | -865.6593 | [13 empty] | 40098.1092 | 59.969 | 3771.7305 | 350 | 223.0157 | 16 | 378 | 10 | 0 | -103 | 7749.48 | 24.7986
| 40098.1092 | 59.968 | 3768.793 |  |  |  | 25.6012 | 25.8553 |  | 0 | 3791.8648 | 3774.178 | 3773.1446 | 3765.4462 | 3739.9846 | 633 | [6 empty] | 0 | 633 | -853.9431 | [13 empty] | 40098.1092 | 59.968 | 3768.793 | 350 | 223.0157 | 16 | 378.5 | 10 | 0 | -103 | 7749.81 | 25.6012
| 40098.1092 | 59.963 | 3768.5029 |  |  |  | 29.599 | 27.1656 |  | 0 | 3793.1751 | 3774.1589 | 3773.212 | 3765.4462 | 3740.0706 | 633 | [6 empty] | 0 | 633 | -800.0104 | [13 empty] | 40098.1092 | 59.963 | 3768.5029 | 350 | 223.0157 | 16 | 379 | 10 | 0 | -103 | 7750.14 | 29.599
| 40098.1093 | 59.965 | 3768.9175 |  |  |  | 27.9999 | 27.4576 |  | 0 | 3793.467 | 3774.1413 | 3773.28 | 3765.4462 | 3740.1561 | 633 | [6 empty] | 0 | 633 | -820.7448 | [13 empty] | 40098.1093 | 59.965 | 3768.9175 | 350 | 223.0157 | 16 | 379.5 | 10 | 0 | -103 | 7750.47 | 27.9999
| 40098.1093 | 59.97 | 3767.3662 |  |  |  | 23.999 | 26.2471 |  | 0 | 3792.2565 | 3774.1187 | 3773.3435 | 3765.4462 | 3740.2409 | 633 | [6 empty] | 0 | 633 | -877.6551 | [13 empty] | 40098.1093 | 59.97 | 3767.3662 | 350 | 223.0157 | 16 | 380 | 10 | 0 | -103 | 7750.8 | 23.999
| 40098.1093 | 59.973 | 3764.7861 |  |  |  | 21.6003 | 24.6207 |  | 0 | 3790.6302 | 3774.0876 | 3773.4011 | 3765.4462 | 3740.3252 | 633 | [6 empty] | 0 | 633 | -915.7237 | [13 empty] | 40098.1093 | 59.973 | 3764.7861 | 350 | 223.0157 | 16 | 380.5 | 10 | 0 | -103 | 7751.13 | 21.6003
| 40098.1093 | 59.968 | 3760.2954 |  |  |  | 25.6012 | 24.9639 |  | 0 | 3790.9733 | 3774.0417 | 3773.4595 | 3765.4462 | 3740.409 | 633 | [6 empty] | 0 | 633 | -853.9431 | [13 empty] | 40098.1093 | 59.968 | 3760.2954 | 350 | 223.0157 | 16 | 381 | 10 | 0 | -103 | 7751.46 | 25.6012
| 40098.1094 | 59.965 | 3759.5918 |  |  |  | 27.9999 | 26.0265 |  | 0 | 3792.0359 | 3773.9939 | 3773.521 | 3765.4462 | 3740.4921 | 633 | [6 empty] | 0 | 633 | -820.7448 | [13 empty] | 40098.1094 | 59.965 | 3759.5918 | 350 | 223.0157 | 16 | 381.5 | 10 | 0 | -103 | 7751.79 | 27.9999
| 40098.1094 | 59.968 | 3761.8938 |  |  |  | 25.6012 | 25.8776 |  | 0 | 3791.8871 | 3773.954 | 3773.5816 | 3765.4462 | 3740.5748 | 633 | [6 empty] | 0 | 633 | -853.9431 | [13 empty] | 40098.1094 | 59.968 | 3761.8938 | 350 | 223.0157 | 16 | 382 | 10 | 0 | -103 | 7752.12 | 25.6012
| 40098.1094 | 59.969 | 3761.7766 |  |  |  | 24.7986 | 25.5 |  | 0 | 3791.5094 | 3773.9139 | 3773.6406 | 3765.4462 | 3740.6569 | 633 | [6 empty] | 0 | 633 | -865.6593 | [13 empty] | 40098.1094 | 59.969 | 3761.7766 | 350 | 223.0157 | 16 | 382.5 | 10 | 0 | -103 | 7752.45 | 24.7986
| 40098.1094 | 59.967 | 3760.5825 |  |  |  | 26.4008 | 25.8152 |  | 0 | 3791.8247 | 3773.8702 | 3773.7002 | 3765.4462 | 3740.7384 | 633 | [6 empty] | 0 | 633 | -842.5825 | [13 empty] | 40098.1094 | 59.967 | 3760.5825 | 350 | 223.0157 | 16 | 383 | 10 | 0 | -103 | 7752.78 | 26.4008
| 40098.1094 | 59.964 | 3760.1575 |  |  |  | 28.7994 | 26.8597 |  | 0 | 3792.8692 | 3773.8254 | 3773.7628 | 3765.4462 | 3740.8194 | 633 | [6 empty] | 0 | 633 | -810.2449 | [13 empty] | 40098.1094 | 59.964 | 3760.1575 | 350 | 223.0157 | 16 | 383.5 | 10 | 0 | -103 | 7753.11 | 28.7994
| 40098.1095 | 59.966 | 3759.781 |  |  |  | 27.2003 | 26.9789 |  | 0 | 3792.9884 | 3773.7796 | 3773.8254 | 3765.4462 | 3740.8999 | 633 | [6 empty] | 0 | 633 | -831.5203 | [13 empty] | 40098.1095 | 59.966 | 3759.781 | 350 | 223.0157 | 16 | 384 | 10 | 0 | -103 | 7753.44 | 27.2003
| 40098.1095 | 59.979 | 3759.4949 |  |  |  | 16.7999 | 23.4163 |  | 0 | 3789.4257 | 3773.7333 | 3773.8761 | 3765.4462 | 3740.9798 | 633 | [6 empty] | 0 | 633 | -1002.7702 | [13 empty] | 40098.1095 | 59.979 | 3759.4949 | 350 | 223.0157 | 16 | 384.5 | 10 | 0 | -103 | 7753.77 | 16.7999
| 40098.1095 | 59.99 | 3757.7729 |  |  |  | 7.9987 | 18.0201 |  | 0 | 3784.0296 | 3773.6816 | 3773.909 | 3765.4462 | 3741.0593 | 633 | [6 empty] | 0 | 633 | -1214.4224 | [13 empty] | 40098.1095 | 59.99 | 3757.7729 | 350 | 223.0157 | 16 | 385 | 10 | 0 | -103 | 7754.1 | 7.9987
| 40098.1095 | 59.983 | 3753.2771 |  |  |  | 13.5986 | 16.4726 |  | 0 | 3782.482 | 3773.6158 | 3773.9366 | 3765.4462 | 3741.1382 | 633 | [6 empty] | 0 | 633 | -1070.64 | [13 empty] | 40098.1095 | 59.983 | 3753.2771 | 350 | 223.0157 | 16 | 385.5 | 10 | 0 | -103 | 7754.43 | 13.5986
| 40098.1096 | 59.974 | 3753.0874 |  |  |  | 20.8008 | 17.9875 |  | 0 | 3783.9969 | 3773.5498 | 3773.969 | 3765.4462 | 3741.2166 | 633 | [6 empty] | 0 | 633 | -929.1579 | [13 empty] | 40098.1096 | 59.974 | 3753.0874 | 350 | 223.0157 | 16 | 386 | 10 | 0 | -103 | 7754.76 | 20.8008
| 40098.1096 | 59.967 | 3751.6367 |  |  |  | 26.4008 | 20.9321 |  | 0 | 3786.9416 | 3773.4795 | 3774.0105 | 3765.4462 | 3741.2945 | 633 | [6 empty] | 0 | 633 | -842.5825 | [13 empty] | 40098.1096 | 59.967 | 3751.6367 | 350 | 223.0157 | 16 | 386.5 | 10 | 0 | -103 | 7755.09 | 26.4008
| 40098.1096 | 59.965 | 3753.751 |  |  |  | 27.9999 | 23.4058 |  | 0 | 3789.4153 | 3773.4165 | 3774.0598 | 3765.4462 | 3741.3719 | 633 | [6 empty] | 0 | 633 | -820.7448 | [13 empty] | 40098.1096 | 59.965 | 3753.751 | 350 | 223.0157 | 16 | 387 | 10 | 0 | -103 | 7755.42 | 27.9999
| 40098.1096 | 59.962 | 3758.2246 |  |  |  | 30.3986 | 25.8533 |  | 0 | 3791.8627 | 3773.3681 | 3774.1164 | 3765.4462 | 3741.4488 | 633 | [6 empty] | 0 | 633 | -790.0311 | [13 empty] | 40098.1096 | 59.962 | 3758.2246 | 350 | 223.0157 | 16 | 387.5 | 10 | 0 | -103 | 7755.75 | 30.3986
| 40098.1097 | 59.962 | 3759.2498 |  |  |  | 30.3986 | 27.4441 |  | 0 | 3793.4536 | 3773.3233 | 3774.1778 | 3765.4462 | 3741.5253 | 633 | [6 empty] | 0 | 633 | -790.0311 | [13 empty] | 40098.1097 | 59.962 | 3759.2498 | 350 | 223.0157 | 16 | 388 | 10 | 0 | -103 | 7756.08 | 30.3986
| 40098.1097 | 59.961 | 3758.041 |  |  |  | 31.2012 | 28.7591 |  | 0 | 3794.7685 | 3773.2749 | 3774.243 | 3765.4462 | 3741.6012 | 633 | [6 empty] | 0 | 633 | -780.2611 | [13 empty] | 40098.1097 | 59.961 | 3758.041 | 350 | 223.0157 | 16 | 388.5 | 10 | 0 | -103 | 7756.41 | 31.2012
| 40098.1097 | 59.961 | 3760.9648 |  |  |  | 31.2012 | 29.6138 |  | 0 | 3795.6233 | 3773.2361 | 3774.3104 | 3765.4462 | 3741.6767 | 633 | [6 empty] | 0 | 633 | -780.2611 | [13 empty] | 40098.1097 | 59.961 | 3760.9648 | 350 | 223.0157 | 16 | 389 | 10 | 0 | -103 | 7756.74 | 31.2012
| 40098.1097 | 59.96 | 3762.0222 |  |  |  | 32.0007 | 30.4492 |  | 0 | 3796.4587 | 3773.2008 | 3774.3801 | 3765.4462 | 3741.7516 | 633 | [6 empty] | 0 | 633 | -770.7656 | [13 empty] | 40098.1097 | 59.96 | 3762.0222 | 350 | 223.0157 | 16 | 389.5 | 10 | 0 | -103 | 7757.07 | 32.0007
| 40098.1097 | 59.963 | 3763.8223 |  |  |  | 29.599 | 30.1517 |  | 0 | 3796.1611 | 3773.1714 | 3774.4484 | 3765.4462 | 3741.8262 | 633 | [6 empty] | 0 | 633 | -800.0104 | [13 empty] | 40098.1097 | 59.963 | 3763.8223 | 350 | 223.0157 | 16 | 390 | 10 | 0 | -103 | 7757.4 | 29.599
| 40098.1098 | 59.959 | 3763.1001 |  |  |  | 32.8003 | 31.0787 |  | 0 | 3797.0881 | 3773.14 | 3774.5191 | 3765.4462 | 3741.9002 | 633 | [6 empty] | 0 | 633 | -761.4983 | [13 empty] | 40098.1098 | 59.959 | 3763.1001 | 350 | 223.0157 | 16 | 390.5 | 10 | 0 | -103 | 7757.73 | 32.8003
| 40098.1098 | 59.956 | 3763.8582 |  |  |  | 35.199 | 32.5208 |  | 0 | 3798.5302 | 3773.1111 | 3774.5939 | 3765.4462 | 3741.9738 | 633 | [6 empty] | 0 | 633 | -734.9872 | [13 empty] | 40098.1098 | 59.956 | 3763.8582 | 350 | 223.0157 | 16 | 391 | 10 | 0 | -103 | 7758.06 | 35.199
| 40098.1098 | 59.951 | 3764.1577 |  |  |  | 39.1998 | 34.8584 |  | 0 | 3800.8679 | 3773.0833 | 3774.6755 | 3765.4462 | 3742.0469 | 633 | [6 empty] | 0 | 633 | -694.6501 | [13 empty] | 40098.1098 | 59.951 | 3764.1577 | 350 | 223.0157 | 16 | 391.5 | 10 | 0 | -103 | 7758.39 | 39.1998
| 40098.1098 | 59.953 | 3766.1267 |  |  |  | 37.6007 | 35.8182 |  | 0 | 3801.8277 | 3773.0617 | 3774.7596 | 3765.4462 | 3742.1196 | 633 | [6 empty] | 0 | 633 | -710.2296 | [13 empty] | 40098.1098 | 59.953 | 3766.1267 | 350 | 223.0157 | 16 | 392 | 10 | 0 | -103 | 7758.72 | 37.6007
| 40098.1099 | 59.954 | 3768.3389 |  |  |  | 36.8011 | 36.1623 |  | 0 | 3802.1717 | 3773.0471 | 3774.8442 | 3765.4462 | 3742.1918 | 633 | [6 empty] | 0 | 633 | -718.2843 | [13 empty] | 40098.1099 | 59.954 | 3768.3389 | 350 | 223.0157 | 16 | 392.5 | 10 | 0 | -103 | 7759.05 | 36.8011
| 40098.1099 | 59.957 | 3767.9722 |  |  |  | 34.3994 | 35.5453 |  | 0 | 3801.5547 | 3773.0315 | 3774.9264 | 3765.4462 | 3742.2636 | 633 | [6 empty] | 0 | 633 | -743.6168 | [13 empty] | 40098.1099 | 59.957 | 3767.9722 | 350 | 223.0157 | 16 | 393 | 10 | 0 | -103 | 7759.38 | 34.3994
| 40098.1099 | 59.956 | 3767.4375 |  |  |  | 35.199 | 35.4241 |  | 0 | 3801.4335 | 3773.0144 | 3775.0077 | 3765.4462 | 3742.3349 | 633 | [6 empty] | 0 | 633 | -734.9872 | [13 empty] | 40098.1099 | 59.956 | 3767.4375 | 350 | 223.0157 | 16 | 393.5 | 10 | 0 | -103 | 7759.71 | 35.199
| 40098.1099 | 59.961 | 3765.6064 |  |  |  | 31.2012 | 33.9461 |  | 0 | 3799.9555 | 3772.9917 | 3775.084 | 3765.4462 | 3742.4058 | 633 | [6 empty] | 0 | 633 | -780.2611 | [13 empty] | 40098.1099 | 59.961 | 3765.6064 | 350 | 223.0157 | 16 | 394 | 10 | 0 | -103 | 7760.04 | 31.2012
| 40098.11 | 59.963 | 3762.688 |  |  |  | 29.599 | 32.4246 |  | 0 | 3798.434 | 3772.9603 | 3775.1552 | 3765.4462 | 3742.4763 | 633 | [6 empty] | 0 | 633 | -800.0104 | [13 empty] | 40098.11 | 59.963 | 3762.688 | 350 | 223.0157 | 16 | 394.5 | 10 | 0 | -103 | 7760.37 | 29.599
| 40098.11 | 59.961 | 3761.5703 |  |  |  | 31.2012 | 31.9964 |  | 0 | 3798.0058 | 3772.9257 | 3775.2246 | 3765.4462 | 3742.5463 | 633 | [6 empty] | 0 | 633 | -780.2611 | [13 empty] | 40098.11 | 59.961 | 3761.5703 | 350 | 223.0157 | 16 | 395 | 10 | 0 | -103 | 7760.7 | 31.2012
| 40098.11 | 59.959 | 3761.9199 |  |  |  | 32.8003 | 32.2778 |  | 0 | 3798.2872 | 3772.8923 | 3775.2945 | 3765.4462 | 3742.6159 | 633 | [6 empty] | 0 | 633 | -761.4983 | [13 empty] | 40098.11 | 59.959 | 3761.9199 | 350 | 223.0157 | 16 | 395.5 | 10 | 0 | -103 | 7761.03 | 32.8003
| 40098.11 | 59.963 | 3759.627 |  |  |  | 29.599 | 31.3402 |  | 0 | 3797.3496 | 3772.8522 | 3775.3611 | 3765.4462 | 3742.6851 | 633 | [6 empty] | 0 | 633 | -800.0104 | [13 empty] | 40098.11 | 59.963 | 3759.627 | 350 | 223.0157 | 16 | 396 | 10 | 0 | -103 | 7761.36 | 29.599
| 40098.11 | 59.963 | 3758.522 |  |  |  | 29.599 | 30.7308 |  | 0 | 3796.7402 | 3772.8091 | 3775.4255 | 3765.4462 | 3742.7538 | 633 | [6 empty] | 0 | 633 | -800.0104 | [13 empty] | 40098.11 | 59.963 | 3758.522 | 350 | 223.0157 | 16 | 396.5 | 10 | 0 | -103 | 7761.69 | 29.599
| 40098.1101 | 59.965 | 3752.4287 |  |  |  | 27.9999 | 29.775 |  | 0 | 3795.7844 | 3772.7479 | 3775.4867 | 3765.4462 | 3742.8222 | 633 | [6 empty] | 0 | 633 | -820.7448 | [13 empty] | 40098.1101 | 59.965 | 3752.4287 | 350 | 223.0157 | 16 | 397 | 10 | 0 | -103 | 7762.02 | 27.9999
| 40098.1101 | 59.968 | 3750.1016 |  |  |  | 25.6012 | 28.3141 |  | 0 | 3794.3236 | 3772.6801 | 3775.5431 | 3765.4462 | 3742.8901 | 633 | [6 empty] | 0 | 633 | -853.9431 | [13 empty] | 40098.1101 | 59.968 | 3750.1016 | 350 | 223.0157 | 16 | 397.5 | 10 | 0 | -103 | 7762.35 | 25.6012
| 40098.1101 | 59.968 | 3753.8296 |  |  |  | 25.6012 | 27.3646 |  | 0 | 3793.3741 | 3772.6238 | 3775.5963 | 3765.4462 | 3742.9577 | 633 | [6 empty] | 0 | 633 | -853.9431 | [13 empty] | 40098.1101 | 59.968 | 3753.8296 | 350 | 223.0157 | 16 | 398 | 10 | 0 | -103 | 7762.68 | 25.6012
| 40098.1101 | 59.968 | 3753.5103 |  |  |  | 25.6012 | 26.7474 |  | 0 | 3792.7569 | 3772.5669 | 3775.6474 | 3765.4462 | 3743.0248 | 633 | [6 empty] | 0 | 633 | -853.9431 | [13 empty] | 40098.1101 | 59.968 | 3753.5103 | 350 | 223.0157 | 16 | 398.5 | 10 | 0 | -103 | 7763.01 | 25.6012
| 40098.1102 | 59.97 | 3753.5229 |  |  |  | 23.999 | 25.7855 |  | 0 | 3791.7949 | 3772.5104 | 3775.6953 | 3765.4462 | 3743.0915 | 633 | [6 empty] | 0 | 633 | -877.6551 | [13 empty] | 40098.1102 | 59.97 | 3753.5229 | 350 | 223.0157 | 16 | 399 | 10 | 0 | -103 | 7763.34 | 23.999
| 40098.1102 | 59.973 | 3752.7407 |  |  |  | 21.6003 | 24.3207 |  | 0 | 3790.3301 | 3772.4519 | 3775.7386 | 3765.4462 | 3743.1579 | 633 | [6 empty] | 0 | 633 | -915.7237 | [13 empty] | 40098.1102 | 59.973 | 3752.7407 | 350 | 223.0157 | 16 | 399.5 | 10 | 0 | -103 | 7763.67 | 21.6003
| 40098.1102 | 59.971 | 3753.1782 |  |  |  | 23.1995 | 23.9283 |  | 0 | 3789.9377 | 3772.3951 | 3775.7805 | 3765.4462 | 3743.2238 | 633 | [6 empty] | 0 | 633 | -889.988 | [13 empty] | 40098.1102 | 59.971 | 3753.1782 | 350 | 223.0157 | 16 | 400 | 10 | 0 | -103 | 7764 | 23.1995
| 40098.1102 | 59.965 | 3752.729 |  |  |  | 27.9999 | 25.3533 |  | 0 | 3791.3628 | 3772.3372 | 3775.8263 | 3765.4462 | 3743.2893 | 633 | [6 empty] | 0 | 633 | -820.7448 | [13 empty] | 40098.1102 | 59.965 | 3752.729 | 350 | 223.0157 | 16 | 400.5 | 10 | 0 | -103 | 7764.33 | 27.9999
| 40098.1103 | 59.967 | 3753.2905 |  |  |  | 26.4008 | 25.7199 |  | 0 | 3791.7294 | 3772.2814 | 3775.8729 | 3765.4462 | 3743.3545 | 633 | [6 empty] | 0 | 633 | -842.5825 | [13 empty] | 40098.1103 | 59.967 | 3753.2905 | 350 | 223.0157 | 16 | 401 | 10 | 0 | -103 | 7764.66 | 26.4008
| 40098.1103 | 59.967 | 3752.8716 |  |  |  | 26.4008 | 25.9582 |  | 0 | 3791.9677 | 3772.2246 | 3775.92 | 3765.4462 | 3743.4193 | 633 | [6 empty] | 0 | 633 | -842.5825 | [13 empty] | 40098.1103 | 59.967 | 3752.8716 | 350 | 223.0157 | 16 | 401.5 | 10 | 0 | -103 | 7764.99 | 26.4008
| 40098.1103 | 59.972 | 3752.3586 |  |  |  | 22.3999 | 24.7128 |  | 0 | 3790.7223 | 3772.1667 | 3775.9631 | 3765.4462 | 3743.4837 | 633 | [6 empty] | 0 | 633 | -902.6725 | [13 empty] | 40098.1103 | 59.972 | 3752.3586 | 350 | 223.0157 | 16 | 402 | 10 | 0 | -103 | 7765.32 | 22.3999
| 40098.1103 | 59.976 | 3749.3979 |  |  |  | 19.1986 | 22.7828 |  | 0 | 3788.7923 | 3772.1005 | 3776.0004 | 3765.4462 | 3743.5477 | 633 | [6 empty] | 0 | 633 | -957.2998 | [13 empty] | 40098.1103 | 59.976 | 3749.3979 | 350 | 223.0157 | 16 | 402.5 | 10 | 0 | -103 | 7765.65 | 19.1986
| 40098.1103 | 59.975 | 3747.4758 |  |  |  | 20.0012 | 21.8093 |  | 0 | 3787.8187 | 3772.0291 | 3776.0347 | 3765.4462 | 3743.6114 | 633 | [6 empty] | 0 | 633 | -942.9922 | [13 empty] | 40098.1103 | 59.975 | 3747.4758 | 350 | 223.0157 | 16 | 403 | 10 | 0 | -103 | 7765.98 | 20.0012
| 40098.1104 | 59.969 | 3740.3704 |  |  |  | 24.7986 | 22.8555 |  | 0 | 3788.865 | 3771.9376 | 3776.0718 | 3765.4462 | 3743.6747 | 633 | [6 empty] | 0 | 633 | -865.6593 | [13 empty] | 40098.1104 | 59.969 | 3740.3704 | 350 | 223.0157 | 16 | 403.5 | 10 | 0 | -103 | 7766.31 | 24.7986
| 40098.1104 | 59.973 | 3741.2852 |  |  |  | 21.6003 | 22.4162 |  | 0 | 3788.4257 | 3771.8493 | 3776.1074 | 3765.4462 | 3743.7376 | 633 | [6 empty] | 0 | 633 | -915.7237 | [13 empty] | 40098.1104 | 59.973 | 3741.2852 | 350 | 223.0157 | 16 | 404 | 10 | 0 | -103 | 7766.64 | 21.6003
| 40098.1104 | 59.974 | 3746.6509 |  |  |  | 20.8008 | 21.8508 |  | 0 | 3787.8603 | 3771.7769 | 3776.1412 | 3765.4462 | 3743.8002 | 633 | [6 empty] | 0 | 633 | -929.1579 | [13 empty] | 40098.1104 | 59.974 | 3746.6509 | 350 | 223.0157 | 16 | 404.5 | 10 | 0 | -103 | 7766.97 | 20.8008
| 40098.1104 | 59.978 | 3745.7383 |  |  |  | 17.5995 | 20.3628 |  | 0 | 3786.3723 | 3771.7023 | 3776.1705 | 3765.4462 | 3743.8624 | 633 | [6 empty] | 0 | 633 | -987.1409 | [13 empty] | 40098.1104 | 59.978 | 3745.7383 | 350 | 223.0157 | 16 | 405 | 10 | 0 | -103 | 7767.3 | 17.5995
| 40098.1105 | 59.981 | 3743.3506 |  |  |  | 15.2008 | 18.5561 |  | 0 | 3784.5656 | 3771.6213 | 3776.1945 | 3765.4462 | 3743.9242 | 633 | [6 empty] | 0 | 633 | -1035.5619 | [13 empty] | 40098.1105 | 59.981 | 3743.3506 | 350 | 223.0157 | 16 | 405.5 | 10 | 0 | -103 | 7767.63 | 15.2008
| 40098.1105 | 59.981 | 3741.6182 |  |  |  | 15.2008 | 17.3818 |  | 0 | 3783.3912 | 3771.5358 | 3776.215 | 3765.4462 | 3743.9857 | 633 | [6 empty] | 0 | 633 | -1035.5619 | [13 empty] | 40098.1105 | 59.981 | 3741.6182 | 350 | 223.0157 | 16 | 406 | 10 | 0 | -103 | 7767.96 | 15.2008
| 40098.1105 | 59.981 | 3740.3064 |  |  |  | 15.2008 | 16.6184 |  | 0 | 3782.6279 | 3771.4471 | 3776.2332 | 3765.4462 | 3744.0468 | 633 | [6 empty] | 0 | 633 | -1035.5619 | [13 empty] | 40098.1105 | 59.981 | 3740.3064 | 350 | 223.0157 | 16 | 406.5 | 10 | 0 | -103 | 7768.29 | 15.2008
| 40098.1105 | 59.982 | 3738.4844 |  |  |  | 14.4012 | 15.8424 |  | 0 | 3781.8519 | 3771.3537 | 3776.2491 | 3765.4462 | 3744.1076 | 633 | [6 empty] | 0 | 633 | -1052.7755 | [13 empty] | 40098.1105 | 59.982 | 3738.4844 | 350 | 223.0157 | 16 | 407 | 10 | 0 | -103 | 7768.62 | 14.4012
| 40098.1106 | 59.982 | 3738.9014 |  |  |  | 14.4012 | 15.338 |  | 0 | 3781.3475 | 3771.262 | 3776.2635 | 3765.4462 | 3744.1681 | 633 | [6 empty] | 0 | 633 | -1052.7755 | [13 empty] | 40098.1106 | 59.982 | 3738.9014 | 350 | 223.0157 | 16 | 407.5 | 10 | 0 | -103 | 7768.95 | 14.4012
| 40098.1106 | 59.984 | 3737.4036 |  |  |  | 12.7991 | 14.4494 |  | 0 | 3780.4588 | 3771.1667 | 3776.2753 | 3765.4462 | 3744.2282 | 633 | [6 empty] | 0 | 633 | -1089.0498 | [13 empty] | 40098.1106 | 59.984 | 3737.4036 | 350 | 223.0157 | 16 | 408 | 10 | 0 | -103 | 7769.28 | 12.7991
| 40098.1106 | 59.982 | 3737.2732 |  |  |  | 14.4012 | 14.4325 |  | 0 | 3780.442 | 3771.0714 | 3776.287 | 3765.4462 | 3744.288 | 633 | [6 empty] | 0 | 633 | -1052.7755 | [13 empty] | 40098.1106 | 59.982 | 3737.2732 | 350 | 223.0157 | 16 | 408.5 | 10 | 0 | -103 | 7769.61 | 14.4012
| 40098.1106 | 59.981 | 3736.3083 |  |  |  | 15.2008 | 14.7014 |  | 0 | 3780.7109 | 3770.9741 | 3776.2994 | 3765.4462 | 3744.3474 | 633 | [6 empty] | 0 | 633 | -1035.5619 | [13 empty] | 40098.1106 | 59.981 | 3736.3083 | 350 | 223.0157 | 16 | 409 | 10 | 0 | -103 | 7769.94 | 15.2008
| 40098.1106 | 59.979 | 3736.272 |  |  |  | 16.7999 | 15.4359 |  | 0 | 3781.4453 | 3770.8771 | 3776.3138 | 3765.4462 | 3744.4065 | 633 | [6 empty] | 0 | 633 | -1002.7702 | [13 empty] | 40098.1106 | 59.979 | 3736.272 | 350 | 223.0157 | 16 | 409.5 | 10 | 0 | -103 | 7770.27 | 16.7999
| 40098.1107 | 59.98 | 3735.4482 |  |  |  | 16.0004 | 15.6335 |  | 0 | 3781.6429 | 3770.7784 | 3776.3286 | 3765.4462 | 3744.4653 | 633 | [6 empty] | 0 | 633 | -1018.9023 | [13 empty] | 40098.1107 | 59.98 | 3735.4482 | 350 | 223.0157 | 16 | 410 | 10 | 0 | -103 | 7770.6 | 16.0004
| 40098.1107 | 59.978 | 3735.6497 |  |  |  | 17.5995 | 16.3216 |  | 0 | 3782.331 | 3770.6809 | 3776.3453 | 3765.4462 | 3744.5237 | 633 | [6 empty] | 0 | 633 | -987.1409 | [13 empty] | 40098.1107 | 59.978 | 3735.6497 | 350 | 223.0157 | 16 | 410.5 | 10 | 0 | -103 | 7770.93 | 17.5995
| 40098.1107 | 59.978 | 3737.5405 |  |  |  | 17.5995 | 16.7688 |  | 0 | 3782.7783 | 3770.5891 | 3776.3631 | 3765.4462 | 3744.5818 | 633 | [6 empty] | 0 | 633 | -987.1409 | [13 empty] | 40098.1107 | 59.978 | 3737.5405 | 350 | 223.0157 | 16 | 411 | 10 | 0 | -103 | 7771.26 | 17.5995
| 40098.1107 | 59.98 | 3738.012 |  |  |  | 16.0004 | 16.4999 |  | 0 | 3782.5093 | 3770.4991 | 3776.3801 | 3765.4462 | 3744.6396 | 633 | [6 empty] | 0 | 633 | -1018.9023 | [13 empty] | 40098.1107 | 59.98 | 3738.012 | 350 | 223.0157 | 16 | 411.5 | 10 | 0 | -103 | 7771.59 | 16.0004
| 40098.1108 | 59.981 | 3736.7476 |  |  |  | 15.2008 | 16.0452 |  | 0 | 3782.0546 | 3770.4061 | 3776.3957 | 3765.4462 | 3744.6971 | 633 | [6 empty] | 0 | 633 | -1035.5619 | [13 empty] | 40098.1108 | 59.981 | 3736.7476 | 350 | 223.0157 | 16 | 412 | 10 | 0 | -103 | 7771.92 | 15.2008
| 40098.1108 | 59.98 | 3736.6931 |  |  |  | 16.0004 | 16.0295 |  | 0 | 3782.039 | 3770.3135 | 3776.4112 | 3765.4462 | 3744.7543 | 633 | [6 empty] | 0 | 633 | -1018.9023 | [13 empty] | 40098.1108 | 59.98 | 3736.6931 | 350 | 223.0157 | 16 | 412.5 | 10 | 0 | -103 | 7772.25 | 16.0004
| 40098.1108 | 59.978 | 3736.0674 |  |  |  | 17.5995 | 16.579 |  | 0 | 3782.5884 | 3770.2197 | 3776.4282 | 3765.4462 | 3744.8111 | 633 | [6 empty] | 0 | 633 | -987.1409 | [13 empty] | 40098.1108 | 59.978 | 3736.0674 | 350 | 223.0157 | 16 | 413 | 10 | 0 | -103 | 7772.58 | 17.5995
| 40098.1108 | 59.976 | 3736.0942 |  |  |  | 19.1986 | 17.4959 |  | 0 | 3783.5053 | 3770.1264 | 3776.4475 | 3765.4462 | 3744.8676 | 633 | [6 empty] | 0 | 633 | -957.2998 | [13 empty] | 40098.1108 | 59.976 | 3736.0942 | 350 | 223.0157 | 16 | 413.5 | 10 | 0 | -103 | 7772.91 | 19.1986
| 40098.1109 | 59.972 | 3736.575 |  |  |  | 22.3999 | 19.2123 |  | 0 | 3785.2217 | 3770.035 | 3776.4714 | 3765.4462 | 3744.9239 | 633 | [6 empty] | 0 | 633 | -902.6725 | [13 empty] | 40098.1109 | 59.972 | 3736.575 | 350 | 223.0157 | 16 | 414 | 10 | 0 | -103 | 7773.24 | 22.3999
| 40098.1109 | 59.971 | 3738.571 |  |  |  | 23.1995 | 20.6078 |  | 0 | 3786.6172 | 3769.9495 | 3776.499 | 3765.4462 | 3744.9798 | 633 | [6 empty] | 0 | 633 | -889.988 | [13 empty] | 40098.1109 | 59.971 | 3738.571 | 350 | 223.0157 | 16 | 414.5 | 10 | 0 | -103 | 7773.57 | 23.1995
| 40098.1109 | 59.969 | 3738.8748 |  |  |  | 24.7986 | 22.0746 |  | 0 | 3788.084 | 3769.8653 | 3776.5304 | 3765.4462 | 3745.0354 | 633 | [6 empty] | 0 | 633 | -865.6593 | [13 empty] | 40098.1109 | 59.969 | 3738.8748 | 350 | 223.0157 | 16 | 415 | 10 | 0 | -103 | 7773.9 | 24.7986
| 40098.1109 | 59.974 | 3738.9346 |  |  |  | 20.8008 | 21.6287 |  | 0 | 3787.6382 | 3769.7817 | 3776.5604 | 3765.4462 | 3745.0907 | 633 | [6 empty] | 0 | 633 | -929.1579 | [13 empty] | 40098.1109 | 59.974 | 3738.9346 | 350 | 223.0157 | 16 | 415.5 | 10 | 0 | -103 | 7774.23 | 20.8008
| 40098.1109 | 59.975 | 3738.647 |  |  |  | 20.0012 | 21.0591 |  | 0 | 3787.0686 | 3769.6978 | 3776.5887 | 3765.4462 | 3745.1457 | 633 | [6 empty] | 0 | 633 | -942.9922 | [13 empty] | 40098.1109 | 59.975 | 3738.647 | 350 | 223.0157 | 16 | 416 | 10 | 0 | -103 | 7774.56 | 20.0012
| 40098.111 | 59.976 | 3737.6841 |  |  |  | 19.1986 | 20.4079 |  | 0 | 3786.4174 | 3769.6117 | 3776.6151 | 3765.4462 | 3745.2004 | 633 | [6 empty] | 0 | 633 | -957.2998 | [13 empty] | 40098.111 | 59.976 | 3737.6841 | 350 | 223.0157 | 16 | 416.5 | 10 | 0 | -103 | 7774.89 | 19.1986
| 40098.111 | 59.972 | 3737.3821 |  |  |  | 22.3999 | 21.1051 |  | 0 | 3787.1146 | 3769.5253 | 3776.6433 | 3765.4462 | 3745.2549 | 633 | [6 empty] | 0 | 633 | -902.6725 | [13 empty] | 40098.111 | 59.972 | 3737.3821 | 350 | 223.0157 | 16 | 417 | 10 | 0 | -103 | 7775.22 | 22.3999
| 40098.111 | 59.969 | 3737.8921 |  |  |  | 24.7986 | 22.3978 |  | 0 | 3788.4073 | 3769.4407 | 3776.6747 | 3765.4462 | 3745.309 | 633 | [6 empty] | 0 | 633 | -865.6593 | [13 empty] | 40098.111 | 59.969 | 3737.8921 | 350 | 223.0157 | 16 | 417.5 | 10 | 0 | -103 | 7775.55 | 24.7986
| 40098.111 | 59.971 | 3740.0168 |  |  |  | 23.1995 | 22.6784 |  | 0 | 3788.6879 | 3769.3623 | 3776.7068 | 3765.4462 | 3745.3628 | 633 | [6 empty] | 0 | 633 | -889.988 | [13 empty] | 40098.111 | 59.971 | 3740.0168 | 350 | 223.0157 | 16 | 418 | 10 | 0 | -103 | 7775.88 | 23.1995
| 40098.1111 | 59.974 | 3740.3289 |  |  |  | 20.8008 | 22.0212 |  | 0 | 3788.0307 | 3769.285 | 3776.7369 | 3765.4462 | 3745.4164 | 633 | [6 empty] | 0 | 633 | -929.1579 | [13 empty] | 40098.1111 | 59.974 | 3740.3289 | 350 | 223.0157 | 16 | 418.5 | 10 | 0 | -103 | 7776.21 | 20.8008
| 40098.1111 | 59.972 | 3742.0527 |  |  |  | 22.3999 | 22.1538 |  | 0 | 3788.1632 | 3769.2128 | 3776.7672 | 3765.4462 | 3745.4697 | 633 | [6 empty] | 0 | 633 | -902.6725 | [13 empty] | 40098.1111 | 59.972 | 3742.0527 | 350 | 223.0157 | 16 | 419 | 10 | 0 | -103 | 7776.54 | 22.3999
| 40098.1111 | 59.972 | 3742.4238 |  |  |  | 22.3999 | 22.2399 |  | 0 | 3788.2494 | 3769.1419 | 3776.7976 | 3765.4462 | 3745.5227 | 633 | [6 empty] | 0 | 633 | -902.6725 | [13 empty] | 40098.1111 | 59.972 | 3742.4238 | 350 | 223.0157 | 16 | 419.5 | 10 | 0 | -103 | 7776.87 | 22.3999
| 40098.1111 | 59.972 | 3742.5244 |  |  |  | 22.3999 | 22.2959 |  | 0 | 3788.3054 | 3769.0717 | 3776.8279 | 3765.4462 | 3745.5754 | 633 | [6 empty] | 0 | 633 | -902.6725 | [13 empty] | 40098.1111 | 59.972 | 3742.5244 | 350 | 223.0157 | 16 | 420 | 10 | 0 | -103 | 7777.2 | 22.3999
| 40098.1112 | 59.977 | 3742.2451 |  |  |  | 18.399 | 20.932 |  | 0 | 3786.9415 | 3769.0011 | 3776.8546 | 3765.4462 | 3745.6278 | 633 | [6 empty] | 0 | 633 | -971.9914 | [13 empty] | 40098.1112 | 59.977 | 3742.2451 | 350 | 223.0157 | 16 | 420.5 | 10 | 0 | -103 | 7777.53 | 18.399
| 40098.1112 | 59.982 | 3741.7231 |  |  |  | 14.4012 | 18.6462 |  | 0 | 3784.6557 | 3768.9295 | 3776.875 | 3765.4462 | 3745.6799 | 633 | [6 empty] | 0 | 633 | -1052.7755 | [13 empty] | 40098.1112 | 59.982 | 3741.7231 | 350 | 223.0157 | 16 | 421 | 10 | 0 | -103 | 7777.86 | 14.4012
| 40098.1112 | 59.978 | 3740.0854 |  |  |  | 17.5995 | 18.2799 |  | 0 | 3784.2893 | 3768.854 | 3776.8944 | 3765.4462 | 3745.7318 | 633 | [6 empty] | 0 | 633 | -987.1409 | [13 empty] | 40098.1112 | 59.978 | 3740.0854 | 350 | 223.0157 | 16 | 421.5 | 10 | 0 | -103 | 7778.19 | 17.5995
| 40098.1112 | 59.976 | 3740.6292 |  |  |  | 19.1986 | 18.6014 |  | 0 | 3784.6109 | 3768.7803 | 3776.9146 | 3765.4462 | 3745.7834 | 633 | [6 empty] | 0 | 633 | -957.2998 | [13 empty] | 40098.1112 | 59.976 | 3740.6292 | 350 | 223.0157 | 16 | 422 | 10 | 0 | -103 | 7778.52 | 19.1986
| 40098.1112 | 59.973 | 3739.9644 |  |  |  | 21.6003 | 19.6511 |  | 0 | 3785.6605 | 3768.7053 | 3776.9374 | 3765.4462 | 3745.8348 | 633 | [6 empty] | 0 | 633 | -915.7237 | [13 empty] | 40098.1112 | 59.973 | 3739.9644 | 350 | 223.0157 | 16 | 422.5 | 10 | 0 | -103 | 7778.85 | 21.6003
| 40098.1113 | 59.974 | 3740.7751 |  |  |  | 20.8008 | 20.0535 |  | 0 | 3786.0629 | 3768.6327 | 3776.9611 | 3765.4462 | 3745.8858 | 633 | [6 empty] | 0 | 633 | -929.1579 | [13 empty] | 40098.1113 | 59.974 | 3740.7751 | 350 | 223.0157 | 16 | 423 | 10 | 0 | -103 | 7779.18 | 20.8008
| 40098.1113 | 59.977 | 3742.8325 |  |  |  | 18.399 | 19.4744 |  | 0 | 3785.4839 | 3768.5659 | 3776.9831 | 3765.4462 | 3745.9367 | 633 | [6 empty] | 0 | 633 | -971.9914 | [13 empty] | 40098.1113 | 59.977 | 3742.8325 | 350 | 223.0157 | 16 | 423.5 | 10 | 0 | -103 | 7779.51 | 18.399
| 40098.1113 | 59.977 | 3741.2678 |  |  |  | 18.399 | 19.098 |  | 0 | 3785.1075 | 3768.4953 | 3777.0041 | 3765.4462 | 3745.9872 | 633 | [6 empty] | 0 | 633 | -971.9914 | [13 empty] | 40098.1113 | 59.977 | 3741.2678 | 350 | 223.0157 | 16 | 424 | 10 | 0 | -103 | 7779.84 | 18.399
| 40098.1113 | 59.978 | 3739.7761 |  |  |  | 17.5995 | 18.5735 |  | 0 | 3784.583 | 3768.4213 | 3777.0237 | 3765.4462 | 3746.0375 | 633 | [6 empty] | 0 | 633 | -987.1409 | [13 empty] | 40098.1113 | 59.978 | 3739.7761 | 350 | 223.0157 | 16 | 424.5 | 10 | 0 | -103 | 7780.17 | 17.5995
| 40098.1114 | 59.979 | 3738.9658 |  |  |  | 16.7999 | 17.9528 |  | 0 | 3783.9622 | 3768.3456 | 3777.0415 | 3765.4462 | 3746.0875 | 633 | [6 empty] | 0 | 633 | -1002.7702 | [13 empty] | 40098.1114 | 59.979 | 3738.9658 | 350 | 223.0157 | 16 | 425 | 10 | 0 | -103 | 7780.5 | 16.7999
| 40098.1114 | 59.981 | 3738.7061 |  |  |  | 15.2008 | 16.9896 |  | 0 | 3782.999 | 3768.2696 | 3777.0568 | 3765.4462 | 3746.1373 | 633 | [6 empty] | 0 | 633 | -1035.5619 | [13 empty] | 40098.1114 | 59.981 | 3738.7061 | 350 | 223.0157 | 16 | 425.5 | 10 | 0 | -103 | 7780.83 | 15.2008
| 40098.1114 | 59.977 | 3738.8787 |  |  |  | 18.399 | 17.4829 |  | 0 | 3783.4923 | 3768.1944 | 3777.0732 | 3765.4462 | 3746.1868 | 633 | [6 empty] | 0 | 633 | -971.9914 | [13 empty] | 40098.1114 | 59.977 | 3738.8787 | 350 | 223.0157 | 16 | 426 | 10 | 0 | -103 | 7781.16 | 18.399
| 40098.1114 | 59.974 | 3739.8596 |  |  |  | 20.8008 | 18.6442 |  | 0 | 3784.6536 | 3768.1222 | 3777.0926 | 3765.4462 | 3746.236 | 633 | [6 empty] | 0 | 633 | -929.1579 | [13 empty] | 40098.1114 | 59.974 | 3739.8596 | 350 | 223.0157 | 16 | 426.5 | 10 | 0 | -103 | 7781.49 | 20.8008
| 40098.1115 | 59.971 | 3738.1016 |  |  |  | 23.1995 | 20.2385 |  | 0 | 3786.248 | 3768.0458 | 3777.1159 | 3765.4462 | 3746.285 | 633 | [6 empty] | 0 | 633 | -889.988 | [13 empty] | 40098.1115 | 59.971 | 3738.1016 | 350 | 223.0157 | 16 | 427 | 10 | 0 | -103 | 7781.82 | 23.1995
| 40098.1115 | 59.971 | 3738.5579 |  |  |  | 23.1995 | 21.2748 |  | 0 | 3787.2843 | 3767.9709 | 3777.1417 | 3765.4462 | 3746.3338 | 633 | [6 empty] | 0 | 633 | -889.988 | [13 empty] | 40098.1115 | 59.971 | 3738.5579 | 350 | 223.0157 | 16 | 427.5 | 10 | 0 | -103 | 7782.15 | 23.1995
| 40098.1115 | 59.971 | 3743.5068 |  |  |  | 23.1995 | 21.9485 |  | 0 | 3787.9579 | 3767.909 | 3777.1691 | 3765.4462 | 3746.3823 | 633 | [6 empty] | 0 | 633 | -889.988 | [13 empty] | 40098.1115 | 59.971 | 3743.5068 | 350 | 223.0157 | 16 | 428 | 10 | 0 | -103 | 7782.48 | 23.1995
| 40098.1115 | 59.972 | 3743.4187 |  |  |  | 22.3999 | 22.1065 |  | 0 | 3788.1159 | 3767.8471 | 3777.1967 | 3765.4462 | 3746.4306 | 633 | [6 empty] | 0 | 633 | -902.6725 | [13 empty] | 40098.1115 | 59.972 | 3743.4187 | 350 | 223.0157 | 16 | 428.5 | 10 | 0 | -103 | 7782.81 | 22.3999
| 40098.1116 | 59.968 | 3745.2507 |  |  |  | 25.6012 | 23.3296 |  | 0 | 3789.3391 | 3767.7902 | 3777.2273 | 3765.4462 | 3746.4786 | 633 | [6 empty] | 0 | 633 | -853.9431 | [13 empty] | 40098.1116 | 59.968 | 3745.2507 | 350 | 223.0157 | 16 | 429 | 10 | 0 | -103 | 7783.14 | 25.6012
| 40098.1116 | 59.966 | 3745.7441 |  |  |  | 27.2003 | 24.6844 |  | 0 | 3790.6938 | 3767.7348 | 3777.2611 | 3765.4462 | 3746.5264 | 633 | [6 empty] | 0 | 633 | -831.5203 | [13 empty] | 40098.1116 | 59.966 | 3745.7441 | 350 | 223.0157 | 16 | 429.5 | 10 | 0 | -103 | 7783.47 | 27.2003
| 40098.1116 | 59.966 | 3747.3396 |  |  |  | 27.2003 | 25.5649 |  | 0 | 3791.5744 | 3767.6837 | 3777.297 | 3765.4462 | 3746.5739 | 633 | [6 empty] | 0 | 633 | -831.5203 | [13 empty] | 40098.1116 | 59.966 | 3747.3396 | 350 | 223.0157 | 16 | 430 | 10 | 0 | -103 | 7783.8 | 27.2003
| 40098.1116 | 59.971 | 3750.7002 |  |  |  | 23.1995 | 24.737 |  | 0 | 3790.7465 | 3767.6413 | 3777.3306 | 3765.4462 | 3746.6212 | 633 | [6 empty] | 0 | 633 | -889.988 | [13 empty] | 40098.1116 | 59.971 | 3750.7002 | 350 | 223.0157 | 16 | 430.5 | 10 | 0 | -103 | 7784.13 | 23.1995
| 40098.1116 | 59.973 | 3749.75 |  |  |  | 21.6003 | 23.6392 |  | 0 | 3789.6486 | 3767.5966 | 3777.3613 | 3765.4462 | 3746.6683 | 633 | [6 empty] | 0 | 633 | -915.7237 | [13 empty] | 40098.1116 | 59.973 | 3749.75 | 350 | 223.0157 | 16 | 431 | 10 | 0 | -103 | 7784.46 | 21.6003
| 40098.1117 | 59.972 | 3746.2166 |  |  |  | 22.3999 | 23.2054 |  | 0 | 3789.2149 | 3767.5435 | 3777.3908 | 3765.4462 | 3746.7151 | 633 | [6 empty] | 0 | 633 | -902.6725 | [13 empty] | 40098.1117 | 59.972 | 3746.2166 | 350 | 223.0157 | 16 | 431.5 | 10 | 0 | -103 | 7784.79 | 22.3999
| 40098.1117 | 59.969 | 3744.6826 |  |  |  | 24.7986 | 23.763 |  | 0 | 3789.7725 | 3767.4867 | 3777.4216 | 3765.4462 | 3746.7617 | 633 | [6 empty] | 0 | 633 | -865.6593 | [13 empty] | 40098.1117 | 59.969 | 3744.6826 | 350 | 223.0157 | 16 | 432 | 10 | 0 | -103 | 7785.12 | 24.7986
| 40098.1117 | 59.972 | 3743.7451 |  |  |  | 22.3999 | 23.2859 |  | 0 | 3789.2954 | 3767.428 | 3777.4509 | 3765.4462 | 3746.808 | 633 | [6 empty] | 0 | 633 | -902.6725 | [13 empty] | 40098.1117 | 59.972 | 3743.7451 | 350 | 223.0157 | 16 | 432.5 | 10 | 0 | -103 | 7785.45 | 22.3999
| 40098.1117 | 59.974 | 3743.1489 |  |  |  | 20.8008 | 22.4161 |  | 0 | 3788.4256 | 3767.368 | 3777.478 | 3765.4462 | 3746.8542 | 633 | [6 empty] | 0 | 633 | -929.1579 | [13 empty] | 40098.1117 | 59.974 | 3743.1489 | 350 | 223.0157 | 16 | 433 | 10 | 0 | -103 | 7785.78 | 20.8008
| 40098.1118 | 59.973 | 3740.2986 |  |  |  | 21.6003 | 22.1306 |  | 0 | 3788.1401 | 3767.3013 | 3777.5043 | 3765.4462 | 3746.9001 | 633 | [6 empty] | 0 | 633 | -915.7237 | [13 empty] | 40098.1118 | 59.973 | 3740.2986 | 350 | 223.0157 | 16 | 433.5 | 10 | 0 | -103 | 7786.11 | 21.6003
| 40098.1118 | 59.97 | 3739.4526 |  |  |  | 23.999 | 22.7846 |  | 0 | 3788.794 | 3767.2329 | 3777.532 | 3765.4462 | 3746.9458 | 633 | [6 empty] | 0 | 633 | -877.6551 | [13 empty] | 40098.1118 | 59.97 | 3739.4526 | 350 | 223.0157 | 16 | 434 | 10 | 0 | -103 | 7786.44 | 23.999
| 40098.1118 | 59.971 | 3733.376 |  |  |  | 23.1995 | 22.9298 |  | 0 | 3788.9392 | 3767.1499 | 3777.56 | 3765.4462 | 3746.9912 | 633 | [6 empty] | 0 | 633 | -889.988 | [13 empty] | 40098.1118 | 59.971 | 3733.376 | 350 | 223.0157 | 16 | 434.5 | 10 | 0 | -103 | 7786.77 | 23.1995
| 40098.1118 | 59.974 | 3731.8296 |  |  |  | 20.8008 | 22.1846 |  | 0 | 3788.1941 | 3767.0636 | 3777.586 | 3765.4462 | 3747.0365 | 633 | [6 empty] | 0 | 633 | -929.1579 | [13 empty] | 40098.1118 | 59.974 | 3731.8296 | 350 | 223.0157 | 16 | 435 | 10 | 0 | -103 | 7787.1 | 20.8008
| 40098.1119 | 59.982 | 3737.5825 |  |  |  | 14.4012 | 19.4604 |  | 0 | 3785.4699 | 3766.9917 | 3777.6052 | 3765.4462 | 3747.0815 | 633 | [6 empty] | 0 | 633 | -1052.7755 | [13 empty] | 40098.1119 | 59.982 | 3737.5825 | 350 | 223.0157 | 16 | 435.5 | 10 | 0 | -103 | 7787.43 | 14.4012
| 40098.1119 | 59.985 | 3736.2295 |  |  |  | 11.9995 | 16.8491 |  | 0 | 3782.8586 | 3766.9168 | 3777.618 | 3765.4462 | 3747.1263 | 633 | [6 empty] | 0 | 633 | -1108.1038 | [13 empty] | 40098.1119 | 59.985 | 3736.2295 | 350 | 223.0157 | 16 | 436 | 10 | 0 | -103 | 7787.76 | 11.9995
| 40098.1119 | 59.985 | 3734.8967 |  |  |  | 11.9995 | 15.1518 |  | 0 | 3781.1612 | 3766.8391 | 3777.6266 | 3765.4462 | 3747.1708 | 633 | [6 empty] | 0 | 633 | -1108.1038 | [13 empty] | 40098.1119 | 59.985 | 3734.8967 | 350 | 223.0157 | 16 | 436.5 | 10 | 0 | -103 | 7788.09 | 11.9995
| 40098.1119 | 59.985 | 3733.4338 |  |  |  | 11.9995 | 14.0485 |  | 0 | 3780.0579 | 3766.7582 | 3777.6325 | 3765.4462 | 3747.2152 | 633 | [6 empty] | 0 | 633 | -1108.1038 | [13 empty] | 40098.1119 | 59.985 | 3733.4338 | 350 | 223.0157 | 16 | 437 | 10 | 0 | -103 | 7788.42 | 11.9995
| 40098.1119 | 59.987 | 3733.1152 |  |  |  | 10.4004 | 12.7716 |  | 0 | 3778.7811 | 3766.677 | 3777.6353 | 3765.4462 | 3747.2593 | 633 | [6 empty] | 0 | 633 | -1148.2845 | [13 empty] | 40098.1119 | 59.987 | 3733.1152 | 350 | 223.0157 | 16 | 437.5 | 10 | 0 | -103 | 7788.75 | 10.4004
| 40098.112 | 59.989 | 3730.5098 |  |  |  | 8.8013 | 11.382 |  | 0 | 3777.3915 | 3766.5898 | 3777.6347 | 3765.4462 | 3747.3033 | 633 | [6 empty] | 0 | 633 | -1191.4888 | [13 empty] | 40098.112 | 59.989 | 3730.5098 | 350 | 223.0157 | 16 | 438 | 10 | 0 | -103 | 7789.08 | 8.8013
| 40098.112 | 59.989 | 3729.1802 |  |  |  | 8.8013 | 10.4788 |  | 0 | 3776.4882 | 3766.4999 | 3777.6319 | 3765.4462 | 3747.347 | 633 | [6 empty] | 0 | 633 | -1191.4888 | [13 empty] | 40098.112 | 59.989 | 3729.1802 | 350 | 223.0157 | 16 | 438.5 | 10 | 0 | -103 | 7789.41 | 8.8013
| 40098.112 | 59.986 | 3725.4587 |  |  |  | 11.2 | 10.7312 |  | 0 | 3776.7406 | 3766.4015 | 3777.6298 | 3765.4462 | 3747.3905 | 633 | [6 empty] | 0 | 633 | -1127.8363 | [13 empty] | 40098.112 | 59.986 | 3725.4587 | 350 | 223.0157 | 16 | 439 | 10 | 0 | -103 | 7789.74 | 11.2
| 40098.112 | 59.987 | 3724.7847 |  |  |  | 10.4004 | 10.6154 |  | 0 | 3776.6248 | 3766.3019 | 3777.6274 | 3765.4462 | 3747.4338 | 633 | [6 empty] | 0 | 633 | -1148.2845 | [13 empty] | 40098.112 | 59.987 | 3724.7847 | 350 | 223.0157 | 16 | 439.5 | 10 | 0 | -103 | 7790.07 | 10.4004
| 40098.1121 | 59.99 | 3720.1079 |  |  |  | 7.9987 | 9.6995 |  | 0 | 3775.709 | 3766.1917 | 3777.6228 | 3765.4462 | 3747.4769 | 633 | [6 empty] | 0 | 633 | -1214.4224 | [13 empty] | 40098.1121 | 59.99 | 3720.1079 | 350 | 223.0157 | 16 | 440 | 10 | 0 | -103 | 7790.4 | 7.9987
| 40098.1121 | 59.994 | 3720.9382 |  |  |  | 4.8004 | 7.9848 |  | 0 | 3773.9943 | 3766.0839 | 3777.6142 | 3765.4462 | 3747.5198 | 633 | [6 empty] | 0 | 633 | -1315.3043 | [13 empty] | 40098.1121 | 59.994 | 3720.9382 | 350 | 223.0157 | 16 | 440.5 | 10 | 0 | -103 | 7790.73 | 4.8004
| 40098.1121 | 59.996 | 3725.6614 |  |  |  | 3.2013 | 6.3106 |  | 0 | 3772.32 | 3765.9879 | 3777.6016 | 3765.4462 | 3747.5624 | 633 | [6 empty] | 0 | 633 | -1372.3029 | [13 empty] | 40098.1121 | 59.996 | 3725.6614 | 350 | 223.0157 | 16 | 441 | 10 | 0 | -103 | 7791.06 | 3.2013
| 40098.1121 | 60.001 | 3725.6768 |  |  |  | -0.79956 | 3.822 |  | 0 | 3769.8315 | 3765.8924 | 3777.5832 | 3765.4462 | 3747.6049 | 633 | [6 empty] | 0 | 633 | -1539.1807 | [13 empty] | 40098.1121 | 60.001 | 3725.6768 | 350 | 223.0157 | 16 | 441.5 | 10 | 0 | -103 | 7791.39 | -0.79956
| 40098.1122 | 60.003 | 3727.7542 |  |  |  | -2.3987 | 1.6448 |  | 0 | 3767.6542 | 3765.8022 | 3777.5597 | 3765.4462 | 3747.6472 | 633 | [6 empty] | 0 | 633 | -1617.8139 | [13 empty] | 40098.1122 | 60.003 | 3727.7542 | 350 | 223.0157 | 16 | 442 | 10 | 0 | -103 | 7791.72 | -2.3987
| 40098.1122 | 60.004 | 3727.8247 |  |  |  | -3.2013 | -0.051339 |  | 0 | 3765.9581 | 3765.7126 | 3777.5324 | 3765.4462 | 3747.6893 | 633 | [6 empty] | 0 | 633 | -1660.3885 | [13 empty] | 40098.1122 | 60.004 | 3727.8247 | 350 | 223.0157 | 16 | 442.5 | 10 | 0 | -103 | 7792.05 | -3.2013
| 40098.1122 | 60.006 | 3727.6833 |  |  |  | -4.8004 | -1.7135 |  | 0 | 3764.2959 | 3765.6232 | 3777.5012 | 3765.4462 | 3747.7312 | 633 | [6 empty] | 0 | 633 | -1752.2634 | [13 empty] | 40098.1122 | 60.006 | 3727.6833 | 350 | 223.0157 | 16 | 443 | 10 | 0 | -103 | 7792.38 | -4.8004
| 40098.1122 | 60.012 | 3727.2314 |  |  |  | -9.6008 | -4.4741 |  | 0 | 3761.5354 | 3765.533 | 3777.4637 | 3765.4462 | 3747.7728 | 633 | [6 empty] | 0 | 633 | -2101.3015 | [13 empty] | 40098.1122 | 60.012 | 3727.2314 | 350 | 223.0157 | 16 | 443.5 | 10 | 0 | -103 | 7792.71 | -9.6008
| 40098.1122 | 60.014 | 3725.0122 |  |  |  | -11.2 | -6.8281 |  | 0 | 3759.1813 | 3765.4381 | 3777.4209 | 3765.4462 | 3747.8143 | 633 | [6 empty] | 0 | 633 | -2250.6438 | [13 empty] | 40098.1122 | 60.014 | 3725.0122 | 350 | 223.0157 | 16 | 444 | 10 | 0 | -103 | 7793.04 | -11.2
| 40098.1123 | 60.019 | 3726.4463 |  |  |  | -15.2008 | -9.7586 |  | 0 | 3756.2509 | 3765.347 | 3777.3715 | 3765.4462 | 3747.8556 | 633 | [6 empty] | 0 | 633 | -2737.3899 | [13 empty] | 40098.1123 | 60.019 | 3726.4463 | 350 | 223.0157 | 16 | 444.5 | 10 | 0 | -103 | 7793.37 | -15.2008
| 40098.1123 | 60.021 | 3726.0156 |  |  |  | -16.7999 | -12.223 |  | 0 | 3753.7864 | 3765.2554 | 3777.3165 | 3765.4462 | 3747.8967 | 633 | [6 empty] | 0 | 633 | -2996.4048 | [13 empty] | 40098.1123 | 60.021 | 3726.0156 | 350 | 223.0157 | 16 | 445 | 10 | 0 | -103 | 7793.7 | -16.7999
| 40098.1123 | 60.025 | 3719.123 |  |  |  | -20.0012 | -14.9454 |  | 0 | 3751.064 | 3765.1481 | 3777.2554 | 3765.4462 | 3747.9376 | 633 | [6 empty] | 0 | 633 | -3696.6312 | [13 empty] | 40098.1123 | 60.025 | 3719.123 | 350 | 223.0157 | 16 | 445.5 | 10 | 0 | -103 | 7794.03 | -20.0012
| 40098.1123 | 60.026 | 3716.3745 |  |  |  | -20.8008 | -16.9948 |  | 0 | 3749.0147 | 3765.0349 | 3777.1899 | 3765.4462 | 3747.9783 | 633 | [6 empty] | 0 | 633 | -3925.7644 | [13 empty] | 40098.1123 | 60.026 | 3716.3745 | 350 | 223.0157 | 16 | 446 | 10 | 0 | -103 | 7794.36 | -20.8008
| 40098.1124 | 60.027 | 3717.3325 |  |  |  | -21.6003 | -18.6067 |  | 0 | 3747.4027 | 3764.9245 | 3777.1209 | 3765.4462 | 3748.0189 | 633 | [6 empty] | 0 | 633 | -4185.1799 | [13 empty] | 40098.1124 | 60.027 | 3717.3325 | 350 | 223.0157 | 16 | 446.5 | 10 | 0 | -103 | 7794.69 | -21.6003
| 40098.1124 | 60.029 | 3717.5598 |  |  |  | -23.1995 | -20.2142 |  | 0 | 3745.7953 | 3764.8151 | 3777.0486 | 3765.4462 | 3748.0592 | 633 | [6 empty] | 0 | 633 | -4822.5278 | [13 empty] | 40098.1124 | 60.029 | 3717.5598 | 350 | 223.0157 | 16 | 447 | 10 | 0 | -103 | 7795.02 | -23.1995
| 40098.1124 | 60.029 | 3717.1421 |  |  |  | -23.1995 | -21.259 |  | 0 | 3744.7504 | 3764.7053 | 3776.9742 | 3765.4462 | 3748.0994 | 633 | [6 empty] | 0 | 633 | -4822.5278 | [13 empty] | 40098.1124 | 60.029 | 3717.1421 | 350 | 223.0157 | 16 | 447.5 | 10 | 0 | -103 | 7795.35 | -23.1995
| 40098.1124 | 60.037 | 3715.166 |  |  |  | -29.599 | -24.178 |  | 0 | 3741.8314 | 3764.5914 | 3776.8934 | 3765.4462 | 3748.1393 | 633 | [6 empty] | 0 | 633 | -12347.6627 | [13 empty] | 40098.1124 | 60.037 | 3715.166 | 350 | 223.0157 | 16 | 448 | 10 | 0 | -103 | 7795.68 | -29.599
| 40098.1125 | 60.036 | 3713.6318 |  |  |  | -28.7994 | -25.7955 |  | 0 | 3740.2139 | 3764.4745 | 3776.8093 | 3765.4462 | 3748.1791 | 633 | [6 empty] | 0 | 633 | -10333.13 | [13 empty] | 40098.1125 | 60.036 | 3713.6318 | 350 | 223.0157 | 16 | 448.5 | 10 | 0 | -103 | 7796.01 | -28.7994
| 40098.1125 | 60.037 | 3710.2834 |  |  |  | -29.599 | -27.1267 |  | 0 | 3738.8827 | 3764.3505 | 3776.7225 | 3765.4462 | 3748.2187 | 633 | [6 empty] | 0 | 633 | -12347.6627 | [13 empty] | 40098.1125 | 60.037 | 3710.2834 | 350 | 223.0157 | 16 | 449 | 10 | 0 | -103 | 7796.34 | -29.599
| 40098.1125 | 60.037 | 3710.1577 |  |  |  | -29.599 | -27.992 |  | 0 | 3738.0174 | 3764.2268 | 3776.6341 | 3765.4462 | 3748.2582 | 633 | [6 empty] | 0 | 633 | -12347.6627 | [13 empty] | 40098.1125 | 60.037 | 3710.1577 | 350 | 223.0157 | 16 | 449.5 | 10 | 0 | -103 | 7796.67 | -29.599
| 40098.1125 | 60.036 | 3699.3557 |  |  |  | -28.7994 | -28.2746 |  | 0 | 3737.7348 | 3764.079 | 3776.5455 | 3765.4462 | 3748.2974 | 633 | [6 empty] | 0 | 633 | -10333.13 | [13 empty] | 40098.1125 | 60.036 | 3699.3557 | 350 | 223.0157 | 16 | 450 | 10 | 0 | -103 | 7797 | -28.7994
| 40098.1125 | 60.041 | 3698.5911 |  |  |  | -32.8003 | -29.8586 |  | 0 | 3736.1508 | 3763.9301 | 3776.4537 | 3765.4462 | 3748.3365 | 633 | [6 empty] | 0 | 633 | -56273.7268 | [13 empty] | 40098.1125 | 60.041 | 3698.5911 | 350 | 223.0157 | 16 | 450.5 | 10 | 0 | -103 | 7797.33 | -32.8003
| 40098.1126 | 60.043 | 3704.5913 |  |  |  | -34.3994 | -31.4479 |  | 0 | 3734.5616 | 3763.7956 | 3776.3587 | 3765.4462 | 3748.3753 | 633 | [6 empty] | 0 | 633 | 72422.1067 | [13 empty] | 40098.1126 | 60.043 | 3704.5913 | 350 | 223.0157 | 16 | 451 | 10 | 0 | -103 | 7797.66 | -34.3994
| 40098.1126 | 60.044 | 3703.2754 |  |  |  | -35.199 | -32.7608 |  | 0 | 3733.2487 | 3763.6587 | 3776.2612 | 3765.4462 | 3748.4141 | 633 | [6 empty] | 0 | 633 | 33787.1524 | [13 empty] | 40098.1126 | 60.044 | 3703.2754 | 350 | 223.0157 | 16 | 451.5 | 10 | 0 | -103 | 7797.99 | -35.199
| 40098.1126 | 60.043 | 3702.4824 |  |  |  | -34.3994 | -33.3343 |  | 0 | 3732.6752 | 3763.5206 | 3776.1628 | 3765.4462 | 3748.4526 | 633 | [6 empty] | 0 | 633 | 72422.1067 | [13 empty] | 40098.1126 | 60.043 | 3702.4824 | 350 | 223.0157 | 16 | 452 | 10 | 0 | -103 | 7798.32 | -34.3994
| 40098.1126 | 60.046 | 3701.3164 |  |  |  | -36.8011 | -34.5477 |  | 0 | 3731.4618 | 3763.3805 | 3776.0621 | 3765.4462 | 3748.4909 | 633 | [6 empty] | 0 | 633 | 16330.3877 | [13 empty] | 40098.1126 | 60.046 | 3701.3164 | 350 | 223.0157 | 16 | 452.5 | 10 | 0 | -103 | 7798.65 | -36.8011
| 40098.1127 | 60.048 | 3700.8259 |  |  |  | -38.4003 | -35.8961 |  | 0 | 3730.1134 | 3763.2399 | 3775.9588 | 3765.4462 | 3748.5291 | 633 | [6 empty] | 0 | 633 | 10774.2652 | [13 empty] | 40098.1127 | 60.048 | 3700.8259 | 350 | 223.0157 | 16 | 453 | 10 | 0 | -103 | 7798.98 | -38.4003
| 40098.1127 | 60.046 | 3699.5286 |  |  |  | -36.8011 | -36.2129 |  | 0 | 3729.7966 | 3763.0971 | 3775.8553 | 3765.4462 | 3748.5671 | 633 | [6 empty] | 0 | 633 | 16330.3877 | [13 empty] | 40098.1127 | 60.046 | 3699.5286 | 350 | 223.0157 | 16 | 453.5 | 10 | 0 | -103 | 7799.31 | -36.8011
| 40098.1127 | 60.046 | 3699.7261 |  |  |  | -36.8011 | -36.4188 |  | 0 | 3729.5907 | 3762.9553 | 3775.7518 | 3765.4462 | 3748.605 | 633 | [6 empty] | 0 | 633 | 16330.3877 | [13 empty] | 40098.1127 | 60.046 | 3699.7261 | 350 | 223.0157 | 16 | 454 | 10 | 0 | -103 | 7799.64 | -36.8011
| 40098.1127 | 60.043 | 3690.0996 |  |  |  | -34.3994 | -35.712 |  | 0 | 3730.2975 | 3762.7927 | 3775.6504 | 3765.4462 | 3748.6427 | 633 | [6 empty] | 0 | 633 | 72422.1067 | [13 empty] | 40098.1127 | 60.043 | 3690.0996 | 350 | 223.0157 | 16 | 454.5 | 10 | 0 | -103 | 7799.97 | -34.3994
| 40098.1128 | 60.043 | 3690.4773 |  |  |  | -34.3994 | -35.2526 |  | 0 | 3730.7569 | 3762.6316 | 3775.5504 | 3765.4462 | 3748.6802 | 633 | [6 empty] | 0 | 633 | 72422.1067 | [13 empty] | 40098.1128 | 60.043 | 3690.4773 | 350 | 223.0157 | 16 | 455 | 10 | 0 | -103 | 7800.3 | -34.3994
| 40098.1128 | 60.044 | 3696.8645 |  |  |  | -35.199 | -35.2338 |  | 0 | 3730.7756 | 3762.4854 | 3775.4509 | 3765.4462 | 3748.7175 | 633 | [6 empty] | 0 | 633 | 33787.1524 | [13 empty] | 40098.1128 | 60.044 | 3696.8645 | 350 | 223.0157 | 16 | 455.5 | 10 | 0 | -103 | 7800.63 | -35.199
| 40098.1128 | 60.043 | 3696.8772 |  |  |  | -34.3994 | -34.9418 |  | 0 | 3731.0677 | 3762.34 | 3775.3525 | 3765.4462 | 3748.7547 | 633 | [6 empty] | 0 | 633 | 72422.1067 | [13 empty] | 40098.1128 | 60.043 | 3696.8772 | 350 | 223.0157 | 16 | 456 | 10 | 0 | -103 | 7800.96 | -34.3994
Note on L13: TC allowable range 0.050 to 1.000 with 1.0 turning filter off. Beginning Target slope should align with Actual slope.

## Graph 20 to 52s
60.0421

## Form 1 Summary Data
[6 empty] | Interconnection Performance | [9 empty] | Value A Data |  | BA Performance | [8 empty] | Value B |  | 12 to 24 second Average Period Evaluation | [11 empty] | Value B | 18 to 30 second Average Period Evaluation | [12 empty] | Value B | 20 to 40 second Average Period Evaluation | [12 empty] | Value B | 18 to 52 second Average Period Evaluation | [12 empty] | Value B | 20 to 52 second Average Period Evaluation
[18 empty] | JOU | Non- |  |  | Transferred | Contingent | [5 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent
Date | A Point | FPointA | A Value | t(0) Time | C Value | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias
| Time | Hz | Hz |  | Hz | 12 to 24 sec | 12 to 24 sec | 18 to 30 sec | 18 to 30 sec | 20 to 40 sec | 20 to 40 sec | 18 to 52 sec | 18 to 52 sec | 20 to 52 sec | 20 to 52 sec |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting
[6 empty] | Average | Average | Average | Average | Average | Average | Average | Average | Average | Average | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Adjusted | Unadjusted |  | Setting |  | EPFR
[6 empty] | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW | Hz | MW | MW | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW | Hz | MW | MW | MW | MW | MW | MW | MW | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | P.U. | P.U. | P.U. | MW | MW | MW | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | P.U. | P.U. | P.U. | MW | MW | MW | Hz | MW | MW | MW | MW | MW | MW | MW | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW | Hz | MW | MW | MW | MW | MW | MW | MW | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW
2009-10-12 02:27 | 40098.1024 | 60.039 | 60.0421 | 40098.1024 | 59.836 | 59.8826 | -397.1996 | 59.8844 | -401.67 | 59.8891 | -414.4045 | 59.8883 | -411.9963 | 59.8891 | -413.9515 | 60.0421 | 3645.7271 | 350 | 165.3359 | 0 | 229.25 | -4.2125 | 15 | -103 | 7651.305 | -43.389 | 59.8826 | 3770.653 | 335 | 212.1391 | 0.85714 | 235.5 | 11.7428 | 0 | 0.66639 | 0.97871 | 0.92302 | -103 | 7632 | 120.9512 | 59.8844 | 3779.0294 | 335 | 213.4637 | 1.4286 | 237 | 11.5571 | 0 | 0.71519 | 1.0566 | 0.92302 | -103 | 7632 | 119.0383 | 59.8893 | 3783.8625 | 335 | 213.0775 | 3.5455 | 238.5 | 11.0727 | 0 | 0.75492 | 1.1297 | 0.92302 | -103 | 7632 | 114.0486 | 59.8883 | 3787.2724 | 335 | 213.9682 | 6.0556 | 239.75 | 11.1667 | 0 | 0.73946 | 1.1505 | 0.92302 | -103 | 7632 | 115.0166 | 59.8891 | 3788.3545 | 335 | 165.3359 | 6.3529 | 240 | 11.0882 | 0 | 0.74696 | 1.1652 | 0.92302 | -103 | 7632 | 114.2087